## ANNEXURE IV
99.9751 |  | TRANSMISSION SYSTEM OUTAGE DATA
PERIOD : 2020-21
Sl. No. | Name of the Transmission Element | OUTAGE |  | RESTORATION |  | OUTAGE PERIOD | DURATION OF OUTAGE ATTRIBUTABLE TO | [5 empty] | Deemed Availability | Reason of Outage | MVA capacity for ICTs / Autos | Ckm and number of Sub-Conductor for lines | Time considered for availability (hrs) (365 X 24) | Element wise availbility (C19 - C7 - C8/60) / C19 | ( OH l x Cktkm l x NSC l ) ( OH t x MVA t x 2.5 ) | (THY x Ckt KM X NSC) (THY X MVA x 2.5)
|  | DATE | TIME | DATE | TIME |  | UTILITY ITSELF |  | OTHERS |  | System Constraints/Natural Calamities
|  | dd/mm/yy | hh:mm | dd/mm/yy | hh:mm | hh:mm | Hrs | Min | Hrs | Min | Hrs | Min
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
400KV LINES
1 | 400 kV Indravati - Indravati PG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.97 | 8760 | 100% | 0 | 69554.4
2 | 400kV Lapanga -IBTPS Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.491 | 8760 | 100% | 0 | 429082.32
3 | 400kV Lapanga -IBTPS Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.491 | 8760 | 100% | 0 | 429082.32
4 | 400kV Meramundali -New Duburi Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 96.6 | 8760 | 100% | 0 | 1692432
5 | 400kV Meramundali -New Duburi Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 96.6 | 8760 | 100% | 0 | 1692432
6 | 400kV Meramundali -Lapanga Ckt- I (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 199.25 | 8760 | 100% | 0 | 3490860
7 | 400kV Meramundali -Lapanga Ckt- II (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 199.25 | 8760 | 100% | 0 | 3490860
8 | 400kV Lapanga-Vedant Ckt- I (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17 | 8760 | 100% | 0 | 297840
9 | 400kV Lapanga-Vedant Ckt- II (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17 | 8760 | 100% | 0 | 297840
10 | 400kV Meramundali -Mendhasal Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 100.451 | 8760 | 100% | 0 | 1759901.52
11 | 400kV Meramundali -Mendhasal Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 100.451 | 8760 | 100% | 0 | 1759901.52
12 | 400 kV Meramundali - JSPL Ckt- I |  |  |  |  | 0.0375 | 0 | 53 | [7 empty] | 37.916 | 8760 | 99.99% | 66.9849 | 664288.32
|  | 2020-05-16 | 19:27 | 2020-05-16 | 20:21 | 0:54 | 0 | 53 | [5 empty] | Tripped
13 | 400 kV Meramundali - JSPL Ckt- II |  |  |  |  | 0.0375 | 0 | 53 | [7 empty] | 37.916 | 8760 | 99.99% | 66.9849 | 664288.32
|  | 2020-05-16 | 19:28 | 2020-05-16 | 20:21 | 0:54 | 0 | 53 | [5 empty] | Tripped
14 | 400kV Rengali - Kuchei PG-Kolaghat |  |  |  |  | 0 | 0 | 0 | [7 empty] | 241.5 | 8760 | 100% | 0 | 4231080
1196.886
220KV LINES
15 | 220kV Atri-Pandiabil Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 26.7 | 8760 | 100% | 0 | 233892
16 | 220kV Pandiabil-Samagara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.9 | 8760 | 100% | 0 | 402084
17 | 220kV Atri-Pandiabil Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 26.7 | 8760 | 100% | 0 | 233892
18 | 220kV Pandiabil-Samagara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.9 | 8760 | 100% | 0 | 402084
19 | 220kV Balasore- Bhadrak |  |  |  |  | 0.093056 | 13 | 49 | [7 empty] | 67.95 | 8760 | 99.84% | 938.8425 | 595242
|  | 2020-08-09 | 03:55 | 2020-08-09 | 04:43 | 0:48 | 0 | 48 | [5 empty] | Tripped at Balasore end.
|  | 2020-08-12 | 16:41 | 2020-08-12 | 16:46 | 0:05 | 0 | 5 | [5 empty] | LBB protection.
|  | 2020-08-21 | 15:46 | 2020-08-21 | 15:49 | 0:03 | 0 | 3 | [5 empty] | LBB Trip relay,96 OPTD
|  | 2021-02-02 | 13:22 | 2021-02-02 | 14:40 | 1:18 | 0 | 53 | [5 empty] | At Balasore end: Siemens B/U relay: B-Ph O/C, E/F, Fault current: IL3=1.33KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
20 | 220kV Balimela-Jayanagar-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 92.072 | 8760 | 100% | 0 | 806550.72
21 | 220kV Balimela-Jayanagar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 92.072 | 8760 | 100% | 0 | 806550.72
22 | 220kV Balimela-Jayanagar-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 93.46 | 8760 | 100% | 0 | 818709.6
23 | 220kV Balimela-Malkangiri Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 22.41 | 8760 | 100% | 0 | 196311.6
24 | 220kV Balimela-Malkangiri Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 22.41 | 8760 | 100% | 0 | 196311.6
25 | 220kV Balimela PH -Balimela |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 0.2 | 8760 | 100% | 0 | 1752
26 | 220kV Balimela PH -Upper Sileru |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.76 | 8760 | 100% | 0 | 216897.6
27 | 220kV Barkote-Bonai |  |  |  |  | 0.0069444 | 0 | 10 | [7 empty] | 55.807 | 8760 | 100% | 9.3012 | 488869.32
|  | 2020-06-27 | 17:04 | 2020-06-27 | 17:14 | 0:10 | 0 | 10 | [5 empty] | DP Relay( Distance-45.36 Kms , Loop- L3_N , Il3-5.93 kA , In-5.92 kA)
28 | 220kV Bonai-Tarkera |  |  |  |  | 0.064583 | 0 | 10 | [7 empty] | 47.467 | 8760 | 100% | 7.9112 | 415810.92
|  | 2020-06-27 | 17:04 | 2020-06-27 | 18:37 | 1:33 | 0 | 10 | [5 empty] | DP Relay( Distance-45.36 Kms , Loop- L3_N , Il3-5.93 kA , In-5.92 kA)
29 | 220kV Bhanjanagar-Narasinghpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 87.17 | 8760 | 100% | 0 | 763609.2
30 | 220kV Narasinghpur- Meramundali |  |  |  |  | 0 | 0 | 0 | [7 empty] | 57.3 | 8760 | 100% | 0 | 501948
31 | 220kV Bhanjanagar-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 134.14 | 8760 | 100% | 0 | 1175066.4
32 | 220kV Bhanjanagar-Mendhasal ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 136.47 | 8760 | 100% | 0 | 1195477.2
33 | 220kV Bhanjanagar-Nayagarh ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 69 | 8760 | 100% | 0 | 604440
34 | 220kV Nayagarh-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 68.58 | 8760 | 100% | 0 | 600760.8
35 | 220kV Bidanasi -Mendhasal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
36 | 220kV Bidanasi -Mendhasal Ckt-II |  |  |  |  | 0.41736 | 0 | 9 | [7 empty] | 15 | 8760 | 100% | 2.25 | 131400
|  | 2020-06-05 | 5:45 | 2020-06-05 | 9:50 | 5:17 | 0 | 5 | [5 empty] | Bidanasi End : Main-1 - B-pahae to Ground, Distance-11.17km, Z1 , Ib- 5.4kAmp. [Jumper snapped at Loc. No-69. ]
|  | 2020-06-12 | 7:40 | 2020-06-12 | 3:50 | 4:44 | 0 | 4 | [5 empty] | Tripped on O/C Y-phase to ground fault with fault distance-19.04 Km & Iy-1.44 KAmp.[Jumper snapped at Loc. No-50.]
37 | 220kV Bidanasi -Cuttack Ckt-I |  |  |  |  | 0.41736 | 12 | 19 | [7 empty] | 9.3 | 8760 | 99.86% | 114.545 | 81468
|  | 2020-04-25 | 11:18 | 2020-04-25 | 11:26 | 0:08 | 0 | 6 | [5 empty] | Tripped on V/F trip,V/F warn,86A&86B trip
|  | 2020-04-29 | 23:12 | 2020-04-29 | 23:16 | 0:04 | 0 | 4 | [5 empty] | P/S failure from Bidanasi end
|  | 2020-06-05 | 5:45 | 2020-06-05 | 9:50 | 5:17 | 0 | 5 | [5 empty] | Bidanasi End : Main-1 - B-pahae to Ground, Distance-11.17km, Z1 , Ib- 5.4kAmp. [Jumper snapped at Loc. No-69. ]
|  | 2020-06-12 | 7:40 | 2020-06-12 | 3:50 | 4:44 | 0 | 4 | [5 empty] | Tripped on O/C Y-phase to ground fault with fault distance-19.04 Km & Iy-1.44 KAmp.[Jumper snapped at Loc. No-50.]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
38 | 220kV Bidanasi -Cuttack Ckt-II |  |  |  |  | 0.42569 | 12 | 25 | [7 empty] | 9.3 | 8760 | 99.86% | 115.475 | 81468
|  | 2020-04-25 | 11:18 | 2020-04-25 | 11:26 | 0:08 | 0 | 6 | [5 empty] | Tripped on V/F trip,V/F warn,86A&86B trip
|  | 2020-04-29 | 23:12 | 2020-04-29 | 23:16 | 0:04 | 0 | 4 | [5 empty] | P/S failure from Bidanasi end
|  | 2020-05-29 | 3:29 | 2020-05-29 | 3:35 | 0:06 | 0 | 6 | [5 empty] | Tripped on Group-A/B trip, M/R at Bidanasi end
|  | 2020-06-05 | 5:45 | 2020-06-05 | 9:50 | 5:17 | 0 | 5 | [5 empty] | Bidanasi End : Main-1 - B-pahae to Ground, Distance-11.17km, Z1 , Ib- 5.4kAmp. [Jumper snapped at Loc. No-69. ]
|  | 2020-06-12 | 7:40 | 2020-06-12 | 3:50 | 4:44 | 0 | 4 | [5 empty] | Tripped on O/C Y-phase to ground fault with fault distance-19.04 Km & Iy-1.44 KAmp.[Jumper snapped at Loc. No-50.]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
39 | 220kV Bisra PG-Tarkera-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.335 | 8760 | 100% | 0 | 134334.6
40 | 220kV Budhipadar-Aditya Aluminium Ckt.-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.507 | 8760 | 100% | 0 | 179641.32
41 | 220kV Budhipadar-Aditya Aluminium Ckt.-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.507 | 8760 | 100% | 0 | 179641.32
42 | 220kV Budhipadar-Basundhara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35.29 | 8760 | 100% | 0 | 309140.4
43 | 220kV Budhipadar-Basundhara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35.29 | 8760 | 100% | 0 | 309140.4
44 | 220kV Budhipadar-IbTPS -I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 100% | 0 | 227760
45 | 220kV Budhipadar-IbTPS -II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 100% | 0 | 227760
46 | 220kV Budhipadar-IbTPS -III |  |  |  |  | 0.53333 | 4 | 30 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 99.95% | 114.21 | 222328.8
|  | 2020-07-22 | 19:51 | 2020-07-23 | 8:39 | 12:48 | 4 | 30 | [5 empty] | At Budhipadar End,D/P-I(ABB RELZ 100)TRZ1,ZM1,ZM2,ZM3,PSR,PSN,C SZ,D/P-II(SIEMENS 7SA52) Dist Gen Trip, Relay Trip L1,L2&L3, Dist Trip Z1, F.D=4.9Kms(19.5%), IL1=17.8KA, AT IBTPS End D/P operated in Zone-I &II, FL=L1-E, IL1=3.6KA
47 | 220kV Budhipadar-IbTPS -IV |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 100% | 0 | 222328.8
48 | 220kV Budhipadar-Raigarh-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 60 | 8760 | 100% | 0 | 525600
49 | 220kV Budhipadar-Korba-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 60 | 8760 | 100% | 0 | 525600
50 | 220kV Budhipadar-Lapanga-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20 | 8760 | 100% | 0 | 175200
51 | 220kV Budhipadar-Lapanga-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20 | 8760 | 100% | 0 | 175200
52 | 220kV Budhipadar-SPS Feeder-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.424 | 8760 | 100% | 0 | 117594.24
53 | 220kV Budhipadar-SPS Feeder-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.424 | 8760 | 100% | 0 | 117594.24
54 | 220kV Budhipadar-Bhusan Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.92 | 8760 | 100% | 0 | 130699.2
55 | 220kV Budhipadar-Bhusan Ckt II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.92 | 8760 | 100% | 0 | 130699.2
56 | 220kV Chandaka -Mendhasal Ckt-I |  |  |  |  | 0.51528 | 0 | 23 | [7 empty] | 19 | 8760 | 100% | 7.2833 | 166440
|  | 2020-06-15 | 0:29 | 2020-06-15 | 12:51 | 12:22 | 0 | 23 | [5 empty] | Tripped by DP,IL2-2.89ka,d- 20.4km,zone2 optd,d%-96%
57 | 220kV Chandaka- Mendhasal ckt II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.9 | 8760 | 100% | 0 | 174324
58 | 220kV Chandaka- Mendhasal ckt III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.9 | 8760 | 100% | 0 | 174324
59 | 220kV Chandaka- Chandaka-B |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.1 | 8760 | 100% | 0 | 876
60 | 220kV Chandaka-B-Mendhasal ckt IV |  |  |  |  | 0 | 0 | 0 | [7 empty] | 18.96 | 8760 | 100% | 0 | 166089.6
61 | 220kV Duburi-Duburi (New) Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.38 | 8760 | 100% | 0 | 55888.8
62 | 220kV Duburi-Duburi (New) Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.38 | 8760 | 100% | 0 | 55888.8
63 | 220kV Duburi-NINL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6 | 8760 | 100% | 0 | 52560
64 | 220kV Indravati PH-Therubali-I (TVL) |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 100% | 0 | 755112
65 | 220kV Indravati PH-Therubali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 100% | 0 | 755112
66 | 220kV Indravati PH-Therubali-III |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 91 | 8760 | 100% | 0 | 797160
67 | 220kV Indravati PH-Jayapatna-Kasipur-Therubali-IV |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 115 | 8760 | 100% | 0 | 1007400
68 | 220kV Jayanagar-Jeypore PG-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
69 | 220kV Jayanagar-Jeypore PG-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
70 | 220kV Jayanagar-Jeypore PG-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
71 | 220kV Jayanagar-Jeypore PG-IV |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
72 | 220kV Jayanagar-Laxmipur ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65 | 8760 | 100% | 0 | 569400
73 | 220kV Jayanagar-Laxmipur ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65 | 8760 | 100% | 0 | 569400
74 | 220kV Jindal-Jamsedpur DVC |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.8 | 8760 | 100% | 0 | 182208
75 | 220kV Joda-RCPur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.5 | 8760 | 100% | 0 | 135780
76 | 220kV Joda-JSPL |  |  |  |  | 0.069444 | 1 | 13 | [7 empty] | 21 | 8760 | 99.99% | 25.55 | 183960
|  | 2020-05-04 | 10:37 | 2020-05-04 | 11:02 | 0:25 | 0 | 25 | [5 empty] | Tripped at Both End . AT Joda end - Dp Relay Tripped,Zone-01, F.D- 11.610KM, F.L-L1-N, Fault
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
77 | 220kV Joda-TSIL Ckt. |  |  |  |  | 0.069444 | 1 | 13 | [7 empty] | 7.3 | 8760 | 99.99% | 8.8817 | 63948
|  | 2020-05-04 | 10:37 | 2020-05-04 | 11:02 | 0:25 | 0 | 25 | [5 empty] | Tripped at Both End . AT Joda end - Dp Relay Tripped,Zone-01, F.D- 11.610KM, F.L-L1-N, Fault
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
78 | 220kV Katapalli- HINDALCO Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
79 | 220kV Katapalli- HINDALCO Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
75 | 220kV Katapalli- Bargarh New Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 52.035 | 8760 | 99.99% | 0 | 455826.6
76 | 220kV Bargarh New- New Bolangir Ckt-I |  |  |  |  | 0.010417 | 0 | 15 | [7 empty] | 65.885 | 8760 | 100% | 16.4713 | 577152.6
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-10-24 | 13:18 | 2020-10-24 | 13:30 | 0:12 | 0 | 12 | [5 empty] | Tripped on distance protection.
77 | 220kV Katapalli- Bolangir PG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 118.45 | 8760 | 100% | 0 | 1037622
78 | 220kV Bolangir PG- New Bolangir Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
79 | 220kV Keonjhar PG - Keonjhar Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
80 | 220kV Keonjhar PG - Keonjhar Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
81 | 220kV Bolangir PG- New Bolangir Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.7 | 5844 | 100% | 0 | 15778.8
82 | 220kV Kuchei PG-Balasore Ckt I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.859 | 8760 | 100% | 0 | 673284.84
83 | 220kV Kuchei PG-Balasore Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.859 | 8760 | 100% | 0 | 673284.84
84 | 220kV Lapanga-Katapali-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 49.72 | 8760 | 100% | 0 | 435547.2
85 | 220kV Lapanga-Katapali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 49.72 | 8760 | 100% | 0 | 435547.2
86 | 220kV Laxmipur - Therubali ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 59 | 8760 | 100% | 0 | 516840
87 | 220kV Laxmipur - Therubali ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 59 | 8760 | 100% | 0 | 516840
88 | 220kV Laxmipur - Utkal Alumina ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.04 | 8760 | 100% | 0 | 271910.4
89 | 220kV Laxmipur - Utkal Alumina ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.04 | 8760 | 100% | 0 | 271910.4
90 | 220kV Laxmipur - NALCO ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 36.99 | 8760 | 100% | 0 | 324032.4
91 | 220kV Laxmipur - NALCO ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 36.99 | 8760 | 100% | 0 | 324032.4
92 | 220kV Meramundali-Bhusan Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
93 | 220kV Meramundali-Bhusan Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
94 | 220kV Meramundali-Duburi-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 95.556 | 1404 | 100% | 0 | 134160.624
95 | 220kV Meramundali-Goda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 70.97 | 7356 | 100% | 0 | 522055.32
96 | 220kV Goda-Duburi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 36.69 | 7356 | 100% | 0 | 269891.64
97 | 220kV Meramundali-Duburi-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 95.556 | 8760 | 100% | 0 | 837070.56
98 | 220kV NALCO-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
99 | 220kV NALCO-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
100 | 220kV Narendrapur-Atri Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 150.35 | 8760 | 100% | 0 | 1317066
101 | 220kV Atri-Mendhasal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.85 | 8760 | 100% | 0 | 217686
102 | 220kV Narendrapur-Atri Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 150.35 | 8760 | 100% | 0 | 1317066
103 | 220kV Narendrapur-Tata Gopalpur Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.1 | 2436 | 100% | 0 | 19731.6
104 | 220kV Narendrapur-Tata Gopalpur Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.1 | 2436 | 100% | 0 | 19731.6
105 | 220kV Atri-Infocity-II Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 21.3 | 8760 | 100% | 0 | 186588
106 | 220kV Infocity-II-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.47 | 8760 | 100% | 0 | 47917.2
107 | 220kV New Duburi -Balasore |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 140.97 | 8760 | 100% | 49.3395 | 1234897.2
|  | 2021-01-05 | 12:24 | 2021-01-05 | 12:45 | 0:21 | 0 | 21 | [5 empty] | tripped at Balasore end.(Main-2, Zone-2 B-ph,AR fail,126.6KM,1.464KA)
108 | 220kV New Duburi -Bhadrak |  |  |  |  | 0.090972 | 1 | 40 | [7 empty] | 73.798 | 8760 | 99.98% | 122.9967 | 646470.48
|  | 2020-08-09 | 03:55 | 2020-08-09 | 05:14 | 1:19 | 0 | 48 | [5 empty] | FACIA-MAIN 1 & 2 DP OPERATED, GR- A/B RELAY OPTD MAIN 1 DP- GENERAL TRIP, B PH TRIP, ZONE 3 TRIP, E/F TRIP, PICK UP TIME= 1054ms,TRIP TIME=1003ms, DIST=111.8KM, IL3= KA MAIN 2 DP- GENERAL TRIP, B PH TRIP, ZONE 3 TRIP, E/F TRIP, PICK UP TIME= 1055ms,TRIP TIME=1003ms, DIST=111.6KM, IL3= 2.07KA BHADRAK END DATA NO FAULT DATA AVAILABLE AS PER SHIFT INCHARGE OF BHADRAK GSS. [132KV BUS CONDUCTOR SNAPPED AT
|  | 2021-02-02 | 13:22 | 2021-02-02 | 14:14 | 0:52 | 0 | 52 | [5 empty] | Tripped from both ends , ( B-phase LA of interconnection between 220kv and 132 kv switchyard burst at bhadrak end ) along with 220kv Baleswar-Bhadrak
109 | 220kV New Duburi-Paradeep Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 113.433 | 8760 | 100% | 0 | 993673.08
110 | 220kV New Duburi-Paradeep Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 113.433 | 8760 | 100% | 0 | 993673.08
111 | 220kV Paradeep - IOCL Ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6 | 8760 | 100% | 0 | 52560
112 | 220kV Paradeep - ESSAR Steel Ckt -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.868 | 8760 | 100% | 0 | 77683.68
113 | 220kV Paradeep - ESSAR Steel Ckt -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.868 | 8760 | 100% | 0 | 77683.68
114 | 220kV Rengali PH-Nalco-TTPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 71.337 | 8760 | 100% | 0 | 624912.12
115 | 220kV Rengali GD-Rengali PG -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.4 | 8760 | 100% | 0 | 3504
116 | 220kV Rengali GD-Rengali PG -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.4 | 8760 | 100% | 0 | 3504
117 | 220kV Rengali GD-Chandiposh (T)-Tarkera - II |  |  |  |  | 1900-01-01 18:14 | 106 | 17 | [7 empty] | 162.08 | 8760 | 98.79% | 17226.4027 | 1419820.8
|  | 2020-06-01 | 14:28 | 2020-06-01 | 15:20 | 0:52 | 0 | 52 | [5 empty] | At Tarkera end: DP Relay, Zone I , 120.42 Kms , L1_N , IL1=1.06 kA , In=1.22 kA) At Rengali end: B/U Relay, IA=1862.5A, IB=81.6A, IC=61.2A, IN=1202.11A
|  | 2020-06-02 | 15:37 | 2020-06-03 | 15:41 | 24:04 | 24 | 4 | [5 empty] | At Tarkera end: DP Relay, Zone I, 105.54 Kms , L2-N , IL2=1.54 kA , In=1.54 kA At Rengali end: B/U Relay, IA=59.9A, IB=2260A, IC=58.6A, IN=1230.49A, IG=2343.77A
|  | 2020-06-04 | 16:06 | 2020-06-04 | 17:51 | 1:45 | 1 | 45 | [5 empty] | Tarkera end: DP Relay,Zone I , 102.31 Kms , L1-N , IL1=1.56 kA , In=1.44 kA. Rengali end:B/U Relay ,IA=2333.2A, IB=71.1A, IC=68.7A, IN=1222.0A , IG=2396.23A .
|  | 2020-06-07 | 19:00 | 2020-06-08 | 10:09 | 15:09 | 15 | 9 | [5 empty] | DP Relay, Zone I , 68.85 Km , L3-N , IL3- 2.08 kA , In-1.92 kA. Rengali end: DP Relay, Fault= ABS, 242.65 km, L2-L3, IL2=50.77 A, IL3=2982.75A, IN=3170.38A. B/U Relay, IA=61.6, IB=4526.1A, IC=4278.1A, IN=1070.07A, IG=2251.91A.
|  | 2020-07-02 | 10:26 | 2020-07-02 | 10:46 | 00:20 | 0 | 20 | [5 empty] | At Tarkera end:-DP Relay( Zone I , Distance- 87.94 Kms , Loop- L1_N , Il1-1.69 kA , In- 1.72 kA) At Rengali end:- DP RELAY OPERATED,FAULT ABS DIST=204.6 KM ,FAULT REAL DIST=152.68 %,LOOP=L1- N,IL1=2258.22 A,IN=2274.38A.
|  | 2020-07-02 | 12:03 | 2020-07-02 | 16:59 | 04:56 | 4 | 56 | [5 empty] | At Tarkera end:-DP Relay( Zone I , Distance- 150.42 Kms , Loop- L1_N , Il1-0.86 kA , In- 0.73 kA) At Rengali end:-DP RELAY OPERATED,FAULT ABS DIST=81.61 KM ,FAULT REAL DIST=60.91 %,LOOP=L1- N,IL1=3613.2917 A,IN=3760.37A.
|  | 2020-07-22 | 21:15 | 2020-07-23 | 20:02 | 22:47 | 22 | 47 | [5 empty] | At Tarkera end, DP Relay( Zone I , Distance-65.78 Kms , Loop- L3_N , Il3-2.55 kA )[B Phase insulator damaged at Loc.456] At Rengali end:-NUMERICAL B/U RELAY OPERATED,IA=52.3,IB=68.8A,IC=2435.1A ,IN=1229.70A,IG=2480.96A.
|  | 2020-10-03 | 16:53 | 2020-10-04 | 16:42 | 23:49 | 23 | 49 | [5 empty] | Tarkera end: DP, Z1, B-E, 116.02km, 1.57kA. At Rengali S/Y end:DP (Loop- L3_N , Distance - 107 km , IL3=4.1 kA ,In=4.2KA)
|  | 2020-10-10 | 16:08 | 2020-10-11 | 16:43 | 0:35 | 0 | 35 | [5 empty] | DP(Zone- I , B Phase, Loop=L3_N, Distance=65.427kms, IL3=2.38 kA , In=2.18 kA) At Rengali S/Y end: DP ( Zone-II,B phase,Loop- L3_N , Distance - 75.19 km , IL3=5.00 kA ,In=5.2KA).
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
118 | 220kV Rengali GD-Barkote |  |  |  |  | 1899-12-31 01:20 | 0 | 35 | [7 empty] | 48.776 | 8760 | 99.99% | 28.4527 | 427277.76
|  | 2020-10-10 | 16:08 | 2020-10-11 | 17:28 | 25:20 | 0 | 35 | [5 empty] | DP RELAY OPERATED,D=34.4KM,Z1,IA=8.0 1IN,Zone-1 AT BARKOTE -DP RELAY OPERATED,D=13.1KM. [Replacement of snapped R ph double suspension insulator string, damaged Y ph single suspension string and damaged B ph single suspension string at loc no-336 of the said ckt]
119 | 220kV Rengali PH-Rengali GD -I |  |  |  |  | 0.63125 | 0 | 56 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 99.99% | 4.6667 | 43800
|  | 2020-06-07 | 19:00 | 2020-06-08 | 10:09 | 15:09 | 0 | 56 | [5 empty] | DP Relay, Zone I , 68.85 Km , L3-N , IL3- 2.08 kA , In-1.92 kA. Rengali end: DP Relay, Fault= ABS, 242.65 km, L2-L3, IL2=50.77 A, IL3=2982.75A, IN=3170.38A. B/U Relay, IA=61.6, IB=4526.1A, IC=4278.1A, IN=1070.07A, IG=2251.91A.
120 | 220kV Rengali PH-Rengali GD -II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
121 | 220kV Rengali PH -STPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 29.5 | 8760 | 100% | 0 | 258420
122 | 220kV STPS (Kaniha)-TTPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 34.5 | 8760 | 100% | 0 | 302220
123 | 220kV STPS (Kaniha)-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
124 | 220kV STPS (Kaniha)-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
125 | 220kV Tarkera-Budhipadar-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 109 | 8760 | 100% | 0 | 954840
126 | 220kV Tarkera-Budhipadar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 109 | 8760 | 100% | 0 | 954840
127 | 220kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
128 | 220kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
129 | 220kV Tarkera-RSP-III |  |  |  |  | 0.58056 | 13 | 56 | [7 empty] | 4 | 8760 | 99.84% | 55.7333 | 35040
|  | 2020-07-14 | 00:25 | 2020-07-14 | 18:21 | 13:56 | 13 | 56 | [5 empty] | Differential Relay ( R Phase Trip , Il1-8.45 kA) , Distance Protection Relay ( Distance-3.7 km , Loop-A- G) at tarkera end.
130 | 220kV Tarkera-RSP-IV |  |  |  |  | 1900-01-09 11:36 | 13 | 56 | [7 empty] | 4 | 8760 | 99.84% | 55.7333 | 35040
|  | 2020-07-14 | 00:25 | 2020-07-24 | 12:01 | 251:36 | 13 | 56 | [5 empty] | Differential Relay ( R Phase Trip , Il1-8.17 kA) , Distance Protection Relay ( Distance-3.3 km , Loop-A- G) at tarkera end.
131 | 220kV Therubali-Narendrapur-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 196 | 8760 | 100% | 0 | 1716960
132 | 220kV Therubali-Narendrapur-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 196 | 8760 | 100% | 0 | 1716960
133 | 220kV Therubali-Bhanjanagar-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 171.46 | 8760 | 100% | 0 | 1501989.6
134 | 220kV Therubali-Bhanjanagar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 171.46 | 8760 | 100% | 0 | 1501989.6
135 | 220kV Bhanjanagar- Aska New - I |  |  |  |  | 0.089583 | 13 | 17 | [7 empty] | 28.6 | 8760 | 99.85% | 379.9033 | 250536
|  | 2020-05-01 | 13:25 | 2020-05-01 | 13:42 | 0:17 | 0 | 17 | [5 empty] | E/F on B-Ph
|  | 2020-06-27 | 13:55 | 2020-06-27 | 15:10 | 1:15 | 0 | 23 | [5 empty] | B PH TO E/F,Z-1,D=1.2KM at bhanjanagar end.
|  | 2020-08-01 | 14:15 | 2020-08-01 | 14:52 | 0:37 | 0 | 37 | [5 empty] | AN TRIP, ZONE-1 , D: 726.5 MTR, IA= 8.091 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
136 | 220kV Bhanjanagar- Aska New - II |  |  |  |  | 0.23403 | 13 | 7 | [7 empty] | 28.6 | 8760 | 99.85% | 375.1367 | 250536
|  | 2020-05-01 | 13:25 | 2020-05-01 | 18:12 | 4:47 | 0 | 17 | [5 empty] | E/F on B-Ph
|  | 2020-07-15 | 19:43 | 2020-07-15 | 19:56 | 0:13 | 0 | 13 | [5 empty] | BACKUP RELAY: RPH O/C, IR=1.16 KA, DP RELAY DIDN’T OPERATE. BREAKER DIDN’T TRIP AT ASKANEW END
|  | 2020-08-01 | 14:15 | 2020-08-01 | 14:52 | 0:37 | 0 | 37 | [5 empty] | AN TRIP, ZONE-1 , D: 726.5 MTR, IA= 8.091 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
137 | 220kV TTPS-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
138 | 220kV TTPS-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
139 | 220kV TTPS- Joda I |  |  |  |  | 0.78056 | 15 | 18 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 154 | 8760 | 99.83% | 2356.2 | 1349040
|  | 2020-05-04 | 10:37 | 2020-05-04 | 11:02 | 0:25 | 0 | 50 | [5 empty] | Tripped at Both End . AT Joda end - Dp Relay Tripped,Zone-01, F.D- 11.610KM, F.L-L1-N, Fault
|  | 2020-05-08 | 21:36 | 2020-05-08 | 21:52 | 0:16 | 0 | 28 | [5 empty] | Tripped at Both End. AT Joda end -Dp Relay Tripped,Zone-01, F.D- 93.98KM, F.L-L1-L3, Fault Current :- IL1- 2278.49A, IL2-261.51A, IL3- 1129.94A, IN-1387.43A,P/S restored bt Ckt-II
|  | 2020-05-16 | 19:32 | 2020-05-16 | 19:39 | 0:07 | 0 | 14 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped,Zone-01, F.D- 129.44KM, F.L-L1-L2, Fault Current :- IL1-1769.66A, IL2-1120.37A, IL3-137.18A, IN-1021.07A
|  | 2020-05-16 | 19:59 | 2020-05-17 | 13:55 | 17:56 | 0 | 14 | [5 empty] | Tripped at Both End .AT Joda end -Dp Relay Tripped,Zone-01, F.D- 110.84KM, F.L-L1-N, Fault Current :- IL1-1214.99A, IL2-287.94A, IL3-317.30A, IN-1312.36A
|  | 2020-05-28 | 19:52 | 2020-05-28 | 20:14 | 0:22 | 0 | 44 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped, Zone-01, F.D- 89.61KM, F.L- L2-L3, Fault Current :- IL1-79.37A, IL2- 2270.84A, IL3-1392.12A, IN-1345.99A
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
140 | 220kV TTPS-Joda-II |  |  |  |  | 1899-12-31 18:35 | 15 | 18 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 154 | 8760 | 99.83% | 2356.2 | 1349040
|  | 2020-05-04 | 10:37 | 2020-05-05 | 15:12 | 1899-12-31 04:35 | 0 | 50 | [5 empty] | Tripped at Both End . AT Joda end - Dp Relay Tripped,Zone-01, F.D- 11.610KM, F.L-L1-N, Fault, P/S restored bt Ckt-I
|  | 2020-05-08 | 21:36 | 2020-05-08 | 21:50 | 0:14 | 0 | 28 | [5 empty] | Tripped at Both End. AT Joda end -Dp Relay Tripped,Zone-01, F.D- 51.91KM, F.L-L3-N, Fault Current :- IL1- 423.31A, IL2-246.36A, IL3-1205.08A, IN-1755.15A
|  | 2020-05-16 | 19:32 | 2020-05-16 | 19:41 | 0:09 | 0 | 14 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped,Zone-02, F.D- 131.55KM, F.L-L2-N, Fault Current :- IL1-237.67A, IL2-914.80A, IL3-148.03A, IN-1021.07A,P/S restored bt Ckt-I.
|  | 2020-05-16 | 19:46 | 2020-05-16 | 20:22 | 0:36 | 0 | 14 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped,Zone-01, F.D- 113.71KM, F.L-L2-N, Fault Current :- IL1-189.29A, IL2-1275.70A, IL3-197.87A, IN-1307.69A, P/S restored bt Ckt-I.
|  | 2020-05-28 | 19:52 | 2020-05-28 | 20:24 | 0:32 | 0 | 44 | [5 empty] | Tripped at Both End .AT Joda end -Dp Relay Tripped,Zone-01, F.D- 83.86KM, F.L- L3-N, Fault Current :- IL1-150.78A, IL2- 553.42A, IL3-1134.15A, IN-1584.03A, P/S restored bt Ckt-I.
|  | 2020-06-23 | 11:41 | 2020-06-23 | 0:48 | 12:29 | 0 | 48 | [5 empty] | Tripped from Joda end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
141 | 220kV U. Kolab-Jayanagar-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
142 | 220kV U. Kolab-Jayanagar-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
143 | 220kV U. Kolab-Therubali Ckt-III |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 128 | 8760 | 100% | 0 | 1121280
132 KV
144 | 132kV Akhusing-Mohana |  |  |  |  | 0.87917 | 0 | 39 | [7 empty] | 69.2 | 8760 | 99.99% | 44.98 | 606192
|  | 2020-11-07 | 16:09 | 2020-11-08 | 13:15 | 21:06 | 0 | 39 | [5 empty] | Tripped on E/F [Breakdown due to tree fall upon conductor on Y & B Phase because of tree cutting by local people of Dumulapadar village at Loc No-314- 315]
145 | 132kV Akhusing-Parlakhemundi |  |  |  |  | 0.05 | 12 | 40 | [7 empty] | 76.1 | 8760 | 99.86% | 963.9333 | 666636
|  | 2020-05-18 | 13:31 | 2020-05-18 | 13.44 | 0:13 | 0 | 13 | [5 empty] | Tripped
|  | 2020-05-16 | 15:09 | 2020-05-16 | 15:18 | 0:09 | 0 | 6 | [5 empty] | Auto-tripped, R, B Phase fault, Z1 Trip
|  | 2020-10-03 | 14:47 | 2020-10-03 | 14:52 | 0:05 | 0 | 5 | [5 empty] | Tripped at Podagada
|  | 2020-10-15 | 19:04 | 2020-10-15 | 19:49 | 0:45 | 0 | 16 | [5 empty] | Tripped of Podagad end & JNR With O/C [Conductor y Phase CVT of JNR incoming side snapped at podagada end.]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
146 | 132kV Angul-Boinda |  |  |  |  | 0.14722 | 13 | 53 | [7 empty] | 38.1 | 8760 | 99.84% | 528.955 | 333756
|  | 2020-04-25 | 4:17 | 2020-04-25 | 4:52 | 0:35 | 0 | 35 | [5 empty] | At Angul end: Fault loop-L2N,Fault dist-1.8709 KM
|  | 2020-05-20 | 7:34 | 2020-05-20 | 8:02 | 0:28 | 0 | 13 | [5 empty] | Trig signal- Trip, Fault Distance- 17.954 KM, Fault loop-L2N
|  | 2020-06-03 | 17:41 | 2020-06-03 | 17:55 | 0:14 | 0 | 14 | [5 empty] | O/C on R-phase, DP, 2426.2 A, 33.665 km, L1-N
|  | 2020-08-19 | 23:31 | 2020-08-19 | 23:36 | 0:05 | 0 | 5 | [5 empty] | Tripped at Angul end. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY AT RAIRAKHOL GRID END.]
|  | 2020-08-20 | 07:42 | 2020-08-20 | 07:49 | 0:07 | 0 | 7 | [5 empty] | O/C in Y-Phase, Fault Current(Y- PH)-1.06 KA and E/F.
|  | 2020-08-20 | 07:27 | 2020-08-20 | 07:40 | 0:13 | 0 | 6 | [5 empty] | Tripped at Angul end. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY AT RAIRAKHOL GRID END.]
|  | 2020-08-25 | 14:25 | 2020-08-25 | 14:33 | 0:08 | 0 | 3 | [5 empty] | TRIPPED AT ANGUL END
|  | 2020-10-13 | 20:36 | 2020-10-13 | 20:46 | 0:10 | 0 | 10 | [5 empty] | Trig Signal- ZM01 Fault Abs Dist.- 26.915 KM Fault Loop- L3N, Fault current IR=231.47 A, IY= 385.90 A, IB= 3124.93 A
|  | 2020-10-29 | 15:17 | 2020-10-29 | 17:03 | 1:46 | 0 | 20 | [5 empty] | Tripped on E/F at both ends. [ one big mango tree has been uprooted by the railway authority which was in close proximity to 132 KV TTPS-Angul and 132 KV Chainpal-Angul double circuit
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
147 | 132kV Boinda- RTSS Boinda |  |  |  |  | 0.125 | 13 | 22 | [7 empty] | 2.947 | 8760 | 99.85% | 39.3916 | 25815.72
|  | 2020-06-03 | 17:41 | 2020-06-03 | 17:55 | 0:14 | 0 | 14 | [5 empty] | O/C on R-phase, DP, 2426.2 A, 33.665 km, L1-N
|  | 2020-08-18 | 09:28 | 2020-08-18 | 09:36 | 0:08 | 0 | 8 | [5 empty] | Tripped [DUE TO CIRCUIT BREAKER PROBLEM AT BOINDA]
|  | 2020-08-20 | 07:38 | 2020-08-20 | 07:40 | 0:02 | 0 | 2 | [5 empty] | TRIPPED ON B/U RELAY INDICATING B-PHASE O/C & E/F AT RAIRAKHOL GRID END. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY]
|  | 2020-08-19 | 23:31 | 2020-08-19 | 23:36 | 0:05 | 0 | 5 | [5 empty] | Tripped at Angul end. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY AT RAIRAKHOL GRID END.]
|  | 2020-08-20 | 07:42 | 2020-08-20 | 07:49 | 0:07 | 0 | 7 | [5 empty] | O/C in Y-Phase, Fault Current(Y- PH)-1.06 KA and E/F.
|  | 2020-08-20 | 07:27 | 2020-08-20 | 07:40 | 0:13 | 0 | 6 | [5 empty] | Tripped at Angul end. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY AT RAIRAKHOL GRID END.]
|  | 2020-08-25 | 14:25 | 2020-08-25 | 14:33 | 0:08 | 0 | 3 | [5 empty] | TRIPPED AT ANGUL END
|  | 2020-09-04 | 16:34 | 2020-09-04 | 16:41 | 0:07 | 0 | 7 | [5 empty] | Tripped at Rairakhol end.
|  | 2020-10-13 | 20:36 | 2020-10-13 | 20:46 | 0:10 | 0 | 10 | [5 empty] | Trig Signal- ZM01 Fault Abs Dist.- 26.915 KM Fault Loop- L3N, Fault current IR=231.47 A, IY= 385.90 A, IB= 3124.93 A
|  | 2020-10-29 | 15:17 | 2020-10-29 | 17:03 | 1:46 | 0 | 20 | [5 empty] | Tripped on E/F at both ends. [ one big mango tree has been uprooted by the railway authority which was in close proximity to 132 KV TTPS-Angul and 132 KV Chainpal-Angul double circuit
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
148 | 132kV Angul-Nandira (MCL)- I |  |  |  |  | 0.29514 | 1 | 31 | [7 empty] | 10.826 | 8760 | 99.98% | 16.4194 | 94835.76
|  | 2020-10-29 | 15:17 | 2020-10-29 | 17:03 | 1:46 | 1 | 22 | [5 empty] | Tripped on E/F at both ends. [ one big mango tree has been uprooted by the railway authority which was in close proximity to 132 KV TTPS-Angul and 132 KV Chainpal-Angul double circuit
|  | 2021-03-11 | 18:55 | 2021-03-12 | 0:14 | 5:19 | 0 | 9 | [5 empty] | TRIPPED DUE TO RAIN AND LIGHTENING O/C R-Ph. P/S restored from TTPS end.
149 | 132kV Angul-Nandira (MCL)- II |  |  |  |  | 0.29514 | 1 | 31 | [7 empty] | 10.826 | 8760 | 99.98% | 16.4194 | 94835.76
|  | 2020-10-29 | 15:17 | 2020-10-29 | 17:03 | 1:46 | 1 | 22 | [5 empty] | Tripped on E/F at both ends. [ one big mango tree has been uprooted by the railway authority which was in close proximity to 132 KV TTPS-Angul and 132 KV Chainpal-Angul double circuit
|  | 2021-03-11 | 18:55 | 2021-03-12 | 0:14 | 5:19 | 0 | 9 | [5 empty] | TRIPPED DUE TO RAIN AND LIGHTENING O/C R-Ph. P/S restored from TTPS end.
150 | 132kV Joda -Barbil |  |  |  |  | 0.30139 | 18 | 47 | [7 empty] | 10.22 | 8760 | 99.79% | 191.9657 | 89527.2
|  | 2020-05-28 | 19:52 | 2020-05-28 | 20:14 | 0:22 | 0 | 22 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped, Zone-01, F.D- 89.61KM, F.L- L2-L3, Fault Current :- IL1-79.37A, IL2- 2270.84A, IL3-1392.12A, IN-1345.99A
|  | 2020-05-28 | 7:46 | 2020-05-28 | 7:53 | 0:07 | 0 | 7 | [5 empty] | Tripped as D/P relay operated with following indications at Joda grid end: Zone-1,Location- 1.48Km,Tripped phase- A-G IA=5570A, IB=256A, IC=306A, IN=1A, IG=5009A [due to Heavy lightning, thunderstorm and rain ]
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
|  | 2020-07-04 | 13:20 | 2020-07-04 | 18:12 | 0:24 | 0 | 24 | [5 empty] | 220kV I/C failed at joda Grid S/S
|  | 2020-09-17 | 17:19 | 2020-09-17 | 17:41 | 0:22 | 0 | 22 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault type- ABC, Zone- I, Location- 2.75KM, IA- 2.25KA, IB- 7.43KA, IC- 8.43KA, IG- 6.69KA [heavy lightning rain at JODA]
|  | 2020-10-10 | 22:37 | 2020-10-10 | 03:21 | 4:44 | 4 | 44 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault Phase- AC, Zone- I, Location- 0.75KM, IA- 7.331KA, IB- 244A, IC- 7.476KA [B-Phase jumper snapped in gantry tower of Joda Grid S/S.]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
151 | 132kV Barbil - Bolani |  |  |  |  | 0.44861 | 22 | 15 | [7 empty] | 7.8 | 8760 | 99.75% | 173.55 | 68328
|  | 04.04.20 | 13:02 | 04.04.20 | 13:20 | 0:18 | 0 | 18 | [5 empty] | Tripped on E/F at Barbil end
|  | 24.04.20 | 12:48 | 24.04.20 | 13:03 | 0:15 | 0 | 15 | [5 empty] | Tripped at Barbil end
|  | 2020-05-28 | 19:52 | 2020-05-28 | 20:14 | 0:22 | 0 | 22 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped, Zone-01, F.D- 89.61KM, F.L- L2-L3, Fault Current :- IL1-79.37A, IL2- 2270.84A, IL3-1392.12A, IN-1345.99A
|  | 2020-05-28 | 7:46 | 2020-05-28 | 7:53 | 0:07 | 0 | 7 | [5 empty] | Tripped as D/P relay operated with following indications at Joda grid end: Zone-1,Location- 1.48Km,Tripped phase- A-G IA=5570A, IB=256A, IC=306A, IN=1A, IG=5009A [due to Heavy lightning, thunderstorm and rain ]
|  | 2020-05-10 | 16:47 | 2020-05-10 | 17:05 | 0:18 | 0 | 18 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid end: Zone-1, Location-31.18Km, Tripped phase- C-G IA=97A, IB=250A, IC=2724A, IG=2415A [Due to heavy lightning & rain]
|  | 2020-05-16 | 17:05 | 2020-05-16 | 17:10 | 0:05 | 0 | 5 | [5 empty] | 132 KV Barbil - Bolani-Beekay Steel fdr tripped at Beekay Steel end due to E/F
|  | 2020-05-25 | 8:42 | 2020-05-25 | 9:16 | 0:34 | 0 | 34 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid End: Zone-1, Location-4.90Km, IA=8939, IB=8760A, IC=190A, IG=13A
|  | 2020-05-28 | 6:56 | 2020-05-28 | 7:28 | 0:32 | 0 | 32 | [5 empty] | Tripped as D/P relay operated At RKL grid end:- Zone-1, Location-34.50Km, IA=3287A, IB=322A, IC=3684A, IG=1823A At Beekay Steel end:-Zone-1, Location-36,.8Km, IA=606.2A, IB=348.7A, IC=635.28A [due to Heavy lightning, thunderstorm and rain ]
|  | 2020-05-29 | 0:56 | 2020-05-29 | 1:28 | 0:32 | 0 | 32 | [5 empty] | Tripped as D/P relay operated RKL grid end. Zone-1, Location- 12.86Km, Tripped phase- C-G IA=117A, IB=273A, IC=4845A, IG=2.342kA [due to Heavy lightning, winderstorm and rain]
|  | 2020-05-29 | 17:39 | 2020-05-29 | 18:01 | 0:22 | 0 | 22 | [5 empty] | Tripped as D/P relay operated with following indications at RKL grid end: Zone-1, Location-27.13Km, Tripped phase- A-G, IA=3.563kA, IB=263A, IC=4.145kA, IG=2.342kA [Due to thunderstorm]
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
|  | 2020-06-06 | 17:11 | 2020-06-06 | 17:30 | 0:19 | 0 | 19 | [5 empty] | At Rourkela end:-DP, Z1, 35.88km, C Phase-G IA=153A, IB=293A, IC=2434A, IG=1994A. At Beekay steel end:-DP, Z1, 28.31km, IA=192.8A, IB=298.9A, IC=347.9A.
|  | 2020-07-04 | 13:20 | 2020-07-04 | 18:12 | 0:24 | 0 | 24 | [5 empty] | 220kV I/C failed at joda Grid S/S
|  | 2020-07-16 | 13:39 | 2020-07-16 | 13:52 | 0:13 | 0 | 13 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid end. Zone-1; Location-0.53Km IA=195A, IB=8497A, IC=184A,IG=8402A
|  | 2020-09-17 | 17:19 | 2020-09-17 | 17:45 | 0:26 | 0 | 22 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault type- ABC, Zone- I, Location- 2.75KM, IA- 2.25KA, IB-7.43KA, IC- 8.43KA, IG-6.69KA
|  | 2020-10-10 | 22:37 | 2020-10-10 | 03:21 | 4:44 | 4 | 44 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault Phase- AC, Zone- I, Location- 0.75KM, IA- 7.331KA, IB- 244A, IC- 7.476KA [B-Phase jumper snapped in gantry tower of Joda Grid S/S.]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
152 | 132kV Bolani - Arya Iron & Steel |  |  |  |  | 1899-12-31 02:28 | 37 | 57 | [7 empty] | 3.17 | 8760 | 99.57% | 120.3015 | 27769.2
|  | 04.04.20 | 13:02 | 04.04.20 | 13:20 | 0:18 | 0 | 18 | [5 empty] | Tripped on E/F at Barbil end
|  | 24.04.20 | 12:48 | 24.04.20 | 13:03 | 0:15 | 0 | 15 | [5 empty] | Tripped at Barbil end
|  | 2020-05-28 | 19:52 | 2020-05-28 | 20:14 | 0:22 | 0 | 22 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped, Zone-01, F.D- 89.61KM, F.L- L2-L3, Fault Current :- IL1-79.37A, IL2- 2270.84A, IL3-1392.12A, IN-1345.99A
|  | 2020-05-28 | 7:46 | 2020-05-28 | 7:53 | 0:07 | 0 | 7 | [5 empty] | Tripped as D/P relay operated with following indications at Joda grid end: Zone-1,Location- 1.48Km,Tripped phase- A-G IA=5570A, IB=256A, IC=306A, IN=1A, IG=5009A [due to Heavy lightning, thunderstorm and rain ]
|  | 2020-05-10 | 16:47 | 2020-05-10 | 17:05 | 0:18 | 0 | 18 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid end: Zone-1, Location-31.18Km, Tripped phase- C-G IA=97A, IB=250A, IC=2724A, IG=2415A [Due to heavy lightning & rain]
|  | 2020-05-16 | 17:05 | 2020-05-16 | 17:10 | 0:05 | 0 | 5 | [5 empty] | 132 KV Barbil - Bolani-Beekay Steel fdr tripped at Beekay Steel end due to E/F
|  | 2020-05-25 | 8:42 | 2020-05-25 | 9:16 | 0:34 | 0 | 34 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid End: Zone-1, Location-4.90Km, IA=8939, IB=8760A, IC=190A, IG=13A
|  | 2020-05-28 | 6:56 | 2020-05-28 | 7:28 | 0:32 | 0 | 32 | [5 empty] | Tripped as D/P relay operated At RKL grid end:- Zone-1, Location-34.50Km, IA=3287A, IB=322A, IC=3684A, IG=1823A At Beekay Steel end:-Zone-1, Location-36,.8Km, IA=606.2A, IB=348.7A, IC=635.28A [due to Heavy lightning, thunderstorm and rain ]
|  | 2020-05-29 | 0:56 | 2020-05-29 | 1:28 | 0:32 | 0 | 32 | [5 empty] | Tripped as D/P relay operated RKL grid end. Zone-1, Location- 12.86Km, Tripped phase- C-G IA=117A, IB=273A, IC=4845A, IG=2.342kA [due to Heavy lightning, winderstorm and rain]
|  | 2020-05-29 | 17:39 | 2020-05-29 | 18:01 | 0:22 | 0 | 22 | [5 empty] | Tripped as D/P relay operated with following indications at RKL grid end: Zone-1, Location-27.13Km, Tripped phase- A-G, IA=3.563kA, IB=263A, IC=4.145kA, IG=2.342kA [Due to thunderstorm]
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
|  | 2020-06-06 | 17:11 | 2020-06-06 | 17:30 | 0:19 | 0 | 19 | [5 empty] | At Rourkela end:-DP, Z1, 35.88km, C Phase-G IA=153A, IB=293A, IC=2434A, IG=1994A. At Beekay steel end:-DP, Z1, 28.31km, IA=192.8A, IB=298.9A, IC=347.9A.
|  | 2020-07-04 | 13:20 | 2020-07-04 | 18:12 | 0:24 | 0 | 24 | [5 empty] | 220kV I/C failed at joda Grid S/S
|  | 2020-07-16 | 13:39 | 2020-07-16 | 13:52 | 0:13 | 0 | 13 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid end. Zone-1; Location-0.53Km IA=195A, IB=8497A, IC=184A,IG=8402A
|  | 2020-09-17 | 17:19 | 2020-09-17 | 17:45 | 0:26 | 0 | 22 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault type- ABC, Zone- I, Location- 2.75KM, IA- 2.25KA, IB-7.43KA, IC- 8.43KA, IG-6.69KA
|  | 2020-10-10 | 22:37 | 2020-10-10 | 3:24 | 4:47 | 4 | 47 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault Phase- AC, Zone- I, Location- 0.75KM, IA- 7.331KA, IB- 244A, IC- 7.476KA [B-Phase jumper snapped in gantry tower of Joda Grid S/S.]
|  | 2020-12-17 | 16:47 | 2020-12-17 | 21:05 | 4:18 | 4 | 18 | [5 empty] | Tripped on E/F due to B-ph CT jumper snap at Nalda RTSS.
|  | 2020-12-19 | 07:43 | 2020-12-19 | 19:04 | 11:21 | 11 | 21 | [5 empty] | Tripped at RKL on E/F with following relay indications: Ia=345.7A; Ib=5.88kA; Ic=264.3A: In=5.273kA [Y-ph Jumper snapped at Loc-38 of RKL jurisdiction]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
153 | 132kV Arya Iron & Steel-Nalda (T) |  |  |  |  | 1899-12-31 02:28 | 37 | 57 | [7 empty] | 13.98 | 8760 | 99.57% | 530.541 | 122464.8
|  | 04.04.20 | 13:02 | 04.04.20 | 13:20 | 0:18 | 0 | 18 | [5 empty] | Tripped on E/F at Barbil end
|  | 24.04.20 | 12:48 | 24.04.20 | 13:03 | 0:15 | 0 | 15 | [5 empty] | Tripped at Barbil end
|  | 2020-05-28 | 19:52 | 2020-05-28 | 20:14 | 0:22 | 0 | 22 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped, Zone-01, F.D- 89.61KM, F.L- L2-L3, Fault Current :- IL1-79.37A, IL2- 2270.84A, IL3-1392.12A, IN-1345.99A
|  | 2020-05-28 | 7:46 | 2020-05-28 | 7:53 | 0:07 | 0 | 7 | [5 empty] | Tripped as D/P relay operated with following indications at Joda grid end: Zone-1,Location- 1.48Km,Tripped phase- A-G IA=5570A, IB=256A, IC=306A, IN=1A, IG=5009A [due to Heavy lightning, thunderstorm and rain ]
|  | 2020-05-10 | 16:47 | 2020-05-10 | 17:05 | 0:18 | 0 | 18 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid end: Zone-1, Location-31.18Km, Tripped phase- C-G IA=97A, IB=250A, IC=2724A, IG=2415A [Due to heavy lightning & rain]
|  | 2020-05-16 | 17:05 | 2020-05-16 | 17:10 | 0:05 | 0 | 5 | [5 empty] | 132 KV Barbil - Bolani-Beekay Steel fdr tripped at Beekay Steel end due to E/F
|  | 2020-05-25 | 8:42 | 2020-05-25 | 9:16 | 0:34 | 0 | 34 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid End: Zone-1, Location-4.90Km, IA=8939, IB=8760A, IC=190A, IG=13A
|  | 2020-05-28 | 6:56 | 2020-05-28 | 7:28 | 0:32 | 0 | 32 | [5 empty] | Tripped as D/P relay operated At RKL grid end:- Zone-1, Location-34.50Km, IA=3287A, IB=322A, IC=3684A, IG=1823A At Beekay Steel end:-Zone-1, Location-36,.8Km, IA=606.2A, IB=348.7A, IC=635.28A [due to Heavy lightning, thunderstorm and rain ]
|  | 2020-05-29 | 0:56 | 2020-05-29 | 1:28 | 0:32 | 0 | 32 | [5 empty] | Tripped as D/P relay operated RKL grid end. Zone-1, Location- 12.86Km, Tripped phase- C-G IA=117A, IB=273A, IC=4845A, IG=2.342kA [due to Heavy lightning, winderstorm and rain]
|  | 2020-05-29 | 17:39 | 2020-05-29 | 18:01 | 0:22 | 0 | 22 | [5 empty] | Tripped as D/P relay operated with following indications at RKL grid end: Zone-1, Location-27.13Km, Tripped phase- A-G, IA=3.563kA, IB=263A, IC=4.145kA, IG=2.342kA [Due to thunderstorm]
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
|  | 2020-06-06 | 17:11 | 2020-06-06 | 17:30 | 0:19 | 0 | 19 | [5 empty] | At Rourkela end:-DP, Z1, 35.88km, C Phase-G IA=153A, IB=293A, IC=2434A, IG=1994A. At Beekay steel end:-DP, Z1, 28.31km, IA=192.8A, IB=298.9A, IC=347.9A.
|  | 2020-07-04 | 13:20 | 2020-07-04 | 18:12 | 0:24 | 0 | 24 | [5 empty] | 220kV I/C failed at joda Grid S/S
|  | 2020-07-16 | 13:39 | 2020-07-16 | 13:52 | 0:13 | 0 | 13 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid end. Zone-1; Location-0.53Km IA=195A, IB=8497A, IC=184A,IG=8402A
|  | 2020-09-17 | 17:19 | 2020-09-17 | 17:45 | 0:26 | 0 | 22 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault type- ABC, Zone- I, Location- 2.75KM, IA- 2.25KA, IB-7.43KA, IC- 8.43KA, IG-6.69KA
|  | 2020-10-10 | 22:37 | 2020-10-10 | 3:24 | 4:47 | 4 | 47 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault Phase- AC, Zone- I, Location- 0.75KM, IA- 7.331KA, IB- 244A, IC- 7.476KA [B-Phase jumper snapped in gantry tower of Joda Grid S/S.]
|  | 2020-12-17 | 16:47 | 2020-12-17 | 21:05 | 4:18 | 4 | 18 | [5 empty] | Tripped on E/F due to B-ph CT jumper snap at Nalda RTSS.
|  | 2020-12-19 | 07:43 | 2020-12-19 | 19:04 | 11:21 | 11 | 21 | [5 empty] | Tripped at RKL on E/F with following relay indications: Ia=345.7A; Ib=5.88kA; Ic=264.3A: In=5.273kA [Y-ph Jumper snapped at Loc-38 of RKL jurisdiction]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
154 | 132kV Arya Iron & Steel- BRPL |  |  |  |  | 1899-12-31 02:28 | 37 | 57 | [7 empty] | 9.008 | 8760 | 99.57% | 341.8536 | 78910.08
|  | 04.04.20 | 13:02 | 04.04.20 | 13:20 | 0:18 | 0 | 18 | [5 empty] | Tripped on E/F at Barbil end
|  | 24.04.20 | 12:48 | 24.04.20 | 13:03 | 0:15 | 0 | 15 | [5 empty] | Tripped at Barbil end
|  | 2020-05-28 | 19:52 | 2020-05-28 | 20:14 | 0:22 | 0 | 22 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped, Zone-01, F.D- 89.61KM, F.L- L2-L3, Fault Current :- IL1-79.37A, IL2- 2270.84A, IL3-1392.12A, IN-1345.99A
|  | 2020-05-28 | 7:46 | 2020-05-28 | 7:53 | 0:07 | 0 | 7 | [5 empty] | Tripped as D/P relay operated with following indications at Joda grid end: Zone-1,Location- 1.48Km,Tripped phase- A-G IA=5570A, IB=256A, IC=306A, IN=1A, IG=5009A [due to Heavy lightning, thunderstorm and rain ]
|  | 2020-05-10 | 16:47 | 2020-05-10 | 17:05 | 0:18 | 0 | 18 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid end: Zone-1, Location-31.18Km, Tripped phase- C-G IA=97A, IB=250A, IC=2724A, IG=2415A [Due to heavy lightning & rain]
|  | 2020-05-16 | 17:05 | 2020-05-16 | 17:10 | 0:05 | 0 | 5 | [5 empty] | 132 KV Barbil - Bolani-Beekay Steel fdr tripped at Beekay Steel end due to E/F
|  | 2020-05-25 | 8:42 | 2020-05-25 | 9:16 | 0:34 | 0 | 34 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid End: Zone-1, Location-4.90Km, IA=8939, IB=8760A, IC=190A, IG=13A
|  | 2020-05-28 | 6:56 | 2020-05-28 | 7:28 | 0:32 | 0 | 32 | [5 empty] | Tripped as D/P relay operated At RKL grid end:- Zone-1, Location-34.50Km, IA=3287A, IB=322A, IC=3684A, IG=1823A At Beekay Steel end:-Zone-1, Location-36,.8Km, IA=606.2A, IB=348.7A, IC=635.28A [due to Heavy lightning, thunderstorm and rain ]
|  | 2020-05-29 | 0:56 | 2020-05-29 | 1:28 | 0:32 | 0 | 32 | [5 empty] | Tripped as D/P relay operated RKL grid end. Zone-1, Location- 12.86Km, Tripped phase- C-G IA=117A, IB=273A, IC=4845A, IG=2.342kA [due to Heavy lightning, winderstorm and rain]
|  | 2020-05-29 | 17:39 | 2020-05-29 | 18:01 | 0:22 | 0 | 22 | [5 empty] | Tripped as D/P relay operated with following indications at RKL grid end: Zone-1, Location-27.13Km, Tripped phase- A-G, IA=3.563kA, IB=263A, IC=4.145kA, IG=2.342kA [Due to thunderstorm]
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
|  | 2020-06-06 | 17:11 | 2020-06-06 | 17:30 | 0:19 | 0 | 19 | [5 empty] | At Rourkela end:-DP, Z1, 35.88km, C Phase-G IA=153A, IB=293A, IC=2434A, IG=1994A. At Beekay steel end:-DP, Z1, 28.31km, IA=192.8A, IB=298.9A, IC=347.9A.
|  | 2020-07-04 | 13:20 | 2020-07-04 | 18:12 | 0:24 | 0 | 24 | [5 empty] | 220kV I/C failed at joda Grid S/S
|  | 2020-07-16 | 13:39 | 2020-07-16 | 13:52 | 0:13 | 0 | 13 | [5 empty] | Tripped as D/P Relay operated with following indications at RKL Grid end. Zone-1; Location-0.53Km IA=195A, IB=8497A, IC=184A,IG=8402A
|  | 2020-09-17 | 17:19 | 2020-09-17 | 17:45 | 0:26 | 0 | 22 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault type- ABC, Zone- I, Location- 2.75KM, IA- 2.25KA, IB-7.43KA, IC- 8.43KA, IG-6.69KA
|  | 2020-10-10 | 22:37 | 2020-10-10 | 3:24 | 4:47 | 4 | 47 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault Phase- AC, Zone- I, Location- 0.75KM, IA- 7.331KA, IB- 244A, IC- 7.476KA [B-Phase jumper snapped in gantry tower of Joda Grid S/S.]
|  | 2020-12-17 | 16:47 | 2020-12-17 | 21:05 | 4:18 | 4 | 18 | [5 empty] | Tripped on E/F due to B-ph CT jumper snap at Nalda RTSS.
|  | 2020-12-19 | 07:43 | 2020-12-19 | 19:04 | 11:21 | 11 | 21 | [5 empty] | Tripped at RKL on E/F with following relay indications: Ia=345.7A; Ib=5.88kA; Ic=264.3A: In=5.273kA [Y-ph Jumper snapped at Loc-38 of RKL jurisdiction]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
155 | 132kV Nalda-Beekay Steel |  |  |  |  | 0.85139 | 32 | 26 | [7 empty] | 5.4 | 8760 | 99.63% | 175.14 | 47304
|  | 2020-10-10 | 22:37 | 2020-10-10 | 3:24 | 4:47 | 4 | 47 | [5 empty] | Tripped at Joda Grid S/S end due to D/P relay operation at Joda Grid S/S end with following relay indication:- Fault Phase- AC, Zone- I, Location- 0.75KM, IA- 7.331KA, IB- 244A, IC- 7.476KA [B-Phase jumper snapped in gantry tower of Joda Grid S/S.]
|  | 2020-12-17 | 16:47 | 2020-12-17 | 21:05 | 4:18 | 4 | 18 | [5 empty] | Tripped on E/F due to B-ph CT jumper snap at Nalda RTSS.
|  | 2020-12-19 | 07:43 | 2020-12-19 | 19:04 | 11:21 | 11 | 21 | [5 empty] | Tripped at RKL on E/F with following relay indications: Ia=345.7A; Ib=5.88kA; Ic=264.3A: In=5.273kA [Y-ph Jumper snapped at Loc-38 of RKL jurisdiction]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
156 | 132kV Beekay Steel - Bhalulata |  |  |  |  | 0.65208 | 15 | 39 | [7 empty] | 27 | 8760 | 99.82% | 422.55 | 236520
|  | 2020-12-17 | 16:47 | 2020-12-17 | 21:05 | 4:18 | 4 | 18 | [5 empty] | Tripped on E/F due to B-ph CT jumper snap at Nalda RTSS.
|  | 2020-12-19 | 07:43 | 2020-12-19 | 19:04 | 11:21 | 11 | 21 | [5 empty] | Tripped at RKL on E/F with following relay indications: Ia=345.7A; Ib=5.88kA; Ic=264.3A: In=5.273kA [Y-ph Jumper snapped at Loc-38 of RKL jurisdiction]
157 | 132 kV Aska New -Chatrapur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 48.8 | 8760 | 100% | 0 | 427488
158 | 132 kV Aska-Aska New-II |  |  |  |  | 0.098611 | 13 | 30 | [7 empty] | 6.98 | 8760 | 99.85% | 94.23 | 61144.8
|  | 2020-05-01 | 13:25 | 2020-05-01 | 13:42 | 0:17 | 0 | 17 | [5 empty] | E/F on B-Ph
|  | 2020-06-27 | 13:55 | 2020-06-27 | 15:10 | 1:15 | 0 | 23 | [5 empty] | B PH TO E/F,Z-1,D=1.2KM at bhanjanagar end.
|  | 2020-07-15 | 19:43 | 2020-07-15 | 19:56 | 0:13 | 0 | 13 | [5 empty] | BACKUP RELAY: RPH O/C, IR=1.16 KA, DP RELAY DIDN’T OPERATE. BREAKER DIDN’T TRIP AT ASKANEW END
|  | 2020-08-01 | 14:15 | 2020-08-01 | 14:52 | 0:37 | 0 | 37 | [5 empty] | AN TRIP, ZONE-1 , D: 726.5 MTR, IA= 8.091 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
159 | 132kV Aska New- Berhampur |  |  |  |  | 0.0048611 | 0 | 7 | [7 empty] | 40 | 8760 | 100% | 4.6667 | 350400
|  | 2020-05-26 | 13:13 | 2020-05-26 | 13:20 | 0:07 | 0 | 7 | [5 empty] | TRIPPED ON O/C
160 | 132kV Aska- Aska New- I |  |  |  |  | 0.098611 | 13 | 30 | [7 empty] | 6.66 | 8760 | 99.85% | 89.91 | 58341.6
|  | 2020-05-01 | 13:25 | 2020-05-01 | 13:42 | 0:17 | 0 | 17 | [5 empty] | E/F on B-Ph
|  | 2020-06-27 | 13:55 | 2020-06-27 | 15:10 | 1:15 | 0 | 23 | [5 empty] | B PH TO E/F,Z-1,D=1.2KM at bhanjanagar end.
|  | 2020-07-15 | 19:43 | 2020-07-15 | 19:56 | 0:13 | 0 | 13 | [5 empty] | BACKUP RELAY: RPH O/C, IR=1.16 KA, DP RELAY DIDN’T OPERATE. BREAKER DIDN’T TRIP AT ASKANEW END
|  | 2020-08-01 | 14:15 | 2020-08-01 | 14:52 | 0:37 | 0 | 37 | [5 empty] | AN TRIP, ZONE-1 , D: 726.5 MTR, IA= 8.091 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
161 | 132 kV Aska-Purusottampur |  |  |  |  | 0.025694 | 0 | 37 | [7 empty] | 28.21 | 8760 | 99.99% | 17.3962 | 247119.6
|  | 2020-08-01 | 14:15 | 2020-08-01 | 14:52 | 0:37 | 0 | 37 | [5 empty] | AN TRIP, ZONE-1 , D: 726.5 MTR, IA= 8.091 KA
162 | 132 kV Badagada (Kesura) -Nimapara |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 36.27 | 8760 | 100% | 4.836 | 317725.2
|  | 2020-07-15 | 09:58 | 2020-07-15 | 10:06 | 0:08 | 0 | 8 | [5 empty] | DP Relay Z-1, Distance 32.92 KM, Ia- 1.97 KA , Y phase-N, at Kesura End
163 | 132 kV Balasore-Udala |  |  |  |  | 1899-12-31 05:17 | 16 | 37 | [7 empty] | 70.86 | 8760 | 99.81% | 1177.457 | 620733.6
|  | 2020-04-26 | 4:26 | 2020-04-26 | 5:00 | 0:34 | 0 | 34 | [5 empty] | At Balasore end: DP relay-SEL 311C : B-G-T, Z-2, 45.87Km, Fault current-1.687KA, Siemens B/U relay: Y-Ph, E/F, 1.63KA At Udala end:Z-1, Y-Ph, 7.8Km, Fault Current- 0.19KA
|  | 2020-05-20 | 12:44 | 2020-05-20 | 18:35 | 5:51 | 0 | 59 | [5 empty] | Tripped due to snapping of B Ph wavetrap jumper.
|  | 2020-07-01 | 15:31 | 2020-07-01 | 15:58 | 0:27 | 0 | 27 | [5 empty] | At Udala-Y-Phase -G,Distance - 18.8 Km ,Zone-1, Ia-0.16KA,Ib-0.15 KA,Ic-0.12KA. Zone-1,Distance -31.6 Km, If- 2239 Amp
|  | 2020-08-26 | 17:15 | 2020-08-27 | 13:58 | 20:43 | 0 | 55 | [5 empty] | At Balasore end: DP RELAY:- Z-I, A-B-C-T, 22.21Km, Fault current: Ia-4117A, Ib-4590A, Ic-3898A . B/U: Gen Trip, O/C, R-Ph, Y-Ph, B-Ph, Ir- 4.04KA, Iy-4.58KA, Ib-3.96KA [Suspension insulator string punctured at Loc no-76 ( R & Y) and 77 ( R, Y & B) whcih were replaced]
|  | 2020-09-07 | 20:05 | 2020-09-07 | 20:21 | 0:16 | 0 | 16 | [5 empty] | Relay Indication at Balasore Grid end DP Relay:SEL 311C, Distance - 42.13 Km ,Zone-1, Y-Phase G., 1- 232A,IL2- 1754 A,IL3-68A. Relay Indication at Udala Grid end Distance - 14 Km ,Zone-1, Y-Phase G,Ia-.23KA, Ib-0.13K A,Ic- 0.08KA.[heavy lightning & rain ]
|  | 2020-10-13 | 13:34 | 2020-10-13 | 14:11 | 0:37 | 0 | 37 | [5 empty] | At Balasore end: B-PH TO G (A,B,C) ,Zone-2, Distance : 52.15KM,Fault current : Ib= 1.476KA. B/U : Y-PH O/C, E/F ,Fault current : Iy= 1.45KA [heavy lightning & rain ] At Udala end: Zone-, B-G, Distance:
|  | 2021-01-05 | 12:25 | 2021-01-05 | 13:14 | 0:49 | 0 | 49 | [5 empty] | trip on B/U relay
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
164 | 132 kV Betanati-Udala |  |  |  |  | 1899-12-31 06:58 | 19 | 51 | [7 empty] | 49.89 | 8760 | 99.77% | 990.3165 | 437036.4
|  | 2020-04-18 | 16:28 | 2020-04-18 | 17:27 | 0:59 | 0 | 59 | [5 empty] | At Baripada end: Rph,Z1,dist-9KM At Udala end: Rph,Z1,dist-24KM, Fault current-2.809KA At Balasore end:DP relay-SEL 311C : A-G-T, Z-1, 24Km, Fault current- 2809A At Udala end:Z-1, R-Ph, 09 Km,
|  | 2020-04-26 | 4:26 | 2020-04-26 | 5:00 | 0:34 | 0 | 34 | [5 empty] | At Baripada end: Y-ph,Z1,dist- 7.8KM At Udala end: Y-ph,Z2,dist- 45.87KM, Fault Current-1.687KA
|  | 2020-05-20 | 12:44 | 2020-05-20 | 18:35 | 5:51 | 0 | 59 | [5 empty] | Tripped due to snapping of B Ph wavetrap jumper.
|  | 2020-07-01 | 15:31 | 2020-07-01 | 15:59 | 00:28 | 0 | 28 | [5 empty] | Tripped at Udala Grid
|  | 2020-08-26 | 17:15 | 2020-08-27 | 13:58 | 20:43 | 0 | 55 | [5 empty] | At Balasore end: DP RELAY:- Z-I, A-B-C-T, 22.21Km, Fault current: Ia-4117A, Ib-4590A, Ic-3898A . B/U: Gen Trip, O/C, R-Ph, Y-Ph, B-Ph, Ir- 4.04KA, Iy-4.58KA, Ib-3.96KA [Suspension insulator string punctured at Loc no-76 ( R & Y) and 77 ( R, Y & B) whcih were replaced]
|  | 2020-08-26 | 18:14 | 2020-08-26 | 19:18 | 1:04 | 1 | 4 | [5 empty] | Tripped on Back up relay at Baripda end.
|  | 2020-08-26 | 20:00 | 2020-08-26 | 20:46 | 00:46 | 0 | 46 | [5 empty] | Tripped on Back up relay at Baripda end.
|  | 2020-08-26 | 20:56 | 2020-08-26 | 21:20 | 00:24 | 0 | 24 | [5 empty] | Tripped on Back up relay at Baripda end.
|  | 2020-09-07 | 20:05 | 2020-09-07 | 20:26 | 0:21 | 0 | 16 | [5 empty] | Relay Indication at Balasore Grid end DP Relay:SEL 311C, Distance - 42.13 Km ,Zone-1, Y-Phase G., 1- 232A,IL2- 1754 A,IL3-68A. Relay Indication at Udala Grid end Distance - 14 Km ,Zone-1, Y-Phase G,Ia-.23KA, Ib-0.13K A,Ic- 0.08KA.[heavy lightning & rain ]
|  | 2020-10-13 | 13:34 | 2020-10-13 | 14:11 | 0:37 | 0 | 37 | [5 empty] | At Balasore end: B-PH TO G (A,B,C) ,Zone-2, Distance : 52.15KM,Fault current : Ib= 1.476KA. B/U : Y-PH O/C, E/F ,Fault current : Iy= 1.45KA [heavy lightning & rain ] At Udala end: Zone-, B-G, Distance:
|  | 2021-01-05 | 12:25 | 2021-01-05 | 13:14 | 0:49 | 0 | 49 | [5 empty] | trip on B/U relay
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
165 | 132 kV Baripada- Betanati |  |  |  |  | 0.097917 | 14 | 44 | [7 empty] | 24.43 | 8760 | 99.83% | 359.9353 | 214006.8
|  | 2020-04-18 | 16:28 | 2020-04-18 | 17:27 | 0:59 | 0 | 59 | [5 empty] | At Baripada end: Rph,Z1,dist-9KM At Udala end: Rph,Z1,dist-24KM, Fault current-2.809KA At Balasore end:DP relay-SEL 311C : A-G-T, Z-1, 24Km, Fault current- 2809A At Udala end:Z-1, R-Ph, 09 Km,
|  | 2020-04-26 | 4:26 | 2020-04-26 | 5:00 | 0:34 | 0 | 34 | [5 empty] | At Baripada end: Y-ph,Z1,dist- 7.8KM At Udala end: Y-ph,Z2,dist- 45.87KM, Fault Current-1.687KA
|  | 2020-07-01 | 15:31 | 2020-07-01 | 15:59 | 00:28 | 0 | 28 | [5 empty] | Tripped at Betnoti Grid
|  | 2020-08-26 | 18:14 | 2020-08-26 | 18:41 | 0:27 | 0 | 27 | [5 empty] | Baripada Grid End Relay Details Back Up Relay Details E/F Bkr Fail INT IE – Trip , PU Time- 191 ms,Trip Time- 145 ms, IL1- O.07 KA, IL2 – 0.06 KA, IL3 – 0.01 KA
|  | 2020-09-07 | 20:05 | 2020-09-07 | 20:26 | 0:21 | 0 | 16 | [5 empty] | Relay Indication at Balasore Grid end DP Relay:SEL 311C, Distance - 42.13 Km ,Zone-1, Y-Phase G., 1- 232A,IL2- 1754 A,IL3-68A. Relay Indication at Udala Grid end Distance - 14 Km ,Zone-1, Y-Phase G,Ia-.23KA, Ib-0.13K A,Ic- 0.08KA.[heavy lightning & rain ]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
166 | 132 kV Balasore-Basta |  |  |  |  | 0.097222 | 0 | 30 | [7 empty] | 32.51 | 8760 | 99.99% | 16.255 | 284787.6
|  | 2020-09-16 | 08:31 | 2020-09-16 | 10:51 | 2:20 | 0 | 30 | [5 empty] | Tripped on Distance Protection, Y ph to GND , DP Operated; Zone-1, Loc-18 KM, Iy= 1.873 A
167 | 132 kV Balasore- Balasore Alloy |  |  |  |  | 0.0375 | 0 | 54 | [7 empty] | 6.45 | 8760 | 99.99% | 5.805 | 56502
|  | 2020-05-28 | 2:55 | 2020-05-28 | 3:49 | 0:54 | 0 | 54 | [5 empty] | Numerical B/U relay: STARTED PHASE:N, TRIPPED PHASE:N, Ia= 1.156KA, Ib=1.0205KA, Ic=1.172KA
168 | 132 kV Balasore-Birla Tyre |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.598 | 8760 | 100% | 0 | 22758.48
169 | 132 kV Balasore-Soro |  |  |  |  | 1899-12-31 02:55 | 14 | 48 | [7 empty] | 29.6 | 8760 | 99.83% | 438.08 | 259296
|  | 2020-05-10 | 13:52 | 2020-05-10 | 14:13 | 0:21 | 0 | 21 | [5 empty] | At Balasore end: DP realy: Z-2, Y-G, Iy-2.063KA, 35.15Km [Due to heavy lightning & rain]
|  | 2020-08-02 | 12:08 | 2020-08-02 | 16:05 | 3:17 | 0 | 37 | [5 empty] | B-N, fault distance-19.40Km, fault current-3.713KA
|  | 2020-08-03 | 14:05 | 2020-08-03 | 17:23 | 03:18 | 0 | 49 | [5 empty] | Y-N, fault distance-9.943Km, fault current-5.842KA
|  | 2020-09-11 | 12:28 | 2020-09-12 | 11:02 | 22:34 | 0 | 18 | [5 empty] | At Balasore end: Y-N,Z-2, fault distance-40.60Km, fault current-2.301KA
|  | 2020-10-08 | 11:13 | 2020-10-08 | 11:56 | 0:43 | 0 | 43 | [5 empty] | Main protection operated with Zone- 1 at Bdk end, Fault loop L2-L3, Fault Current-L1-187.93A,L2-2931.2A,L3- 2662.78A,Fault Distance-29.263KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
170 | 132 kV Balasore-Somnathpur |  |  |  |  | 0.00625 | 0 | 9 | [7 empty] | 4 | 8760 | 100% | 0.6 | 35040
|  | 2020-06-28 | 8:44 | 2020-06-28 | 8:53 | 0:09 | 0 | 9 | [5 empty] | At Balasore end: ABB REX: Trip L1, L2, L3.[All 3 nos of LA failed in 33KV HIL fdr at Somanathpur end]
171 | 132 kV Somnathpur-Stork |  |  |  |  | 0.040278 | 0 | 58 | [7 empty] | 0.1 | 8760 | 99.99% | 0.096667 | 876
|  | 2020-04-27 | 22:59 | 2020-04-27 | 23:48 | 0:49 | 0 | 49 | [5 empty] | At Somnathpur end: O/C &E/F Fault current: I1=1.35KA,I2=1.42KA,I3=1.31KA
|  | 2020-06-28 | 8:44 | 2020-06-28 | 8:53 | 0:09 | 0 | 9 | [5 empty] | At Balasore end: ABB REX: Trip L1, L2, L3.[All 3 nos of LA failed in 33KV HIL fdr at Somanathpur end]
172 | 132 kV Somnathpur-EMAMI |  |  |  |  | 0.00625 | 0 | 9 | [7 empty] | 6 | 8760 | 100% | 0.9 | 52560
|  | 2020-06-28 | 8:44 | 2020-06-28 | 8:53 | 0:09 | 0 | 9 | [5 empty] | At Balasore end: ABB REX: Trip L1, L2, L3.[All 3 nos of LA failed in 33KV HIL fdr at Somanathpur end]
173 | 132kV Balugaon-Chandpur |  |  |  |  | 0.049306 | 1 | 11 | [7 empty] | 43.12 | 8760 | 99.99% | 51.0253 | 377731.2
|  | 2020-08-13 | 15:01 | 2020-08-13 | 16:12 | 1:11 | 1 | 11 | [5 empty] | DP relay indication at Chatrapur end Y-Ph, B-Ph, Zone-1, Distance=46.22 Km, Ir=134.4A, Iy=2.005 KA, Ib=1.844 KA
174 | 132 kv Balugaon-Solari(T) |  |  |  |  | 0.049306 | 1 | 11 | [7 empty] | 14.1 | 8760 | 99.99% | 16.685 | 123516
|  | 2020-08-13 | 15:01 | 2020-08-13 | 16:12 | 1:11 | 1 | 11 | [5 empty] | DP relay indication at Chatrapur end Y-Ph, B-Ph, Zone-1, Distance=46.22 Km, Ir=134.4A, Iy=2.005 KA, Ib=1.844 KA
175 | 132 kv Banki-Nuapatna |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.61 | 8760 | 100% | 0 | 180543.6
176 | 132 kV Bargarh-ACC Ckt I |  |  |  |  | 0.072917 | 14 | 49 | [7 empty] | 2.87 | 8760 | 99.83% | 42.5238 | 25141.2
|  | 2020-05-28 | 14:15 | 2020-05-28 | 14:20 | 0:05 | 0 | 5 | [5 empty] | OVER CURRENT
|  | 2020-06-16 | 14:06 | 2020-06-16 | 17:34 | 0:28 | 0 | 28 | [5 empty] | E/F
|  | 2020-06-24 | 10:56 | 2020-06-24 | 11:01 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-07-10 | 04:16 | 2020-07-10 | 04:25 | 00:09 | 0 | 9 | [5 empty] | E/F
|  | 2020-07-19 | 10:03 | 2020-07-19 | 10:55 | 00:52 | 0 | 52 | [5 empty] | E/F
|  | 2020-07-28 | 12:22 | 2020-07-28 | 12:25 | 00:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-08-02 | 00:05 | 2020-08-02 | 00:11 | 0:06 | 0 | 6 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-08-02 | 23:56 | 2020-08-03 | 0:03 | 0:07 | 0 | 7 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-08-03 | 00:16 | 2020-08-03 | 00:20 | 0:04 | 0 | 4 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-08-06 | 11:12 | 2020-08-06 | 11:18 | 0:06 | 0 | 6 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-09-17 | 13:59 | 2020-09-17 | 14:21 | 0:22 | 0 | 22 | [5 empty] | OVERCURRENT [33 Kv Main Bus B- Ph Disc Insulator Punctured]
|  | 2020-09-30 | 19:58 | 2020-09-30 | 20:20 | 0:22 | 0 | 22 | [5 empty] | EARTHFAULT [DUE TO 33 KV B-PH LA BRUST OF 40 MVA TFR-III]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
177 | 132 kV Bargarh-ACC Ckt II |  |  |  |  | 0.072917 | 14 | 49 | [7 empty] | 2.87 | 8760 | 99.83% | 42.5238 | 25141.2
|  | 2020-05-28 | 14:15 | 2020-05-28 | 14:20 | 0:05 | 0 | 5 | [5 empty] | OVER CURRENT
|  | 2020-06-16 | 14:06 | 2020-06-16 | 17:34 | 0:28 | 0 | 28 | [5 empty] | E/F
|  | 2020-06-24 | 10:56 | 2020-06-24 | 11:01 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-07-10 | 04:16 | 2020-07-10 | 04:25 | 00:09 | 0 | 9 | [5 empty] | E/F
|  | 2020-07-19 | 10:03 | 2020-07-19 | 10:55 | 00:52 | 0 | 52 | [5 empty] | E/F
|  | 2020-07-28 | 12:22 | 2020-07-28 | 12:25 | 00:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-08-02 | 00:05 | 2020-08-02 | 00:11 | 0:06 | 0 | 6 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-08-02 | 23:56 | 2020-08-03 | 0:03 | 0:07 | 0 | 7 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-08-03 | 00:16 | 2020-08-03 | 00:20 | 0:04 | 0 | 4 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-08-06 | 11:12 | 2020-08-06 | 11:18 | 0:06 | 0 | 6 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-09-17 | 13:59 | 2020-09-17 | 14:21 | 0:22 | 0 | 22 | [5 empty] | OVERCURRENT [33 Kv Main Bus B- Ph Disc Insulator Punctured]
|  | 2020-09-30 | 19:58 | 2020-09-30 | 20:20 | 0:22 | 0 | 22 | [5 empty] | EARTHFAULT [DUE TO 33 KV B-PH LA BRUST OF 40 MVA TFR-III]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
178 | 132 kV Bargarh-Katapalli |  |  |  |  | 0.072917 | 14 | 49 | [7 empty] | 31.92 | 8760 | 99.83% | 472.948 | 279619.2
|  | 2020-05-28 | 14:15 | 2020-05-28 | 14:20 | 0:05 | 0 | 5 | [5 empty] | OVER CURRENT
|  | 2020-06-16 | 14:06 | 2020-06-16 | 17:34 | 0:28 | 0 | 28 | [5 empty] | E/F
|  | 2020-06-24 | 10:56 | 2020-06-24 | 11:01 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-07-10 | 04:16 | 2020-07-10 | 04:25 | 00:09 | 0 | 9 | [5 empty] | E/F
|  | 2020-07-19 | 10:03 | 2020-07-19 | 10:55 | 00:52 | 0 | 52 | [5 empty] | E/F
|  | 2020-07-28 | 12:22 | 2020-07-28 | 12:25 | 00:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-08-02 | 00:05 | 2020-08-02 | 00:11 | 0:06 | 0 | 6 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-08-02 | 23:56 | 2020-08-03 | 0:03 | 0:07 | 0 | 7 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-08-03 | 00:16 | 2020-08-03 | 00:20 | 0:04 | 0 | 4 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-08-06 | 11:12 | 2020-08-06 | 11:18 | 0:06 | 0 | 6 | [5 empty] | OVERCURRENT & tripped at bargarh end.
|  | 2020-09-17 | 13:59 | 2020-09-17 | 14:21 | 0:22 | 0 | 22 | [5 empty] | OVERCURRENT [33 Kv Main Bus B- Ph Disc Insulator Punctured]
|  | 2020-09-30 | 19:58 | 2020-09-30 | 20:20 | 0:22 | 0 | 22 | [5 empty] | EARTHFAULT [DUE TO 33 KV B-PH LA BRUST OF 40 MVA TFR-III]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
179 | 132 kV Bargarh New-Ghens Ckt -I |  |  |  |  | 0.0083333 | 0 | 12 | [7 empty] | 29.13 | 8760 | 100% | 5.826 | 255178.8
|  | 2020-10-24 | 13:18 | 2020-10-24 | 13:30 | 0:12 | 0 | 12 | [5 empty] | Tripped on distance protection.
180 | 132 kV Bargarh New-Ghens Ckt -II |  |  |  |  | 0.0083333 | 0 | 12 | [7 empty] | 29.13 | 8760 | 100% | 5.826 | 255178.8
|  | 2020-10-24 | 13:18 | 2020-10-24 | 13:30 | 0:12 | 0 | 12 | [5 empty] | Tripped on distance protection.
181 | 132kV Baripada-Kuchei PG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.1 | 8760 | 100% | 0 | 27156
182 | 132kV BCMohanty-Bamnipal(Tisco) |  |  |  |  | 0.25903 | 6 | 13 | [7 empty] | 10 | 8760 | 99.93% | 62.1667 | 87600
|  | 2020-05-01 | 23:59 | 2020-05-02 | 5:22 | 5:23 | 5 | 23 | [5 empty] | Tripped due to bursting of R Ph. LA in the Incomer Fdr at BC Mohanty S/S.
|  | 2020-06-01 | 14:41 | 2020-06-01 | 15:31 | 0:50 | 0 | 50 | [5 empty] | E/F
183 | 132kV BCMohanty-Tomka (T) |  |  |  |  | 0.26667 | 6 | 13 | [7 empty] | 11.46 | 8760 | 99.93% | 71.243 | 100389.6
|  | 2020-05-01 | 23:59 | 2020-05-02 | 5:22 | 5:23 | 5 | 23 | [5 empty] | Tripped due to bursting of R Ph. LA in the Incomer Fdr at BC Mohanty S/S.
|  | 2020-06-01 | 14:44 | 2020-06-01 | 15:45 | 1:01 | 0 | 50 | [5 empty] | E/F
184 | 132kV Berhampur-Digapahandi |  |  |  |  | 0.42153 | 14 | 46 | [7 empty] | 31.48 | 8760 | 99.83% | 464.8547 | 275764.8
|  | 2020-05-26 | 13:13 | 2020-05-26 | 13:20 | 0:07 | 0 | 7 | [5 empty] | TRIPPED ON O/C
|  | 2020-05-15 | 6:19 | 2020-05-15 | 6:37 | 0:18 | 0 | 18 | [5 empty] | DP relay, Zone-1, Digapahandi end 19.07KM
|  | 2020-05-18 | 12:06 | 2020-05-18 | 17:30 | 5:24 | 0 | 56 | [5 empty] | Tripped. [B Ph Jumper snap at Loc- 50. ]
|  | 2020-08-20 | 12:06 | 2020-08-20 | 12:10 | 0:04 | 0 | 4 | [5 empty] | No tripping at Berhampur End. Auto failed at Narendrapur End.Power supply failure from Narendrapur.
|  | 2020-09-27 | 16:38 | 2020-09-27 | 16:59 | 0:21 | 0 | 21 | [5 empty] | DP relay operated, master trip optd. Zone-1 R-phase fault loc. 302.3m [Heavy rain outside]
|  | 2021-03-04 | 18:58 | 2021-03-04 | 22:51 | 3:53 | 1 | 0 | [5 empty] | Differential O/C E/F @ Digapahandi
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
185 | 132kV Bhadrak-FACOR |  |  |  |  | 0.10556 | 14 | 7 | [7 empty] | 4.564 | 8760 | 99.84% | 64.4285 | 39980.64
|  | 2020-05-22 | 14:23 | 2020-05-22 | 14:41 | 0:18 | 0 | 18 | [5 empty] | Tripped on 86 A & E/F
|  | 2020-08-09 | 03:55 | 2020-08-09 | 04:43 | 0:48 | 0 | 48 | [5 empty] | Tripped at Balasore end.
|  | 2020-08-12 | 16:41 | 2020-08-12 | 16:46 | 0:05 | 0 | 5 | [5 empty] | LBB protection.
|  | 2020-08-21 | 15:46 | 2020-08-21 | 15:49 | 0:03 | 0 | 3 | [5 empty] | LBB Trip relay,96 OPTD
|  | 2021-02-02 | 13:22 | 2021-02-02 | 14:40 | 1:18 | 0 | 53 | [5 empty] | At Balasore end: Siemens B/U relay: B-Ph O/C, E/F, Fault current: IL3=1.33KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
186 | 132kV Bhadrak-Dhamara Ckt-I |  |  |  |  | 0.50139 | 23 | 37 | [7 empty] | 63.9 | 8760 | 99.73% | 1509.105 | 559764
|  | 2020-05-20 | 2:24 | 2020-05-20 | 13:00 | 10:36 | 10 | 36 | [5 empty] | Tripped on zone-I,Dist=52.99 km,IA=1.788 KA,IB=322.9A,IC=352.3A
|  | 2020-08-12 | 16:41 | 2020-08-12 | 16:46 | 0:05 | 0 | 5 | [5 empty] | LBB protection.
|  | 2020-08-21 | 15:46 | 2020-08-21 | 15:49 | 0:03 | 0 | 3 | [5 empty] | LBB Trip relay,96 OPTD
|  | 2021-02-02 | 13:22 | 2021-02-02 | 14:40 | 1:18 | 0 | 53 | [5 empty] | At Balasore end: Siemens B/U relay: B-Ph O/C, E/F, Fault current: IL3=1.33KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
187 | 132kV Bhadrak-Dhamara Ckt-II |  |  |  |  | 0.059722 | 13 | 1 | [7 empty] | 35.3 | 8760 | 99.85% | 459.4883 | 309228
|  | 2020-08-12 | 16:41 | 2020-08-12 | 16:46 | 0:05 | 0 | 5 | [5 empty] | LBB protection.
|  | 2020-08-21 | 15:46 | 2020-08-21 | 15:49 | 0:03 | 0 | 3 | [5 empty] | LBB Trip relay,96 OPTD
|  | 2021-02-02 | 13:22 | 2021-02-02 | 14:40 | 1:18 | 0 | 53 | [5 empty] | At Balasore end: Siemens B/U relay: B-Ph O/C, E/F, Fault current: IL3=1.33KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
188 | 132kV Bhadrak-Bhadrak Traction |  |  |  |  | 0.10694 | 14 | 9 | [7 empty] | 8.086 | 8760 | 99.84% | 114.4169 | 70833.36
|  | 2020-08-09 | 03:55 | 2020-08-09 | 04:43 | 0:48 | 0 | 48 | [5 empty] | Tripped at Balasore end.
|  | 2020-08-12 | 16:41 | 2020-08-12 | 16:46 | 0:05 | 0 | 5 | [5 empty] | LBB protection.
|  | 2020-08-21 | 15:46 | 2020-08-21 | 15:49 | 0:03 | 0 | 3 | [5 empty] | LBB Trip relay,96 OPTD
|  | 2020-09-06 | 12:20 | 2020-09-06 | 12:40 | 0:20 | 0 | 20 | [5 empty] | General Trip,Y-Ph and B-Ph O/C PU,IL2=0.25 KA,IL3-0.25 KA,Fault loop=L2-L3.
|  | 2021-02-02 | 13:22 | 2021-02-02 | 14:40 | 1:18 | 0 | 53 | [5 empty] | At Balasore end: Siemens B/U relay: B-Ph O/C, E/F, Fault current: IL3=1.33KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
189 | 132kV Bhadrak- Dhamara Port Traction |  |  |  |  | 0.038889 | 12 | 56 | [7 empty] | 35.7 | 8760 | 99.85% | 461.72 | 312732
|  | 2020-08-09 | 03:55 | 2020-08-09 | 04:43 | 0:48 | 0 | 48 | [5 empty] | Tripped at Balasore end.
|  | 2020-08-12 | 16:41 | 2020-08-12 | 16:46 | 0:05 | 0 | 5 | [5 empty] | LBB protection.
|  | 2020-08-21 | 15:46 | 2020-08-21 | 15:49 | 0:03 | 0 | 3 | [5 empty] | LBB Trip relay,96 OPTD
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
190 | 132kV Bhadrak-Jajpur Town |  |  |  |  | 0 | 0 | 0 | [7 empty] | 40.12 | 8760 | 100% | 0 | 351451.2
191 | 132kV Bhanjanagar-Aska-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.32 | 8760 | 100% | 0 | 291883.2
192 | 132kV Bhanjanagar-Aska-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.72 | 8760 | 100% | 0 | 295387.2
193 | 132kV Bhanjanagar- Phulbani |  |  |  |  | 0.098611 | 21 | 24 | [7 empty] | 86.5 | 8652 | 99.75% | 1851.1 | 748398
|  | 13.04.20 | 15:10 | 13.04.20 | 15:35 | 0:25 | 0 | 25 | [5 empty] | At Bhanjanagar end; B-N Trip, Zone- 1 Dist -38.35 kM
|  | 14.04.20 | 12:07 | 14.04.20 | 12:20 | 0:13 | 0 | 13 | [5 empty] | At Bhanjanagar end: CN TRIP, ZONE 1, D : 60.44 KM
|  | 2020-05-20 | 13:32 | 2020-05-20 | 15:03 | 1:31 | 1 | 31 | [5 empty] | Tripped due to B Phase PT burst at B.Nagar Grid S/S.
|  | 2020-08-01 | 12:34 | 2020-08-01 | 18:05 | 05:31 | 5 | 31 | [5 empty] | BCN,Z=1,D=22.35KM IF=.3.05KA
|  | 2020-08-07 | 08:01 | 2020-08-07 | 08:24 | 00:23 | 0 | 23 | [5 empty] | CN,Z-1,D=36.81KM
|  | 2020-08-08 | 09:29 | 2020-08-08 | 10:37 | 01:08 | 1 | 8 | [5 empty] | CN,Z-1,D=34.99KM IF -1964A
|  | 2020-10-13 | 09:45 | 2020-10-13 | 09:58 | 0:13 | 0 | 13 | [5 empty] | O/C R,Y&B TRIP,L1-580A,L2- 670A,L3-720A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
194 | 132kV Bhanjanagar- G. Udaygiri |  |  |  |  | 0 | 0 | 0 | [7 empty] | 53.4 | 108 | 100% | 0 | 5767.2
195 | 132KV G. Udaygiri -Phulbani |  |  |  |  | 0 | 0 | 0 | [7 empty] | 54.5 | 108 | 100% | 0 | 5886
196 | 132kV Pratapsasan -Phulnakhara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.64 | 12 | 100% | 0 | 175.68
197 | 132kV Pratapsasan -Phulnakhara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.64 | 12 | 100% | 0 | 175.68
198 | 132kV Bhubaneswar-Phulnakhara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 22.74 | 8760 | 100% | 0 | 199202.4
199 | 132kV Bhubaneswar-Mancheswar-B UG Cable |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.18 | 2508 | 100% | 0 | 12991.44
200 | 132kV Chandaka-Mancheswar-B UG Cable |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.8 | 8760 | 100% | 0 | 94608
201 | 132kV Bidanasi-BPPL-Chandaka |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35.34 | 5100 | 100% | 0 | 180234
202 | 132kV Bidanasi-Brajabiahripur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.1 | 3660 | 100% | 0 | 36966
203 | 132kV Brajabiharipur-BPPL-Chandaka |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.1 | 3660 | 100% | 0 | 121146
204 | 132 kV Bargarh- Barpali |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20 | 8244 | 100% | 0 | 164880
205 | 132 kV Bargarh- Bargarh New |  |  |  |  | 0 | 0 | 0 | [7 empty] | 26.6 | 516 | 100% | 0 | 13725.6
206 | 132 kV Bargarh New -Barpalli |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.6 | 516 | 100% | 0 | 5469.6
207 | 132 kV Barpalli- New Bolangir |  |  |  |  | 0.0055556 | 13 | 24 | [7 empty] | 59.2 | 8760 | 99.85% | 793.28 | 518592
|  | 08.04.20 | 10:36 | 08.04.20 | 10:40 | 0:04 | 0 | 4 | [5 empty] | Tripped on E/F at Bolangir New end
|  | 2020-05-01 | 15:15 | 2020-05-01 | 15:27 | 0:12 | 0 | 12 | [5 empty] | Tripped on distance protection.
|  | 2020-05-01 | 15:29 | 2020-05-01 | 19:35 | 4:06 | 0 | 6 | [5 empty] | Tripped on distance protection.
|  | 2020-05-20 | 11:51 | 2020-05-20 | 11:58 | 00:07 | 0 | 7 | [5 empty] | At Bolangir N end: DP, Z2, Y-E, 1.812kA, 48.06km.
|  | 2020-05-20 | 11:59 | 2020-05-20 | 12:09 | 00:10 | 0 | 10 | [5 empty] | Tripped on distance protection.
|  | 2020-05-21 | 12:19 | 2020-05-21 | 17:53 | 5:34 | 0 | 39 | [5 empty] | Tripped on distance protection.
|  | 2020-06-05 | 10:57 | 2020-06-05 | 12:35 | 1:38 | 0 | 2 | [5 empty] | Tripped.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-07-30 | 08:39 | 2020-07-30 | 08:40 | 0:01 | 0 | 1 | [5 empty] | Tripped on directional o/c displayed on back up o/c and e/f relay.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
208 | 132 kV Barpalli-Dunguripalli RTSS |  |  |  |  | 0.51528 | 13 | 51 | [7 empty] | 12.8 | 8760 | 99.84% | 177.28 | 112128
|  | 08.04.20 | 10:36 | 08.04.20 | 10:40 | 0:04 | 0 | 4 | [5 empty] | Tripped on E/F at Bolangir New end
|  | 2020-05-01 | 15:15 | 2020-05-01 | 15:27 | 0:12 | 0 | 12 | [5 empty] | Tripped on distance protection.
|  | 2020-05-01 | 15:29 | 2020-05-01 | 19:35 | 4:06 | 0 | 6 | [5 empty] | Tripped on distance protection.
|  | 2020-05-20 | 11:51 | 2020-05-20 | 11:58 | 0:07 | 0 | 7 | [5 empty] | At Bolangir N end: DP, Z2, Y-E, 1.812kA, 48.06km.
|  | 2020-05-20 | 11:59 | 2020-05-20 | 12:09 | 0:10 | 0 | 10 | [5 empty] | Tripped on distance protection.
|  | 2020-05-21 | 12:19 | 2020-05-21 | 17:53 | 5:34 | 0 | 39 | [5 empty] | Tripped on distance protection.
|  | 2020-05-03 | 6:53 | 2020-05-03 | 6:55 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-05-03 | 7:24 | 2020-05-03 | 7:35 | 0:11 | 0 | 11 | [5 empty] | O/C
|  | 2020-05-04 | 4:49 | 2020-05-04 | 4:51 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-05-04 | 6:02 | 2020-05-04 | 6:04 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-05-04 | 8:05 | 2020-05-04 | 8:06 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2020-05-04 | 12:54 | 2020-05-04 | 12:55 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2020-05-04 | 14:32 | 2020-05-04 | 14:37 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2020-05-04 | 14:43 | 2020-05-04 | 14:45 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-05-04 | 21:11 | 2020-05-04 | 21:12 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2020-06-05 | 10:57 | 2020-06-05 | 12:35 | 1:38 | 0 | 2 | [5 empty] | Tripped.
|  | 2020-10-09 | 01:14 | 2020-10-09 | 01:15 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-21 | 21:50 | 2021-01-21 | 21:53 | 0:03 | 0 | 3 | [5 empty] | O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
209 | 132 kV New Bolangir 'T' (on 132 kV Bolangir - Sonepur Line) |  |  |  |  | 0.28125 | 14 | 15 | [7 empty] | 2.011 | 8760 | 99.84% | 28.6568 | 17616.36
|  | 2020-05-02 | 10:08 | 2020-05-02 | 10:13 | 0:05 | 0 | 5 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-05-06 | 13:26 | 2020-05-06 | 13:31 | 0:05 | 0 | 5 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-05-06 | 14:09 | 2020-05-06 | 14:17 | 0:08 | 0 | 8 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-05-04 | 19:05 | 2020-05-04 | 19:10 | 0:05 | 0 | 5 | [5 empty] | Feeder tripped from balangir
|  | 2020-05-04 | 19:31 | 2020-05-04 | 19:36 | 0:05 | 0 | 5 | [5 empty] | Feeder tripped from balangir
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-08-10 | 15:34 | 2020-08-10 | 15:49 | 0:15 | 0 | 15 | [5 empty] | AC Supply failed from New Bolangir
|  | 2020-08-19 | 15:40 | 2020-08-19 | 16:27 | 0:47 | 0 | 47 | [5 empty] | Tripped on Distance protection as well as in o/c and e/f in back up relay.
|  | 2020-09-20 | 13:30 | 2020-09-20 | 13:32 | 0:02 | 0 | 2 | [5 empty] | AC Supply failed from New Bolangir
|  | 2020-09-23 | 13:48 | 2020-09-23 | 13:57 | 0:09 | 0 | 9 | [5 empty] | AC Supply failed from New Bolangir
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
210 | 132 kV New Bolangir - Bolangir Ckt - II |  |  |  |  | 1899-12-31 02:04 | 12 | 57 | [7 empty] | 3.008 | 8760 | 99.85% | 38.9536 | 26350.08
|  | 24.04.20 | 5:16 | 24.04.20 | 5:22 | 0:06 | 0 | 6 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-07-30 | 08:39 | 2020-07-30 | 08:40 | 0:01 | 0 | 1 | [5 empty] | Tripped on directional o/c displayed on back up o/c and e/f relay.
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 0:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-02-02 | 16:28 | 2021-02-02 | 12:46 | 20:45 | 0 | 8 | [5 empty] | Tripped from Balangir end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
211 | 132kV Bolangir-Sonepur |  |  |  |  | 0.23819 | 15 | 0 | [7 empty] | 53.05 | 8760 | 99.83% | 795.75 | 464718
|  | 2020-05-02 | 10:08 | 2020-05-02 | 10:13 | 0:05 | 0 | 5 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-05-06 | 13:26 | 2020-05-06 | 13:31 | 0:05 | 0 | 5 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-05-06 | 14:09 | 2020-05-06 | 14:17 | 0:08 | 0 | 8 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-05-04 | 19:05 | 2020-05-04 | 19:10 | 0:05 | 0 | 5 | [5 empty] | Feeder tripped from balangir
|  | 2020-05-04 | 19:31 | 2020-05-04 | 19:36 | 0:05 | 0 | 5 | [5 empty] | Feeder tripped from balangir
|  | 2020-06-05 | 11:08 | 2020-06-05 | 11:36 | 0:28 | 0 | 28 | [5 empty] | At Bolangir-Tripped
|  | 2020-06-05 | 12:02 | 2020-06-05 | 12:13 | 0:11 | 0 | 11 | [5 empty] | At Bolangir-Tripped
|  | 2020-06-05 | 12:32 | 2020-06-05 | 12:34 | 0:02 | 0 | 2 | [5 empty] | At Bolangir-Tripped
|  | 2020-06-05 | 12:40 | 2020-06-05 | 12:44 | 0:04 | 0 | 4 | [5 empty] | At Bolangir-Tripped
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-08-10 | 15:34 | 2020-08-10 | 15:49 | 00:15 | 0 | 15 | [5 empty] | AC Supply failed from New Bolangir
|  | 2020-08-19 | 15:40 | 2020-08-19 | 16:27 | 00:47 | 0 | 47 | [5 empty] | Tripped on Distance protection as well as in o/c and e/f in back up relay.
|  | 2020-09-20 | 13:30 | 2020-09-20 | 13:32 | 0:02 | 0 | 2 | [5 empty] | AC Supply failed from New Bolangir
|  | 2020-09-23 | 13:48 | 2020-09-23 | 13:57 | 0:09 | 0 | 9 | [5 empty] | AC Supply failed from New Bolangir
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
212 | 132 kV Sonepur - Boudh |  |  |  |  | 0.23819 | 15 | 19 | [7 empty] | 50.25 | 8760 | 99.83% | 769.6625 | 440190
|  | 2020-05-02 | 10:08 | 2020-05-02 | 10:13 | 0:05 | 0 | 5 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-05-06 | 13:26 | 2020-05-06 | 13:31 | 0:05 | 0 | 5 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-05-06 | 14:09 | 2020-05-06 | 14:17 | 0:08 | 0 | 8 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-05-04 | 19:05 | 2020-05-04 | 19:10 | 0:05 | 0 | 5 | [5 empty] | Feeder tripped from balangir
|  | 2020-05-04 | 19:31 | 2020-05-04 | 19:36 | 0:05 | 0 | 5 | [5 empty] | Feeder tripped from balangir
|  | 2020-06-05 | 11:08 | 2020-06-05 | 11:36 | 0:28 | 0 | 28 | [5 empty] | At Bolangir-Tripped
|  | 2020-06-05 | 12:02 | 2020-06-05 | 12:13 | 0:11 | 0 | 11 | [5 empty] | At Bolangir-Tripped
|  | 2020-06-05 | 12:32 | 2020-06-05 | 12:34 | 0:02 | 0 | 2 | [5 empty] | At Bolangir-Tripped
|  | 2020-06-05 | 12:40 | 2020-06-05 | 12:44 | 0:04 | 0 | 4 | [5 empty] | At Bolangir-Tripped
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-08-02 | 10:23 | 2020-08-02 | 10:27 | 00:04 | 0 | 4 | [5 empty] | feeder tripped on over current in Y phase
|  | 2020-08-02 | 11:19 | 2020-08-02 | 11:24 | 00:05 | 0 | 5 | [5 empty] | feeder tripped on over current in B phase
|  | 2020-08-03 | 18:55 | 2020-08-03 | 19:00 | 00:05 | 0 | 5 | [5 empty] | feeder tripped on E/F
|  | 2020-08-10 | 13:52 | 2020-08-10 | 13:57 | 00:05 | 0 | 5 | [5 empty] | feeder tripped on over current in B phase
|  | 2020-08-10 | 15:34 | 2020-08-10 | 15:49 | 00:15 | 0 | 15 | [5 empty] | AC Supply failed from New Bolangir
|  | 2020-08-19 | 15:40 | 2020-08-19 | 16:27 | 00:47 | 0 | 47 | [5 empty] | Tripped on Distance protection as well as in o/c and e/f in back up relay.
|  | 2020-09-20 | 13:30 | 2020-09-20 | 13:32 | 0:02 | 0 | 2 | [5 empty] | AC Supply failed from New Bolangir
|  | 2020-09-23 | 13:48 | 2020-09-23 | 13:57 | 0:09 | 0 | 9 | [5 empty] | AC Supply failed from New Bolangir
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
213 | 132kV New Bolangir-Patnagarh Ckt - I |  |  |  |  | 0.0090278 | 0 | 13 | [7 empty] | 39.41 | 8760 | 100% | 8.5388 | 345231.6
|  | 2020-05-30 | 7:38 | 2020-05-30 | 7:48 | 0:10 | 0 | 10 | [5 empty] | Tripped on back up o/c and e/f.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
214 | 132kV New Bolangir-Patnagarh Ckt - II |  |  |  |  | 0.011806 | 0 | 13 | [7 empty] | 39.41 | 8760 | 100% | 8.5388 | 345231.6
|  | 2020-05-30 | 7:38 | 2020-05-30 | 7:52 | 0:14 | 0 | 10 | [5 empty] | Tripped on distance protection.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
215 | 132kV Duburi- BRPL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.632 | 8760 | 100% | 0 | 66856.32
216 | 132kV BRPL-Mesco |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.436 | 8760 | 100% | 0 | 38859.36
217 | 132kV Lapanga-Jharsuguda Ckt-I |  |  |  |  | 0.038889 | 1 | 4 | [7 empty] | 10.4 | 8760 | 99.99% | 11.0933 | 91104
|  | 2020-05-24 | 15:08 | 2020-05-24 | 16:04 | 0:56 | 0 | 32 | [5 empty] | Due to CT brust at lapanga grid switchyard.
|  | 2020-09-23 | 13:17 | 2020-09-23 | 13:49 | 00:32 | 0 | 32 | [5 empty] | Tripped from Lapanga end.
218 | 132kV Budhipadar-Jharsuguda Ckt-II |  |  |  |  | 0.40694 | 1 | 26 | [7 empty] | 4.5 | 8760 | 99.98% | 6.45 | 39420
|  | 2020-09-06 | 01:51 | 2020-09-06 | 02:48 | 0:57 | 0 | 57 | [5 empty] | Tripped at Budhipadar end
|  | 2021-02-05 | 09:26 | 2021-02-05 | 18:15 | 8:49 | 0 | 29 | [5 empty] | Dir E/F
219 | 132kV Budhipadar-Jharsuguda Ckt-I |  |  |  |  | 0.081944 | 13 | 26 | [7 empty] | 7 | 8760 | 99.85% | 94.0333 | 61320
|  | 2020-05-24 | 15:08 | 2020-05-24 | 16:11 | 1:03 | 0 | 32 | [5 empty] | Due to CT brust at lapanga grid switchyard.
|  | 2020-09-06 | 01:51 | 2020-09-06 | 02:12 | 0:21 | 0 | 21 | [5 empty] | Tripped at Budhipadar end
|  | 2020-09-23 | 13:17 | 2020-09-23 | 13:51 | 0:34 | 0 | 33 | [5 empty] | O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
220 | 132kV Budhipadar-Rajgangpur ckt |  |  |  |  | 0.075 | 0 | 12 | [7 empty] | 79 | 8760 | 100% | 15.8 | 692040
|  | 2020-05-30 | 0:10 | 2020-05-30 | 1:39 | 1:29 | 0 | 2 | [5 empty] | DP OPERATED CGT ZONE-1 LOC- 17.80KM IC-1838A IG-2050A
|  | 2020-06-04 | 17:04 | 2020-06-04 | 18:38 | 0:19 | 0 | 10 | [5 empty] | Rajgangpur end:AGT,IA=1555A,IG= 1684A, Z1,LOC=41.99km. Budhipadar end: AGT, IA=1113.08A, 38.532km, Z1.
221 | 132kV Budhipadar-Sundargarh-I |  |  |  |  | 0.34861 | 14 | 9 | [7 empty] | 31.21 | 8760 | 99.84% | 441.6215 | 273399.6
|  | 2020-05-14 | 18:54 | 2020-05-14 | 19:44 | 0:50 | 0 | 50 | [5 empty] | At-Sundargarh, E/F
|  | 2020-06-04 | 16:41 | 2020-06-04 | 17:22 | 0:41 | 0 | 3 | [5 empty] | At Budhipadar End D/P operated inZone-I, FL= L2-E, F.D=5.7Kms, IL2=6.46KA
|  | 2020-09-23 | 13:17 | 2020-09-23 | 13:53 | 0:36 | 0 | 36 | [5 empty] | B/U:-E/F, Ir=0.05 KA, Iy=0.08 KA, Ib=0.03 KA
|  | 2021-02-05 | 09:26 | 2021-02-05 | 15:41 | 6:15 | 0 | 40 | [5 empty] | Dir E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
222 | 132kV Budhipadar-Sundargarh-II |  |  |  |  | 1899-12-31 00:52 | 13 | 39 | [7 empty] | 31.21 | 8760 | 99.84% | 426.0165 | 273399.6
|  | 2020-05-14 | 18:54 | 2020-05-18 | 18:22 | 23:28 | 0 | 50 | [5 empty] | At-Sundargarh, O/C,B-phase, IL1=0.17 KA,IL2=0.24 KA,IL3=2.31KA DP:Zone-1,CGT,Loc.-1.51,A=171 A,B=239 A,C=2306 A,N=2715 A, B- phase CVT Burst
|  | 2020-06-04 | 16:41 | 2020-06-04 | 16:44 | 0:03 | 0 | 3 | [5 empty] | At Budhipadar End D/P operated inZone-I, FL= Bphase-G, F.D=4.61Kms, Ib= 6.563KA
|  | 2020-06-04 | 17:04 | 2020-06-04 | 18:25 | 1:21 | 0 | 10 | [5 empty] | At Budhipadar End D/P operated inZone-I, FL= 34.5Kms, F.L=L1-E, IL1=1.836KA At Sundargarh End D/P operated inZone-I, FL= 142.1Kms, F.L=L1- E, IL1=624.24A
|  | 2020-09-23 | 13:17 | 2020-09-23 | 13:54 | 00:37 | 0 | 36 | [5 empty] | DP:CGT, Zone-1, Loc.-242.81 km, Ir=50 A ,Iy=78 A,Ib=27 A, In=130 A B/U:Ir=0.05 KA,Iy=0.08 KA, Ib=0.03 KA, In=0.03 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
223 | 132kV Budhipadar-MCL(Jorbaga)-I |  |  |  |  | 0.26042 | 0 | 40 | [7 empty] | 22.6 | 8760 | 99.99% | 15.0667 | 197976
|  | 2021-02-05 | 09:26 | 2021-02-05 | 15:41 | 6:15 | 0 | 40 | [5 empty] | Dir E/F
224 | 132kV Budhipadar-MCL(Jorbaga)-II |  |  |  |  | 0.29306 | 1 | 27 | [7 empty] | 22.6 | 8760 | 99.98% | 32.77 | 197976
|  | 2020-07-22 | 19:51 | 2020-07-22 | 20:38 | 0:47 | 0 | 47 | [5 empty] | At Budhipadar End,D/P operated in Zone-I, FD = 10.22Kms,,FL=YPh- E, Iy=7.927KA,
|  | 2021-02-05 | 09:26 | 2021-02-05 | 15:41 | 6:15 | 0 | 40 | [5 empty] | Dir E/F
225 | 132kV Budhipadar-MSP |  |  |  |  | 0.26042 | 6 | 7 | [7 empty] | 0.592 | 8760 | 99.93% | 3.6211 | 5185.92
|  | 2021-02-05 | 09:26 | 2021-02-05 | 15:41 | 6:15 | 6 | 7 | [5 empty] | Dir E/F
226 | 132kV Budhipadar-Brajrajnagar (Remja) |  |  |  |  | 0.79653 | 26 | 11 | [7 empty] | 11.75 | 8760 | 99.7% | 307.6542 | 102930
|  | 2020-09-01 | 23:58 | 2020-09-02 | 9:13 | 9:15 | 9 | 15 | [5 empty] | FFS
|  | 2020-09-02 | 09:59 | 2020-09-02 | 10:38 | 0:39 | 0 | 39 | [5 empty] | FFS
|  | 2020-09-23 | 13:17 | 2020-09-23 | 13:49 | 00:32 | 0 | 32 | [5 empty] | FFS
|  | 2021-01-27 | 23:28 | 2021-01-28 | 0:05 | 0:37 | 0 | 37 | [5 empty] | At Budhipadar End only,B/U (Siemens), Gen Trip,Directional L3 Pu,Directional E/F trip and Master Trip
|  | 2021-02-05 | 09:26 | 2021-02-05 | 15:41 | 6:15 | 0 | 47 | [5 empty] | Dir E/F
|  | 2021-03-13 | 13:00 | 2021-03-13 | 15:21 | 2:21 | 2 | 21 | [5 empty] | Tripped due to E/F on Yph
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
227 | 132kV Brajrajnagar- RTSS Kecchobahal |  |  |  |  | 0.40139 | 16 | 10 | [7 empty] | 11.75 | 5820 | 99.72% | 189.9583 | 68385
|  | 2021-01-27 | 23:28 | 2021-01-28 | 0:30 | 1:02 | 1 | 2 | [5 empty] | B-ph PT burst at RTSS end
|  | 2021-02-05 | 09:26 | 2021-02-05 | 15:41 | 6:15 | 0 | 47 | [5 empty] | Dir E/F
|  | 2021-03-13 | 13:00 | 2021-03-13 | 15:21 | 2:21 | 2 | 21 | [5 empty] | Tripped due to E/F on Yph
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
228 | 132kV Budhipadar - Kalunga |  |  |  |  | 0.29097 | 0 | 39 | [7 empty] | 99 | 8760 | 99.99% | 64.35 | 867240
|  | 2020-06-04 | 17:04 | 2020-06-04 | 18:25 | 1:21 | 0 | 10 | [5 empty] | DP R Phase, E/F, Zone 3, 142.1 km, Ir-624.2 A, Iy-104.7 A, Ib-106.4 A Backup Relay- R Phase, E/F, Ir- 83.96 A, Iy-409.4 A, Ib-99.43 A, In- 494.3 A
|  | 2021-02-05 | 09:26 | 2021-02-05 | 15:04 | 5:38 | 0 | 29 | [5 empty] | D/P Operated Zone-III ,Fault ,Distance = 322.7 KM,O/C R-Ph and
229 | 132kV Burla-Chipilima Ckt-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 19.5 | 8760 | 100% | 0 | 170820
230 | 132kV Burla-Hindalco-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 9 | 8760 | 100% | 0 | 78840
231 | 132kV Burla-Hindalco-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 9 | 8760 | 100% | 0 | 78840
232 | 132kV Burla-Katapali-Chipilima Ckt-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 22.26 | 8760 | 100% | 0 | 194997.6
233 | 132kV Burla-Katapalli |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 7 | 8760 | 100% | 0 | 61320
234 | 132kV Burla-Lapanga-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 43.6 | 8760 | 100% | 0 | 381936
235 | 132kV Burla-Lapanga-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 43.6 | 8760 | 100% | 0 | 381936
236 | 132kV Lapanga-Budhipadar Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 16 | 8760 | 100% | 0 | 140160
237 | 132kV Burla-Sambalpur |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 19.5 | 8760 | 100% | 0 | 170820
238 | 132kV Chainpal-Angul |  |  |  |  | 0.30347 | 13 | 45 | [7 empty] | 14.93 | 8760 | 99.84% | 205.2875 | 130786.8
|  | 2020-06-03 | 17:40 | 2020-06-03 | 18:16 | 0:36 | 0 | 14 | [5 empty] | O/C on R-phase, DP, 3247.65 A, 6.10km, L1-N
|  | 2020-10-29 | 15:17 | 2020-10-29 | 16:39 | 1:22 | 1 | 22 | [5 empty] | Tripped on E/F at both ends. [ one big mango tree has been uprooted by the railway authority which was in close proximity to 132 KV TTPS-Angul and 132 KV Chainpal-Angul double circuit
|  | 2021-03-11 | 18:55 | 2021-03-12 | 0:14 | 5:19 | 0 | 9 | [5 empty] | TRIPPED DUE TO RAIN AND LIGHTENING O/C R-Ph. P/S restored from TTPS end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
239 | 132kV Chainpal-FCI-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.29 | 2580 | 100% | 0 | 18808.2
240 | 132kV Chainpal-Global-FCI-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.6 | 6180 | 100% | 0 | 71688
241 | 132kV Chainpal-FCI-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7 | 8760 | 100% | 0 | 61320
242 | 132kV Chainpal-Talcher Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.448 | 8760 | 100% | 0 | 3924.48
243 | 132kV Chandaka-Bhubaneswar-I |  |  |  |  | 0.01875 | 0 | 18 | [7 empty] | 5.5 | 8760 | 100% | 1.65 | 48180
|  | 2020-06-15 | 0:31 | 2020-06-15 | 0:47 | 0:16 | 0 | 9 | [5 empty] | 220/132 kV Auto-I Tripped
|  | 2020-06-30 | 9:04 | 2020-06-30 | 9:15 | 0:11 | 0 | 9 | [5 empty] | 220/132 kV Auto-I Tripped
244 | 132kV Chandaka-Bhubaneswar-II |  |  |  |  | 0.01875 | 0 | 18 | [7 empty] | 5.5 | 8760 | 100% | 1.65 | 48180
|  | 2020-06-15 | 0:31 | 2020-06-15 | 0:47 | 0:16 | 0 | 9 | [5 empty] | 220/132 kV Auto-I Tripped
|  | 2020-06-30 | 9:04 | 2020-06-30 | 9:15 | 0:11 | 0 | 9 | [5 empty] | 220/132 kV Auto-I Tripped
245 | 132kV Chandaka-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 18.1 | 8760 | 100% | 0 | 158556
246 | 132kV Chandaka-Nimapara |  |  |  |  | 0.15139 | 13 | 54 | [7 empty] | 65 | 8760 | 99.84% | 903.5 | 569400
|  | 2020-06-29 | 13:21 | 2020-06-29 | 13:26 | 0:05 | 0 | 5 | [5 empty] | DP Relay Z-1, Distance 12.53KM, Ib- 4.077 KA C-N at Chandaka end.
|  | 2020-06-30 | 9:03 | 2020-06-30 | 9:21 | 0:18 | 0 | 18 | [5 empty] | DP Relay Z-2, Distance 105.97KM, B-G-T at Nimapara end.
|  | 2020-07-15 | 09:58 | 2020-07-15 | 10:08 | 0:10 | 0 | 8 | [5 empty] | DP Relay Z-1, Distance 48.72 KM, Ia- 1.97 KA , Y phase-N, at Chandaka End
|  | 2020-09-29 | 10:22 | 2020-09-29 | 10:33 | 00:11 | 0 | 11 | [5 empty] | At Chandaka End: Distance- 40.33KMs, Zone-1,(R ph to E) At Nimapara End-No Tripping
|  | 2020-11-17 | 12:48 | 2020-11-17 | 15:47 | 2:59 | 1 | 6 | [5 empty] | DP realy from Chandaka end 48.5KM, Ia-1.35KA
|  | 2020-11-18 | 12:15 | 2020-11-18 | 12:21 | 0:06 | 0 | 6 | [5 empty] | DP realy from Chandaka end Z-1, Distance-30.KM, Ia-2.7KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
247 | 132kV Chandaka-Ransingpur |  |  |  |  | 0.032639 | 12 | 47 | [7 empty] | 27.85 | 8760 | 99.85% | 356.0158 | 243966
|  | 2020-06-30 | 9:03 | 2020-06-30 | 9:21 | 0:18 | 0 | 18 | [5 empty] | DP Relay Operated
|  | 2020-06-15 | 0:30 | 2020-06-15 | 0:53 | 0:23 | 0 | 23 | [5 empty] | DP Relay Operated
|  | 2020-06-29 | 13:21 | 2020-06-29 | 13:27 | 0:06 | 0 | 6 | [5 empty] | P/S failed from Chandaka Grid end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
248 | 132kV Chandaka- Mancheswar-B Ckt -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.2 | 8760 | 100% | 0 | 98112
249 | 132kV Chandaka B-Unit-8 |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.4 | 8760 | 100% | 0 | 99864
250 | 132kV Chandpur - Khurdha |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35.93 | 2928 | 100% | 0 | 105203.04
251 | 132kV Chandpur - Atri |  |  |  |  | 0.017361 | 0 | 25 | [7 empty] | 43.03 | 5832 | 99.99% | 17.9292 | 250950.96
|  | 2020-09-30 | 13:54 | 2020-09-30 | 13:58 | 0:04 | 0 | 4 | [5 empty] | DP, Bph-3.853 kA, 20.35 km
|  | 2020-10-03 | 13:58 | 2020-10-03 | 14:19 | 0:21 | 0 | 21 | [5 empty] | Chandpur end: Dist. Protection operated, Z1, B-phase, IL1 =0.13 kA, IL2=0.13 kA ,IL3=0.17 kA, Dist.-16.1 km Atri end: DP, Rph & Yph, 5.69 kA, 5.50 kA, 17.92 km[heavy rain and lightning]
252 | 132kV Atri - Khurdha Ckt-II |  |  |  |  | 0.0034722 | 0 | 4 | [7 empty] | 10.29 | 5832 | 100% | 0.686 | 60011.28
|  | 2020-08-24 | 12:08 | 2020-08-24 | 12:13 | 0:05 | 0 | 4 | [5 empty] | O/C, Ir-1.4kA, Iy-1.6kA, Ib-1.6kA.
253 | 132kV Atri - Khurdha Ckt-I |  |  |  |  | 0.0027778 | 0 | 18 | [7 empty] | 10.24 | 5832 | 99.99% | 3.072 | 59719.68
|  | 2020-08-24 | 12:08 | 2020-08-24 | 12:12 | 0:04 | 0 | 4 | [5 empty] | O/C, Ir-1.4kA, Iy-1.6kA, Ib-1.6kA.
|  | 2020-10-03 | 14.04 | 2020-10-03 | 14.51 | 00:47 | 0 | 14 | [5 empty] | O/C, E/F, Yph & Bph, 3.3 kA, 1.1
254 | 132kV Khurdha- Shamuka |  |  |  |  | 0.069444 | 13 | 40 | [7 empty] | 54.74 | 2928 | 99.53% | 748.1133 | 160278.72
|  | 2020-07-03 | 12:10 | 2020-07-03 | 12:17 | 0:07 | 0 | 7 | [5 empty] | Source Failure
|  | 2020-07-04 | 11:25 | 2020-07-04 | 11:34 | 0:09 | 0 | 9 | [5 empty] | Source Failure
|  | 2020-07-15 | 13:05 | 2020-07-15 | 18:29 | 0:53 | 0 | 53 | [5 empty] | DP operate, Cphase-G, Distance= - 5.2 km,Zone- Z1,Ia=363.036A,Ib=704.279A, Ic=470.334A, In=14499.373A at Shamuka end.
|  | 2020-07-27 | 17:07 | 2020-07-27 | 17:38 | 0:31 | 0 | 31 | [5 empty] | Tripped at Shamuka end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
255 | 132kV Atri-Shamuka |  |  |  |  | 0.53472 | 13 | 16 | [7 empty] | 68.94 | 5832 | 99.77% | 914.604 | 402058.08
|  | 2020-08-13 | 14:42 | 2020-08-13 | 15:06 | 0:02 | 0 | 2 | [5 empty] | At Shamuka end. DP Relay operate.Zone- Z1, Bphase- G, Distance= 26.9km, Ia=564.648A, Ib=458.075A,Ic,=389.975A,Ig=1404 .703A. Heavy rain and Lightning
|  | 2020-09-18 | 11:55 | 2020-09-18 | 12:11 | 0:16 | 0 | 16 | [5 empty] | O/C, Bph, 404 A
|  | 2020-09-30 | 10:11 | 2020-09-30 | 10:28 | 0:17 | 0 | 17 | [5 empty] | DP, Rph-2.4 kA, Yph-2.1 kA, 54.73 km
|  | 2020-10-01 | 05:43 | 2020-10-01 | 05:48 | 0:05 | 0 | 5 | [5 empty] | DP, Rph & Yph, 2.4 kA, 2.2 kA, 54.62 km
|  | 2020-10-01 | 05:49 | 2020-10-01 | 17:59 | 12:10 | 0 | 8 | [5 empty] | DP, Rph & Yph, 2.4 kA, 2.2 kA, 54.83 km
|  | 2020-10-03 | 14:04 | 2020-10-03 | 14:18 | 00:14 | 0 | 14 | [5 empty] | DP, Yph & Bph, 3.7 kA, 7.5 kA, 7.11 km
|  | 2020-10-07 | 12:35 | 2020-10-07 | 12:42 | 00:07 | 0 | 7 | [5 empty] | DP, Yph-N, 2.34 kA, 42.88 km
|  | 2020-10-17 | 02:31 | 2020-10-17 | 02:38 | 00:07 | 0 | 7 | [5 empty] | DP, Yph-N, 1.95 kA, 54.6 km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
256 | 132kV Atri - Argul Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.4 | 8760 | 100% | 0 | 169944
257 | 132kV Atri - Argul Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.4 | 8760 | 100% | 0 | 169944
258 | 132kV Atri - Banki |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.5 | 8760 | 100% | 0 | 179580
259 | 132kV Khurdha-Kaipadar (T) |  |  |  |  | 0.0027778 | 0 | 4 | [7 empty] | 11.26 | 8760 | 100% | 0.75067 | 98637.6
|  | 2020-08-24 | 12:08 | 2020-08-24 | 12:12 | 0:04 | 0 | 4 | [5 empty] | O/C, Ir-1.4kA, Iy-1.6kA, Ib-1.6kA.
260 | 132kV Chandikhol-Kendrapada |  |  |  |  | 0.080556 | 13 | 27 | [7 empty] | 31.2 | 8760 | 99.85% | 419.64 | 273312
|  | 2020-05-09 | 10:02 | 2020-05-09 | 10:06 | 0:04 | 0 | 4 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-05-19 | 21:45 | 2020-05-19 | 21:49 | 0:04 | 0 | 4 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-05-29 | 17:30 | 2020-05-29 | 17:32 | 0:02 | 0 | 2 | [5 empty] | Tripped from Kendrapara, No relay indication at Chandikhol Grid
|  | 2020-06-21 | 6:00 | 2020-06-21 | 6:14 | 0:14 | 0 | 14 | [5 empty] | B/U,E/F, M/R.
|  | 2020-08-12 | 13:09 | 2020-08-12 | 13:23 | 0:14 | 0 | 14 | [5 empty] | TRIPPED ON DP RELAY WITH DIST.15.5KM,Z-1 WITH M/R
|  | 2020-09-03 | 12:42 | 2020-09-03 | 12:47 | 00:05 | 0 | 5 | [5 empty] | TRIPPED ON DP RELAY WITH DIST:-25.80KM,Z-1,B-PHASE WITH M/R
|  | 2020-09-09 | 15:44 | 2020-09-09 | 16:54 | 1:10 | 0 | 38 | [5 empty] | TRIPPED ON E/F WITH M/R.
|  | 2020-10-14 | 06:29 | 2020-10-14 | 06:37 | 0:08 | 0 | 6 | [5 empty] | Tripeed On Differential Relay With M/R Due To 132Kv R -Ph CT Brust And Charged After Replacement Of New CT.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
261 | 132kV Chatrapur-Balugaon |  |  |  |  | 0 | 0 | 0 | [7 empty] | 53.79 | 8760 | 100% | 0 | 471200.4
262 | 132kV Chatrapur-Ganjam |  |  |  |  | 0.18264 | 12 | 43 | [7 empty] | 12.6 | 8760 | 99.85% | 160.23 | 110376
|  | 2020-07-01 | 14:54 | 2020-07-01 | 15:08 | 0:14 | 0 | 14 | [5 empty] | 132kv Incoming Breaker Tripped with Distance relay optd at ganjam end. Showing fault indication at DP relay as distance at 8.87Km,A-N, Zone- 1&2
|  | 2020-08-20 | 12:05 | 2020-08-20 | 12:10 | 00:05 | 0 | 5 | [5 empty] | 132KV Supply Failure from Chatrapur end
|  | 2020-10-03 | 23:23 | 2020-10-03 | 23:37 | 0:14 | 0 | 14 | [5 empty] | Incoming supply failure from Chatrapur end.
|  | 2020-12-10 | 07:38 | 2020-12-10 | 11:33 | 3:55 | 0 | 10 | [5 empty] | Tripped on DP relay at both end At Narendrapur end :- Zone-1, 10.31KM, R-ph to Earth, IL1- 3985A,IL2-279A, IL3-476A. At Chatrapur end:- Zone-1, R-ph to Earth,Dist-0.0Km,IL1-440.9A, IL2- 289.0A, IL3-481.2A. Jumper snap at loc.1 at Chatrapur end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
263 | 132kV Chatrapur-IRE-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.8 | 8760 | 100% | 0 | 50808
264 | 132kV Chatrapur-IRE-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.8 | 8760 | 100% | 0 | 50808
265 | 132kV Chatrapur-Rambha (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.5 | 8760 | 100% | 0 | 249660
266 | 132kV Chhend-Adhunik Metalics |  |  |  |  | 0.027778 | 0 | 40 | [7 empty] | 24.04 | 8760 | 99.99% | 16.0267 | 210590.4
|  | 2020-06-23 | 19:09 | 2020-06-23 | 19:49 | 0:40 | 0 | 40 | [5 empty] | DP Relay ( Loop- A_G, Distance- 8.96 Kms , Ia-5.34 kA , In-4.84 kA)
267 | 132kV Chhend-Nuagaon(T) |  |  |  |  | 0.036806 | 0 | 53 | [7 empty] | 34.6 | 8760 | 99.99% | 30.5633 | 303096
|  | 2020-06-23 | 19:09 | 2020-06-23 | 19:49 | 0:40 | 0 | 40 | [5 empty] | DP Relay ( Loop- A_G, Distance- 8.96 Kms , Ia-5.34 kA , In-4.84 kA)
|  | 2020-07-14 | 00:36 | 2020-07-14 | 00:49 | 0:13 | 0 | 13 | [5 empty] | At Tarkera end, DP Relay- Tripped Phase- AGT, , Zone- 1, Fault location- 3.77 km, IA=6430A, IN=6187A,IG=6191 A; Master Trip operated. [Heavy rain & Lightening with thunderstorm.]
268 | 132kV Chipilima-Katapalli Ckt-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 100% | 0 | 110901.6
269 | 132kV Chipilima-Katapalli Ckt-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 100% | 0 | 110901.6
270 | 132kV Choudwar-Bidanasi |  |  |  |  | 0.020139 | 0 | 20 | [7 empty] | 15.41 | 8760 | 100% | 5.1367 | 134991.6
|  | 2020-06-08 | 14:46 | 2020-06-08 | 15:07 | 0:21 | 0 | 13 | [5 empty] | At choudwar end: O/C R,Y, B. At Bidanasi end: O/C R & B-phase to ground fault with M/R. Fault distance-10.4 Km, Ir-4.56KAmp, Ib- 5.1 Kamp
|  | 2020-07-25 | 1.34 | 2020-07-25 | 1.42 | 0:08 | 0 | 7 | [5 empty] | Tripped on M/T relay only at Bidanasi end.
271 | 132kV Choudwar-Kendrapara Road Traction |  |  |  |  | 0.014583 | 0 | 13 | [7 empty] | 4.6 | 8760 | 100% | 0.99667 | 40296
|  | 2020-06-08 | 14:46 | 2020-06-08 | 15:07 | 0:21 | 0 | 13 | [5 empty] | At choudwar end: O/C R,Y, B. At Bidanasi end: O/C R & B-phase to ground fault with M/R. Fault distance-10.4 Km, Ir-4.56KAmp, Ib- 5.1 Kamp
272 | 132kV Cuttack-Jagatsingpur |  |  |  |  | 0.44583 | 17 | 30 | [7 empty] | 34.71 | 8760 | 99.8% | 607.425 | 304059.6
|  | 2020-05-20 | 6:19 | 2020-05-20 | 06:42 | 0:23 | 0 | 23 | [5 empty] | Tripped on O/C in R-Y-B ph,E/F. IL1=0.01KA,IL2=2.36KA,IL3=0.01 KA
|  | 2020-05-20 | 8:35 | 2020-05-20 | 13:07 | 4:32 | 4 | 32 | [5 empty] | Tripped on O/C in R-Y-B ph,E/F. IL1=0.01KA,IL2=2.34KA,IL3=0.01 KA
|  | 2020-06-05 | 5:45 | 2020-06-05 | 9:50 | 5:17 | 0 | 5 | [5 empty] | Bidanasi End : Main-1 - B-pahae to Ground, Distance-11.17km, Z1 , Ib- 5.4kAmp. [Jumper snapped at Loc. No-69. ]
|  | 2021-03-27 | 18:17 | 2021-03-27 | 18:47 | 0:30 | 0 | 30 | [5 empty] | Tripped due to o/c in Y-ph,E/F. Dist.- 31.72 km.,Zone-2 Iy=2.710kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
273 | 132kV Cuttack-Phulnakhara |  |  |  |  | 0.42153 | 15 | 44 | [7 empty] | 20.26 | 8760 | 99.82% | 318.7573 | 177477.6
|  | 2020-04-18 | 19:32 | 2020-04-19 | 16:33 | 21:01 | 1 | 1 | [5 empty] | Tripped on O/C in Y-Ph., DP relay optd- Distance=11.495km, Zone-1, B-G, Ia=515mA, Ib=9.65A, Ic=501mA. ( Y-ph insulator string failure at Loc.No.17)
|  | 2020-04-25 | 11:18 | 2020-04-25 | 11:26 | 0:08 | 0 | 6 | [5 empty] | Tripped on V/F trip,V/F warn,86A&86B trip
|  | 2020-04-29 | 23:12 | 2020-04-29 | 23:16 | 0:04 | 0 | 4 | [5 empty] | P/S failure from Bidanasi end
|  | 2020-05-10 | 18:22 | 2020-05-10 | 18:28 | 00:06 | 0 | 6 | [5 empty] | At Cuttack end: O/C R-ph & E/F, Zone-1
|  | 2020-05-29 | 3:29 | 2020-05-30 | 0:49 | 21:20 | 1 | 41 | [5 empty] | Tripped from Cuttack Grid end on O/C Y-ph, Zone-1 Dist- 0.515KM
|  | 2020-06-05 | 5:45 | 2020-06-05 | 9:50 | 5:17 | 0 | 5 | [5 empty] | Bidanasi End : Main-1 - B-pahae to Ground, Distance-11.17km, Z1 , Ib- 5.4kAmp. [Jumper snapped at Loc. No-69. ]
|  | 2020-06-12 | 7:40 | 2020-06-12 | 3:50 | 4:44 | 0 | 4 | [5 empty] | Tripped on O/C Y-phase to ground fault with fault distance-19.04 Km & Iy-1.44 KAmp.[Jumper snapped at Loc. No-50.]
|  | 2020-07-15 | 04:49 | 2020-07-15 | 05:20 | 00:31 | 0 | 31 | [5 empty] | Insulator string punctured at middle conductor(R-phase) at Location No. 01 of 132KV Cuttack-Phulnakhara LILO Line.
|  | 2020-10-04 | 10:59 | 2020-10-04 | 11:05 | 0:06 | 0 | 6 | [5 empty] | Tripped on O/C in R-Y-B ph,E/F. IL1=0.02KA,IL2=0.88KA,IL3=0.86 KA.[heavy lightneing observed at phulnakhara end]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
274 | 132kV Dhenkanal-Khuntuni-Grid Steel -ICCL |  |  |  |  | 0.66042 | 14 | 15 | [7 empty] | 39.18 | 8760 | 99.84% | 558.315 | 343216.8
|  | 2020-05-23 | 20:44 | 2020-05-23 | 21:05 | 0:21 | 0 | 9 | [5 empty] | Only B/U relay operated (O/C)
|  | 2020-08-19 | 18:41 | 2020-08-19 | 19:11 | 0:30 | 0 | 30 | [5 empty] | R phase O/C and E/F, Distance - 75.55km,zone3 At K.Kata end: Y-G Fault, Ir= 0.28 KA, Iy=0.96 KA, Ib= 0.26 KA
|  | 2020-08-10 | 13:32 | 2020-08-10 | 14:37 | 1:05 | 0 | 25 | [5 empty] | No tripping of CB but 1. DP Relay actuated, with indication : IR=312A, IY=142A, IB=1.427kA, No indication of Fault Loop, distance and Zone 2. B/U relay operated in E/F
|  | 2020-08-19 | 18:40 | 2020-08-20 | 7:54 | 13:15 | 0 | 31 | [5 empty] | No tripping of CB but DP Relay actuated, with indication : IY=1.42kA, Fault Loop=Y_G, distance=32.25kM and Zone-2
|  | 2020-08-23 | 11:53 | 2020-08-23 | 12:03 | 0:10 | 0 | 10 | [5 empty] | 1. DP Relay actuated, with indication :IR=1.68KA,Fault Loop=R-N, distance=-1KM and Zone-2 2. B/U relay operated in E/F
|  | 2020-08-31 | 12:10 | 2020-08-31 | 12:26 | 0:16 | 0 | 16 | [5 empty] | 1. DP Relay actuated, with indication : IR=1.968KA,Fault Loop=R-N, distance=36.33KM and Zone-2 2. B/U relay operated in E/F
|  | 2020-09-02 | 12:09 | 2020-09-02 | 12:23 | 0:14 | 0 | 14 | [5 empty] | CB tripped, 1. Fault Loop-B-N, Ib=2.23kA, Distance= 30.3KM, Zone-2 2. B/U-E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
275 | 132kV Khuntuni- Shree Cement |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.45 | 540 | 100% | 0 | 3483
276 | 132kV Dhenkanal-Joranda (T) |  |  |  |  | 0.90417 | 20 | 18 | [7 empty] | 19.35 | 8760 | 99.77% | 392.805 | 169506
|  | 2020-05-23 | 20:44 | 2020-05-23 | 20:53 | 0:09 | 0 | 9 | [5 empty] | Only B/U relay operated (O/C)
|  | 2020-06-01 | 14:01 | 2020-06-01 | 14:08 | 0:07 | 0 | 7 | [5 empty] | E/E,B/U Relay operated
|  | 2020-08-04 | 06:26 | 2020-08-04 | 12:52 | 6:26 | 6 | 26 | [5 empty] | B/U relay operated in E/F [BREAKDOWN due to snapping of Overhead earth wire at Loc No-39 to 43]
|  | 2020-08-13 | 16:41 | 2020-08-13 | 16:51 | 0:10 | 0 | 10 | [5 empty] | B/U relay operated in E/F
|  | 2020-08-19 | 18:41 | 2020-08-19 | 19:11 | 0:30 | 0 | 30 | [5 empty] | R phase O/C and E/F, Distance - 75.55km,zone3 At K.Kata end: Y-G Fault, Ir= 0.28 KA, Iy=0.96 KA, Ib= 0.26 KA
|  | 2020-08-10 | 13:32 | 2020-08-10 | 14:37 | 1:05 | 0 | 25 | [5 empty] | No tripping of CB but 1. DP Relay actuated, with indication : IR=312A, IY=142A, IB=1.427kA, No indication of Fault Loop, distance and Zone 2. B/U relay operated in E/F
|  | 2020-08-19 | 18:40 | 2020-08-20 | 7:54 | 13:15 | 0 | 31 | [5 empty] | No tripping of CB but DP Relay actuated, with indication : IY=1.42kA, Fault Loop=Y_G, distance=32.25kM and Zone-2
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
277 | 132kV Digapahandi-Chikiti ckt - I |  |  |  |  | 0.24722 | 13 | 28 | [7 empty] | 29.1 | 8760 | 99.85% | 391.88 | 254916
|  | 2020-05-26 | 13:13 | 2020-05-26 | 13:20 | 0:07 | 0 | 7 | [5 empty] | TRIPPED ON O/C
|  | 2020-05-18 | 12:06 | 2020-05-18 | 17:30 | 5:24 | 0 | 56 | [5 empty] | Tripped. [B Ph Jumper snap at Loc- 50. ]
|  | 2020-08-20 | 12:06 | 2020-08-20 | 12:10 | 0:04 | 0 | 4 | [5 empty] | No tripping at Berhampur End. Auto failed at Narendrapur End.Power supply failure from Narendrapur.
|  | 2020-09-27 | 16:38 | 2020-09-27 | 16:59 | 0:21 | 0 | 21 | [5 empty] | DP relay operated, master trip optd. Zone-1 R-phase fault loc. 302.3m [Heavy rain outside]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
278 | 132kV Digapahandi-Chikiti ckt - II |  |  |  |  | 0.24722 | 13 | 28 | [7 empty] | 29.1 | 8760 | 99.85% | 391.88 | 254916
|  | 2020-05-26 | 13:13 | 2020-05-26 | 13:20 | 0:07 | 0 | 7 | [5 empty] | TRIPPED ON O/C
|  | 2020-05-18 | 12:06 | 2020-05-18 | 17:30 | 5:24 | 0 | 56 | [5 empty] | Tripped. [B Ph Jumper snap at Loc- 50. ]
|  | 2020-08-20 | 12:06 | 2020-08-20 | 12:10 | 0:04 | 0 | 4 | [5 empty] | No tripping at Berhampur End. Auto failed at Narendrapur End.Power supply failure from Narendrapur.
|  | 2020-09-27 | 16:38 | 2020-09-27 | 16:59 | 0:21 | 0 | 21 | [5 empty] | DP relay operated, master trip optd. Zone-1 R-phase fault loc. 302.3m [Heavy rain outside]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
279 | 132kV Duburi-BC Mohanty |  |  |  |  | 0.22431 | 5 | 23 | [7 empty] | 11.97 | 8760 | 99.94% | 64.4385 | 104857.2
|  | 2020-05-01 | 23:59 | 2020-05-02 | 5:22 | 5:23 | 5 | 23 | [5 empty] | Tripped due to bursting of R Ph. LA in the Incomer Fdr at BC Mohanty S/S.
280 | 132kV Duburi-BRPL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.43 | 8760 | 100% | 0 | 38806.8
281 | 132kV Duburi-Jajpur Road-I |  |  |  |  | 0.93819 | 1 | 19 | [7 empty] | 13.2 | 8760 | 99.98% | 17.38 | 115632
|  | 2020-07-25 | 11:48 | 2020-07-25 | 12:54 | 1:06 | 1 | 6 | [5 empty] | DP RELAY OPERATED, Ir=315.5AA, Iy=3.44KA, Ib=241.9A, Zone-4, Distance=0.0KM, FR=3.592Ω [Post insulator of Y-Phase BUS-I 132 KV Chandikhol feeder Punctured ]
|  | 2020-11-03 | 15:00 | 2020-11-04 | 12:25 | 21:25 | 0 | 13 | [5 empty] | At Anandapur-Trippedon DP, Zone- 1, R-Phase to ground, Fault Dist.- 0.00 Km, Fault Current IA=2.486KA, IN=3.194KA,VAN =2.65KV,VBN=87.00KV, VCN=86.254KV. At JajpurRoad-H/T [R-ph LA burst at Anandapur end]
282 | 132kV Duburi-Jajpur Road-II |  |  |  |  | 0.93819 | 1 | 19 | [7 empty] | 13.2 | 8760 | 99.98% | 17.38 | 115632
|  | 2020-07-25 | 11:48 | 2020-07-25 | 12:54 | 1:06 | 1 | 6 | [5 empty] | DP RELAY OPERATED, Ir=315.5AA, Iy=3.44KA, Ib=241.9A, Zone-4, Distance=0.0KM, FR=3.592Ω [Post insulator of Y-Phase BUS-I 132 KV Chandikhol feeder Punctured ]
|  | 2020-11-03 | 15:00 | 2020-11-04 | 12:25 | 21:25 | 0 | 13 | [5 empty] | At Anandapur-Trippedon DP, Zone- 1, R-Phase to ground, Fault Dist.- 0.00 Km, Fault Current IA=2.486KA, IN=3.194KA,VAN =2.65KV,VBN=87.00KV, VCN=86.254KV. At JajpurRoad-H/T [R-ph LA burst at Anandapur end]
283 | 132kV Duburi-Jakhapura (T) |  |  |  |  | 0.21458 | 17 | 13 | [7 empty] | 12.45 | 8760 | 99.8% | 214.3475 | 109062
|  | 2021-01-11 | 02:35 | 2021-01-11 | 07:41 | 5:06 | 5 | 6 | [5 empty] | tripped from both end . (Duburi-DP relay ,Zone-1, 10.16KM, B-ph to Earth, IL3-6.49KA)
|  | 2021-01-11 | 13:35 | 2021-01-11 | 13:38 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-15 | 13:55 | 2021-01-15 | 13:59 | 00:04 | 0 | 4 | [5 empty] | O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
284 | 132kV JSWCL- Mesco |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.464 | 8760 | 100% | 0 | 47864.64
285 | 132kV Duburi-JSWCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.26 | 8760 | 100% | 0 | 81117.6
286 | 132kV ICCL-Choudwar |  |  |  |  | 0.01875 | 0 | 24 | [7 empty] | 0.5 | 8760 | 100% | 0.2 | 4380
|  | 2020-06-08 | 14:53 | 2020-06-08 | 15:12 | 0:19 | 0 | 17 | [5 empty] | Master trip at choudwar
|  | 2020-07-25 | 1.34 | 2020-07-25 | 1.42 | 0:08 | 0 | 7 | [5 empty] | Tripped on M/T relay only at Bidanasi end.
287 | 132kV Jabamayee FAlloys-Duburi-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12 | 8760 | 100% | 0 | 105120
288 | 132kVJajpur Road-Anandpur Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.6 | 8760 | 100% | 0 | 259296
289 | 132kVJajpur Road-Anandpur Ckt-II |  |  |  |  | 0.89236 | 0 | 13 | [7 empty] | 29.6 | 8760 | 100% | 6.4133 | 259296
|  | 2020-11-03 | 15:00 | 2020-11-04 | 12:25 | 21:25 | 0 | 13 | [5 empty] | At Anandapur-Trippedon DP, Zone- 1, R-Phase to ground, Fault Dist.- 0.00 Km, Fault Current IA=2.486KA, IN=3.194KA,VAN =2.65KV,VBN=87.00KV, VCN=86.254KV. At JajpurRoad-H/T [R-ph LA burst at Anandapur end]
290 | 132kV Bhadrak-Agarpada |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.07 | 8760 | 100% | 0 | 245893.2
291 | 132kV Agarpada-Anandpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 41 | 8760 | 100% | 0 | 359160
292 | 132kVJajpur Road-Chandikhol |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.31 | 8760 | 100% | 0 | 300555.6
293 | 132kVJajpur Road-Jajpur Town |  |  |  |  | 0 | 0 | 0 | [7 empty] | 25.05 | 8760 | 100% | 0 | 219438
294 | 132kVJajpur Road- Kendrapara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 63.11 | 2964 | 100% | 0 | 187058.04
295 | 132kVJajpur Road-RAMCO |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.13 | 5796 | 100% | 0 | 168837.48
296 | 132kV RAMCO- Kendrapara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 41.43 | 5796 | 100% | 0 | 240128.28
297 | 132kV Kuchei PG- Jaleswar |  |  |  |  | 0.43819 | 13 | 54 | [7 empty] | 78.88 | 8760 | 99.84% | 1096.432 | 690988.8
|  | 2020-04-17 | 21:38 | 2020-04-17 | 22:06 | 0:28 | 0 | 28 | [5 empty] | At Bhograi end: Zone-1,Y-ph E/F ,Fault Loc -18.69KMIY-2.432KA.
|  | 2020-04-24 | 13:42 | 2020-04-24 | 16:44 | 3:02 | 0 | 7 | [5 empty] | At Jaleswar end; Y PH TO B PH , DISTANCE 41.8 Km , Z-1 , Fault current -651.4 A(Y-PH),683.7 A(B- PH) At Baripada PG end: Y PH TO B PH , DISTANCE 38.78 Km , Z-1 , Fault current -3 KA(Y-PH),2.965 KA(B-PH)
|  | 2020-06-15 | 14:49 | 2020-06-15 | 18:28 | 3:06 | 0 | 28 | [5 empty] | At Baripada(PG) end: DP, Y-B Phase, 29.63 Km , Z1 , Iy 2.69 kA , Ib 2.51 kA
|  | 2020-08-14 | 11:50 | 2020-08-14 | 12:14 | 0:24 | 0 | 7 | [5 empty] | DP RELAY INDICATION AT KUCHEI END. Z-1,Loc-44.15 KM,Ir-732.5 A,Iy-1.738 KA,Ib-249.7A,Vrn-53.02KV,Vyn- 46.75KV,Vbn-74.66KV .
|  | 2020-08-15 | 14:59 | 2020-08-15 | 15:42 | 0:43 | 0 | 12 | [5 empty] | DP RELAY INDICATION AT KUCHEI END Z- 1,Loc-20.73 KM,Ir-497.6 A,Iy-208.2 A, Ib- 2.359 KA,Vrn-45.46KV,Vyn-75.71KV, Vbn- 41.95KV.
|  | 2020-08-19 | 03:26 | 2020-08-19 | 04:35 | 1:09 | 0 | 15 | [5 empty] | DP RELAY INDICATION AT KUCHEI END. Z-1,Loc-22.23 KM,Ir-2.784KA,Iy- 3.727KA, Ib-174A,Vrn-36.08KV,Vyn- 41.86KV, Vbn-76.94KV.
|  | 2020-08-23 | 16:17 | 2020-08-23 | 17:56 | 1:39 | 0 | 11 | [5 empty] | DP RELAY INDICATION AT JALESWAR END. Z1, Rph-Bph-Ground, Distance :- 37.1 KM , Ir-238.6 A, Iy-256.7 A, Ib- 764.7 A, Vrn-13.27 KV, Vyn-73.033 KV, Vbn-20.67 KV AT KUCHEI END.
|  | 2020-10-04 | 12:48 | 2020-10-04 | 13:44 | 00:56 | 0 | 6 | [5 empty] | DP RELAY INDICATION AT JALESWAR END: Z1, Yph- Ground, Distance :-51.1 KM, Ir- 249.2A, Iy-515.6A, Ib-124.9A, Vrn- 73.61 KV, Vyn-30.72 KV, Vbn- 73.23 KV AT KUCHEI END: Z1, yph- Ground, Distance :-16.72 KM , Ir- 244.7A, Iy-3.62KA, Ib-108.4A, Vrn-
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
298 | 132kV Kuchei PG- Bhogarai |  |  |  |  | 0.47292 | 13 | 39 | [7 empty] | 100.91 | 8760 | 99.84% | 1377.4215 | 883971.6
|  | 2020-04-24 | 13:42 | 2020-04-24 | 14:13 | 0:31 | 0 | 7 | [5 empty] | At Bhograi end: ZONE-1,R-PH to Gnd,Fault Loc -74.9KM
|  | 2020-06-15 | 14:49 | 2020-06-15 | 18:33 | 3:43 | 0 | 28 | [5 empty] | At Bhograi end: DP, Z1, R-B-Gnd, 38.7km ,IR-528.2 A, IB-74 A.
|  | 2020-08-14 | 11:50 | 2020-08-14 | 12:41 | 0:52 | 0 | 14 | [5 empty] | Bhograi end: D.P OPTD. Z-1,Rph- GROUND,29.3KM,Ir-644A,Iy- 101.5A,Ib-193.3A,Vr-23.076K.V,Vy- 13.534K.V,Vb-17.372K.V Baripada PG end: D.P OPTD. Z-1,Rph- Yph-GROUND,48.42KM,Ir- 2.508K.A,Iy-1.742K.A,Ib-A,Vr- 52.88K.V,Vy-71.42K.V,Vb-57.94K.V
|  | 2020-08-15 | 14:59 | 2020-08-15 | 17:15 | 2:16 | 0 | 14 | [5 empty] | Bhograi end: D.P OPTD. Z-1,Rph-Bph- GROUND,55.3KM,Ir-428.2A,Iy-0 A,Ib- 57.7A,Vr-19.34K.V,Vy-27.97K.V,Vb- 4.19K.V Baripada PG end: D.P OPTD. Z-1,Rph- Bph,27.15KM,Ir-3.33K.A,Iy-0.152K.A,Ib- 2.59K.A,Vr-47.39K.V,Vy-72.22K.V,Vb- 43.49K.V
|  | 2020-08-19 | 03:26 | 2020-08-19 | 04:39 | 1:13 | 0 | 15 | [5 empty] | NO TRIPPING AT BHOGRAI END. Baripada PG end: D.P OPTD. Z-1,Rph- GROUND,13.42KM,Ir-2.757K.A,Iy- 411.5A,Ib-124 A,Vr-38.08K.V,Vy- 43.87K.V,Vb-72.17K.V
|  | 2020-08-23 | 16:17 | 2020-08-23 | 18:02 | 1:45 | 0 | 14 | [5 empty] | NO TRIPPING AT BHOGRAI END. Baripada PG end: D.P OPTD. Z- 1,Rph-GROUND,45.59KM,Ir- 1.72K.A,Iy-1.665A,Ib-698.6 A,Vr- 47.6K.V,Vy-73.55K.V,Vb- 54.34K.V
|  | 2020-09-07 | 15:45 | 2020-09-07 | 16:46 | 1:01 | 0 | 7 | [5 empty] | Z-1, R-GROUND,LOC.- 17.23KM,IR-2.432KA at Kuchei end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
299 | 132kV Jaleswar-Bhogarai |  |  |  |  | 0.25208 | 13 | 47 | [7 empty] | 57.13 | 8760 | 99.84% | 787.4418 | 500458.8
|  | 2020-04-17 | 21:38 | 2020-04-17 | 22:12 | 0:34 | 0 | 14 | [5 empty] | At Bhograi end: Y-ph, E/F , Dist- 18.69 kM ,Z-1 ,FC-2.4kA
|  | 2020-04-24 | 13:42 | 2020-04-24 | 13:49 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bhograi end
|  | 2020-06-15 | 14:49 | 2020-06-15 | 18:33 | 3:43 | 0 | 28 | [5 empty] | At Bhograi end: DP, Z1, R-B-Gnd, 38.7km ,IR-528.2 A, IB-74 A.
|  | 2020-08-14 | 11:50 | 2020-08-14 | 11:57 | 0:07 | 0 | 7 | [5 empty] | KUCHEI CKT-1 & 2 TRIPPED
|  | 2020-08-15 | 14:59 | 2020-08-15 | 15:11 | 0:12 | 0 | 12 | [5 empty] | KUCHEI CKT-1 & 2 TRIPPED
|  | 2020-08-19 | 03:26 | 2020-08-19 | 03:41 | 0:15 | 0 | 15 | [5 empty] | KUCHEI CKT-1 & 2 TRIPPED
|  | 2020-08-23 | 16:17 | 2020-08-23 | 16:28 | 0:11 | 0 | 11 | [5 empty] | KUCHEI CKT-1 & 2 TRIPPED
|  | 2020-09-07 | 15:45 | 2020-09-07 | 16:46 | 1:01 | 0 | 7 | [5 empty] | Z-1, R-GROUND,LOC.- 17.23KM,IR-2.432KA at Kuchei end.
|  | 2020-10-04 | 12:48 | 2020-10-04 | 13:44 | 00:56 | 0 | 6 | [5 empty] | DP RELAY INDICATION AT JALESWAR END: Z1, Yph- Ground, Distance :-51.1 KM, Ir- 249.2A, Iy-515.6A, Ib-124.9A, Vrn- 73.61 KV, Vyn-30.72 KV, Vbn- 73.23 KV AT KUCHEI END: Z1, yph- Ground, Distance :-16.72 KM , Ir- 244.7A, Iy-3.62KA, Ib-108.4A, Vrn-
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
300 | 132kVJaleswar-Jaleswar (T) |  |  |  |  | 0.35486 | 13 | 47 | [7 empty] | 2.34 | 8760 | 99.84% | 32.253 | 20498.4
|  | 2020-04-17 | 21:38 | 2020-04-17 | 22:12 | 0:34 | 0 | 14 | [5 empty] | At Bhograi end: Y-ph, E/F , Dist- 18.69 kM ,Z-1 ,FC-2.4kA
|  | 2020-04-24 | 13:42 | 2020-04-24 | 16:44 | 3:02 | 0 | 7 | [5 empty] | At Jaleswar end; Y PH TO B PH , DISTANCE 41.8 Km , Z-1 , Fault current -651.4 A(Y-PH),683.7 A(B- PH) At Baripada PG end: Y PH TO B PH , DISTANCE 38.78 Km , Z-1 , Fault current -3 KA(Y-PH),2.965 KA(B-PH)
|  | 2020-06-15 | 14:49 | 2020-06-15 | 18:33 | 3:43 | 0 | 28 | [5 empty] | At Bhograi end: DP, Z1, R-B-Gnd, 38.7km ,IR-528.2 A, IB-74 A.
|  | 2020-08-14 | 11:50 | 2020-08-14 | 11:57 | 0:07 | 0 | 7 | [5 empty] | KUCHEI CKT-1 & 2 TRIPPED
|  | 2020-08-15 | 14:59 | 2020-08-15 | 15:11 | 0:12 | 0 | 12 | [5 empty] | KUCHEI CKT-1 & 2 TRIPPED
|  | 2020-08-19 | 03:26 | 2020-08-19 | 03:41 | 0:15 | 0 | 15 | [5 empty] | KUCHEI CKT-1 & 2 TRIPPED
|  | 2020-08-23 | 16:17 | 2020-08-23 | 16:28 | 0:11 | 0 | 11 | [5 empty] | KUCHEI CKT-1 & 2 TRIPPED
|  | 2020-09-07 | 15:45 | 2020-09-07 | 16:46 | 1:01 | 0 | 7 | [5 empty] | Z-1, R-GROUND,LOC.- 17.23KM,IR-2.432KA at Kuchei end.
|  | 2020-10-04 | 12:48 | 2020-10-04 | 13:44 | 00:56 | 0 | 6 | [5 empty] | DP RELAY INDICATION AT JALESWAR END: Z1, Yph- Ground, Distance :-51.1 KM, Ir- 249.2A, Iy-515.6A, Ib-124.9A, Vrn- 73.61 KV, Vyn-30.72 KV, Vbn- 73.23 KV AT KUCHEI END: Z1, yph- Ground, Distance :-16.72 KM , Ir- 244.7A, Iy-3.62KA, Ib-108.4A, Vrn-
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
301 | 132 kV Jaleswar-Basta |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23.41 | 8760 | 100% | 0 | 205071.6
302 | 132kVJayanagar-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 44.87 | 8760 | 100% | 0 | 393061.2
303 | 132kVJayanagar-Jayanagar(T) |  |  |  |  | 0.44653 | 10 | 41 | [7 empty] | 39.6 | 8760 | 99.88% | 423.06 | 346896
|  | 2020-05-12 | 10:08 | 2020-05-12 | 20:27 | 10:19 | 10 | 19 | [5 empty] | B Phase CT burst. (Jayanagar, Tentulikhunti affected due to damage to the Reserve Bus isolator)
|  | 2021-02-12 | 12:55 | 2021-02-12 | 13:19 | 0:24 | 0 | 22 | [5 empty] | Tripped
304 | 132kVJayanagar-Podagada |  |  |  |  | 0.0041667 | 0 | 6 | [7 empty] | 38.0419 | 8760 | 100% | 3.8042 | 333247.044
|  | 2020-05-16 | 15:09 | 2020-05-16 | 15:15 | 0:06 | 0 | 6 | [5 empty] | Auto-tripped due to fault in Rayagada Feeder
305 | 132kV Podagada-Rayagada |  |  |  |  | 0.034722 | 12 | 27 | [7 empty] | 72.1572 | 8760 | 99.86% | 898.3571 | 632097.072
|  | 2020-05-16 | 15:09 | 2020-05-16 | 15:18 | 0:09 | 0 | 6 | [5 empty] | Auto-tripped, R, B Phase fault, Z1 Trip
|  | 2020-10-03 | 14:47 | 2020-10-03 | 14:52 | 0:05 | 0 | 5 | [5 empty] | Tripped at Podagada
|  | 2020-10-15 | 19:04 | 2020-10-15 | 19:49 | 0:45 | 0 | 16 | [5 empty] | Tripped of Podagad end & JNR With O/C [Conductor y Phase CVT of JNR incoming side snapped at podagada end.]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
306 | 132kVJaynagar-Tentulikhunti Ckt -I |  |  |  |  | 0.46667 | 14 | 23 | [7 empty] | 55.6 | 8760 | 99.84% | 799.7133 | 487056
|  | 2020-05-02 | 18:41 | 2020-05-02 | 18:54 | 0:13 | 0 | 13 | [5 empty] | Tripped from Tentulikhunti
|  | 2020-05-12 | 10:08 | 2020-05-12 | 20:27 | 10:19 | 1 | 30 | [5 empty] | B Phase CT burst. (Jayanagar, Tentulikhunti affected due to damage to the Reserve Bus isolator)
|  | 2020-05-29 | 11:44 | 2020-05-29 | 11:50 | 0:06 | 0 | 6 | [5 empty] | At Jayanagar-Tripped
|  | 2020-05-29 | 17:25 | 2020-05-29 | 17:37 | 0:12 | 0 | 12 | [5 empty] | Tripped on over current [due to 33KV Indravati feeder backup relay operated and CB not tripped]
|  | 2021-02-12 | 12:55 | 2021-02-12 | 13:17 | 0:22 | 0 | 22 | [5 empty] | Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
307 | 132kVJayanagar-Tentulikhunti Ckt -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 57.49 | 1116 | 100% | 0 | 64158.84
308 | 132kVJharsuguda-Jharsuguda(T) |  |  |  |  | 0.4375 | 13 | 51 | [7 empty] | 0.15 | 8760 | 99.84% | 2.0775 | 1314
|  | 2020-05-24 | 15:08 | 2020-05-24 | 16:04 | 0:56 | 0 | 32 | [5 empty] | Due to CT brust at lapanga grid switchyard.
|  | 2020-08-06 | 21:38 | 2020-08-06 | 21:43 | 0:05 | 0 | 5 | [5 empty] | Dir O/C
|  | 2020-08-08 | 08:47 | 2020-08-08 | 08:50 | 0:03 | 0 | 3 | [5 empty] | Dir O/C
|  | 2020-08-09 | 15:41 | 2020-08-09 | 15:44 | 0:03 | 0 | 3 | [5 empty] | Dir O/C
|  | 2020-08-10 | 07:37 | 2020-08-10 | 07:40 | 0:03 | 0 | 3 | [5 empty] | Dir O/C
|  | 2020-09-06 | 01:51 | 2020-09-06 | 02:14 | 0:23 | 0 | 23 | [5 empty] | Tripped at Budhipadar end
|  | 2020-09-18 | 12:45 | 2020-09-18 | 12:48 | 0:03 | 0 | 3 | [5 empty] | Dir O/C
|  | 2020-10-27 | 03:36 | 2020-10-27 | 03:38 | 00:02 | 0 | 2 | [5 empty] | DIR O/C
|  | 2020-10-27 | 03:42 | 2020-10-27 | 03:45 | 00:03 | 0 | 3 | [5 empty] | Dir O/C,
|  | 2020-11-05 | 12:24 | 2020-11-05 | 12:25 | 0:01 | 0 | 1 | [5 empty] | Dir O/C,
|  | 2020-11-05 | 21:07 | 2020-11-05 | 21:09 | 0:02 | 0 | 2 | [5 empty] | Dir O/C,
|  | 2020-11-09 | 07:40 | 2020-11-09 | 07:42 | 0:02 | 0 | 2 | [5 empty] | Dir O/C,
|  | 2021-02-05 | 09:26 | 2021-02-05 | 18:15 | 8:49 | 0 | 29 | [5 empty] | Dir E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
309 | 132kVJharsuguda-Ultratech |  |  |  |  | 0.04375 | 30 | 3 | [7 empty] | 31 | 8760 | 99.66% | 931.55 | 271560
|  | 2020-05-24 | 15:08 | 2020-05-24 | 16:11 | 1:03 | 0 | 32 | [5 empty] | Due to CT brust at lapanga grid switchyard.
|  | 2020-05-31 | 8:01 | 2020-05-31 | 20:58 | 12:58 | 12 | 58 | [5 empty] | snapped conductor at loc no-32to 33
|  | 2020-06-01 | 6:14 | 2020-06-01 | 2:52 | 0:46 | 0 | 46 | [5 empty] | E/F
|  | 2020-07-22 | 19:51 | 2020-07-22 | 22:17 | 02:26 | 2 | 15 | [5 empty] | B-phase PT brust at Ultratech switchyard.
|  | 2020-07-27 | 10:20 | 2020-07-27 | 10:33 | 00:13 | 0 | 13 | [5 empty] | Dir E/F at Jharsuguda
|  | 2020-07-28 | 14:36 | 2020-07-28 | 14:58 | 00:22 | 0 | 22 | [5 empty] | Dir E/F at Jharsuguda
|  | 2020-09-06 | 01:51 | 2020-09-06 | 02:48 | 0:57 | 0 | 57 | [5 empty] | Tripped at Budhipadar end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
310 | 132kV Joda- Banaspani(T) |  |  |  |  | 0.11181 | 13 | 41 | [7 empty] | 2.99 | 8760 | 99.84% | 40.9132 | 26192.4
|  | 2020-05-04 | 10:37 | 2020-05-04 | 11:02 | 0:25 | 0 | 25 | [5 empty] | Tripped at Both End . AT Joda end - Dp Relay Tripped,Zone-01, F.D- 11.610KM, F.L-L1-N, Fault
|  | 2020-05-08 | 21:36 | 2020-05-08 | 21:52 | 0:16 | 0 | 14 | [5 empty] | Tripped at Both End. AT Joda end -Dp Relay Tripped,Zone-01, F.D- 93.98KM, F.L-L1-L3, Fault Current :- IL1- 2278.49A, IL2-261.51A, IL3- 1129.94A, IN-1387.43A,P/S restored bt Ckt-II
|  | 2020-05-16 | 19:32 | 2020-05-16 | 19:41 | 0:09 | 0 | 7 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped,Zone-02, F.D- 131.55KM, F.L-L2-N, Fault Current :- IL1-237.67A, IL2-914.80A, IL3-148.03A, IN-1021.07A,P/S restored bt Ckt-I.
|  | 2020-05-16 | 19:46 | 2020-05-16 | 20:22 | 0:36 | 0 | 7 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped,Zone-01, F.D- 113.71KM, F.L-L2-N, Fault Current :- IL1-189.29A, IL2-1275.70A, IL3-197.87A, IN-1307.69A, P/S restored bt Ckt-I.
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
311 | 132kVJoda-FAP |  |  |  |  | 0.069444 | 13 | 13 | [7 empty] | 1.03 | 8760 | 99.85% | 13.6132 | 9022.8
|  | 2020-05-04 | 10:37 | 2020-05-04 | 11:02 | 0:25 | 0 | 25 | [5 empty] | Tripped at Both End . AT Joda end - Dp Relay Tripped,Zone-01, F.D- 11.610KM, F.L-L1-N, Fault
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
312 | 132kVJoda-Kenduposi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 49.42 | 8760 | 100% | 0 | 432919.2
313 | 132kV Joda-Palasponga |  |  |  |  | 0.26875 | 17 | 54 | [7 empty] | 41.6 | 8760 | 99.8% | 744.64 | 364416
|  | 2020-04-24 | 12:30 | 2020-04-24 | 13:05 | 0:35 | 0 | 35 | [5 empty] | At Polasponga end; E/F ,Zone- 1,Dist=34.13kM, Ia=254A, Ib=335A, Ic=201A, IG= 501A, In=0A
|  | 2020-04-28 | 12:46 | 2020-04-28 | 13:06 | 0:20 | 0 | 20 | [5 empty] | At Polasponga end: O/C (R,Y,B PH), Ia=1431.6A, Ib=1407.9A, Ic=1380.9A, In = 0.04A, Ig= 4A
|  | 2020-05-08 | 21:36 | 2020-05-08 | 21:52 | 0:16 | 0 | 14 | [5 empty] | Tripped at Both End. AT Joda end -Dp Relay Tripped,Zone-01, F.D- 93.98KM, F.L-L1-L3, Fault Current :- IL1- 2278.49A, IL2-261.51A, IL3- 1129.94A, IN-1387.43A,P/S restored bt Ckt-II
|  | 2020-05-16 | 19:32 | 2020-05-16 | 19:41 | 0:09 | 0 | 7 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped,Zone-02, F.D- 131.55KM, F.L-L2-N, Fault Current :- IL1-237.67A, IL2-914.80A, IL3-148.03A, IN-1021.07A,P/S restored bt Ckt-I.
|  | 2020-05-16 | 19:46 | 2020-05-16 | 20:22 | 0:36 | 0 | 7 | [5 empty] | Tripped at Both End . AT Joda end -Dp Relay Tripped,Zone-01, F.D- 113.71KM, F.L-L2-N, Fault Current :- IL1-189.29A, IL2-1275.70A, IL3-197.87A, IN-1307.69A, P/S restored bt Ckt-I.
|  | 2020-05-04 | 8:44 | 2020-05-04 | 9:12 | 0:28 | 0 | 28 | [5 empty] | Tripped at Both End. AT Joda end - Dp Relay Tripped,Zone- 01, F.D- 3.33KM, F.L-L2-N, Fault Current :- IL1-292.24A, IL2-5914.91A, IL3-242.10A, IN-5728.95A At PPNG end: E/F ZONE1 Loc=33.25KM, Ia=310A, Ib=354A, Ic=256A, IG= 546A, In=0A.
|  | 2020-05-06 | 23:06 | 2020-05-06 | 23:11 | 0:05 | 0 | 5 | [5 empty] | Tripped at Both End . AT Joda end - B/U Relay, Directional O/C Trip , Fault Current :-IL1-0.66KA, IL2- 0.70KA, IL3-0.60KA
|  | 2020-05-07 | 14:29 | 2020-05-07 | 14:34 | 0:05 | 0 | 5 | [5 empty] | O/C (R PH), Ia=422.5A, Ib=319.2A, Ic=273.1A, In = 0.04A, Ig= 5A
|  | 2020-05-08 | 17:50 | 2020-05-08 | 18:01 | 0:11 | 0 | 11 | [5 empty] | Tripped at Both End. AT Joda end - Dp Relay Tripped,Zone-01, F.D- 2.024KM, F.L-L2-N, Fault Current :- IL1-241.48A, IL2-6272.78A, IL3- 110.23A, IN-6050.51A
|  | 2020-05-20 | 13:48 | 2020-05-20 | 14:05 | 0:17 | 0 | 17 | [5 empty] | AT Joda end -Dp Relay Tripped,Zone- 01, F.D- 1.91KM, F.L-L2-N, Fault Current :- IL1-192.60A, IL2-5938.66A, IL3-50.82A, IN-5703.39A At PPNG end: E/F ZONE1 Loc=32.26KM, Ia=201A, Ib=185A, Ic=69A, IG= 437A, In=0A.
|  | 2020-05-20 | 14:06 | 2020-05-20 | 14:20 | 00:14 | 0 | 14 | [5 empty] | AT Joda end -Dp Relay Tripped,Zone- 01, F.D- 3.12KM, F.L-L2-N, Fault Current :- IL1-175A, IL2-5542.79A, IL3-125.38A, IN-5237.78A
|  | 2020-05-23 | 6:56 | 2020-05-23 | 6:58 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=222.5A, Ib=145.2A, Ic=56.1A, In = 0.04A, Ig= 5A
|  | 2020-05-26 | 10:21 | 2020-05-26 | 10:23 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=219.9A, Ib=185.1A, Ic=72.1A, In = 0.04A, Ig= 6A
|  | 2020-05-31 | 7:04 | 2020-05-31 | 7:07 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=221.2A, Ib=173.5A, Ic=82.7A, In = 0.04A, Ig= 5A
|  | 2020-05-31 | 20:40 | 2020-05-31 | 20:50 | 0:10 | 0 | 10 | [5 empty] | O/C (R PH), Ia=429.5A, Ib=383.9A, Ic=321.9A, In = 0.06A, Ig= 2.43A
|  | 2020-06-04 | 16:38 | 2020-06-04 | 17:05 | 0:27 | 0 | 27 | [5 empty] | O/C (R,Y,B PH), Ia=679.5A, Ib=706.6A, Ic=620.6A, Ig= 9.9A,In=0.11A
|  | 2020-06-09 | 10:34 | 2020-06-09 | 10:39 | 0:05 | 0 | 5 | [5 empty] | O/C (R,Y,B PH), Ia=435.9A, Ib=495.2A, Ic=508.8A, In = 0.09A, Ig= 31.6A,
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
|  | 2020-07-03 | 08:13 | 2020-07-03 | 08:20 | 00:07 | 0 | 7 | [5 empty] | O/C (R PH), Ia=1422.6A, Ib=1141.4A, Ic=201.7A, Ig= 611.97A,In=0.1A
|  | 2020-07-05 | 10:20 | 2020-07-05 | 10:30 | 00:10 | 0 | 10 | [5 empty] | Failed from Joda end
|  | 2020-07-06 | 06:09 | 2020-07-06 | 06:15 | 00:06 | 0 | 6 | [5 empty] | O/C (R PH), Ia=428A, Ib=357.1A, Ic=288.6A, Ig= 2.43A,In=0.06A
|  | 2020-07-04 | 13:20 | 2020-07-04 | 13:54 | 0:34 | 0 | 24 | [5 empty] | Failed from Joda end
|  | 2020-09-18 | 10:42 | 2020-09-18 | 11:14 | 0:32 | 0 | 32 | [5 empty] | Joda end detail - Zone-I, Fault loop - L1-N, Il1-7460.59A, Il2- 140.64A, Il3-151.16A,In-7378.38A, Distance- 1.08Km
|  | 2020-10-04 | 13:36 | 2020-10-04 | 13:38 | 0:02 | 0 | 2 | [5 empty] | TRIP,Ia=236.3A,Ib=88.0A,Ic=129.4 A, In=0.10A,Ig=142.35A
|  | 2020-10-05 | 07:10 | 2020-10-05 | 07:19 | 0:09 | 0 | 9 | [5 empty] | ABC tripped Ia=1547.6A, Ib=1422.7A, Ic=1410.9A,In = 0A, Ig= 39.4A
|  | 2021-01-07 | 13:21 | 2021-01-07 | 13:25 | 0:04 | 0 | 4 | [5 empty] | E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
314 | 132kV Palasponga- Keonjhargarh (T) |  |  |  |  | 0.37778 | 21 | 45 | [7 empty] | 19.43 | 8760 | 99.75% | 422.6025 | 170206.8
|  | 2020-04-24 | 12:30 | 2020-04-24 | 13:05 | 0:35 | 0 | 35 | [5 empty] | At Polasponga end; E/F ,Zone- 1,Dist=34.13kM, Ia=254A, Ib=335A, Ic=201A, IG= 501A, In=0A
|  | 2020-04-28 | 12:46 | 2020-04-28 | 13:06 | 0:20 | 0 | 20 | [5 empty] | At Polasponga end: O/C (R,Y,B PH), Ia=1431.6A, Ib=1407.9A, Ic=1380.9A, In = 0.04A, Ig= 4A
|  | 2020-05-04 | 8:44 | 2020-05-04 | 9:12 | 0:28 | 0 | 28 | [5 empty] | Tripped at Both End. AT Joda end - Dp Relay Tripped,Zone- 01, F.D- 3.33KM, F.L-L2-N, Fault Current :- IL1-292.24A, IL2-5914.91A, IL3-242.10A, IN-5728.95A At PPNG end: E/F ZONE1 Loc=33.25KM, Ia=310A, Ib=354A, Ic=256A, IG= 546A, In=0A.
|  | 2020-05-06 | 23:06 | 2020-05-06 | 23:11 | 0:05 | 0 | 5 | [5 empty] | Tripped at Both End . AT Joda end - B/U Relay, Directional O/C Trip , Fault Current :-IL1-0.66KA, IL2- 0.70KA, IL3-0.60KA
|  | 2020-05-07 | 14:29 | 2020-05-07 | 14:34 | 0:05 | 0 | 5 | [5 empty] | O/C (R PH), Ia=422.5A, Ib=319.2A, Ic=273.1A, In = 0.04A, Ig= 5A
|  | 2020-05-08 | 17:50 | 2020-05-08 | 18:01 | 0:11 | 0 | 11 | [5 empty] | Tripped at Both End. AT Joda end - Dp Relay Tripped,Zone-01, F.D- 2.024KM, F.L-L2-N, Fault Current :- IL1-241.48A, IL2-6272.78A, IL3- 110.23A, IN-6050.51A
|  | 2020-05-20 | 13:48 | 2020-05-20 | 14:05 | 0:17 | 0 | 17 | [5 empty] | AT Joda end -Dp Relay Tripped,Zone- 01, F.D- 1.91KM, F.L-L2-N, Fault Current :- IL1-192.60A, IL2-5938.66A, IL3-50.82A, IN-5703.39A At PPNG end: E/F ZONE1 Loc=32.26KM, Ia=201A, Ib=185A, Ic=69A, IG= 437A, In=0A.
|  | 2020-05-20 | 14:06 | 2020-05-20 | 14:20 | 00:14 | 0 | 14 | [5 empty] | AT Joda end -Dp Relay Tripped,Zone- 01, F.D- 3.12KM, F.L-L2-N, Fault Current :- IL1-175A, IL2-5542.79A, IL3-125.38A, IN-5237.78A
|  | 2020-05-23 | 6:56 | 2020-05-23 | 6:58 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=222.5A, Ib=145.2A, Ic=56.1A, In = 0.04A, Ig= 5A
|  | 2020-05-26 | 10:21 | 2020-05-26 | 10:23 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=219.9A, Ib=185.1A, Ic=72.1A, In = 0.04A, Ig= 6A
|  | 2020-05-31 | 7:04 | 2020-05-31 | 7:07 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=221.2A, Ib=173.5A, Ic=82.7A, In = 0.04A, Ig= 5A
|  | 2020-05-31 | 20:40 | 2020-05-31 | 20:50 | 0:10 | 0 | 10 | [5 empty] | O/C (R PH), Ia=429.5A, Ib=383.9A, Ic=321.9A, In = 0.06A, Ig= 2.43A
|  | 2020-06-04 | 16:38 | 2020-06-04 | 17:05 | 0:27 | 0 | 27 | [5 empty] | O/C (R,Y,B PH), Ia=679.5A, Ib=706.6A, Ic=620.6A, Ig= 9.9A,In=0.11A
|  | 2020-06-09 | 10:34 | 2020-06-09 | 10:39 | 0:05 | 0 | 5 | [5 empty] | O/C (R,Y,B PH), Ia=435.9A, Ib=495.2A, Ic=508.8A, In = 0.09A, Ig= 31.6A,
|  | 2020-06-01 | 20:08 | 2020-06-01 | 20:09 | 0:01 | 0 | 1 | [5 empty] | O/C (R PH), Ia=219.6A, Ib=174.5A, Ic=62.32A, Inm = 6.532A, Ind= 5.962A
|  | 2020-06-05 | 11:51 | 2020-06-05 | 11:52 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2020-06-06 | 3:22 | 2020-06-06 | 3:23 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2020-06-06 | 7:32 | 2020-06-06 | 7:33 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2020-06-14 | 14:46 | 2020-06-14 | 14:49 | 0:43 | 0 | 43 | [5 empty] | O/C (R PH), Ia=220.8A, Ib=137.7A, Ic=100.1A, Inm = 7.113A, Ind= 6.007A
|  | 2020-06-14 | 16:08 | 2020-06-14 | 16:11 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=220.9A, Ib=193.6A, Ic=36.56A, Inm = 6.962A, Ind= 5.462A
|  | 2020-06-14 | 18:06 | 2020-06-14 | 18:09 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=220.4A, Ib=166.1A, Ic=60.29A, Inm = 7.074A, Ind= 5.951A
|  | 2020-06-14 | 19:01 | 2020-06-14 | 19:05 | 0:04 | 0 | 4 | [5 empty] | O/C (R PH), Ia=225.6A, Ib=180.1A, Ic=80.2A, Inm = 6.98A, Ind= 5.438A
|  | 2020-06-14 | 19:43 | 2020-06-14 | 19:46 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=222.4A, Ib=160.6A, Ic=70.76A, Inm = 6.84A, Ind= 7.23A
|  | 2020-06-17 | 19:52 | 2020-06-17 | 19:55 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=219.3A, Ib=192.7A, Ic=33.22A, Inm = 6.948A, Ind= 5.346A
|  | 2020-06-18 | 15:04 | 2020-06-18 | 15:06 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.2A, Ib=157.0A, Ic=70.75A, Inm=6.578,Ind=5.235
|  | 2020-06-19 | 10:25 | 2020-06-19 | 10:27 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=219.9A, Ib=143.5A, Ic=67.71A, Inm = 6.6A, Ind= 5.75A
|  | 2020-06-19 | 10:39 | 2020-06-19 | 10:41 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.9A, Ib=171.2A, Ic=79.91A, Inm = 7.15A, Ind= 7.09A
|  | 2020-06-19 | 17:46 | 2020-06-19 | 17:49 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=220.5A, Ib=181.5A, Ic=46.38A, Inm = 6,853A, Ind= 6.273A
|  | 2020-06-20 | 18:21 | 2020-06-20 | 18:23 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.1A, Ib=167.2A, Ic=58.87A, Inm = 7.006A, Ind= 5.805A
|  | 2020-06-20 | 23:09 | 2020-06-20 | 23:11 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=219.6A, Ib=188.7A, Ic=35.27A, Inm = 7.132A, Ind= 6.021A
|  | 2020-06-21 | 12:46 | 2020-06-21 | 12:48 | 0:28 | 0 | 28 | [5 empty] | O/C (R PH), Ia=220.3A, Ib=143.4A, Ic=31.66A, Inm = 7.332A, Ind= 6.043A
|  | 2020-06-22 | 9:34 | 2020-06-22 | 9:36 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.8A, Ib=192.4A, Ic=34.65A, Inm = 6.819A, Ind= 5.729A
|  | 2020-06-22 | 16:48 | 2020-06-22 | 16:50 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=231.5A, Ib=178A, Ic=61.02A, Inm = 7.018A, Ind= 6.258A
|  | 2020-06-25 | 8:06 | 2020-06-25 | 8:08 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=221.9A, Ib=159.9A, Ic=68.83A, Inm = 6.924A, Ind= 5.734A
|  | 2020-06-30 | 11:05 | 2020-06-30 | 11:07 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.7A, Ib=167.3A, Ic=60.99A, Inm = 7.221A, Ind= 5.807A
|  | 2020-06-23 | 11:41 | 2020-06-23 | 12:56 | 1:15 | 0 | 48 | [5 empty] | Tripped from both ends. Power Supply restored by 220 kV Joda-TTPS Ckt-II
|  | 2020-07-19 | 10:08 | 2020-07-19 | 10:10 | 00:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=219.3A, Ib=166.8A, Ic=57.3,Inm = 6.642A, Ind= 4.937A
|  | 2020-07-19 | 23:13 | 2020-07-19 | 23:16 | 00:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=221.7A, Ib=178.9A, Ic=47.52,Inm = 5.78A, Ind= 5.421A
|  | 2020-07-03 | 14:05 | 2020-07-03 | 14:08 | 00:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=220.6A, Ib=192.8A, Ic=39.03,Inm = 7.106A, Ind= 5.333A
|  | 2020-07-11 | 08:08 | 2020-07-11 | 08:10 | 00:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.1A, Ib=142.8A, Ic=130,Inm = 7.355A, Ind= 7.223A
|  | 2020-07-11 | 08:43 | 2020-07-11 | 08:46 | 00:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=223A, Ib=120.9A, Ic=114.5,Inm = 7.091A, Ind= 6.597A
|  | 2020-07-22 | 09:06 | 2020-07-22 | 09:08 | 00:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.7A, Ib=198.9A, Ic=38.33A, Inm = 7.052A, Ind= 5.305A
|  | 2020-07-23 | 21:14 | 2020-07-23 | 21:18 | 00:04 | 0 | 4 | [5 empty] | O/C (R PH), Ia=226.3A, Ib=201.7A, Ic=37.84A, Inm = 6.397A, Ind= 4.26A
|  | 2020-07-27 | 11:42 | 2020-07-27 | 11:44 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=224.7A, Ib=179.6A, Ic=49.95A, Inm = 6.595A, Ind= 5.39A
|  | 2020-07-29 | 02:10 | 2020-07-29 | 02:13 | 00:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=226.5A, Ib=198A, Ic=41.12A, Inm=6.731,Ind=5.158A
|  | 2020-07-03 | 08:13 | 2020-07-03 | 08:20 | 00:07 | 0 | 7 | [5 empty] | O/C (R PH), Ia=1422.6A, Ib=1141.4A, Ic=201.7A, Ig= 611.97A,In=0.1A
|  | 2020-07-05 | 10:20 | 2020-07-05 | 10:30 | 00:10 | 0 | 10 | [5 empty] | Failed from Joda end
|  | 2020-07-06 | 06:09 | 2020-07-06 | 06:15 | 00:06 | 0 | 6 | [5 empty] | O/C (R PH), Ia=428A, Ib=357.1A, Ic=288.6A, Ig= 2.43A,In=0.06A
|  | 2020-07-04 | 13:20 | 2020-07-04 | 13:54 | 0:34 | 0 | 24 | [5 empty] | Failed from Joda end
|  | 2020-08-09 | 07:26 | 2020-08-09 | 07:28 | 00:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=226.5A, Ib=164.0A, Ic=7.02A,Inm = 7.12A, Ind= 5.805A
|  | 2020-08-11 | 15:40 | 2020-08-11 | 15:42 | 00:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=228.0A, Ib=138.0A, Ic=132.3A,Inm = 7.048A, Ind= 5.730A
|  | 2020-08-11 | 16:35 | 2020-08-11 | 16:37 | 00:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.2A, Ib=110.5A, Ic=118.2A,Inm = 7.036A, Ind= 5.922A
|  | 2020-08-23 | 09:08 | 2020-08-23 | 09:10 | 00:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=223.0A, Ib=183.7A, Ic=46.64,Inm = 6.851A, Ind= 6.299A
|  | 2020-08-24 | 13:02 | 2020-08-24 | 13:05 | 00:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=226.2A, Ib=163.2A, Ic=78.43,Inm = 7.032A, Ind= 5.931A
|  | 2020-08-24 | 16:57 | 2020-08-24 | 16:59 | 00:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.3A, Ib=152.1A, Ic=77.77,Inm = 7.26A, Ind= 6.131A
|  | 2020-08-30 | 20:58 | 2020-08-30 | 20:59 | 00:01 | 0 | 1 | [5 empty] | O/C (R PH), Ia=223.0A, Ib=123.5A, Ic=119.3A,Inm = 6.578A, Ind= 5.638A
|  | 2020-09-01 | 21:06 | 2020-09-01 | 21:09 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=223.5A, Ib=179.3A, Ic=59.94A,Inm = 4.718A, Ind= 5.179A
|  | 2020-09-04 | 09:58 | 2020-09-04 | 10:01 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=221.6A, Ib=180.9A, Ic=54.91A,Inm = 7.018A, Ind= 6.522A
|  | 2020-09-04 | 20:56 | 2020-09-04 | 20:58 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=219.3A, Ib=187.4A, Ic=43.32A,Inm = 7.219A, Ind= 5.821A
|  | 2020-09-04 | 23:57 | 2020-09-04 | 23:59 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.4A, Ib=194.6A, Ic=29.77A,Inm = 7.023A, Ind= 5.653A
|  | 2020-09-05 | 13:22 | 2020-09-05 | 13:24 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=225.0A, Ib=187.1A, Ic=44.21A,Inm = 5.175A, Ind= 6.089A
|  | 2020-09-09 | 02:36 | 2020-09-09 | 02:39 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=218.8A, Ib=155.3A, Ic=75.66A,Inm = 7.279A, Ind= 6.349A
|  | 2020-09-10 | 10:58 | 2020-09-10 | 11:00 | 0:02 | 0 | 2 | [5 empty] | O/C (R-ph & Y-ph), Ia=226.0A, Ib=221.3A, Ic=44.36A,Inm = 6.76A, Ind= 6.04A
|  | 2020-09-10 | 11:08 | 2020-09-10 | 11:11 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=221.5A, Ib=189.0A, Ic=138.78,Inm = 7.08A, Ind= 5.28A
|  | 2020-09-10 | 23:50 | 2020-09-10 | 23:52 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.5A, Ib=167.6A, Ic=66.3A,Inm = 7.020A, Ind= 6.895A
|  | 2020-09-12 | 18:30 | 2020-09-12 | 18:33 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=219.9A, Ib=158.7A, Ic=84.06A,Inm = 6.92A, Ind= 6.051A
|  | 2020-09-15 | 01:18 | 2020-09-15 | 01:21 | 0:03 | 0 | 3 | [5 empty] | O/C (R PH), Ia=219.8A, Ib=179.5A, Ic=45.06A,Inm = 6.815A, Ind= 5.542A
|  | 2020-09-29 | 01:22 | 2020-09-29 | 01:23 | 0:01 | 0 | 1 | [5 empty] | O/C (R PH), Ia=220.2A, Ib=137.5A, Ic=94.75A,Inm = 6.911A, Ind= 5.988A
|  | 2020-09-29 | 01:32 | 2020-09-29 | 01:34 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=219.1A, Ib=125.8A, Ic=113.8A,Inm = 7.258A, Ind= 6.418A
|  | 2020-09-23 | 21:22 | 2020-09-23 | 21:23 | 0:01 | 0 | 1 | [5 empty] | O/C (R PH), Ia=220.3A, Ib=104.5A, Ic=137.4A,Inm = 7.041A, Ind= 5.614A
|  | 2020-09-18 | 10:42 | 2020-09-18 | 11:14 | 0:32 | 0 | 32 | [5 empty] | Joda end detail - Zone-I, Fault loop - L1-N, Il1-7460.59A, Il2- 140.64A, Il3-151.16A,In-7378.38A, Distance- 1.08Km
|  | 2020-10-02 | 09:19 | 2020-10-02 | 09:21 | 0:28 | 0 | 28 | [5 empty] | O/C (R PH), Ia=222.9A, Ib=171.7A, Ic=56.82A,Inm = 6.911A, Ind= 5.148A
|  | 2020-10-03 | 12:57 | 2020-10-03 | 12:58 | 0:14 | 0 | 14 | [5 empty] | O/C (R PH), Ia=224.8A, Ib=180.5A, Ic=52.18A,Inm = 7.161A, Ind= 6.510A
|  | 2020-10-11 | 15:52 | 2020-10-11 | 15:53 | 0:01 | 0 | 1 | [5 empty] | O/C (R PH), Ia=221.4A, Ib=156.8A, Ic=97.15A,Inm = 7.289A, Ind= 6.904A
|  | 2020-10-14 | 13:36 | 2020-10-14 | 13:37 | 0:01 | 0 | 1 | [5 empty] | O/C (R PH), Ia=222.1A, Ib=149.3A, Ic=92.1A,Inm = 7.05A,
|  | 2020-10-14 | 14:42 | 2020-10-14 | 14:43 | 0:01 | 0 | 1 | [5 empty] | O/C (R PH), Ia=227.5A, Ib=166.2A, Ic=70.33A,Inm = 7.143A, Ind= 6.584A
|  | 2020-10-15 | 16:08 | 2020-10-15 | 16:01 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=220.7A, Ib=160.1A, Ic=69.12A,Inm = 6.805A, Ind= 5.168A
|  | 2020-10-17 | 14:02 | 2020-10-17 | 14:04 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=221.3A, Ib=193.9A, Ic=37.18A,Inm = 7.307A, Ind= 5.652A
|  | 2020-10-19 | 22:02 | 2020-10-19 | 22:21 | 0:01 | 0 | 1 | [5 empty] | O/C (R PH), Ia=220.1A, Ib=156A, Ic=82.36A,Inm = 7.218A, Ind= 7.194A
|  | 2020-10-23 | 17:52 | 2020-10-23 | 17:53 | 0:01 | 0 | 1 | [5 empty] | O/C (R PH), Ia=220.0A, Ib=180.8A, Ic=45.68A,Inm =7.071A, Ind= 6.263A
|  | 2020-10-04 | 13:36 | 2020-10-04 | 13:38 | 0:02 | 0 | 2 | [5 empty] | TRIP,Ia=236.3A,Ib=88.0A,Ic=129.4 A, In=0.10A,Ig=142.35A
|  | 2020-10-05 | 07:10 | 2020-10-05 | 07:19 | 0:09 | 0 | 9 | [5 empty] | ABC tripped Ia=1547.6A, Ib=1422.7A, Ic=1410.9A,In = 0A, Ig= 39.4A
|  | 2021-01-01 | 21:02 | 2021-01-01 | 21:04 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-06 | 00:40 | 2021-01-06 | 00:42 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-08 | 16:20 | 2021-01-08 | 16:22 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-09 | 23:25 | 2021-01-09 | 23:26 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-11 | 10:27 | 2021-01-11 | 10:28 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-11 | 17:32 | 2021-01-11 | 17:34 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-13 | 15:30 | 2021-01-13 | 15:32 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-24 | 11:29 | 2021-01-24 | 11:31 | 00:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-31 | 09:11 | 2021-01-31 | 09:14 | 00:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-07 | 13:21 | 2021-01-07 | 13:25 | 0:04 | 0 | 4 | [5 empty] | E/F
|  | 2021-02-01 | 08:23 | 2021-02-01 | 08:24 | 0:01 | 0 | 1 | [5 empty] | O/C (R PH), Ia=242.6A, Ib=211.2A, Ic=36.91A,Inm = 6.755A, Ind=
|  | 2021-02-01 | 19:19 | 2021-02-01 | 19:21 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=1.038KA, Ib=40.03A, Ic=31.3A,Inm = 1.002KA, Ind= 1.004KA
|  | 2021-02-06 | 10:59 | 2021-02-06 | 11:01 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=243.8A, Ib=201.5A, Ic=48.24A,Inm = 6.974A, Ind=
|  | 2021-02-19 | 06:14 | 2021-02-19 | 06:16 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=240.1A, Ib=190.1A, Ic=54.47A,Inm = 6.791A, Ind=
|  | 2021-02-23 | 12:00 | 2021-02-23 | 12:28 | 0:02 | 0 | 2 | [5 empty] | O/C (R PH), Ia=241.9A, Ib=171.8A, Ic=80.47A,Inm = 6.421A, Ind= 6.33A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
315 | 132kV OPCL-Kamakhyanagar |  |  |  |  | 0.093056 | 14 | 7 | [7 empty] | 54.2 | 8760 | 99.84% | 765.1233 | 474792
|  | 2020-05-29 | 2:33 | 2020-05-29 | 2:50 | 0:17 | 0 | 17 | [5 empty] | Tripped
|  | 2020-06-08 | 13:34 | 2020-06-08 | 13:52 | 0:18 | 0 | 18 | [5 empty] | DP, M/T- 86, 3 phase [Heavy thunder and rain]
|  | 2020-06-14 | 11:55 | 2020-06-14 | 12:15 | 0:20 | 0 | 16 | [5 empty] | O/C [Heavy Thunder & Lightning]
|  | 2020-06-24 | 3:34 | 2020-06-24 | 03:56 | 0:22 | 0 | 21 | [5 empty] | O/C, M/T- 86
|  | 2020-06-29 | 17:18 | 2020-06-29 | 17:34 | 0:16 | 0 | 16 | [5 empty] | Tripped at OPCL end
|  | 2020-07-04 | 07:48 | 2020-07-04 | 08:10 | 0:22 | 0 | 22 | [5 empty] | O/C & M/T- 86 at kamakhyanagar end.
|  | 2020-08-01 | 23:05 | 2020-08-01 | 23:24 | 0:19 | 0 | 17 | [5 empty] | O/C & M/T- 86, Distance-39.885 KM, ‘B’ phase Current-2.05 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
316 | 132kV Kamakhyanagar-Duburi |  |  |  |  | 0.28194 | 15 | 9 | [7 empty] | 61.82 | 8760 | 99.83% | 936.573 | 541543.2
|  | 2020-05-08 | 22:28 | 2020-05-08 | 22:55 | 0:27 | 0 | 27 | [5 empty] | O/C
|  | 2020-05-20 | 11:51 | 2020-05-20 | 11:59 | 0:08 | 0 | 8 | [5 empty] | E/F
|  | 2020-05-29 | 2:33 | 2020-05-29 | 3:11 | 0:38 | 0 | 17 | [5 empty] | Tripped on Master trip-86 with tripping of all transformers at Kamakhyanagar [Due to Thunder & lightening]
|  | 2020-06-08 | 13:34 | 2020-06-08 | 17:53 | 3:19 | 0 | 18 | [5 empty] | Auto Trip
|  | 2020-06-14 | 11:55 | 2020-06-14 | 12:11 | 0:16 | 0 | 16 | [5 empty] | O/C
|  | 2020-06-24 | 3:34 | 2020-06-24 | 03:55 | 0:21 | 0 | 21 | [5 empty] | O/C, M/T- 86
|  | 2020-07-04 | 07:48 | 2020-07-04 | 08:25 | 0:37 | 0 | 22 | [5 empty] | O/C & M/T- 86 at kamakhyanagar end.
|  | 2020-08-01 | 23:05 | 2020-08-01 | 23:22 | 0:17 | 0 | 17 | [5 empty] | M/T- 86 at Kamakhyanagar end.
|  | 2020-08-04 | 15:37 | 2020-08-04 | 16:01 | 0:24 | 0 | 24 | [5 empty] | Auto trip
|  | 2020-09-01 | 10:20 | 2020-09-01 | 10:39 | 0:19 | 0 | 19 | [5 empty] | E/F & M/T- 86
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
317 | 132kV Kamakhya Nagar-Duburi 'T' point to Goda-Kalarangi |  |  |  |  | 0.23819 | 14 | 27 | [7 empty] | 14.62 | 7356 | 99.8% | 211.259 | 107544.72
|  | 2020-06-08 | 13:34 | 2020-06-08 | 17:53 | 3:19 | 0 | 18 | [5 empty] | Auto Trip
|  | 2020-06-14 | 11:55 | 2020-06-14 | 12:11 | 0:16 | 0 | 16 | [5 empty] | O/C
|  | 2020-06-24 | 3:34 | 2020-06-24 | 03:55 | 0:21 | 0 | 21 | [5 empty] | O/C, M/T- 86
|  | 2020-07-04 | 07:48 | 2020-07-04 | 08:25 | 0:37 | 0 | 22 | [5 empty] | O/C & M/T- 86 at kamakhyanagar end.
|  | 2020-08-01 | 23:05 | 2020-08-01 | 23:22 | 0:17 | 0 | 17 | [5 empty] | M/T- 86 at Kamakhyanagar end.
|  | 2020-08-04 | 15:37 | 2020-08-04 | 16:01 | 0:24 | 0 | 24 | [5 empty] | Auto trip
|  | 2020-09-01 | 10:20 | 2020-09-01 | 10:39 | 0:19 | 0 | 19 | [5 empty] | E/F & M/T- 86
|  | 2020-09-21 | 15:39 | 2020-09-21 | 15:49 | 0:10 | 0 | 10 | [5 empty] | At Goda grid s/s- Tripped on E/F- B- ph, IA-188.2A, IB-1.138 KA, IC- 4.93KA, Fault loc- 10.45km [heavy lightening, thundering & rain]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
318 | 132kV Kamakhya Nagar-Duburi 'T' point to Kalarangi |  |  |  |  | 0.064583 | 13 | 12 | [7 empty] | 13.02 | 1404 | 99.06% | 171.864 | 18280.08
|  | 2020-05-08 | 22:28 | 2020-05-08 | 22:55 | 0:27 | 0 | 27 | [5 empty] | O/C
|  | 2020-05-20 | 11:51 | 2020-05-20 | 11:59 | 0:08 | 0 | 8 | [5 empty] | E/F
|  | 2020-05-29 | 2:33 | 2020-05-29 | 3:11 | 0:38 | 0 | 17 | [5 empty] | Tripped on Master trip-86 with tripping of all transformers at Kamakhyanagar [Due to Thunder & lightening]
|  | 2020-05-01 | 11:05 | 2020-05-01 | 11:20 | 0:20 | 0 | 20 | [5 empty] | E/F trip & master relay
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
319 | 132kV Kamakhya Nagar - Kamakhya Nagar RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.94 | 8760 | 100% | 0 | 43274.4
320 | 132kV Katapalli-Sambalpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 21.85 | 8760 | 100% | 0 | 191406
321 | 132kV Katapalli-RTSS Godhbhaga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.66 | 192 | 100% | 0 | 2046.72
322 | 132kV Boinda-Rairakhol |  |  |  |  | 0.12986 | 13 | 39 | [7 empty] | 59 | 8760 | 99.84% | 805.35 | 516840
|  | 2020-06-03 | 17:41 | 2020-06-03 | 17:55 | 0:14 | 0 | 14 | [5 empty] | O/C on R-phase, DP, 2426.2 A, 33.665 km, L1-N
|  | 2020-06-27 | 8:50 | 2020-06-27 | 9:01 | 0:11 | 0 | 11 | [5 empty] | Tripped at Boinda end.
|  | 2020-07-10 | 01:45 | 2020-07-10 | 01:55 | 00:10 | 0 | 10 | [5 empty] | Tripped at Boinda
|  | 2020-08-18 | 09:28 | 2020-08-18 | 09:36 | 0:08 | 0 | 8 | [5 empty] | Tripped [DUE TO CIRCUIT BREAKER PROBLEM AT BOINDA]
|  | 2020-08-20 | 07:38 | 2020-08-20 | 07:40 | 0:02 | 0 | 2 | [5 empty] | TRIPPED ON B/U RELAY INDICATING B-PHASE O/C & E/F AT RAIRAKHOL GRID END. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY]
|  | 2020-08-19 | 23:31 | 2020-08-19 | 23:36 | 0:05 | 0 | 5 | [5 empty] | Tripped at Angul end. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY AT RAIRAKHOL GRID END.]
|  | 2020-08-20 | 07:42 | 2020-08-20 | 07:49 | 0:07 | 0 | 7 | [5 empty] | O/C in Y-Phase, Fault Current(Y- PH)-1.06 KA and E/F.
|  | 2020-08-20 | 07:27 | 2020-08-20 | 07:40 | 0:13 | 0 | 6 | [5 empty] | Tripped at Angul end. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY AT RAIRAKHOL GRID END.]
|  | 2020-08-25 | 14:25 | 2020-08-25 | 14:33 | 0:08 | 0 | 3 | [5 empty] | TRIPPED AT ANGUL END
|  | 2020-09-04 | 16:34 | 2020-09-04 | 16:41 | 0:07 | 0 | 7 | [5 empty] | Tripped at Rairakhol end.
|  | 2020-10-13 | 20:36 | 2020-10-13 | 20:42 | 0:06 | 0 | 6 | [5 empty] | Trig Signal- ZM01 Fault Abs Dist.- 26.915 KM Fault Loop- L3N, Fault current IR=231.47 A, IY= 385.90 A, IB= 3124.93 A
|  | 2020-10-29 | 15:17 | 2020-10-29 | 17:03 | 1:46 | 0 | 20 | [5 empty] | Tripped on E/F at both ends. [ one big mango tree has been uprooted by the railway authority which was in close proximity to 132 KV TTPS-Angul and 132 KV Chainpal-Angul double circuit
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
323 | 132kV Sambalpur-Rairakhol |  |  |  |  | 0 | 0 | 0 | [7 empty] | 63.46 | 7392 | 100% | 0 | 469096.32
324 | 132kV Sambalpur-Maneswar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.2 | 1368 | 100% | 0 | 15321.6
325 | 132kV Maneswar- RTSS Maneswar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.2 | 120 | 100% | 0 | 624
326 | 132kV Maneswar-Rairakhol |  |  |  |  | 0 | 0 | 0 | [7 empty] | 57.46 | 1368 | 100% | 0 | 78605.28
327 | 132kV Kendrapada-Marshaghai ckt-I |  |  |  |  | 0.125 | 14 | 45 | [7 empty] | 16.2 | 8760 | 99.83% | 238.95 | 141912
|  | 2020-05-21 | 6:58 | 2020-05-21 | 7:18 | 0:20 | 0 | 19 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-05-01 | 16:58 | 2020-05-01 | 17:42 | 0:44 | 0 | 41 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-05-19 | 5:49 | 2020-05-19 | 5:58 | 0:09 | 0 | 8 | [5 empty] | O/C & E/F
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:36 | 0:05 | 0 | 5 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 14:06 | 2020-06-06 | 14:12 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-09 | 22:23 | 2020-06-09 | 22:29 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-22 | 5:45 | 2020-06-22 | 6:12 | 0:27 | 0 | 11 | [5 empty] | DP Relay,Dist.-13.13km, Y-Ph.,Z1
|  | 2020-09-06 | 06:47 | 2020-09-06 | 06:53 | 0:06 | 0 | 6 | [5 empty] | DIR. O/C PICKED UP. IL1=0.84KA, IL3=0.84KA
|  | 2020-09-19 | 00:09 | 2020-09-19 | 00:18 | 0:09 | 0 | 9 | [5 empty] | DIR. O/C PICKED UP. IL1=0.8KA , IL3=0.8KA
|  | 2020-09-13 | 16:05 | 2020-09-13 | 16:08 | 0:03 | 0 | 3 | [5 empty] | DIR. O/C PICKED UP .IL1=0.8KA , IL3=0.8KA
|  | 2020-09-16 | 07:00 | 2020-09-16 | 07:05 | 0:05 | 0 | 5 | [5 empty] | DIR. O/C PICKED UP. IL1=0.8KA , IL3=0.8KA
|  | 2020-09-25 | 08:14 | 2020-09-25 | 08:16 | 0:02 | 0 | 2 | [5 empty] | DIR. O/C PICKED UP. IL1=0.84KA , IL3=0.84KA
|  | 2020-09-09 | 15:44 | 2020-09-09 | 16:22 | 0:38 | 0 | 38 | [5 empty] | TRIPPED ON E/F WITH M/R.
|  | 2020-10-14 | 06:29 | 2020-10-14 | 06:35 | 00:06 | 0 | 6 | [5 empty] | Tripeed On Differential Relay With M/R Due To 132Kv R -Ph CT Brust And Charged After Replacement Of New CT.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
328 | 132kV Marshaghai-Paradeep ckt-I |  |  |  |  | 0.084028 | 13 | 5 | [7 empty] | 19.61 | 8760 | 99.85% | 256.5642 | 171783.6
|  | 2020-05-21 | 6:59 | 2020-05-21 | 7:44 | 0:45 | 0 | 19 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-05-19 | 5:49 | 2020-05-19 | 5:57 | 0:08 | 0 | 8 | [5 empty] | O/C & E/F
|  | 2020-09-09 | 15:44 | 2020-09-09 | 16:52 | 1:08 | 0 | 38 | [5 empty] | IL1=0.06KA , IL2=0.15KA , IL3=0.10KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
329 | 132kV Marshaghai-Kendrapara RTSS |  |  |  |  | 0.063194 | 13 | 30 | [7 empty] | 14.08 | 7884 | 99.83% | 190.08 | 111006.72
|  | 2020-05-21 | 6:58 | 2020-05-21 | 7:18 | 0:20 | 0 | 19 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-05-19 | 5:49 | 2020-05-19 | 5:57 | 0:08 | 0 | 8 | [5 empty] | O/C & E/F
|  | 2020-09-06 | 06:47 | 2020-09-06 | 06:53 | 0:06 | 0 | 6 | [5 empty] | DIR. O/C PICKED UP. IL1=0.84KA, IL3=0.84KA
|  | 2020-09-19 | 00:09 | 2020-09-19 | 00:18 | 0:09 | 0 | 9 | [5 empty] | DIR. O/C PICKED UP. IL1=0.8KA , IL3=0.8KA
|  | 2020-09-13 | 16:05 | 2020-09-13 | 16:08 | 0:03 | 0 | 3 | [5 empty] | DIR. O/C PICKED UP .IL1=0.8KA , IL3=0.8KA
|  | 2020-09-16 | 07:00 | 2020-09-16 | 07:05 | 0:05 | 0 | 5 | [5 empty] | DIR. O/C PICKED UP. IL1=0.8KA , IL3=0.8KA
|  | 2020-09-25 | 08:14 | 2020-09-25 | 08:16 | 0:02 | 0 | 2 | [5 empty] | DIR. O/C PICKED UP. IL1=0.84KA , IL3=0.84KA
|  | 2020-09-09 | 15:44 | 2020-09-09 | 16:22 | 0:38 | 0 | 38 | [5 empty] | TRIPPED ON E/F WITH M/R.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
330 | 132kV Kendrapada-Paradeep Ckt-II |  |  |  |  | 1899-12-31 00:08 | 13 | 31 | [7 empty] | 15.77 | 8760 | 99.85% | 213.1578 | 138145.2
|  | 2020-05-21 | 6:58 | 2020-05-21 | 7:43 | 0:45 | 0 | 19 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:45 | 0:14 | 0 | 5 | [5 empty] | DP Relay,Dist.-2.04km
|  | 2020-06-06 | 14:06 | 2020-06-06 | 16:09 | 2:03 | 0 | 6 | [5 empty] | DP Relay, Dist.- 4.02km
|  | 2020-06-09 | 22:23 | 2020-06-10 | 18:08 | 19:45 | 0 | 6 | [5 empty] | DP Relay, Dist.- 12.19km [Due to snapping of conductor.]
|  | 2020-06-22 | 5:45 | 2020-06-22 | 05:56 | 0:11 | 0 | 11 | [5 empty] | B/U,E/F, M/R.
|  | 2020-09-09 | 15:44 | 2020-09-09 | 16:54 | 1:10 | 0 | 38 | [5 empty] | TRIPPED ON E/F WITH M/R.
|  | 2020-10-14 | 06:29 | 2020-10-14 | 06:37 | 00:08 | 0 | 6 | [5 empty] | Tripeed On Differential Relay With M/R Due To 132Kv R -Ph CT Brust And Charged After Replacement Of New CT.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
331 | 132kV Kendrapada-Pattamundai |  |  |  |  | 1899-12-31 08:59 | 22 | 6 | [7 empty] | 19.1 | 8760 | 99.75% | 422.11 | 167316
|  | 2020-05-21 | 6:58 | 2020-05-21 | 7:43 | 0:45 | 0 | 19 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-06-03 | 17:32 | 2020-06-03 | 17:34 | 0:02 | 0 | 2 | [5 empty] | Tripped on O/C(Y- Phase) along with M/R at Pattamundai end.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:45 | 0:14 | 0 | 5 | [5 empty] | DP Relay,Dist.-2.04km
|  | 2020-06-06 | 14:06 | 2020-06-06 | 16:09 | 2:03 | 0 | 6 | [5 empty] | DP Relay, Dist.- 4.02km
|  | 2020-06-09 | 22:23 | 2020-06-10 | 18:08 | 19:45 | 0 | 6 | [5 empty] | DP Relay, Dist.- 12.19km [Due to snapping of conductor.]
|  | 2020-06-22 | 5:45 | 2020-06-22 | 05:56 | 0:11 | 0 | 11 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:36 | 0:05 | 0 | 5 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 14:06 | 2020-06-06 | 14:12 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-09 | 22:23 | 2020-06-09 | 22:29 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-22 | 5:45 | 2020-06-22 | 6:12 | 0:27 | 0 | 11 | [5 empty] | DP Relay,Dist.-13.13km, Y-Ph.,Z1
|  | 2020-07-17 | 22:29 | 2020-07-17 | 22:33 | 00:04 | 0 | 4 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-09-09 | 15:44 | 2020-09-09 | 16:52 | 1:08 | 0 | 38 | [5 empty] | IL1=0.06KA , IL2=0.15KA , IL3=0.10KA
|  | 2020-09-20 | 09:25 | 2020-09-20 | 09:41 | 0:16 | 0 | 16 | [5 empty] | Tripped on Distance protection zone- 1, B-phase showing distance of 14.5 km along with tripping of 132 KV Pattamundai-Olaver Ckt-I.
|  | 2020-10-03 | 10:50 | 2020-10-03 | 14:41 | 3:51 | 3 | 51 | [5 empty] | TRIPPED ON E/F WITH M/R AND DELAY CHARGED FOR S/D
|  | 2020-10-14 | 06:29 | 2020-10-14 | 06:35 | 0:06 | 0 | 6 | [5 empty] | Tripeed On Differential Relay With M/R Due To 132Kv R -Ph CT Brust And Charged After Replacement Of New CT.
|  | 2020-11-17 | 15:15 | 2020-11-17 | 18:40 | 3:25 | 3 | 25 | [5 empty] | Tripped on Distance protection Zone- 1 and M/R with a loud sound in the switchyard due to burst of B-Ph insulator string of 132 KV main bus(B/C section). Fault location- 326.7 m, Ia=456.9 A, Ib=614.1A, Ic=2.475 KA
|  | 2020-12-05 | 23:34 | 2020-12-06 | 0:03 | 0:29 | 0 | 29 | [5 empty] | Incomer breaker Tripped at Pattamundai end on DP -Zone-I along with M/R. Started Phase-CN, Tripped phase A B C. Fault Location- 328.2 m, IA=500.6 A, IB=626.5 A, IC=2.529 . [B-Phase insulator string of 132KV cross bus of 20MVA TRF-II burst. ]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
332 | 132kV Pattamundai-Olavar Ckt - I |  |  |  |  | 1899-12-31 08:47 | 22 | 36 | [7 empty] | 23.94 | 8760 | 99.74% | 541.044 | 209714.4
|  | 2020-05-21 | 6:58 | 2020-05-21 | 7:18 | 0:20 | 0 | 19 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-06-03 | 17:32 | 2020-06-03 | 17:34 | 0:02 | 0 | 2 | [5 empty] | Tripped on O/C(Y- Phase) along with M/R at Pattamundai end.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:45 | 0:14 | 0 | 5 | [5 empty] | DP Relay,Dist.-2.04km
|  | 2020-06-06 | 14:06 | 2020-06-06 | 16:09 | 2:03 | 0 | 6 | [5 empty] | DP Relay, Dist.- 4.02km
|  | 2020-06-09 | 22:23 | 2020-06-10 | 18:08 | 19:45 | 0 | 6 | [5 empty] | DP Relay, Dist.- 12.19km [Due to snapping of conductor.]
|  | 2020-06-22 | 5:45 | 2020-06-22 | 05:56 | 0:11 | 0 | 11 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:36 | 0:05 | 0 | 5 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 14:06 | 2020-06-06 | 14:12 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-09 | 22:23 | 2020-06-09 | 22:29 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-22 | 5:45 | 2020-06-22 | 6:12 | 0:27 | 0 | 11 | [5 empty] | DP Relay,Dist.-13.13km, Y-Ph.,Z1
|  | 2020-07-08 | 18:39 | 2020-07-08 | 18:48 | 00:09 | 0 | 9 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-17 | 00:10 | 2020-07-17 | 00:13 | 00:03 | 0 | 3 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-21 | 19:20 | 2020-07-21 | 19:31 | 00:11 | 0 | 11 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-17 | 22:29 | 2020-07-17 | 22:33 | 00:04 | 0 | 4 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-07-26 | 19:25 | 2020-07-26 | 19:32 | 00:07 | 0 | 7 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-09-09 | 15:44 | 2020-09-09 | 16:52 | 1:08 | 0 | 38 | [5 empty] | IL1=0.06KA , IL2=0.15KA , IL3=0.10KA
|  | 2020-09-20 | 09:25 | 2020-09-20 | 09:54 | 0:29 | 0 | 16 | [5 empty] | Tripped on Distance protection zone- 1, B-phase showing distance of 14.5 km along with tripping of 132 KV Pattamundai-Olaver Ckt-I.
|  | 2020-10-03 | 10:50 | 2020-10-03 | 14:41 | 3:51 | 3 | 51 | [5 empty] | TRIPPED ON E/F WITH M/R AND DELAY CHARGED FOR S/D
|  | 2020-10-14 | 06:29 | 2020-10-14 | 06:35 | 0:06 | 0 | 6 | [5 empty] | Tripeed On Differential Relay With M/R Due To 132Kv R -Ph CT Brust And Charged After Replacement Of New CT.
|  | 2020-11-17 | 15:15 | 2020-11-17 | 18:40 | 3:25 | 3 | 25 | [5 empty] | Tripped on Distance protection Zone- 1 and M/R with a loud sound in the switchyard due to burst of B-Ph insulator string of 132 KV main bus(B/C section). Fault location- 326.7 m, Ia=456.9 A, Ib=614.1A, Ic=2.475 KA
|  | 2020-12-05 | 23:34 | 2020-12-06 | 0:03 | 0:29 | 0 | 29 | [5 empty] | Incomer breaker Tripped at Pattamundai end on DP -Zone-I along with M/R. Started Phase-CN, Tripped phase A B C. Fault Location- 328.2 m, IA=500.6 A, IB=626.5 A, IC=2.529 . [B-Phase insulator string of 132KV cross bus of 20MVA TRF-II burst. ]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
333 | 132kV Pattamundai-Olavar Ckt -II |  |  |  |  | 1900-01-01 17:34 | 22 | 36 | [7 empty] | 23.94 | 8760 | 99.74% | 541.044 | 209714.4
|  | 2020-05-21 | 6:58 | 2020-05-21 | 7:18 | 0:20 | 0 | 19 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-06-03 | 17:32 | 2020-06-03 | 17:34 | 0:02 | 0 | 2 | [5 empty] | Tripped on O/C(Y- Phase) along with M/R at Pattamundai end.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:45 | 0:14 | 0 | 5 | [5 empty] | DP Relay,Dist.-2.04km
|  | 2020-06-06 | 14:06 | 2020-06-06 | 16:09 | 2:03 | 0 | 6 | [5 empty] | DP Relay, Dist.- 4.02km
|  | 2020-06-09 | 22:23 | 2020-06-10 | 18:08 | 19:45 | 0 | 6 | [5 empty] | DP Relay, Dist.- 12.19km [Due to snapping of conductor.]
|  | 2020-06-22 | 5:45 | 2020-06-22 | 05:56 | 0:11 | 0 | 11 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:36 | 0:05 | 0 | 5 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 14:06 | 2020-06-06 | 14:12 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-09 | 22:23 | 2020-06-09 | 22:29 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-22 | 5:45 | 2020-06-22 | 6:12 | 0:27 | 0 | 11 | [5 empty] | DP Relay,Dist.-13.13km, Y-Ph.,Z1
|  | 2020-07-08 | 18:39 | 2020-07-08 | 18:48 | 00:09 | 0 | 9 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-17 | 00:10 | 2020-07-17 | 00:13 | 00:03 | 0 | 3 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-21 | 19:20 | 2020-07-21 | 19:31 | 00:11 | 0 | 11 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-17 | 22:29 | 2020-07-17 | 22:33 | 00:04 | 0 | 4 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-07-26 | 19:25 | 2020-07-26 | 19:32 | 00:07 | 0 | 7 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-09-09 | 15:44 | 2020-09-09 | 16:52 | 1:08 | 0 | 38 | [5 empty] | IL1=0.06KA , IL2=0.15KA , IL3=0.10KA
|  | 2020-09-20 | 09:25 | 2020-09-20 | 09:54 | 0:29 | 0 | 16 | [5 empty] | Tripped on Distance protection zone- 1, B-phase showing distance of 14.5 km along with tripping of 132 KV Pattamundai-Olaver Ckt-I.
|  | 2020-10-03 | 10:50 | 2020-10-03 | 14:41 | 3:51 | 3 | 51 | [5 empty] | TRIPPED ON E/F WITH M/R AND DELAY CHARGED FOR S/D
|  | 2020-10-14 | 06:29 | 2020-10-14 | 06:35 | 0:06 | 0 | 6 | [5 empty] | Tripeed On Differential Relay With M/R Due To 132Kv R -Ph CT Brust And Charged After Replacement Of New CT.
|  | 2020-11-17 | 15:15 | 2020-11-17 | 18:40 | 3:25 | 3 | 25 | [5 empty] | Tripped on Distance protection Zone- 1 and M/R with a loud sound in the switchyard due to burst of B-Ph insulator string of 132 KV main bus(B/C section). Fault location- 326.7 m, Ia=456.9 A, Ib=614.1A, Ic=2.475 KA
|  | 2020-12-05 | 23:34 | 2020-12-06 | 0:03 | 0:29 | 0 | 29 | [5 empty] | Incomer breaker Tripped at Pattamundai end on DP -Zone-I along with M/R. Started Phase-CN, Tripped phase A B C. Fault Location- 328.2 m, IA=500.6 A, IB=626.5 A, IC=2.529 . [B-Phase insulator string of 132KV cross bus of 20MVA TRF-II burst. ]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
334 | 132kV Olavar - Chandabali Ckt - I |  |  |  |  | 1899-12-31 08:47 | 22 | 36 | [7 empty] | 12.5 | 8760 | 99.74% | 282.5 | 109500
|  | 2020-05-21 | 6:58 | 2020-05-21 | 7:18 | 0:20 | 0 | 19 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-06-03 | 17:32 | 2020-06-03 | 17:34 | 0:02 | 0 | 2 | [5 empty] | Tripped on O/C(Y- Phase) along with M/R at Pattamundai end.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:45 | 0:14 | 0 | 5 | [5 empty] | DP Relay,Dist.-2.04km
|  | 2020-06-06 | 14:06 | 2020-06-06 | 16:09 | 2:03 | 0 | 6 | [5 empty] | DP Relay, Dist.- 4.02km
|  | 2020-06-09 | 22:23 | 2020-06-10 | 18:08 | 19:45 | 0 | 6 | [5 empty] | DP Relay, Dist.- 12.19km [Due to snapping of conductor.]
|  | 2020-06-22 | 5:45 | 2020-06-22 | 05:56 | 0:11 | 0 | 11 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:36 | 0:05 | 0 | 5 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 14:06 | 2020-06-06 | 14:12 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-09 | 22:23 | 2020-06-09 | 22:29 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-22 | 5:45 | 2020-06-22 | 6:12 | 0:27 | 0 | 11 | [5 empty] | DP Relay,Dist.-13.13km, Y-Ph.,Z1
|  | 2020-07-08 | 18:39 | 2020-07-08 | 18:48 | 00:09 | 0 | 9 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-17 | 00:10 | 2020-07-17 | 00:13 | 00:03 | 0 | 3 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-21 | 19:20 | 2020-07-21 | 19:31 | 00:11 | 0 | 11 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-17 | 22:29 | 2020-07-17 | 22:33 | 00:04 | 0 | 4 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-07-26 | 19:25 | 2020-07-26 | 19:32 | 00:07 | 0 | 7 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-09-09 | 15:44 | 2020-09-09 | 16:52 | 1:08 | 0 | 38 | [5 empty] | IL1=0.06KA , IL2=0.15KA , IL3=0.10KA
|  | 2020-09-20 | 09:25 | 2020-09-20 | 09:54 | 0:29 | 0 | 16 | [5 empty] | Tripped on Distance protection zone- 1, B-phase showing distance of 14.5 km along with tripping of 132 KV Pattamundai-Olaver Ckt-I.
|  | 2020-10-03 | 10:50 | 2020-10-03 | 14:41 | 3:51 | 3 | 51 | [5 empty] | TRIPPED ON E/F WITH M/R AND DELAY CHARGED FOR S/D
|  | 2020-10-14 | 06:29 | 2020-10-14 | 06:35 | 0:06 | 0 | 6 | [5 empty] | Tripeed On Differential Relay With M/R Due To 132Kv R -Ph CT Brust And Charged After Replacement Of New CT.
|  | 2020-11-17 | 15:15 | 2020-11-17 | 18:40 | 3:25 | 3 | 25 | [5 empty] | Tripped on Distance protection Zone- 1 and M/R with a loud sound in the switchyard due to burst of B-Ph insulator string of 132 KV main bus(B/C section). Fault location- 326.7 m, Ia=456.9 A, Ib=614.1A, Ic=2.475 KA
|  | 2020-12-05 | 23:34 | 2020-12-06 | 0:03 | 0:29 | 0 | 29 | [5 empty] | Incomer breaker Tripped at Pattamundai end on DP -Zone-I along with M/R. Started Phase-CN, Tripped phase A B C. Fault Location- 328.2 m, IA=500.6 A, IB=626.5 A, IC=2.529 . [B-Phase insulator string of 132KV cross bus of 20MVA TRF-II burst. ]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
335 | 132kV Olavar - Chandabali Ckt - II |  |  |  |  | 1899-12-31 08:47 | 22 | 36 | [7 empty] | 12.5 | 8760 | 99.74% | 282.5 | 109500
|  | 2020-05-21 | 6:58 | 2020-05-21 | 7:18 | 0:20 | 0 | 19 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-06-03 | 17:32 | 2020-06-03 | 17:34 | 0:02 | 0 | 2 | [5 empty] | Tripped on O/C(Y- Phase) along with M/R at Pattamundai end.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:45 | 0:14 | 0 | 5 | [5 empty] | DP Relay,Dist.-2.04km
|  | 2020-06-06 | 14:06 | 2020-06-06 | 16:09 | 2:03 | 0 | 6 | [5 empty] | DP Relay, Dist.- 4.02km
|  | 2020-06-09 | 22:23 | 2020-06-10 | 18:08 | 19:45 | 0 | 6 | [5 empty] | DP Relay, Dist.- 12.19km [Due to snapping of conductor.]
|  | 2020-06-22 | 5:45 | 2020-06-22 | 05:56 | 0:11 | 0 | 11 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 13:31 | 2020-06-06 | 13:36 | 0:05 | 0 | 5 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-06 | 14:06 | 2020-06-06 | 14:12 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-09 | 22:23 | 2020-06-09 | 22:29 | 0:06 | 0 | 6 | [5 empty] | B/U,E/F, M/R.
|  | 2020-06-22 | 5:45 | 2020-06-22 | 6:12 | 0:27 | 0 | 11 | [5 empty] | DP Relay,Dist.-13.13km, Y-Ph.,Z1
|  | 2020-07-08 | 18:39 | 2020-07-08 | 18:48 | 00:09 | 0 | 9 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-17 | 00:10 | 2020-07-17 | 00:13 | 00:03 | 0 | 3 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-21 | 19:20 | 2020-07-21 | 19:31 | 00:11 | 0 | 11 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-07-17 | 22:29 | 2020-07-17 | 22:33 | 00:04 | 0 | 4 | [5 empty] | TRIPPED ON BACKUP E/F WITH M/R.
|  | 2020-07-26 | 19:25 | 2020-07-26 | 19:32 | 00:07 | 0 | 7 | [5 empty] | Failed from Pattamundai Grid
|  | 2020-09-09 | 15:44 | 2020-09-09 | 16:52 | 1:08 | 0 | 38 | [5 empty] | IL1=0.06KA , IL2=0.15KA , IL3=0.10KA
|  | 2020-09-20 | 09:25 | 2020-09-20 | 09:54 | 0:29 | 0 | 16 | [5 empty] | Tripped on Distance protection zone- 1, B-phase showing distance of 14.5 km along with tripping of 132 KV Pattamundai-Olaver Ckt-I.
|  | 2020-10-03 | 10:50 | 2020-10-03 | 14:41 | 3:51 | 3 | 51 | [5 empty] | TRIPPED ON E/F WITH M/R AND DELAY CHARGED FOR S/D
|  | 2020-10-14 | 06:29 | 2020-10-14 | 06:35 | 0:06 | 0 | 6 | [5 empty] | Tripeed On Differential Relay With M/R Due To 132Kv R -Ph CT Brust And Charged After Replacement Of New CT.
|  | 2020-11-17 | 15:15 | 2020-11-17 | 18:40 | 3:25 | 3 | 25 | [5 empty] | Tripped on Distance protection Zone- 1 and M/R with a loud sound in the switchyard due to burst of B-Ph insulator string of 132 KV main bus(B/C section). Fault location- 326.7 m, Ia=456.9 A, Ib=614.1A, Ic=2.475 KA
|  | 2020-12-05 | 23:34 | 2020-12-06 | 0:03 | 0:29 | 0 | 29 | [5 empty] | Incomer breaker Tripped at Pattamundai end on DP -Zone-I along with M/R. Started Phase-CN, Tripped phase A B C. Fault Location- 328.2 m, IA=500.6 A, IB=626.5 A, IC=2.529 . [B-Phase insulator string of 132KV cross bus of 20MVA TRF-II burst. ]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
336 | 132kV Therubali-Muniguda-Vedant Alumina |  |  |  |  | 0.13889 | 16 | 59 | [7 empty] | 76.15 | 8760 | 99.81% | 1293.2808 | 667074
|  | 2020-04-13 | 14:54 | 2020-04-13 | 15:02 | 0:08 | 0 | 8 | [5 empty] | P/S Failed from Therubali end
|  | 15.04.20 | 22:37 | 15.04.20 | 22:40 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 16.04.20 | 1:07 | 16.04.20 | 1:10 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 14:37 | 18.04.20 | 14:39 | 0:02 | 0 | 2 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 18:24 | 18.04.20 | 18:34 | 0:10 | 0 | 10 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 16:36 | 23.04.20 | 16:58 | 0:22 | 0 | 22 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 21:52 | 23.04.20 | 21:56 | 0:04 | 0 | 4 | [5 empty] | P/S Failed from Therubali end
|  | 25.04.20 | 6:32 | 25.04.20 | 6:38 | 0:06 | 0 | 6 | [5 empty] | Tripped at Therubali end
|  | 30.04.20 | 19:02 | 30.04.20 | 19:05 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end
|  | 2020-05-03 | 21:55 | 2020-05-03 | 21.57 | 0:02 | 0 | 2 | [5 empty] | Tripped at Theruvali end
|  | 2020-05-05 | 2:10 | 2020-05-05 | 2:15 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 3:50 | 2020-05-05 | 3:54 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 21:19 | 2020-05-05 | 21:27 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:06 | 2020-05-05 | 23:09 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:30 | 2020-05-05 | 23:37 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-01 | 22:29 | 2020-05-01 | 22:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-03 | 0:22 | 2020-05-03 | 0.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-06 | 5:27 | 2020-05-06 | 5:34 | 0:07 | 0 | 7 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 23:03 | 2020-05-06 | 23:06 | 0:03 | 0 | 3 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-06 | 23:30 | 2020-05-06 | 23:37 | 0:07 | 0 | 7 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-12 | 23:12 | 2020-05-12 | 23.14 | 0:02 | 0 | 2 | [5 empty] | At Therubali end: C-A Phase.
|  | 2020-05-13 | 2:01 | 2020-05-13 | 2:02 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-08 | 19:36 | 2020-05-08 | 19.43 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-05-16 | 3:34 | 2020-05-16 | 3:38 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-17 | 22:22 | 2020-05-17 | 22.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:16 | 2020-05-18 | 22.18 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:27 | 2020-05-18 | 22.29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 22:56 | 2020-05-22 | 22:57 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 0:20 | 2020-05-22 | 0:21 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:34 | 2020-05-24 | 21:36 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:48 | 2020-05-24 | 21:50 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-25 | 1:29 | 2020-05-25 | 1:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 3:11 | 2020-05-26 | 3:15 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 23:29 | 2020-05-26 | 23:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 2:32 | 2020-05-26 | 2:34 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:30 | 2020-05-27 | 15:42 | 0:12 | 0 | 12 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:48 | 2020-05-27 | 15:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-06-27 | 0:17 | 2020-06-27 | 0:24 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-07-27 | 20:04 | 2020-07-27 | 20:07 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-27 | 20:27 | 2020-07-27 | 20:31 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 22:45 | 2020-07-21 | 22:49 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:10 | 2020-07-21 | 23:23 | 00:13 | 0 | 13 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:56 | 2020-07-21 | 00:00 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-02 | 22:27 | 2020-07-02 | 22:30 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-03 | 00:17 | 2020-07-03 | 00:19 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 21:28 | 2020-07-08 | 21:31 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 23:20 | 2020-07-08 | 23:25 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-09 | 23:30 | 2020-07-09 | 23:32 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-11 | 22:18 | 2020-07-11 | 22:20 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:23 | 2020-07-16 | 14:26 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-18 | 21:04 | 2020-07-18 | 21:06 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-20 | 22:03 | 2020-07-20 | 22:05 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:29 | 2020-07-22 | 01:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:39 | 2020-07-22 | 01:44 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 02:37 | 2020-07-22 | 02:46 | 00:09 | 0 | 9 | [5 empty] | At kesinga end: O/C
|  | 2020-07-29 | 23:33 | 2020-07-29 | 23:34 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:16 | 2020-07-30 | 00:17 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:25 | 2020-07-30 | 00:28 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 01:39 | 2020-07-30 | 01:40 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 02:42 | 2020-07-30 | 02:44 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:29 | 2020-07-30 | 20:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:54 | 2020-07-30 | 20:57 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 21:10 | 2020-07-30 | 21:12 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-31 | 15:35 | 2020-07-31 | 15:37 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-08-03 | 23.31 | 2020-08-03 | 23.42 | 0:11 | 0 | 11 | [5 empty] | ABCT,IL1=535 A, IL2=494 A, IL3= 474 A. at therubali end.
|  | 2020-09-23 | 18:35 | 2020-09-23 | 18:45 | 0:10 | 0 | 10 | [5 empty] | ABCT, IL1= 534A, IL2=487 A, IL3=453 at Therubali end.
|  | 2020-09-09 | 23:32 | 2020-09-09 | 23:37 | 0:05 | 0 | 5 | [5 empty] | ABCT, IL1= 542A, IL2=509 A, IL3=433 at Therubali end.
|  | 2020-10-19 | 19:45 | 2020-10-19 | 19:52 | 0:07 | 0 | 7 | [5 empty] | trippedABC(Over current.),IA- 513AMP, IB- 518AMP, IC- 509AMP.
|  | 2021-03-22 | 19:39 | 2021-03-22 | 19:49 | 0:10 | 0 | 10 | [5 empty] | Tripped due to O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
337 | 132kV Vedant Alumina-Kesinga |  |  |  |  | 0.275 | 20 | 15 | [7 empty] | 57.28 | 8760 | 99.77% | 1159.92 | 501772.8
|  | 2020-04-13 | 14:54 | 2020-04-13 | 15:02 | 0:08 | 0 | 8 | [5 empty] | P/S Failed from Therubali end
|  | 15.04.20 | 22:37 | 15.04.20 | 22:40 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 16.04.20 | 1:07 | 16.04.20 | 1:10 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 14:37 | 18.04.20 | 14:39 | 0:02 | 0 | 2 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 18:24 | 18.04.20 | 18:34 | 0:10 | 0 | 10 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 16:36 | 23.04.20 | 16:58 | 0:22 | 0 | 22 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 21:52 | 23.04.20 | 21:56 | 0:04 | 0 | 4 | [5 empty] | P/S Failed from Therubali end
|  | 25.04.20 | 6:32 | 25.04.20 | 6:38 | 0:06 | 0 | 6 | [5 empty] | Tripped at Therubali end
|  | 30.04.20 | 19:02 | 30.04.20 | 19:05 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end
|  | 2020-05-03 | 21:55 | 2020-05-03 | 21.57 | 0:02 | 0 | 2 | [5 empty] | Tripped at Theruvali end
|  | 2020-05-05 | 2:10 | 2020-05-05 | 2:15 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 3:50 | 2020-05-05 | 3:54 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 21:19 | 2020-05-05 | 21:27 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:06 | 2020-05-05 | 23:09 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:30 | 2020-05-05 | 23:37 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-01 | 22:29 | 2020-05-01 | 22:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-03 | 0:22 | 2020-05-03 | 0.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-06 | 5:27 | 2020-05-06 | 5:34 | 0:07 | 0 | 7 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 23:03 | 2020-05-06 | 23:06 | 0:03 | 0 | 3 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-06 | 23:30 | 2020-05-06 | 23:37 | 0:07 | 0 | 7 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-12 | 23:12 | 2020-05-12 | 23.14 | 0:02 | 0 | 2 | [5 empty] | At Therubali end: C-A Phase.
|  | 2020-05-13 | 2:01 | 2020-05-13 | 2:02 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-08 | 19:36 | 2020-05-08 | 19.43 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-05-16 | 3:34 | 2020-05-16 | 3:38 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-17 | 22:22 | 2020-05-17 | 22.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:16 | 2020-05-18 | 22.18 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:27 | 2020-05-18 | 22.29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 22:56 | 2020-05-22 | 22:57 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 0:20 | 2020-05-22 | 0:21 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:34 | 2020-05-24 | 21:36 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:48 | 2020-05-24 | 21:50 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-25 | 1:29 | 2020-05-25 | 1:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 3:11 | 2020-05-26 | 3:15 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 23:29 | 2020-05-26 | 23:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 2:32 | 2020-05-26 | 2:34 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:30 | 2020-05-27 | 15:42 | 0:12 | 0 | 12 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:48 | 2020-05-27 | 15:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-06-01 | 23:25 | 2020-06-01 | 23:28 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 0:06 | 2020-06-05 | 0:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 12:02 | 2020-06-05 | 12:04 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 14:24 | 2020-06-11 | 14:26 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 15:08 | 2020-06-11 | 15:13 | 0:05 | 0 | 5 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 20:33 | 2020-06-24 | 20:35 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 21:28 | 2020-06-24 | 21:30 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 23:27 | 2020-06-24 | 23:53 | 0:26 | 0 | 26 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-25 | 0:33 | 2020-06-25 | 0:34 | 0:01 | 0 | 1 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 19:27 | 2020-06-27 | 19:30 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 0:17 | 2020-06-27 | 0:24 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-07-27 | 20:04 | 2020-07-27 | 20:07 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-27 | 20:27 | 2020-07-27 | 20:31 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 22:45 | 2020-07-21 | 22:49 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:10 | 2020-07-21 | 23:23 | 00:13 | 0 | 13 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:56 | 2020-07-21 | 00:00 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-02 | 22:27 | 2020-07-02 | 22:30 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-03 | 00:17 | 2020-07-03 | 00:19 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 21:28 | 2020-07-08 | 21:31 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 23:20 | 2020-07-08 | 23:25 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-09 | 23:30 | 2020-07-09 | 23:32 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-11 | 22:18 | 2020-07-11 | 22:20 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:23 | 2020-07-16 | 14:26 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-18 | 21:04 | 2020-07-18 | 21:06 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-20 | 22:03 | 2020-07-20 | 22:05 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:29 | 2020-07-22 | 01:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:39 | 2020-07-22 | 01:44 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 02:37 | 2020-07-22 | 02:46 | 00:09 | 0 | 9 | [5 empty] | At kesinga end: O/C
|  | 2020-07-29 | 23:33 | 2020-07-29 | 23:34 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:16 | 2020-07-30 | 00:17 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:25 | 2020-07-30 | 00:28 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 01:39 | 2020-07-30 | 01:40 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 02:42 | 2020-07-30 | 02:44 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:29 | 2020-07-30 | 20:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:54 | 2020-07-30 | 20:57 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 21:10 | 2020-07-30 | 21:12 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-31 | 15:35 | 2020-07-31 | 15:37 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-08-01 | 04:56 | 2020-08-01 | 04:58 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:05 | 2020-08-01 | 05:09 | 0:04 | 0 | 4 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:25 | 2020-08-01 | 05:33 | 0:08 | 0 | 8 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 17:21 | 2020-08-01 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 23:51 | 2020-08-01 | 23:53 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-02 | 23:31 | 2020-08-02 | 23:52 | 0:21 | 0 | 21 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-07 | 23:43 | 2020-08-07 | 23:54 | 0:11 | 0 | 11 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-03 | 23.31 | 2020-08-03 | 23.42 | 0:11 | 0 | 11 | [5 empty] | ABCT,IL1=535 A, IL2=494 A, IL3= 474 A. at therubali end.
|  | 2020-08-22 | 19:52 | 2020-08-22 | 19:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-22 | 21:23 | 2020-08-22 | 21:25 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-23 | 21:35 | 2020-08-23 | 21:38 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-26 | 02:35 | 2020-08-26 | 02:41 | 0:06 | 0 | 6 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-30 | 17:25 | 2020-08-30 | 17:27 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 17:33 | 2020-08-30 | 17:35 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 18:07 | 2020-08-30 | 18:09 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 21:57 | 2020-08-30 | 22:12 | 0:15 | 0 | 15 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 22:49 | 2020-08-30 | 22:56 | 0:07 | 0 | 7 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-31 | 10:19 | 2020-08-31 | 10:29 | 0:10 | 0 | 10 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-09-04 | 20:10 | 2020-09-04 | 20:15 | 0:05 | 0 | 5 | [5 empty] | O/C, B-Phase
|  | 2020-09-05 | 21:20 | 2020-09-05 | 21:22 | 0:02 | 0 | 2 | [5 empty] | O/C, B-Phase
|  | 2020-09-10 | 11:12 | 2020-09-10 | 11:17 | 0:05 | 0 | 5 | [5 empty] | DP, 11.5km
|  | 2020-09-10 | 15:58 | 2020-09-10 | 16:07 | 0:09 | 0 | 9 | [5 empty] | DP at both end. Kesinga:10.5km
|  | 2020-09-11 | 10:31 | 2020-09-11 | 10:33 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-12 | 18:29 | 2020-09-12 | 18:31 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 02:05 | 2020-09-13 | 02:06 | 0:01 | 0 | 1 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 19:22 | 2020-09-13 | 19:24 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-15 | 01:27 | 2020-09-15 | 01:31 | 0:04 | 0 | 4 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-16 | 18:40 | 2020-09-16 | 18:42 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-20 | 23:26 | 2020-09-20 | 23:28 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-21 | 03:54 | 2020-09-21 | 04:00 | 0:06 | 0 | 6 | [5 empty] | DP, 76.6km at VAL end.
|  | 2020-09-21 | 18:29 | 2020-09-21 | 18:32 | 0:03 | 0 | 3 | [5 empty] | O/C at Kesing end.
|  | 2020-09-23 | 18:35 | 2020-09-23 | 18:45 | 0:10 | 0 | 10 | [5 empty] | ABCT, IL1= 534A, IL2=487 A, IL3=453 at Therubali end.
|  | 2020-09-09 | 23:32 | 2020-09-09 | 23:37 | 0:05 | 0 | 5 | [5 empty] | ABCT, IL1= 542A, IL2=509 A, IL3=433 at Therubali end.
|  | 2020-10-19 | 19:45 | 2020-10-19 | 19:52 | 0:07 | 0 | 7 | [5 empty] | trippedABC(Over current.),IA- 513AMP, IB- 518AMP, IC-509AMP.
|  | 2021-03-22 | 19:39 | 2021-03-22 | 19:49 | 0:10 | 0 | 10 | [5 empty] | Tripped due to O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
[21 empty] | #DIV/0! | #DIV/0!
338 | 132kV Kesinga-Bhawanipatna |  |  |  |  | 0.43542 | 24 | 36 | [7 empty] | 39.81 | 8760 | 99.72% | 979.326 | 348735.6
|  | 01.04.20 | 19:20 | 01.04.20 | 19:26 | 0:06 | 0 | 6 | [5 empty] | P/S failure from Kesinga end
|  | 11.04.20 | 23:26 | 11.04.20 | 23:36 | 0:10 | 0 | 10 | [5 empty] | P/S Failed from Kesinga end
|  | 13.04.20 | 14:35 | 13.04.20 | 14:47 | 0:12 | 0 | 12 | [5 empty] | P/S Failed from Kesinga end
|  | 16.04.20 | 21:00 | 16.04.20 | 21:05 | 0:05 | 0 | 5 | [5 empty] | P/S Failed from Kesinga end
|  | 23.04.20 | 15:17 | 23.04.20 | 15:36 | 0:19 | 0 | 19 | [5 empty] | Failed from Kesinga end
|  | 23.04.20 | 21:02 | 23.04.20 | 21:12 | 0:10 | 0 | 10 | [5 empty] | Failed from Kesinga end
|  | 27.04.20 | 20:55 | 27.04.20 | 20:59 | 0:04 | 0 | 4 | [5 empty] | Tripped from Kesinga end
|  | 28.04.20 | 22:05 | 28.04.20 | 22:08 | 0:03 | 0 | 3 | [5 empty] | Tripped from Kesinga end
|  | 29.04.20 | 3:59 | 29.04.20 | 4:13 | 0:14 | 0 | 14 | [5 empty] | Tripped from Kesinga end
|  | 2020-04-13 | 14:54 | 2020-04-13 | 15:02 | 0:08 | 0 | 8 | [5 empty] | P/S Failed from Therubali end
|  | 15.04.20 | 22:37 | 15.04.20 | 22:40 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 16.04.20 | 1:07 | 16.04.20 | 1:10 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 14:37 | 18.04.20 | 14:39 | 0:02 | 0 | 2 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 18:24 | 18.04.20 | 18:34 | 0:10 | 0 | 10 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 16:36 | 23.04.20 | 16:58 | 0:22 | 0 | 22 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 21:52 | 23.04.20 | 21:56 | 0:04 | 0 | 4 | [5 empty] | P/S Failed from Therubali end
|  | 25.04.20 | 6:32 | 25.04.20 | 6:38 | 0:06 | 0 | 6 | [5 empty] | Tripped at Therubali end
|  | 30.04.20 | 19:02 | 30.04.20 | 19:05 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end
|  | 2020-05-03 | 21:53 | 2020-05-03 | 21:55 | 0:02 | 0 | 2 | [5 empty] | Tripped at Theruvali end
|  | 2020-05-05 | 2:10 | 2020-05-05 | 2:15 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 3:50 | 2020-05-05 | 3:54 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 21:19 | 2020-05-05 | 21:27 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:06 | 2020-05-05 | 23:09 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:30 | 2020-05-05 | 23:37 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-19 | 21:03 | 2020-05-19 | 21:11 | 0:08 | 0 | 8 | [5 empty] | Tripped at lanjigarh end
|  | 2020-05-19 | 15:43 | 2020-05-19 | 15:47 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-19 | 16:49 | 2020-05-19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-21 | 16:39 | 2020-05-21 | 16:46 | 0:07 | 0 | 7 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-24 | 19:06 | 2020-05-24 | 19:11 | 0:05 | 0 | 5 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 19:34 | 2020-05-24 | 19:40 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 22:13 | 2020-05-24 | 22:18 | 0:05 | 0 | 5 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 23:58 | 2020-05-25 | 0:04 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 3:28 | 2020-05-26 | 3:31 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 21:07 | 2020-05-26 | 21:13 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 22:24 | 2020-05-26 | 22:30 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 1:28 | 2020-05-26 | 1:32 | 0:04 | 0 | 4 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 1:45 | 2020-05-26 | 1:48 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-27 | 20:52 | 2020-05-27 | 20:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-27 | 21:18 | 2020-05-27 | 21:20 | 0:02 | 0 | 2 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-27 | 23:36 | 2020-05-27 | 23:39 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-28 | 14:48 | 2020-05-28 | 14:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-29 | 11:06 | 2020-05-29 | 11:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga-Tripped Due to Circuit Overloading
|  | 2020-05-01 | 22:29 | 2020-05-01 | 22:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-03 | 0:22 | 2020-05-03 | 0.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-06 | 2:10 | 2020-05-06 | 2:14 | 0:04 | 0 | 4 | [5 empty] | Tripped at Kesinga- on Overload
|  | 2020-05-06 | 3:50 | 2020-05-06 | 3:53 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga- on Overload
|  | 2020-05-06 | 5:27 | 2020-05-06 | 5:34 | 0:07 | 0 | 7 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 23:03 | 2020-05-06 | 23:06 | 0:03 | 0 | 3 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-06 | 23:30 | 2020-05-06 | 23:37 | 0:07 | 0 | 7 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-06 | 21:19 | 2020-05-06 | 21:22 | 0:03 | 0 | 3 | [5 empty] | 132 KV P/S FAIL
|  | 2020-05-12 | 23:12 | 2020-05-12 | 23.14 | 0:02 | 0 | 2 | [5 empty] | At Therubali end: C-A Phase.
|  | 2020-05-13 | 2:01 | 2020-05-13 | 2:02 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-08 | 19:36 | 2020-05-08 | 19.43 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-05-15 | 21:39 | 2020-05-15 | 21:49 | 0:10 | 0 | 10 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-16 | 3:34 | 2020-05-16 | 3:38 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-17 | 22:22 | 2020-05-17 | 22.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:16 | 2020-05-18 | 22.18 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:27 | 2020-05-18 | 22.29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 22:56 | 2020-05-22 | 22:57 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 0:20 | 2020-05-22 | 0:21 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:34 | 2020-05-24 | 21:36 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:48 | 2020-05-24 | 21:50 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-25 | 1:29 | 2020-05-25 | 1:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 3:11 | 2020-05-26 | 3:15 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 23:29 | 2020-05-26 | 23:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 2:32 | 2020-05-26 | 2:34 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:30 | 2020-05-27 | 15:42 | 0:12 | 0 | 12 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:48 | 2020-05-27 | 15:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-06-01 | 23:25 | 2020-06-01 | 23:28 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 0:06 | 2020-06-05 | 0:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 12:02 | 2020-06-05 | 12:04 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 14:24 | 2020-06-11 | 14:26 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 15:08 | 2020-06-11 | 15:13 | 0:05 | 0 | 5 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 20:33 | 2020-06-24 | 20:35 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 21:28 | 2020-06-24 | 21:30 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 23:27 | 2020-06-24 | 23:53 | 0:26 | 0 | 26 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-25 | 0:33 | 2020-06-25 | 0:34 | 0:01 | 0 | 1 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 19:27 | 2020-06-27 | 19:30 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 0:17 | 2020-06-27 | 0:24 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-07-21 | 22:45 | 2020-07-21 | 22:49 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:10 | 2020-07-21 | 23:23 | 00:13 | 0 | 13 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:56 | 2020-07-21 | 00:00 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-02 | 22:27 | 2020-07-02 | 22:30 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-03 | 00:17 | 2020-07-03 | 00:19 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 21:28 | 2020-07-08 | 21:31 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 23:20 | 2020-07-08 | 23:25 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-09 | 23:30 | 2020-07-09 | 23:32 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-11 | 22:18 | 2020-07-11 | 22:20 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:23 | 2020-07-16 | 14:26 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-18 | 21:04 | 2020-07-18 | 21:06 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-20 | 22:03 | 2020-07-20 | 22:05 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:29 | 2020-07-22 | 01:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:39 | 2020-07-22 | 01:44 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 02:37 | 2020-07-22 | 02:46 | 00:09 | 0 | 9 | [5 empty] | At kesinga end: O/C
|  | 2020-07-29 | 23:33 | 2020-07-29 | 23:34 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:16 | 2020-07-30 | 00:17 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:25 | 2020-07-30 | 00:28 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 01:39 | 2020-07-30 | 01:40 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 02:42 | 2020-07-30 | 02:44 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:29 | 2020-07-30 | 20:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:54 | 2020-07-30 | 20:57 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 21:10 | 2020-07-30 | 21:12 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-31 | 15:35 | 2020-07-31 | 15:37 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 17:08 | 2020-07-21 | 17:12 | 00:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 18:15 | 2020-07-21 | 18:20 | 00:05 | 0 | 5 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 19:10 | 2020-07-21 | 19:30 | 00:20 | 0 | 20 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 00:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 00:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 00:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-08-01 | 04:56 | 2020-08-01 | 04:58 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:05 | 2020-08-01 | 05:09 | 0:04 | 0 | 4 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:25 | 2020-08-01 | 05:33 | 0:08 | 0 | 8 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 17:21 | 2020-08-01 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 23:51 | 2020-08-01 | 23:53 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-02 | 23:31 | 2020-08-02 | 23:52 | 0:21 | 0 | 21 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-07 | 23:43 | 2020-08-07 | 23:54 | 0:11 | 0 | 11 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-03 | 23.31 | 2020-08-03 | 23.42 | 0:11 | 0 | 11 | [5 empty] | ABCT,IL1=535 A, IL2=494 A, IL3= 474 A. at therubali end.
|  | 2020-08-22 | 19:52 | 2020-08-22 | 19:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-22 | 21:23 | 2020-08-22 | 21:25 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-23 | 21:35 | 2020-08-23 | 21:38 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-26 | 02:35 | 2020-08-26 | 02:41 | 0:06 | 0 | 6 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-30 | 17:25 | 2020-08-30 | 17:27 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 17:33 | 2020-08-30 | 17:35 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 18:07 | 2020-08-30 | 18:09 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 21:57 | 2020-08-30 | 22:12 | 0:15 | 0 | 15 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 22:49 | 2020-08-30 | 22:56 | 0:07 | 0 | 7 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-31 | 10:19 | 2020-08-31 | 10:29 | 0:10 | 0 | 10 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-09-04 | 20:10 | 2020-09-04 | 20:15 | 0:05 | 0 | 5 | [5 empty] | O/C, B-Phase
|  | 2020-09-05 | 21:20 | 2020-09-05 | 21:22 | 0:02 | 0 | 2 | [5 empty] | O/C, B-Phase
|  | 2020-09-10 | 11:12 | 2020-09-10 | 11:17 | 0:05 | 0 | 5 | [5 empty] | DP, 11.5km
|  | 2020-09-10 | 15:58 | 2020-09-10 | 16:07 | 0:09 | 0 | 9 | [5 empty] | DP at both end. Kesinga:10.5km
|  | 2020-09-11 | 10:31 | 2020-09-11 | 10:33 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-12 | 18:29 | 2020-09-12 | 18:31 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 02:05 | 2020-09-13 | 02:06 | 0:01 | 0 | 1 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 19:22 | 2020-09-13 | 19:24 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-15 | 01:27 | 2020-09-15 | 01:31 | 0:04 | 0 | 4 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-16 | 18:40 | 2020-09-16 | 18:42 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-20 | 23:26 | 2020-09-20 | 23:28 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-21 | 03:54 | 2020-09-21 | 04:00 | 0:06 | 0 | 6 | [5 empty] | DP, 76.6km at VAL end.
|  | 2020-09-21 | 18:29 | 2020-09-21 | 18:32 | 0:03 | 0 | 3 | [5 empty] | O/C at Kesing end.
|  | 2020-09-23 | 18:35 | 2020-09-23 | 18:45 | 0:10 | 0 | 10 | [5 empty] | ABCT, IL1= 534A, IL2=487 A, IL3=453 at Therubali end.
|  | 2020-09-09 | 23:32 | 2020-09-09 | 23:37 | 0:05 | 0 | 5 | [5 empty] | ABCT, IL1= 542A, IL2=509 A, IL3=433 at Therubali end.
|  | 2020-10-19 | 19:45 | 2020-10-19 | 19:52 | 0:07 | 0 | 7 | [5 empty] | trippedABC(Over current.),IA- 513AMP, IB- 518AMP, IC-509AMP.
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2021-01-13 | 05:10 | 2021-01-13 | 05:15 | 0:05 | 0 | 5 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 16:09 | 2021-01-13 | 16:14 | 0:05 | 0 | 5 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 17:24 | 2021-01-13 | 17:42 | 0:18 | 0 | 18 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 18:36 | 2021-01-13 | 18:38 | 0:02 | 0 | 2 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-25 | 18:17 | 2021-01-25 | 18:18 | 0:01 | 0 | 1 | [5 empty] | Failed from kesinga end:.
|  | 2021-03-22 | 19:39 | 2021-03-22 | 19:49 | 0:10 | 0 | 10 | [5 empty] | Tripped due to O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
339 | 132kV Bhawanipatna-Junagarh |  |  |  |  | 0.43542 | 24 | 44 | [7 empty] | 24.76 | 8760 | 99.72% | 612.3973 | 216897.6
|  | 01.04.20 | 19:20 | 01.04.20 | 19:26 | 0:06 | 0 | 6 | [5 empty] | P/S failure from Kesinga end
|  | 11.04.20 | 23:26 | 11.04.20 | 23:36 | 0:10 | 0 | 10 | [5 empty] | P/S Failed from Kesinga end
|  | 13.04.20 | 14:35 | 13.04.20 | 14:47 | 0:12 | 0 | 12 | [5 empty] | P/S Failed from Kesinga end
|  | 16.04.20 | 21:00 | 16.04.20 | 21:05 | 0:05 | 0 | 5 | [5 empty] | P/S Failed from Kesinga end
|  | 23.04.20 | 15:17 | 23.04.20 | 15:36 | 0:19 | 0 | 19 | [5 empty] | Failed from Kesinga end
|  | 23.04.20 | 21:02 | 23.04.20 | 21:12 | 0:10 | 0 | 10 | [5 empty] | Failed from Kesinga end
|  | 27.04.20 | 20:55 | 27.04.20 | 20:59 | 0:04 | 0 | 4 | [5 empty] | Tripped from Kesinga end
|  | 28.04.20 | 22:05 | 28.04.20 | 22:08 | 0:03 | 0 | 3 | [5 empty] | Tripped from Kesinga end
|  | 29.04.20 | 3:59 | 29.04.20 | 4:13 | 0:14 | 0 | 14 | [5 empty] | Tripped from Kesinga end
|  | 2020-04-13 | 14:54 | 2020-04-13 | 15:02 | 0:08 | 0 | 8 | [5 empty] | P/S Failed from Therubali end
|  | 15.04.20 | 22:37 | 15.04.20 | 22:40 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 16.04.20 | 1:07 | 16.04.20 | 1:10 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 14:37 | 18.04.20 | 14:39 | 0:02 | 0 | 2 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 18:24 | 18.04.20 | 18:34 | 0:10 | 0 | 10 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 16:36 | 23.04.20 | 16:58 | 0:22 | 0 | 22 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 21:52 | 23.04.20 | 21:56 | 0:04 | 0 | 4 | [5 empty] | P/S Failed from Therubali end
|  | 25.04.20 | 6:32 | 25.04.20 | 6:38 | 0:06 | 0 | 6 | [5 empty] | Tripped at Therubali end
|  | 30.04.20 | 19:02 | 30.04.20 | 19:05 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end
|  | 2020-05-03 | 21:53 | 2020-05-03 | 21:55 | 0:02 | 0 | 2 | [5 empty] | Tripped at Theruvali end
|  | 2020-05-05 | 2:10 | 2020-05-05 | 2:15 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 3:50 | 2020-05-05 | 3:54 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 21:19 | 2020-05-05 | 21:27 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:06 | 2020-05-05 | 23:09 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:30 | 2020-05-05 | 23:37 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-19 | 21:03 | 2020-05-19 | 21:11 | 0:08 | 0 | 8 | [5 empty] | Tripped at lanjigarh end
|  | 2020-05-19 | 15:43 | 2020-05-19 | 15:47 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-19 | 16:49 | 2020-05-19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-21 | 16:39 | 2020-05-21 | 16:46 | 0:07 | 0 | 7 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-24 | 19:06 | 2020-05-24 | 19:11 | 0:05 | 0 | 5 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 19:34 | 2020-05-24 | 19:40 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 22:13 | 2020-05-24 | 22:18 | 0:05 | 0 | 5 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 23:58 | 2020-05-25 | 0:04 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 3:28 | 2020-05-26 | 3:31 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 21:07 | 2020-05-26 | 21:13 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 22:24 | 2020-05-26 | 22:30 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 1:28 | 2020-05-26 | 1:32 | 0:04 | 0 | 4 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 1:45 | 2020-05-26 | 1:48 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-27 | 20:52 | 2020-05-27 | 20:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-27 | 21:18 | 2020-05-27 | 21:20 | 0:02 | 0 | 2 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-27 | 23:36 | 2020-05-27 | 23:39 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-28 | 14:48 | 2020-05-28 | 14:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-29 | 11:06 | 2020-05-29 | 11:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga-Tripped Due to Circuit Overloading
|  | 2020-05-01 | 22:29 | 2020-05-01 | 22:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-03 | 0:22 | 2020-05-03 | 0.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-06 | 2:10 | 2020-05-06 | 2:14 | 0:04 | 0 | 4 | [5 empty] | Tripped at Kesinga- on Overload
|  | 2020-05-06 | 3:50 | 2020-05-06 | 3:53 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga- on Overload
|  | 2020-05-06 | 5:27 | 2020-05-06 | 5:34 | 0:07 | 0 | 7 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 23:03 | 2020-05-06 | 23:06 | 0:03 | 0 | 3 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-06 | 23:30 | 2020-05-06 | 23:37 | 0:07 | 0 | 7 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-06 | 21:19 | 2020-05-06 | 21:22 | 0:03 | 0 | 3 | [5 empty] | 132 KV P/S FAIL
|  | 2020-05-12 | 23:12 | 2020-05-12 | 23.14 | 0:02 | 0 | 2 | [5 empty] | At Therubali end: C-A Phase.
|  | 2020-05-13 | 2:01 | 2020-05-13 | 2:02 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-08 | 19:36 | 2020-05-08 | 19.43 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-05-15 | 21:39 | 2020-05-15 | 21:49 | 0:10 | 0 | 10 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-16 | 3:34 | 2020-05-16 | 3:38 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-17 | 22:22 | 2020-05-17 | 22.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:16 | 2020-05-18 | 22.18 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:27 | 2020-05-18 | 22.29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 22:56 | 2020-05-22 | 22:57 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 0:20 | 2020-05-22 | 0:21 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:34 | 2020-05-24 | 21:36 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:48 | 2020-05-24 | 21:50 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-25 | 1:29 | 2020-05-25 | 1:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 3:11 | 2020-05-26 | 3:15 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 23:29 | 2020-05-26 | 23:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 2:32 | 2020-05-26 | 2:34 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:30 | 2020-05-27 | 15:42 | 0:12 | 0 | 12 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:48 | 2020-05-27 | 15:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-06-01 | 23:25 | 2020-06-01 | 23:28 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 0:06 | 2020-06-05 | 0:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 12:02 | 2020-06-05 | 12:04 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 14:24 | 2020-06-11 | 14:26 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 15:08 | 2020-06-11 | 15:13 | 0:05 | 0 | 5 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 20:33 | 2020-06-24 | 20:35 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 21:28 | 2020-06-24 | 21:30 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 23:27 | 2020-06-24 | 23:53 | 0:26 | 0 | 26 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-25 | 0:33 | 2020-06-25 | 0:34 | 0:01 | 0 | 1 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 19:27 | 2020-06-27 | 19:30 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 0:17 | 2020-06-27 | 0:24 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-07-21 | 22:45 | 2020-07-21 | 22:49 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:10 | 2020-07-21 | 23:23 | 00:13 | 0 | 13 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:56 | 2020-07-21 | 00:00 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-02 | 22:27 | 2020-07-02 | 22:30 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-03 | 00:17 | 2020-07-03 | 00:19 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 21:28 | 2020-07-08 | 21:31 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 23:20 | 2020-07-08 | 23:25 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-09 | 23:30 | 2020-07-09 | 23:32 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-11 | 22:18 | 2020-07-11 | 22:20 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:23 | 2020-07-16 | 14:26 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-18 | 21:04 | 2020-07-18 | 21:06 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-20 | 22:03 | 2020-07-20 | 22:05 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:29 | 2020-07-22 | 01:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:39 | 2020-07-22 | 01:44 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 02:37 | 2020-07-22 | 02:46 | 00:09 | 0 | 9 | [5 empty] | At kesinga end: O/C
|  | 2020-07-29 | 23:33 | 2020-07-29 | 23:34 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:16 | 2020-07-30 | 00:17 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:25 | 2020-07-30 | 00:28 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 01:39 | 2020-07-30 | 01:40 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 02:42 | 2020-07-30 | 02:44 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:29 | 2020-07-30 | 20:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:54 | 2020-07-30 | 20:57 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 21:10 | 2020-07-30 | 21:12 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-31 | 15:35 | 2020-07-31 | 15:37 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 17:08 | 2020-07-21 | 17:12 | 00:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 18:15 | 2020-07-21 | 18:20 | 00:05 | 0 | 5 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 19:10 | 2020-07-21 | 19:30 | 00:20 | 0 | 20 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 00:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 00:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 00:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-08-01 | 04:56 | 2020-08-01 | 04:58 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:05 | 2020-08-01 | 05:09 | 0:04 | 0 | 4 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:25 | 2020-08-01 | 05:33 | 0:08 | 0 | 8 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 17:21 | 2020-08-01 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 23:51 | 2020-08-01 | 23:53 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-02 | 23:31 | 2020-08-02 | 23:52 | 0:21 | 0 | 21 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-07 | 23:43 | 2020-08-07 | 23:54 | 0:11 | 0 | 11 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-03 | 23.31 | 2020-08-03 | 23.42 | 0:11 | 0 | 11 | [5 empty] | ABCT,IL1=535 A, IL2=494 A, IL3= 474 A. at therubali end.
|  | 2020-08-22 | 19:52 | 2020-08-22 | 19:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-22 | 21:23 | 2020-08-22 | 21:25 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-23 | 21:35 | 2020-08-23 | 21:38 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-26 | 02:35 | 2020-08-26 | 02:41 | 0:06 | 0 | 6 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-30 | 17:25 | 2020-08-30 | 17:27 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 17:33 | 2020-08-30 | 17:35 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 18:07 | 2020-08-30 | 18:09 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 21:57 | 2020-08-30 | 22:12 | 0:15 | 0 | 15 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 22:49 | 2020-08-30 | 22:56 | 0:07 | 0 | 7 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-31 | 10:19 | 2020-08-31 | 10:29 | 0:10 | 0 | 10 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-09-04 | 20:10 | 2020-09-04 | 20:15 | 0:05 | 0 | 5 | [5 empty] | O/C, B-Phase
|  | 2020-09-05 | 21:20 | 2020-09-05 | 21:22 | 0:02 | 0 | 2 | [5 empty] | O/C, B-Phase
|  | 2020-09-10 | 11:12 | 2020-09-10 | 11:17 | 0:05 | 0 | 5 | [5 empty] | DP, 11.5km
|  | 2020-09-10 | 15:58 | 2020-09-10 | 16:07 | 0:09 | 0 | 9 | [5 empty] | DP at both end. Kesinga:10.5km
|  | 2020-09-11 | 10:31 | 2020-09-11 | 10:33 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-12 | 18:29 | 2020-09-12 | 18:31 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 02:05 | 2020-09-13 | 02:06 | 0:01 | 0 | 1 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 19:22 | 2020-09-13 | 19:24 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-15 | 01:27 | 2020-09-15 | 01:31 | 0:04 | 0 | 4 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-16 | 18:40 | 2020-09-16 | 18:42 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-20 | 23:26 | 2020-09-20 | 23:28 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-21 | 03:54 | 2020-09-21 | 04:00 | 0:06 | 0 | 6 | [5 empty] | DP, 76.6km at VAL end.
|  | 2020-09-21 | 18:29 | 2020-09-21 | 18:32 | 0:03 | 0 | 3 | [5 empty] | O/C at Kesing end.
|  | 2020-09-23 | 18:35 | 2020-09-23 | 18:45 | 0:10 | 0 | 10 | [5 empty] | ABCT, IL1= 534A, IL2=487 A, IL3=453 at Therubali end.
|  | 2020-09-09 | 23:32 | 2020-09-09 | 23:37 | 0:05 | 0 | 5 | [5 empty] | ABCT, IL1= 542A, IL2=509 A, IL3=433 at Therubali end.
|  | 2020-10-19 | 19:45 | 2020-10-19 | 19:52 | 0:07 | 0 | 7 | [5 empty] | trippedABC(Over current.),IA- 513AMP, IB- 518AMP, IC-509AMP.
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2021-01-13 | 05:10 | 2021-01-13 | 05:15 | 0:05 | 0 | 5 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 16:09 | 2021-01-13 | 16:14 | 0:05 | 0 | 5 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 17:24 | 2021-01-13 | 17:42 | 0:18 | 0 | 18 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 18:36 | 2021-01-13 | 18:38 | 0:02 | 0 | 2 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-25 | 18:17 | 2021-01-25 | 18:18 | 0:01 | 0 | 1 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-18 | 10:50 | 2021-01-18 | 10:55 | 0:05 | 0 | 5 | [5 empty] | trip at Junagarh end in O/C
|  | 2021-01-18 | 15:14 | 2021-01-18 | 15:17 | 0:03 | 0 | 3 | [5 empty] | trip at Junagarh end in O/C
|  | 2021-03-22 | 19:39 | 2021-03-22 | 19:49 | 0:10 | 0 | 10 | [5 empty] | Tripped due to O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
340 | 132kV Kesinga-Junagarh |  |  |  |  | 0.33542 | 24 | 36 | [7 empty] | 53.3 | 8760 | 99.72% | 1311.18 | 466908
|  | 01.04.20 | 19:20 | 01.04.20 | 19:26 | 0:06 | 0 | 6 | [5 empty] | P/S failure from Kesinga end
|  | 11.04.20 | 23:26 | 11.04.20 | 23:36 | 0:10 | 0 | 10 | [5 empty] | P/S Failed from Kesinga end
|  | 13.04.20 | 14:35 | 13.04.20 | 14:47 | 0:12 | 0 | 12 | [5 empty] | P/S Failed from Kesinga end
|  | 16.04.20 | 21:00 | 16.04.20 | 21:05 | 0:05 | 0 | 5 | [5 empty] | P/S Failed from Kesinga end
|  | 23.04.20 | 15:17 | 23.04.20 | 15:36 | 0:19 | 0 | 19 | [5 empty] | Failed from Kesinga end
|  | 23.04.20 | 21:02 | 23.04.20 | 21:12 | 0:10 | 0 | 10 | [5 empty] | Failed from Kesinga end
|  | 27.04.20 | 20:55 | 27.04.20 | 20:59 | 0:04 | 0 | 4 | [5 empty] | Tripped from Kesinga end
|  | 28.04.20 | 22:05 | 28.04.20 | 22:08 | 0:03 | 0 | 3 | [5 empty] | Tripped from Kesinga end
|  | 29.04.20 | 3:59 | 29.04.20 | 4:13 | 0:14 | 0 | 14 | [5 empty] | Tripped from Kesinga end
|  | 2020-04-13 | 14:54 | 2020-04-13 | 15:02 | 0:08 | 0 | 8 | [5 empty] | P/S Failed from Therubali end
|  | 15.04.20 | 22:37 | 15.04.20 | 22:40 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 16.04.20 | 1:07 | 16.04.20 | 1:10 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 14:37 | 18.04.20 | 14:39 | 0:02 | 0 | 2 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 18:24 | 18.04.20 | 18:34 | 0:10 | 0 | 10 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 16:36 | 23.04.20 | 16:58 | 0:22 | 0 | 22 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 21:52 | 23.04.20 | 21:56 | 0:04 | 0 | 4 | [5 empty] | P/S Failed from Therubali end
|  | 25.04.20 | 6:32 | 25.04.20 | 6:38 | 0:06 | 0 | 6 | [5 empty] | Tripped at Therubali end
|  | 30.04.20 | 19:02 | 30.04.20 | 19:05 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end
|  | 2020-05-03 | 21:53 | 2020-05-03 | 21:55 | 0:02 | 0 | 2 | [5 empty] | Tripped at Theruvali end
|  | 2020-05-05 | 2:10 | 2020-05-05 | 2:15 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 3:50 | 2020-05-05 | 3:54 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 21:19 | 2020-05-05 | 21:27 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:06 | 2020-05-05 | 23:09 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:30 | 2020-05-05 | 23:37 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-19 | 21:03 | 2020-05-19 | 21:11 | 0:08 | 0 | 8 | [5 empty] | Tripped at lanjigarh end
|  | 2020-05-19 | 15:43 | 2020-05-19 | 15:47 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-19 | 16:49 | 2020-05-19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-21 | 16:39 | 2020-05-21 | 16:46 | 0:07 | 0 | 7 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-24 | 19:06 | 2020-05-24 | 19:11 | 0:05 | 0 | 5 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 19:34 | 2020-05-24 | 19:40 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 22:13 | 2020-05-24 | 22:18 | 0:05 | 0 | 5 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 23:58 | 2020-05-25 | 0:04 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 3:28 | 2020-05-26 | 3:31 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 21:07 | 2020-05-26 | 21:13 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 22:24 | 2020-05-26 | 22:30 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 1:28 | 2020-05-26 | 1:32 | 0:04 | 0 | 4 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 1:45 | 2020-05-26 | 1:48 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-27 | 20:52 | 2020-05-27 | 20:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-27 | 21:18 | 2020-05-27 | 21:20 | 0:02 | 0 | 2 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-27 | 23:36 | 2020-05-27 | 23:39 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-28 | 14:48 | 2020-05-28 | 14:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-29 | 11:06 | 2020-05-29 | 11:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga-Tripped Due to Circuit Overloading
|  | 2020-05-01 | 22:29 | 2020-05-01 | 22:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-03 | 0:22 | 2020-05-03 | 0.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-06 | 2:10 | 2020-05-06 | 2:14 | 0:04 | 0 | 4 | [5 empty] | Tripped at Kesinga- on Overload
|  | 2020-05-06 | 3:50 | 2020-05-06 | 3:53 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga- on Overload
|  | 2020-05-06 | 5:27 | 2020-05-06 | 5:34 | 0:07 | 0 | 7 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 23:03 | 2020-05-06 | 23:06 | 0:03 | 0 | 3 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-06 | 23:30 | 2020-05-06 | 23:37 | 0:07 | 0 | 7 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-06 | 21:19 | 2020-05-06 | 21:22 | 0:03 | 0 | 3 | [5 empty] | 132 KV P/S FAIL
|  | 2020-05-12 | 23:12 | 2020-05-12 | 23.14 | 0:02 | 0 | 2 | [5 empty] | At Therubali end: C-A Phase.
|  | 2020-05-13 | 2:01 | 2020-05-13 | 2:02 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-08 | 19:36 | 2020-05-08 | 19.43 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-05-15 | 21:39 | 2020-05-15 | 21:49 | 0:10 | 0 | 10 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-16 | 3:34 | 2020-05-16 | 3:38 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-17 | 22:22 | 2020-05-17 | 22.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:16 | 2020-05-18 | 22.18 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:27 | 2020-05-18 | 22.29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 22:56 | 2020-05-22 | 22:57 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 0:20 | 2020-05-22 | 0:21 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:34 | 2020-05-24 | 21:36 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:48 | 2020-05-24 | 21:50 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-25 | 1:29 | 2020-05-25 | 1:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 3:11 | 2020-05-26 | 3:15 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 23:29 | 2020-05-26 | 23:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 2:32 | 2020-05-26 | 2:34 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:30 | 2020-05-27 | 15:42 | 0:12 | 0 | 12 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:48 | 2020-05-27 | 15:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-06-01 | 23:25 | 2020-06-01 | 23:28 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 0:06 | 2020-06-05 | 0:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 12:02 | 2020-06-05 | 12:04 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 14:24 | 2020-06-11 | 14:26 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 15:08 | 2020-06-11 | 15:13 | 0:05 | 0 | 5 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 20:33 | 2020-06-24 | 20:35 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 21:28 | 2020-06-24 | 21:30 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 23:27 | 2020-06-24 | 23:53 | 0:26 | 0 | 26 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-25 | 0:33 | 2020-06-25 | 0:34 | 0:01 | 0 | 1 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 19:27 | 2020-06-27 | 19:30 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 0:17 | 2020-06-27 | 0:24 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-07-21 | 22:45 | 2020-07-21 | 22:49 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:10 | 2020-07-21 | 23:23 | 00:13 | 0 | 13 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:56 | 2020-07-21 | 00:00 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-02 | 22:27 | 2020-07-02 | 22:30 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-03 | 00:17 | 2020-07-03 | 00:19 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 21:28 | 2020-07-08 | 21:31 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 23:20 | 2020-07-08 | 23:25 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-09 | 23:30 | 2020-07-09 | 23:32 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-11 | 22:18 | 2020-07-11 | 22:20 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:23 | 2020-07-16 | 14:26 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-18 | 21:04 | 2020-07-18 | 21:06 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-20 | 22:03 | 2020-07-20 | 22:05 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:29 | 2020-07-22 | 01:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:39 | 2020-07-22 | 01:44 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 02:37 | 2020-07-22 | 02:46 | 00:09 | 0 | 9 | [5 empty] | At kesinga end: O/C
|  | 2020-07-29 | 23:33 | 2020-07-29 | 23:34 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:16 | 2020-07-30 | 00:17 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:25 | 2020-07-30 | 00:28 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 01:39 | 2020-07-30 | 01:40 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 02:42 | 2020-07-30 | 02:44 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:29 | 2020-07-30 | 20:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:54 | 2020-07-30 | 20:57 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 21:10 | 2020-07-30 | 21:12 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-31 | 15:35 | 2020-07-31 | 15:37 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 17:08 | 2020-07-21 | 17:12 | 00:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 18:15 | 2020-07-21 | 18:20 | 00:05 | 0 | 5 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 19:10 | 2020-07-21 | 19:30 | 00:20 | 0 | 20 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 00:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 00:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 00:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-08-01 | 04:56 | 2020-08-01 | 04:58 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:05 | 2020-08-01 | 05:09 | 0:04 | 0 | 4 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:25 | 2020-08-01 | 05:33 | 0:08 | 0 | 8 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 17:21 | 2020-08-01 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 23:51 | 2020-08-01 | 23:53 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-02 | 23:31 | 2020-08-02 | 23:52 | 0:21 | 0 | 21 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-07 | 23:43 | 2020-08-07 | 23:54 | 0:11 | 0 | 11 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-03 | 23.31 | 2020-08-03 | 23.42 | 0:11 | 0 | 11 | [5 empty] | ABCT,IL1=535 A, IL2=494 A, IL3= 474 A. at therubali end.
|  | 2020-08-22 | 19:52 | 2020-08-22 | 19:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-22 | 21:23 | 2020-08-22 | 21:25 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-23 | 21:35 | 2020-08-23 | 21:38 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-26 | 02:35 | 2020-08-26 | 02:41 | 0:06 | 0 | 6 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-30 | 17:25 | 2020-08-30 | 17:27 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 17:33 | 2020-08-30 | 17:35 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 18:07 | 2020-08-30 | 18:09 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 21:57 | 2020-08-30 | 22:12 | 0:15 | 0 | 15 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 22:49 | 2020-08-30 | 22:56 | 0:07 | 0 | 7 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-31 | 10:19 | 2020-08-31 | 10:29 | 0:10 | 0 | 10 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-09-04 | 20:10 | 2020-09-04 | 20:15 | 0:05 | 0 | 5 | [5 empty] | O/C, B-Phase
|  | 2020-09-05 | 21:20 | 2020-09-05 | 21:22 | 0:02 | 0 | 2 | [5 empty] | O/C, B-Phase
|  | 2020-09-10 | 11:12 | 2020-09-10 | 11:17 | 0:05 | 0 | 5 | [5 empty] | DP, 11.5km
|  | 2020-09-10 | 15:58 | 2020-09-10 | 16:07 | 0:09 | 0 | 9 | [5 empty] | DP at both end. Kesinga:10.5km
|  | 2020-09-11 | 10:31 | 2020-09-11 | 10:33 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-12 | 18:29 | 2020-09-12 | 18:31 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 02:05 | 2020-09-13 | 02:06 | 0:01 | 0 | 1 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 19:22 | 2020-09-13 | 19:24 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-15 | 01:27 | 2020-09-15 | 01:31 | 0:04 | 0 | 4 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-16 | 18:40 | 2020-09-16 | 18:42 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-20 | 23:26 | 2020-09-20 | 23:28 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-21 | 03:54 | 2020-09-21 | 04:00 | 0:06 | 0 | 6 | [5 empty] | DP, 76.6km at VAL end.
|  | 2020-09-21 | 18:29 | 2020-09-21 | 18:32 | 0:03 | 0 | 3 | [5 empty] | O/C at Kesing end.
|  | 2020-09-23 | 18:35 | 2020-09-23 | 18:45 | 0:10 | 0 | 10 | [5 empty] | ABCT, IL1= 534A, IL2=487 A, IL3=453 at Therubali end.
|  | 2020-09-09 | 23:32 | 2020-09-09 | 23:37 | 0:05 | 0 | 5 | [5 empty] | ABCT, IL1= 542A, IL2=509 A, IL3=433 at Therubali end.
|  | 2020-10-19 | 19:45 | 2020-10-19 | 19:52 | 0:07 | 0 | 7 | [5 empty] | trippedABC(Over current.),IA- 513AMP, IB- 518AMP, IC-509AMP.
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2021-01-13 | 05:10 | 2021-01-13 | 05:15 | 0:05 | 0 | 5 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 16:09 | 2021-01-13 | 16:14 | 0:05 | 0 | 5 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 17:24 | 2021-01-13 | 17:42 | 0:18 | 0 | 18 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 18:36 | 2021-01-13 | 18:38 | 0:02 | 0 | 2 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-25 | 18:17 | 2021-01-25 | 18:18 | 0:01 | 0 | 1 | [5 empty] | Failed from kesinga end:.
|  | 2021-03-22 | 19:39 | 2021-03-22 | 19:49 | 0:10 | 0 | 10 | [5 empty] | Tripped due to O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
341 | 132kV Bhawanipatna- Lanjigarh RTSS |  |  |  |  | 0.029861 | 13 | 6 | [7 empty] | 34.18 | 5076 | 99.74% | 447.758 | 173497.68
|  | 2020-10-05 | 18:16 | 2020-10-05 | 18:20 | 0:04 | 0 | 4 | [5 empty] | LBB
|  | 2020-10-06 | 06:52 | 2020-10-06 | 06:58 | 0:06 | 0 | 6 | [5 empty] | LBB
|  | 2020-10-06 | 13:11 | 2020-10-06 | 13:13 | 0:02 | 0 | 2 | [5 empty] | LBB
|  | 2020-10-06 | 13:45 | 2020-10-06 | 13:48 | 0:03 | 0 | 3 | [5 empty] | LBB
|  | 2020-10-19 | 19:45 | 2020-10-19 | 19:52 | 0:07 | 0 | 7 | [5 empty] | trippedABC(Over current.),IA- 513AMP, IB- 518AMP, IC-509AMP.
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-12-04 | 04:08 | 2020-12-04 | 04:11 | 0:03 | 0 | 3 | [5 empty] | O/C Y-ph
|  | 2021-01-25 | 18:17 | 2021-01-25 | 18:18 | 0:01 | 0 | 1 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-08 | 12:45 | 2021-01-08 | 12:52 | 00:07 | 0 | 7 | [5 empty] | O/C
|  | 2021-01-20 | 19:51 | 2021-01-20 | 19:54 | 00:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-24 | 06:24 | 2021-01-24 | 06:27 | 00:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-27 | 04:44 | 2021-01-27 | 04:48 | 00:04 | 0 | 4 | [5 empty] | O/C
|  | 2021-01-27 | 14:17 | 2021-01-27 | 14:20 | 00:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-30 | 19:01 | 2021-01-30 | 19:04 | 00:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-03-22 | 19:39 | 2021-03-22 | 19:49 | 0:10 | 0 | 10 | [5 empty] | Tripped due to O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
342 | 132kV Kesinga-Kesinga RTSS |  |  |  |  | 0.66667 | 36 | 44 | [7 empty] | 4.952 | 8760 | 99.58% | 181.9035 | 43379.52
|  | 2020-04-13 | 14:54 | 2020-04-13 | 15:02 | 0:08 | 0 | 8 | [5 empty] | P/S Failed from Therubali end
|  | 15.04.20 | 22:37 | 15.04.20 | 22:40 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 16.04.20 | 1:07 | 16.04.20 | 1:10 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 14:37 | 18.04.20 | 14:39 | 0:02 | 0 | 2 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 18:24 | 18.04.20 | 18:34 | 0:10 | 0 | 10 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 16:36 | 23.04.20 | 16:58 | 0:22 | 0 | 22 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 21:52 | 23.04.20 | 21:56 | 0:04 | 0 | 4 | [5 empty] | P/S Failed from Therubali end
|  | 25.04.20 | 6:32 | 25.04.20 | 6:38 | 0:06 | 0 | 6 | [5 empty] | Tripped at Therubali end
|  | 30.04.20 | 19:02 | 30.04.20 | 19:05 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end
|  | 2020-05-01 | 6:05 | 2020-05-01 | 6:15 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-01 | 8:38 | 2020-05-01 | 8:42 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-01 | 15:30 | 2020-05-01 | 15:35 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-01 | 17:02 | 2020-05-01 | 17:12 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-01 | 21:58 | 2020-05-01 | 22:03 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-02 | 1:51 | 2020-05-02 | 1:55 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-02 | 3:30 | 2020-05-02 | 3:35 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-02 | 7:09 | 2020-05-02 | 7:14 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-02 | 7:16 | 2020-05-02 | 7:19 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-02 | 7:46 | 2020-05-02 | 7:56 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-02 | 14:47 | 2020-05-02 | 14:51 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-02 | 17:00 | 2020-05-02 | 17:03 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-02 | 17:55 | 2020-05-02 | 17:58 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 0:21 | 2020-05-03 | 0:31 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 0:22 | 2020-05-03 | 0:24 | 0:09 | 0 | 9 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 0:49 | 2020-05-03 | 0:59 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 2:40 | 2020-05-03 | 2:45 | 0:09 | 0 | 9 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 3:42 | 2020-05-03 | 3:52 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 11:09 | 2020-05-03 | 11:14 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 11:53 | 2020-05-03 | 11:56 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 14:36 | 2020-05-03 | 14:39 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 14:52 | 2020-05-03 | 15:00 | 0:08 | 0 | 8 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 19:15 | 2020-05-03 | 19:25 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 20:20 | 2020-05-03 | 20:30 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 20:57 | 2020-05-03 | 21:07 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 21:47 | 2020-05-03 | 21:51 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 21:54 | 2020-05-03 | 21:56 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 22:13 | 2020-05-03 | 22:18 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 22:30 | 2020-05-03 | 22:37 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 22:57 | 2020-05-03 | 23:04 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 0:15 | 2020-05-03 | 0:20 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 0:31 | 2020-05-03 | 0:37 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 5:16 | 2020-05-03 | 5:21 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 6:20 | 2020-05-03 | 6:27 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 6:38 | 2020-05-03 | 6:43 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 6:48 | 2020-05-03 | 6:53 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 7:48 | 2020-05-03 | 7:53 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 12:20 | 2020-05-04 | 12:26 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 12:28 | 2020-05-04 | 12:34 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 13:54 | 2020-05-04 | 13:59 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 15:33 | 2020-05-04 | 15:38 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 16:05 | 2020-05-04 | 16:10 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 16:27 | 2020-05-04 | 16:32 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 16:39 | 2020-05-04 | 16:45 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 17:07 | 2020-05-04 | 17:12 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 19:35 | 2020-05-04 | 19:45 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 18:44 | 2020-05-04 | 18:47 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 21:42 | 2020-05-04 | 21:50 | 0:08 | 0 | 8 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 21:54 | 2020-05-04 | 22:04 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 22:23 | 2020-05-04 | 22:28 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 22:24 | 2020-05-04 | 22:29 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 22:31 | 2020-05-04 | 22:41 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-04 | 23:31 | 2020-05-04 | 23:36 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 0:18 | 2020-05-05 | 0:23 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 0:27 | 2020-05-05 | 0:32 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 1:13 | 2020-05-05 | 1:18 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-06 | 8:20 | 2020-05-06 | 8:30 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-06 | 10:25 | 2020-05-06 | 10:35 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-06 | 11:56 | 2020-05-06 | 12:06 | 0:10 | 0 | 10 | [5 empty] | Directional O/C, E/F
|  | 2020-05-19 | 13:02 | 2020-05-19 | 13:07 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-22 | 19:09 | 2020-05-22 | 19:11 | 0:02 | 0 | 2 | [5 empty] | Directional O/C, E/F
|  | 2020-05-30 | 15:45 | 2020-05-30 | 15:50 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-31 | 0:41 | 2020-05-31 | 0:44 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-03 | 21:53 | 2020-05-03 | 21:55 | 0:02 | 0 | 2 | [5 empty] | Tripped at Theruvali end
|  | 2020-05-05 | 2:10 | 2020-05-05 | 2:15 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 3:50 | 2020-05-05 | 3:54 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 21:19 | 2020-05-05 | 21:27 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:06 | 2020-05-05 | 23:09 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:30 | 2020-05-05 | 23:37 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-19 | 21:03 | 2020-05-19 | 21:11 | 0:08 | 0 | 8 | [5 empty] | TRIPPED AT LANJIGARH END
|  | 2020-05-19 | 15:43 | 2020-05-19 | 15:47 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-19 | 16:49 | 2020-05-19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-21 | 16:39 | 2020-05-21 | 16:46 | 0:07 | 0 | 7 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-24 | 19:06 | 2020-05-24 | 19:11 | 0:05 | 0 | 5 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 19:34 | 2020-05-24 | 19:40 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 22:13 | 2020-05-24 | 22:18 | 0:05 | 0 | 5 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 23:58 | 2020-05-25 | 0:04 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 3:28 | 2020-05-26 | 3:31 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 21:07 | 2020-05-26 | 21:13 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 22:24 | 2020-05-26 | 22:30 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 1:28 | 2020-05-26 | 1:32 | 0:04 | 0 | 4 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 1:45 | 2020-05-26 | 1:48 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-27 | 20:52 | 2020-05-27 | 20:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-27 | 21:18 | 2020-05-27 | 21:20 | 0:02 | 0 | 2 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-27 | 23:36 | 2020-05-27 | 23:39 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-28 | 14:48 | 2020-05-28 | 14:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-29 | 11:06 | 2020-05-29 | 11:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga-Tripped Due to Circuit Overloading
|  | 2020-05-01 | 22:29 | 2020-05-01 | 22:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-03 | 0:22 | 2020-05-03 | 0.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-06 | 2:10 | 2020-05-06 | 2:14 | 0:04 | 0 | 4 | [5 empty] | Tripped at Kesinga- on Overload
|  | 2020-05-06 | 3:50 | 2020-05-06 | 3:53 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga- on Overload
|  | 2020-05-06 | 5:27 | 2020-05-06 | 5:34 | 0:07 | 0 | 7 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 23:03 | 2020-05-06 | 23:06 | 0:03 | 0 | 3 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-06 | 23:30 | 2020-05-06 | 23:37 | 0:07 | 0 | 7 | [5 empty] | At Therubali end: Tripped
|  | 2020-05-06 | 21:19 | 2020-05-06 | 21:22 | 0:03 | 0 | 3 | [5 empty] | 132 KV P/S FAIL
|  | 2020-05-12 | 23:12 | 2020-05-12 | 23.14 | 0:02 | 0 | 2 | [5 empty] | At Therubali end: C-A Phase.
|  | 2020-05-13 | 2:01 | 2020-05-13 | 2:02 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-08 | 19:36 | 2020-05-08 | 19.43 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-05-15 | 21:39 | 2020-05-15 | 21:49 | 0:10 | 0 | 10 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-16 | 3:34 | 2020-05-16 | 3:38 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-17 | 22:22 | 2020-05-17 | 22.23 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:16 | 2020-05-18 | 22.18 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-18 | 22:27 | 2020-05-18 | 22.29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 22:56 | 2020-05-22 | 22:57 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-22 | 0:20 | 2020-05-22 | 0:21 | 0:01 | 0 | 1 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:34 | 2020-05-24 | 21:36 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-24 | 21:48 | 2020-05-24 | 21:50 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-25 | 1:29 | 2020-05-25 | 1:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 3:11 | 2020-05-26 | 3:15 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 23:29 | 2020-05-26 | 23:31 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-26 | 2:32 | 2020-05-26 | 2:34 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:30 | 2020-05-27 | 15:42 | 0:12 | 0 | 12 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 15:48 | 2020-05-27 | 15:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:29 | 0:02 | 0 | 2 | [5 empty] | Tripped at Therubali end.
|  | 2020-05-27 | 16:27 | 2020-05-27 | 16:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Therubali end.
|  | 2020-06-01 | 23:25 | 2020-06-01 | 23:28 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 0:06 | 2020-06-05 | 0:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 12:02 | 2020-06-05 | 12:04 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 14:24 | 2020-06-11 | 14:26 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 15:08 | 2020-06-11 | 15:13 | 0:05 | 0 | 5 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 20:33 | 2020-06-24 | 20:35 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 21:28 | 2020-06-24 | 21:30 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 23:27 | 2020-06-24 | 23:53 | 0:26 | 0 | 26 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-25 | 0:33 | 2020-06-25 | 0:34 | 0:01 | 0 | 1 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 19:27 | 2020-06-27 | 19:30 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 0:17 | 2020-06-27 | 0:24 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-07-27 | 20:04 | 2020-07-27 | 20:07 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-27 | 20:27 | 2020-07-27 | 20:31 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 22:45 | 2020-07-21 | 22:49 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:10 | 2020-07-21 | 23:23 | 00:13 | 0 | 13 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:56 | 2020-07-21 | 00:00 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-02 | 22:27 | 2020-07-02 | 22:30 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-03 | 00:17 | 2020-07-03 | 00:19 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 21:28 | 2020-07-08 | 21:31 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 23:20 | 2020-07-08 | 23:25 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-09 | 23:30 | 2020-07-09 | 23:32 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-11 | 22:18 | 2020-07-11 | 22:20 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:23 | 2020-07-16 | 14:26 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-18 | 21:04 | 2020-07-18 | 21:06 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-20 | 22:03 | 2020-07-20 | 22:05 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:29 | 2020-07-22 | 01:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:39 | 2020-07-22 | 01:44 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 02:37 | 2020-07-22 | 02:46 | 00:09 | 0 | 9 | [5 empty] | At kesinga end: O/C
|  | 2020-07-29 | 23:33 | 2020-07-29 | 23:34 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:16 | 2020-07-30 | 00:17 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:25 | 2020-07-30 | 00:28 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 01:39 | 2020-07-30 | 01:40 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 02:42 | 2020-07-30 | 02:44 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:29 | 2020-07-30 | 20:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:54 | 2020-07-30 | 20:57 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 21:10 | 2020-07-30 | 21:12 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-31 | 15:35 | 2020-07-31 | 15:37 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 17:08 | 2020-07-21 | 17:12 | 00:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 18:15 | 2020-07-21 | 18:20 | 00:05 | 0 | 5 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 19:10 | 2020-07-21 | 19:30 | 00:20 | 0 | 20 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 00:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 00:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 00:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-08-01 | 04:56 | 2020-08-01 | 04:58 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:05 | 2020-08-01 | 05:09 | 0:04 | 0 | 4 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:25 | 2020-08-01 | 05:33 | 0:08 | 0 | 8 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 17:21 | 2020-08-01 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 23:51 | 2020-08-01 | 23:53 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-02 | 23:31 | 2020-08-02 | 23:52 | 0:21 | 0 | 21 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-07 | 23:43 | 2020-08-07 | 23:54 | 0:11 | 0 | 11 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-03 | 23.31 | 2020-08-03 | 23.42 | 0:11 | 0 | 11 | [5 empty] | ABCT,IL1=535 A, IL2=494 A, IL3= 474 A. at therubali end.
|  | 2020-08-22 | 19:52 | 2020-08-22 | 19:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-22 | 21:23 | 2020-08-22 | 21:25 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-23 | 21:35 | 2020-08-23 | 21:38 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-26 | 02:35 | 2020-08-26 | 02:41 | 0:06 | 0 | 6 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-30 | 17:25 | 2020-08-30 | 17:27 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 17:33 | 2020-08-30 | 17:35 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 18:07 | 2020-08-30 | 18:09 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 21:57 | 2020-08-30 | 22:12 | 0:15 | 0 | 15 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 22:49 | 2020-08-30 | 22:56 | 0:07 | 0 | 7 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-31 | 10:19 | 2020-08-31 | 10:29 | 0:10 | 0 | 10 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-09-04 | 20:10 | 2020-09-04 | 20:15 | 0:05 | 0 | 5 | [5 empty] | O/C, B-Phase
|  | 2020-09-05 | 21:20 | 2020-09-05 | 21:22 | 0:02 | 0 | 2 | [5 empty] | O/C, B-Phase
|  | 2020-09-10 | 11:12 | 2020-09-10 | 11:17 | 0:05 | 0 | 5 | [5 empty] | DP, 11.5km
|  | 2020-09-10 | 15:58 | 2020-09-10 | 16:07 | 0:09 | 0 | 9 | [5 empty] | DP at both end. Kesinga:10.5km
|  | 2020-09-11 | 10:31 | 2020-09-11 | 10:33 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-12 | 18:29 | 2020-09-12 | 18:31 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 02:05 | 2020-09-13 | 02:06 | 0:01 | 0 | 1 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 19:22 | 2020-09-13 | 19:24 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-15 | 01:27 | 2020-09-15 | 01:31 | 0:04 | 0 | 4 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-16 | 18:40 | 2020-09-16 | 18:42 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-20 | 23:26 | 2020-09-20 | 23:28 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-21 | 03:54 | 2020-09-21 | 04:00 | 0:06 | 0 | 6 | [5 empty] | DP, 76.6km at VAL end.
|  | 2020-09-21 | 18:29 | 2020-09-21 | 18:32 | 0:03 | 0 | 3 | [5 empty] | O/C at Kesing end.
|  | 2020-09-23 | 18:35 | 2020-09-23 | 18:45 | 0:10 | 0 | 10 | [5 empty] | ABCT, IL1= 534A, IL2=487 A, IL3=453 at Therubali end.
|  | 2020-09-09 | 23:32 | 2020-09-09 | 23:37 | 0:05 | 0 | 5 | [5 empty] | ABCT, IL1= 542A, IL2=509 A, IL3=433 at Therubali end.
|  | 2020-10-19 | 19:45 | 2020-10-19 | 19:52 | 0:07 | 0 | 7 | [5 empty] | trippedABC(Over current.),IA- 513AMP, IB- 518AMP, IC-509AMP.
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2021-01-13 | 14:52 | 2021-01-13 | 21:32 | 6:40 | 6 | 40 | [5 empty] | Tripped on E/F due to heavy spark inside CT console box,also indication of TC-1 faulty.
|  | 2021-01-14 | 10:54 | 2021-01-14 | 10:57 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-27 | 04:50 | 2021-01-27 | 04:53 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-13 | 05:10 | 2021-01-13 | 05:15 | 0:05 | 0 | 5 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 16:09 | 2021-01-13 | 16:14 | 0:05 | 0 | 5 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 17:24 | 2021-01-13 | 17:42 | 0:18 | 0 | 18 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 18:36 | 2021-01-13 | 18:38 | 0:02 | 0 | 2 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-25 | 18:17 | 2021-01-25 | 18:18 | 0:01 | 0 | 1 | [5 empty] | Failed from kesinga end:.
|  | 2021-03-22 | 19:39 | 2021-03-22 | 19:49 | 0:10 | 0 | 10 | [5 empty] | Tripped due to O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
343 | 132kV Kesinga-Powmex |  |  |  |  | 0.30556 | 21 | 44 | [7 empty] | 14.53 | 8760 | 99.75% | 315.7853 | 127282.8
|  | 2020-04-13 | 14:54 | 2020-04-13 | 15:02 | 0:08 | 0 | 8 | [5 empty] | P/S Failed from Therubali end
|  | 15.04.20 | 22:37 | 15.04.20 | 22:40 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 16.04.20 | 1:07 | 16.04.20 | 1:10 | 0:03 | 0 | 3 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 14:37 | 18.04.20 | 14:39 | 0:02 | 0 | 2 | [5 empty] | P/S Failed from Therubali end
|  | 18.04.20 | 18:24 | 18.04.20 | 18:34 | 0:10 | 0 | 10 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 16:36 | 23.04.20 | 16:58 | 0:22 | 0 | 22 | [5 empty] | Tripped at Therubali end
|  | 23.04.20 | 21:52 | 23.04.20 | 21:56 | 0:04 | 0 | 4 | [5 empty] | P/S Failed from Therubali end
|  | 25.04.20 | 6:32 | 25.04.20 | 6:38 | 0:06 | 0 | 6 | [5 empty] | Tripped at Therubali end
|  | 30.04.20 | 19:02 | 30.04.20 | 19:05 | 0:03 | 0 | 3 | [5 empty] | Tripped at Therubali end
|  | 2020-05-03 | 21:53 | 2020-05-03 | 21:55 | 0:02 | 0 | 2 | [5 empty] | Tripped at Theruvali end
|  | 2020-05-05 | 2:10 | 2020-05-05 | 2:15 | 0:05 | 0 | 5 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 3:50 | 2020-05-05 | 3:54 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 21:19 | 2020-05-05 | 21:27 | 0:04 | 0 | 4 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:06 | 2020-05-05 | 23:09 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-05 | 23:30 | 2020-05-05 | 23:37 | 0:03 | 0 | 3 | [5 empty] | Directional O/C, E/F
|  | 2020-05-19 | 21:03 | 2020-05-19 | 21:11 | 0:08 | 0 | 8 | [5 empty] | TRIPPED AT LANJIGARH END
|  | 2020-05-19 | 15:43 | 2020-05-19 | 15:47 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-19 | 16:49 | 2020-05-19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Kesinga-Tripped
|  | 2020-05-21 | 16:39 | 2020-05-21 | 16:46 | 0:07 | 0 | 7 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-24 | 19:06 | 2020-05-24 | 19:11 | 0:05 | 0 | 5 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 19:34 | 2020-05-24 | 19:40 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 22:13 | 2020-05-24 | 22:18 | 0:05 | 0 | 5 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-24 | 23:58 | 2020-05-25 | 0:04 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 3:28 | 2020-05-26 | 3:31 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 21:07 | 2020-05-26 | 21:13 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 22:24 | 2020-05-26 | 22:30 | 0:06 | 0 | 6 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 1:28 | 2020-05-26 | 1:32 | 0:04 | 0 | 4 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-26 | 1:45 | 2020-05-26 | 1:48 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesingai end.
|  | 2020-05-27 | 20:52 | 2020-05-27 | 20:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-27 | 21:18 | 2020-05-27 | 21:20 | 0:02 | 0 | 2 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-27 | 23:36 | 2020-05-27 | 23:39 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-28 | 14:48 | 2020-05-28 | 14:51 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga end.
|  | 2020-05-29 | 11:06 | 2020-05-29 | 11:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga-Tripped Due to Circuit Overloading
|  | 2020-06-01 | 23:25 | 2020-06-01 | 23:28 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 0:06 | 2020-06-05 | 0:09 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-05 | 12:02 | 2020-06-05 | 12:04 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 14:24 | 2020-06-11 | 14:26 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-11 | 15:08 | 2020-06-11 | 15:13 | 0:05 | 0 | 5 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 20:33 | 2020-06-24 | 20:35 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 21:28 | 2020-06-24 | 21:30 | 0:02 | 0 | 2 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-24 | 23:27 | 2020-06-24 | 23:53 | 0:26 | 0 | 26 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-25 | 0:33 | 2020-06-25 | 0:34 | 0:01 | 0 | 1 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 19:27 | 2020-06-27 | 19:30 | 0:03 | 0 | 3 | [5 empty] | At Kesinga end: O/C, B Phase.
|  | 2020-06-27 | 0:17 | 2020-06-27 | 0:24 | 0:07 | 0 | 7 | [5 empty] | At Therubali end-Tripped.
|  | 2020-07-27 | 20:04 | 2020-07-27 | 20:07 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-27 | 20:27 | 2020-07-27 | 20:31 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 22:45 | 2020-07-21 | 22:49 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:10 | 2020-07-21 | 23:23 | 00:13 | 0 | 13 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 23:56 | 2020-07-21 | 00:00 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-02 | 22:27 | 2020-07-02 | 22:30 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-03 | 00:17 | 2020-07-03 | 00:19 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 21:28 | 2020-07-08 | 21:31 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-08 | 23:20 | 2020-07-08 | 23:25 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-09 | 23:30 | 2020-07-09 | 23:32 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-11 | 22:18 | 2020-07-11 | 22:20 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 00:04 | 0 | 4 | [5 empty] | At kesinga end: O/C
|  | 2020-07-16 | 14:23 | 2020-07-16 | 14:26 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-18 | 21:04 | 2020-07-18 | 21:06 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-20 | 22:03 | 2020-07-20 | 22:05 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:29 | 2020-07-22 | 01:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 01:39 | 2020-07-22 | 01:44 | 00:05 | 0 | 5 | [5 empty] | At kesinga end: O/C
|  | 2020-07-22 | 02:37 | 2020-07-22 | 02:46 | 00:09 | 0 | 9 | [5 empty] | At kesinga end: O/C
|  | 2020-07-29 | 23:33 | 2020-07-29 | 23:34 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:16 | 2020-07-30 | 00:17 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 00:25 | 2020-07-30 | 00:28 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 01:39 | 2020-07-30 | 01:40 | 00:01 | 0 | 1 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 02:42 | 2020-07-30 | 02:44 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:29 | 2020-07-30 | 20:32 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 20:54 | 2020-07-30 | 20:57 | 00:03 | 0 | 3 | [5 empty] | At kesinga end: O/C
|  | 2020-07-30 | 21:10 | 2020-07-30 | 21:12 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-31 | 15:35 | 2020-07-31 | 15:37 | 00:02 | 0 | 2 | [5 empty] | At kesinga end: O/C
|  | 2020-07-21 | 17:08 | 2020-07-21 | 17:12 | 00:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 18:15 | 2020-07-21 | 18:20 | 00:05 | 0 | 5 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 19:10 | 2020-07-21 | 19:30 | 00:20 | 0 | 20 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 00:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 00:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 00:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-08-01 | 04:56 | 2020-08-01 | 04:58 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:05 | 2020-08-01 | 05:09 | 0:04 | 0 | 4 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 05:25 | 2020-08-01 | 05:33 | 0:08 | 0 | 8 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 17:21 | 2020-08-01 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-01 | 23:51 | 2020-08-01 | 23:53 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-02 | 23:31 | 2020-08-02 | 23:52 | 0:21 | 0 | 21 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-07 | 23:43 | 2020-08-07 | 23:54 | 0:11 | 0 | 11 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-03 | 23.31 | 2020-08-03 | 23.42 | 0:11 | 0 | 11 | [5 empty] | ABCT,IL1=535 A, IL2=494 A, IL3= 474 A. at therubali end.
|  | 2020-08-22 | 19:52 | 2020-08-22 | 19:54 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-22 | 21:23 | 2020-08-22 | 21:25 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-23 | 21:35 | 2020-08-23 | 21:38 | 0:03 | 0 | 3 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-26 | 02:35 | 2020-08-26 | 02:41 | 0:06 | 0 | 6 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-08-30 | 17:25 | 2020-08-30 | 17:27 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 17:33 | 2020-08-30 | 17:35 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 18:07 | 2020-08-30 | 18:09 | 0:02 | 0 | 2 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 21:57 | 2020-08-30 | 22:12 | 0:15 | 0 | 15 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-30 | 22:49 | 2020-08-30 | 22:56 | 0:07 | 0 | 7 | [5 empty] | Tripped at kesinga due to O/C.
|  | 2020-08-31 | 10:19 | 2020-08-31 | 10:29 | 0:10 | 0 | 10 | [5 empty] | Tripped on DP at Lanjigarh end.
|  | 2020-09-04 | 20:10 | 2020-09-04 | 20:15 | 0:05 | 0 | 5 | [5 empty] | O/C, B-Phase
|  | 2020-09-05 | 21:20 | 2020-09-05 | 21:22 | 0:02 | 0 | 2 | [5 empty] | O/C, B-Phase
|  | 2020-09-10 | 11:12 | 2020-09-10 | 11:17 | 0:05 | 0 | 5 | [5 empty] | DP, 11.5km
|  | 2020-09-10 | 15:58 | 2020-09-10 | 16:07 | 0:09 | 0 | 9 | [5 empty] | DP at both end. Kesinga:10.5km
|  | 2020-09-11 | 10:31 | 2020-09-11 | 10:33 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-12 | 18:29 | 2020-09-12 | 18:31 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 02:05 | 2020-09-13 | 02:06 | 0:01 | 0 | 1 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-13 | 19:22 | 2020-09-13 | 19:24 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-15 | 01:27 | 2020-09-15 | 01:31 | 0:04 | 0 | 4 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-16 | 18:40 | 2020-09-16 | 18:42 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-20 | 23:26 | 2020-09-20 | 23:28 | 0:02 | 0 | 2 | [5 empty] | O/C at Kesinga end.
|  | 2020-09-21 | 03:54 | 2020-09-21 | 04:00 | 0:06 | 0 | 6 | [5 empty] | DP, 76.6km at VAL end.
|  | 2020-09-21 | 18:29 | 2020-09-21 | 18:32 | 0:03 | 0 | 3 | [5 empty] | O/C at Kesing end.
|  | 2020-09-23 | 18:35 | 2020-09-23 | 18:45 | 0:10 | 0 | 10 | [5 empty] | ABCT, IL1= 534A, IL2=487 A, IL3=453 at Therubali end.
|  | 2020-09-09 | 23:32 | 2020-09-09 | 23:37 | 0:05 | 0 | 5 | [5 empty] | ABCT, IL1= 542A, IL2=509 A, IL3=433 at Therubali end.
|  | 2020-10-19 | 19:45 | 2020-10-19 | 19:52 | 0:07 | 0 | 7 | [5 empty] | trippedABC(Over current.),IA- 513AMP, IB- 518AMP, IC-509AMP.
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2021-01-13 | 05:10 | 2021-01-13 | 05:15 | 0:05 | 0 | 5 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 16:09 | 2021-01-13 | 16:14 | 0:05 | 0 | 5 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 17:24 | 2021-01-13 | 17:42 | 0:18 | 0 | 18 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-13 | 18:36 | 2021-01-13 | 18:38 | 0:02 | 0 | 2 | [5 empty] | Failed from kesinga end:.
|  | 2021-01-25 | 18:17 | 2021-01-25 | 18:18 | 0:01 | 0 | 1 | [5 empty] | Failed from kesinga end:.
|  | 2021-03-22 | 19:39 | 2021-03-22 | 19:49 | 0:10 | 0 | 10 | [5 empty] | Tripped due to O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
344 | 132kV Kesinga-Kesinga Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.48 | 8760 | 100% | 0 | 100564.8
345 | 132kV Kharagprasad-Kharagprasad (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.17 | 8760 | 100% | 0 | 10249.2
346 | 132kV Kharagprasad-MGM Ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.14 | 8760 | 100% | 0 | 62546.4
347 | 132kV Kharagprasad-Nabhabharat Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.577 | 8760 | 100% | 0 | 5054.52
348 | 132kV Kharagprasad-Nabhabharat Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.577 | 8760 | 100% | 0 | 5054.52
349 | 132kV Kharagprasad-Samal Metallic |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.03 | 8760 | 100% | 0 | 9022.8
350 | 132kV Kuchei PG- Bangiriposhi |  |  |  |  | 0.83819 | 19 | 1 | [7 empty] | 31.13 | 8760 | 99.78% | 591.9888 | 272698.8
|  | 2020-05-15 | 12:59 | 2020-05-15 | 13:41 | 0:42 | 0 | 42 | [5 empty] | At PGCIL End: E/F in B- Ph. Distance-5.47 km., Zone-1, General Trip, Ib-4.40KA.
|  | 2020-06-20 | 12:39 | 2020-06-20 | 13:54 | 1:15 | 1 | 15 | [5 empty] | At Baripada (PG) end:- DP, E/F, Z2, R-E, 17.33km, 1.02kA.
|  | 2020-06-23 | 8:51 | 2020-06-23 | 10:10 | 1:19 | 1 | 19 | [5 empty] | At Baripada (PG) end:- DP, E/F, Z2, R-E, 17.02km, 1.051kA.
|  | 2020-06-29 | 11:43 | 2020-06-29 | 15:17 | 3:34 | 0 | 41 | [5 empty] | At Baripada (PG) end: DP, Z1, Y-B Phase, 3.828km, Iy=5.74kA, Ib=5.442kA.
|  | 2020-07-05 | 09:25 | 2020-07-05 | 10:33 | 01:08 | 1 | 8 | [5 empty] | Relay Indication at PGCIL end General Trip, R-Phase to E/F.Distance -17.02 Km Fault current,Ir -1.460KA. Zone-2
|  | 2020-07-05 | 20:39 | 2020-07-05 | 22:03 | 01:24 | 1 | 4 | [5 empty] | Relay Indication at PGCIL end General Trip, R-Phase to E/F,Distance -35.90 Km Fault current,Ir -1.29KA. Zone-2
|  | 2020-09-25 | 21:06 | 2020-09-26 | 10:13 | 13:17 | 0 | 52 | [5 empty] | DP relay indication details:- Distance-,-5.9km, Fault loop L1-E, No fault current, CVT fuse fail indication. NO indication at Kuchei end. [R-ph jumper piece snapped at LOC. No.-104 ]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
351 | 132kV Bangiriposhi- Rairangapur |  |  |  |  | 1899-12-31 17:47 | 21 | 10 | [7 empty] | 34.2 | 8760 | 99.76% | 723.9 | 299592
|  | 2020-04-17 | 14:51 | 2020-04-17 | 14:58 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bangiriposi end
|  | 2020-05-15 | 12:59 | 2020-05-15 | 13:41 | 0:42 | 0 | 42 | [5 empty] | At PGCIL End: E/F in B- Ph. Distance-5.47 km., Zone-1, General Trip, Ib-4.40KA.
|  | 2020-05-23 | 10:36 | 2020-05-23 | 10:44 | 0:08 | 0 | 8 | [5 empty] | General Trip, O/C Y&B-Ph.Zone-1, Distance-2.4km,.IL1-0.19KA,IL2- 3.08KA,IL3-2.98KA.
|  | 2020-06-20 | 12:39 | 2020-06-20 | 13:54 | 1:15 | 1 | 15 | [5 empty] | At Baripada (PG) end:- DP, E/F, Z2, R-E, 17.33km, 1.02kA.
|  | 2020-06-23 | 8:51 | 2020-06-23 | 10:10 | 1:19 | 1 | 19 | [5 empty] | At Baripada (PG) end:- DP, E/F, Z2, R-E, 17.02km, 1.051kA.
|  | 2020-06-29 | 11:43 | 2020-06-29 | 15:17 | 3:34 | 0 | 41 | [5 empty] | At Baripada (PG) end: DP, Z1, Y-B Phase, 3.828km, Iy=5.74kA, Ib=5.442kA.
|  | 2020-07-05 | 09:25 | 2020-07-05 | 12:05 | 2:40 | 1 | 29 | [5 empty] | Failure From Source Bangriposi Grid
|  | 2020-07-05 | 20:39 | 2020-07-05 | 22:03 | 1:24 | 1 | 4 | [5 empty] | Relay Indication at PGCIL end General Trip, R-Phase to E/F,Distance -35.90 Km Fault current,Ir -1.29KA. Zone-2
|  | 2020-07-05 | 23:01 | 2020-07-05 | 23:11 | 0:10 | 0 | 10 | [5 empty] | At Bangriposi- R-Phase to E/F,Ir- 1.2 Kamp,Iy-0.27 Kamp, Ib- 0.36 Kamp
|  | 2020-07-05 | 23:55 | 2020-07-06 | 0:12 | 0:17 | 0 | 17 | [5 empty] | At Bangriposi- R-Phase toE/F,Ir- 1.23 Kamp,Iy-0.27 Kamp, Ib- 0.36 Kamp
|  | 2020-07-05 | 00:48 | 2020-07-06 | 16:54 | 16:06 | 0 | 18 | [5 empty] | At Bangriposi- R-Phase toE/F Ir- 1.4 Kamp,Iy-0.25 Kamp, Ib- 0.36 Kamp
|  | 2020-07-27 | 17:31 | 2020-07-27 | 17:59 | 0:28 | 0 | 28 | [5 empty] | General Trip ,R-Phase -Earth Fault, IR- 2.30 KAmp, IY-0.21 Kamp,IB- 0.34KAmp, Fault Distance- 5.1 Km
|  | 2020-08-25 | 15:58 | 2020-08-25 | 16:18 | 0:20 | 0 | 20 | [5 empty] | Zone-1, Fault loop L1-E, Distance- 5.3km, IL1-2.75KA, IL2-0.27KA, IL3- 0.42KA
|  | 2020-09-25 | 21:06 | 2020-09-26 | 10:13 | 13:17 | 0 | 52 | [5 empty] | DP relay indication details:- Distance-,-5.9km, Fault loop L1-E, No fault current, CVT fuse fail indication. NO indication at Kuchei end. [R-ph jumper piece snapped at LOC. No.-104 ]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
352 | 132kV Rairangapur- Karanjia |  |  |  |  | 0.8625 | 20 | 14 | [7 empty] | 70.74 | 8760 | 99.77% | 1431.306 | 619682.4
|  | 2020-04-17 | 14:51 | 2020-04-17 | 14:58 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bangiriposi end
|  | 2020-05-15 | 12:59 | 2020-05-15 | 13:41 | 0:42 | 0 | 42 | [5 empty] | At PGCIL End: E/F in B- Ph. Distance-5.47 km., Zone-1, General Trip, Ib-4.40KA.
|  | 2020-05-23 | 10:36 | 2020-05-23 | 10:44 | 0:08 | 0 | 8 | [5 empty] | General Trip, O/C Y&B-Ph.Zone-1, Distance-2.4km,.IL1-0.19KA,IL2- 3.08KA,IL3-2.98KA.
|  | 2020-06-20 | 12:39 | 2020-06-20 | 13:54 | 1:15 | 1 | 15 | [5 empty] | At Baripada (PG) end:- DP, E/F, Z2, R-E, 17.33km, 1.02kA.
|  | 2020-06-23 | 8:51 | 2020-06-23 | 10:10 | 1:19 | 1 | 19 | [5 empty] | At Baripada (PG) end:- DP, E/F, Z2, R-E, 17.02km, 1.051kA.
|  | 2020-06-29 | 11:43 | 2020-06-29 | 15:17 | 3:34 | 0 | 32 | [5 empty] | At Baripada (PG) end: DP, Z1, Y-B Phase, 3.828km, Iy=5.74kA, Ib=5.442kA.
|  | 2020-07-05 | 09:25 | 2020-07-05 | 12:05 | 02:40 | 1 | 8 | [5 empty] | Failure From Source Bangriposi Grid
|  | 2020-07-05 | 20:39 | 2020-07-05 | 22:03 | 01:24 | 1 | 9 | [5 empty] | Relay Indication at PGCIL end General Trip, R-Phase to E/F,Distance -35.90 Km Fault current,Ir -1.29KA. Zone-2
|  | 2020-07-05 | 23:01 | 2020-07-05 | 23:11 | 00:10 | 0 | 10 | [5 empty] | At Bangriposi- R-Phase to E/F,Ir- 1.2 Kamp,Iy-0.27 Kamp, Ib- 0.36 Kamp
|  | 2020-07-05 | 23:55 | 2020-07-06 | 0:12 | 00:17 | 0 | 17 | [5 empty] | At Bangriposi- R-Phase toE/F,Ir- 1.23 Kamp,Iy-0.27 Kamp, Ib- 0.36 Kamp
|  | 2020-07-05 | 00:48 | 2020-07-06 | 16:54 | 16:06 | 0 | 18 | [5 empty] | At Bangriposi- R-Phase toE/F Ir- 1.4 Kamp,Iy-0.25 Kamp, Ib- 0.36 Kamp
|  | 2020-08-25 | 15:58 | 2020-08-25 | 16:18 | 0:20 | 0 | 20 | [5 empty] | Zone-1, Fault loop L1-E, Distance- 5.3km, IL1-2.75KA, IL2-0.27KA, IL3- 0.42KA
|  | 2020-09-25 | 21:06 | 2020-09-26 | 10:13 | 13:17 | 0 | 49 | [5 empty] | DP relay indication details:- Distance-,-5.9km, Fault loop L1-E, No fault current, CVT fuse fail indication. NO indication at Kuchei end. [R-ph jumper piece snapped at LOC. No.-104 ]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
353 | 132kV Karanjia-Dhenkikote |  |  |  |  | 0.8625 | 17 | 17 | [7 empty] | 40.7 | 8760 | 99.8% | 703.4317 | 356532
|  | 2020-04-17 | 14:51 | 2020-04-17 | 14:58 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bangiriposi end
|  | 2020-05-15 | 12:59 | 2020-05-15 | 13:41 | 0:42 | 0 | 42 | [5 empty] | At PGCIL End: E/F in B- Ph. Distance-5.47 km., Zone-1, General Trip, Ib-4.40KA.
|  | 2020-05-23 | 10:36 | 2020-05-23 | 10:44 | 0:08 | 0 | 8 | [5 empty] | General Trip, O/C Y&B-Ph.Zone-1, Distance-2.4km,.IL1-0.19KA,IL2- 3.08KA,IL3-2.98KA.
|  | 2020-06-20 | 12:39 | 2020-06-20 | 13:54 | 1:15 | 1 | 15 | [5 empty] | At Baripada (PG) end:- DP, E/F, Z2, R-E, 17.33km, 1.02kA.
|  | 2020-06-23 | 8:51 | 2020-06-23 | 10:10 | 1:19 | 1 | 19 | [5 empty] | At Baripada (PG) end:- DP, E/F, Z2, R-E, 17.02km, 1.051kA.
|  | 2020-06-29 | 11:43 | 2020-06-29 | 15:17 | 3:34 | 0 | 38 | [5 empty] | At Baripada (PG) end: DP, Z1, Y-B Phase, 3.828km, Iy=5.74kA, Ib=5.442kA.
|  | 2020-08-25 | 15:58 | 2020-08-25 | 16:18 | 0:20 | 0 | 20 | [5 empty] | Zone-1, Fault loop L1-E, Distance- 5.3km, IL1-2.75KA, IL2-0.27KA, IL3- 0.42KA
|  | 2020-09-25 | 21:06 | 2020-09-26 | 10:13 | 13:17 | 0 | 48 | [5 empty] | DP relay indication details:- Distance-,-5.9km, Fault loop L1-E, No fault current, CVT fuse fail indication. NO indication at Kuchei end. [R-ph jumper piece snapped at LOC. No.-104 ]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
354 | 132kV Karanjia-Palasponga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 83.2 | 8760 | 100% | 0 | 728832
355 | 132kV Kuchinda-Rajgangpur |  |  |  |  | 0.083333 | 12 | 59 | [7 empty] | 107.4 | 8760 | 99.85% | 1394.41 | 940824
|  | 2020-05-30 | 0:08 | 2020-05-30 | 1:58 | 1:50 | 0 | 2 | [5 empty] | DP OPERATED BGT ZONE-1 LOC 21.58KM IB-3014A IG-2848A [BAD WEATHER HEAVY LIGHTENING], P/s restored from Lapanga end.
|  | 2020-05-31 | 20:56 | 2020-05-31 | 21:15 | 0:19 | 0 | 19 | [5 empty] | DP OPERATED BGT ZONE-1 LOC-21.04KM IB-2887A IG-2872A [BAD WEATHER HEAVY LIGHTENING]
|  | 2020-06-04 | 17:04 | 2020-06-04 | 17:14 | 0:10 | 0 | 10 | [5 empty] | AGT, IA=1663A, IG=1733A, Z1, 46.39km
|  | 2020-06-06 | 1:05 | 2020-06-06 | 1:12 | 0:07 | 0 | 7 | [5 empty] | BGT,IB=1150A,IG=976A, LOC= 82.76KM,ZONE-2
|  | 2020-07-22 | 19:39 | 2020-07-22 | 19:55 | 00:16 | 0 | 1 | [5 empty] | At Kuchinda end:- No tripping. At Rajgangpur end:- Fault in Zone1 , Fault type- ABGP, Location - 65.02km, Rph-1868A , Yph - 1849A , Bph- 112A , N- 1883A
|  | 2020-07-28 | 11:27 | 2020-07-28 | 11:32 | 00:05 | 0 | 5 | [5 empty] | At Kuchinda end:- No tripping. At Rajgangpur end:- Fault in Zone1 , Fault type- BGT, Location - 3.98km, Bph- 5465 A , N- 5366 A
|  | 2020-08-03 | 15:14 | 2020-08-03 | 15:24 | 00:10 | 0 | 10 | [5 empty] | DP , AGT,Z2,Ia-972A,Ig-822A ,LOC-96.18KM
|  | 2020-08-04 | 11:29 | 2020-08-04 | 11:40 | 00:11 | 0 | 5 | [5 empty] | Fault in Zone1 , Fault type- AGT Location - 4.21km, IA- 50.5KA, IB- 44.4KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
356 | 132kV Kuchinda-Rajgangpur 'T' to Bamra RTSS |  |  |  |  | 0.10972 | 15 | 25 | [7 empty] | 10 | 8760 | 99.82% | 154.1667 | 87600
|  | 2020-05-30 | 0:08 | 2020-05-30 | 1:58 | 1:50 | 1 | 50 | [5 empty] | DP OPERATED BGT ZONE-1 LOC 21.58KM IB-3014A IG-2848A [BAD WEATHER HEAVY LIGHTENING]
|  | 2020-05-31 | 20:56 | 2020-05-31 | 21:15 | 0:19 | 0 | 19 | [5 empty] | DP OPERATED BGT ZONE-1 LOC-21.04KM IB-2887A IG-2872A [BAD WEATHER HEAVY LIGHTENING]
|  | 2020-06-04 | 17:04 | 2020-06-04 | 17:14 | 0:10 | 0 | 10 | [5 empty] | AGT, IA=1663A, IG=1733A, Z1, 46.39km
|  | 2020-06-06 | 1:05 | 2020-06-06 | 1:12 | 0:07 | 0 | 7 | [5 empty] | BGT,IB=1150A,IG=976A, LOC= 82.76KM,ZONE-2
|  | 2020-07-22 | 19:39 | 2020-07-22 | 19:55 | 00:16 | 0 | 1 | [5 empty] | At Kuchinda end:- No tripping. At Rajgangpur end:- Fault in Zone1 , Fault type- ABGP, Location - 65.02km, Rph-1868A , Yph - 1849A , Bph- 112A , N- 1883A
|  | 2020-07-28 | 11:27 | 2020-07-28 | 11:32 | 00:05 | 0 | 5 | [5 empty] | At Kuchinda end:- No tripping. At Rajgangpur end:- Fault in Zone1 , Fault type- BGT, Location - 3.98km, Bph- 5465 A , N- 5366 A
|  | 2020-08-03 | 15:14 | 2020-08-03 | 15:24 | 00:10 | 0 | 10 | [5 empty] | DP , AGT,Z2,Ia-972A,Ig-822A ,LOC-96.18KM
|  | 2020-08-04 | 11:29 | 2020-08-04 | 11:40 | 00:11 | 0 | 5 | [5 empty] | Fault in Zone1 , Fault type- AGT Location - 4.21km, IA- 50.5KA, IB- 44.4KA
|  | 2021-01-09 | 17:50 | 2021-01-09 | 18:05 | 0:15 | 0 | 15 | [5 empty] | Trip at Karanjia end.
|  | 2021-01-09 | 23:26 | 2021-01-09 | 23:38 | 0:12 | 0 | 12 | [5 empty] | Trip at Karanjia end.
|  | 2021-01-10 | 02:08 | 2021-01-10 | 02:19 | 0:11 | 0 | 11 | [5 empty] | Source Failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
357 | 132kV Lapanga - Rengali RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.31 | 8760 | 100% | 0 | 107835.6
358 | 132kV Machkund PH-Jaynagar |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 42.6 | 8760 | 100% | 0 | 373176
359 | 132kV Machkund PH- Machkund (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 107 | 8760 | 100% | 0 | 937320
360 | 132kV Mendhasal-Chandpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.6 | 8760 | 100% | 0 | 303096
361 | 132kV Mendhasal-Khurda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17.6 | 8760 | 100% | 0 | 154176
362 | 132kV Meramundali-BRG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.55 | 8760 | 100% | 0 | 31098
363 | 132kV Meramundali-Chainpal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.728 | 8760 | 100% | 0 | 15137.28
364 | 132kV Meramundali-Chainpal Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.728 | 8760 | 100% | 0 | 15137.28
365 | 132kV Meramundali-Dhenkanal |  |  |  |  | 0.975 | 13 | 29 | [7 empty] | 51.12 | 8760 | 99.85% | 689.268 | 447811.2
|  | 2020-05-23 | 20:44 | 2020-05-23 | 20:53 | 0:09 | 0 | 9
|  | 2020-08-10 | 13:32 | 2020-08-10 | 14:37 | 1:05 | 0 | 25 | [5 empty] | No tripping of CB but 1. DP Relay actuated, with indication : IR=312A, IY=142A, IB=1.427kA, No indication of Fault Loop, distance and Zone 2. B/U relay operated in E/F
|  | 2020-08-19 | 18:40 | 2020-08-20 | 7:54 | 13:15 | 0 | 31 | [5 empty] | No tripping of CB but DP Relay actuated, with indication : IY=1.42kA, Fault Loop=Y_G, distance=32.25kM and Zone-2
|  | 2021-01-25 | 05:51 | 2021-01-25 | 14:46 | 8:55 | 0 | 24 | [5 empty] | At DKL Grid End:Zone-II, Distance:32KM, Fault Loop:Y to N, Iy=1.46KAmp At MRDL Grid End:Zone-I, Distance:6.7KM, Fault Loop:Y to N, Iy=8KAmp, Insulator Puncture at Loc
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
366 | 132kV Meramundali-Kharagprasad Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.517 | 8760 | 100% | 0 | 48328.92
367 | 132kV Meramundali-Kharagprasad Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.517 | 8760 | 100% | 0 | 48328.92
368 | 132kV Meramundali-M.L. Rungta |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.468 | 8760 | 100% | 0 | 65419.68
369 | 132kV Meramundali-Khajuriakata |  |  |  |  | 0.0076389 | 12 | 34 | [7 empty] | 33.5 | 8760 | 99.86% | 420.9833 | 293460
|  | 2020-05-23 | 20:44 | 2020-05-23 | 20:55 | 0:11 | 0 | 11 | [5 empty] | Tripped from MRDL End
|  | 2020-07-03 | 11:04 | 2020-07-03 | 11:13 | 00:09 | 0 | 9 | [5 empty] | Tripped from MRDL End in Zone-III
|  | 2020-07-26 | 12:26 | 2020-07-26 | 12:54 | 00:28 | 0 | 14 | [5 empty] | Tripped from MRDL End
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
370 | 132KV Dhenkanal-Nuapatna-Khajuriakata "T" feeder |  |  |  |  | 0.43819 | 13 | 21 | [7 empty] | 2.4 | 8760 | 99.85% | 32.04 | 21024
|  | 2020-05-23 | 20:44 | 2020-05-23 | 6:44 | 10:00 | 0 | 9 | [5 empty] | DP relay:L1-N, I1=1.12kA, 43.86KM
|  | 2020-06-01 | 14:01 | 2020-06-01 | 14:16 | 0:15 | 0 | 7 | [5 empty] | Tripped in Back-Up Relay (E/F)
|  | 2020-07-03 | 11:03 | 2020-07-03 | 14:53 | 03:50 | 0 | 9 | [5 empty] | DP Relay:1.76KA,24.8KM,L3N, ZONE1
|  | 2020-08-13 | 16:40 | 2020-08-13 | 17:00 | 00:20 | 0 | 10 | [5 empty] | B phase O/C,E/F, Distance - 97.76km,zone3
|  | 2020-08-19 | 18:41 | 2020-08-19 | 19:11 | 00:30 | 0 | 30 | [5 empty] | R phase O/C and E/F, Distance - 75.55km,zone3 At K.Kata end: Y-G Fault, Ir= 0.28 KA, Iy=0.96 KA, Ib= 0.26 KA
|  | 2021-01-25 | 05:51 | 2021-01-25 | 06:07 | 0:16 | 0 | 16 | [5 empty] | E/F,At Nuapatna:- R-Ph O/C, Zone-II, Dist- 76.59 Kms, If= 1.2KA , At DKL End:- No Tripping
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
371 | 132kV Khajuriakata-Nuapatna |  |  |  |  | 0.41528 | 12 | 44 | [7 empty] | 83.99 | 8760 | 99.85% | 1069.4727 | 735752.4
|  | 2020-05-23 | 20:44 | 2020-05-24 | 6:42 | 9:58 | 0 | 11 | [5 empty] | R-G Fault, Zone-I, Dist- 14.3Kms, If=503A
|  | 2020-07-03 | 11:04 | 2020-07-03 | 12:22 | 01:18 | 0 | 9 | [5 empty] | B-G Fault, Zone-I, Dist- 14.6 Kms, If=2.07KA
|  | 2020-07-26 | 12:26 | 2020-07-26 | 12:40 | 00:14 | 0 | 14 | [5 empty] | Tripped in O/C
|  | 2020-08-13 | 16:40 | 2020-08-13 | 17:00 | 00:20 | 0 | 10 | [5 empty] | B phase O/C,E/F, Distance - 97.76km,zone3
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
372 | 132kV Nuapatna-Arati Steel |  |  |  |  | 0.2375 | 12 | 26 | [7 empty] | 66.9 | 8760 | 99.86% | 831.79 | 586044
|  | 2020-05-14 | 8:20 | 2020-05-14 | 13:22 | 5:02 | 0 | 4 | [5 empty] | E/F(Non closing of its own breaker)
|  | 2020-06-01 | 14:18 | 2020-06-01 | 14:33 | 0:15 | 0 | 15 | [5 empty] | Y phase O/C and E/F
|  | 2020-06-08 | 14:53 | 2020-06-08 | 15:18 | 0:25 | 0 | 7 | [5 empty] | E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
373 | 132kV Mohana-Digapahandi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.48 | 8760 | 100% | 0 | 258244.8
374 | 132kV Muniguda-Bissamcuttack RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.85 | 8760 | 100% | 0 | 121326
375 | 132kV Narendrapur-Berhampur Ckt -I |  |  |  |  | 0.0027778 | 0 | 4 | [7 empty] | 11.31 | 8760 | 100% | 0.754 | 99075.6
|  | 2020-08-20 | 12:06 | 2020-08-20 | 12:10 | 0:04 | 0 | 4 | [5 empty] | No tripping at Berhampur End. Auto failed at Narendrapur End.Power supply failure from Narendrapur.
376 | 132kV Narendrapur-Berhampur Ckt - II |  |  |  |  | 0.0027778 | 0 | 4 | [7 empty] | 11.31 | 8760 | 100% | 0.754 | 99075.6
|  | 2020-08-20 | 12:06 | 2020-08-20 | 12:10 | 0:04 | 0 | 4 | [5 empty] | No tripping at Berhampur End. Auto failed at Narendrapur End.Power supply failure from Narendrapur.
377 | 132kV Narendrapur-Chatrapur-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.28 | 8760 | 100% | 0 | 116332.8
378 | 132kV Narendrapur-Chatrapur-II |  |  |  |  | 0.16319 | 0 | 10 | [7 empty] | 13.28 | 8760 | 100% | 2.2133 | 116332.8
|  | 2020-12-10 | 07:38 | 2020-12-10 | 11:33 | 3:55 | 0 | 10 | [5 empty] | Tripped on DP relay at both end At Narendrapur end :- Zone-1, 10.31KM, R-ph to Earth, IL1- 3985A,IL2-279A, IL3-476A. At Chatrapur end:- Zone-1, R-ph to Earth,Dist-0.0Km,IL1-440.9A, IL2- 289.0A, IL3-481.2A. Jumper snap at loc.1 at Chatrapur end.
379 | 132kV Narendrapur-Narendrapur(T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.51 | 8760 | 100% | 0 | 4467.6
380 | 132kV NBVL-Hind Metals |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1 | 8760 | 100% | 0 | 8760
381 | 132kV Nimapara-Konark |  |  |  |  | 0.16528 | 14 | 5 | [7 empty] | 19.91 | 8760 | 99.84% | 280.3992 | 174411.6
|  | 2020-06-15 | 0:30 | 2020-06-15 | 1:00 | 0:30 | 0 | 30 | [5 empty] | DP Relay Z-1, Distance 93.02 KM, Ib- 1.97 KA Bph-E
|  | 2020-06-29 | 13:21 | 2020-06-29 | 13:26 | 0:05 | 0 | 5 | [5 empty] | DP Relay Z-1, Distance 12.53KM, Ib- 4.077 KA C-N at Chandaka end.
|  | 2020-06-30 | 9:03 | 2020-06-30 | 9:21 | 0:18 | 0 | 18 | [5 empty] | DP Relay Z-2, Distance 105.97KM, B-G-T at Nimapara end.
|  | 2020-11-17 | 12:48 | 2020-11-17 | 15:47 | 2:59 | 1 | 6 | [5 empty] | DP realy from Chandaka end 48.5KM, Ia-1.35KA
|  | 2020-11-18 | 12:15 | 2020-11-18 | 12:21 | 0:06 | 0 | 6 | [5 empty] | DP realy from Chandaka end Z-1, Distance-30.KM, Ia-2.7KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
382 | 132kV Nimapara-Puri Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.6 | 8760 | 100% | 0 | 259296
383 | 132kV Nimapara-Samagara |  |  |  |  | 0.073611 | 13 | 50 | [7 empty] | 27.6 | 8760 | 99.84% | 381.8 | 241776
|  | 2020-07-04 | 07:21 | 2020-07-04 | 07:25 | 00:04 | 0 | 4 | [5 empty] | E/F, Ia=0.267kA, Ib=0.271kA,Ic,=0.180kA,Ig=0.131k A at Shamuka end.
|  | 2020-07-04 | 08:04 | 2020-07-04 | 08:10 | 0:06 | 0 | 6 | [5 empty] | E/F, Ia=0.255kA, Ib=0.259kA, Ic,=0.173kA,Ig=0.125kA, at Shamuka end.
|  | 2020-07-03 | 12:10 | 2020-07-03 | 12:17 | 0:07 | 0 | 7 | [5 empty] | Source Failure
|  | 2020-07-04 | 11:25 | 2020-07-04 | 11:34 | 0:09 | 0 | 9 | [5 empty] | Source Failure
|  | 2020-07-15 | 13:05 | 2020-07-15 | 18:29 | 0:53 | 0 | 53 | [5 empty] | DP operate, Cphase-G, Distance= - 5.2 km,Zone- Z1,Ia=363.036A,Ib=704.279A, Ic=470.334A, In=14499.373A at Shamuka end.
|  | 2020-07-27 | 17:07 | 2020-07-27 | 17:38 | 0:31 | 0 | 31 | [5 empty] | Tripped at Shamuka end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
384 | 132kV ICCL- Mania |  |  |  |  | 1899-12-31 03:31 | 13 | 31 | [7 empty] | 18.32 | 8760 | 99.85% | 247.6253 | 160483.2
|  | 2020-05-11 | 5:33 | 2020-05-11 | 5:44 | 0:11 | 0 | 11 | [5 empty] | R PHASE GROUNDED
|  | 2020-05-29 | 3:55 | 2020-05-29 | 4:33 | 0:42 | 0 | 38 | [5 empty] | Y-B LINE FAULT, R PHASE GROUNDED
|  | 2020-05-30 | 3:25 | 2020-05-30 | 3:53 | 0:28 | 0 | 28 | [5 empty] | R PHASE GROUNDED
|  | 2020-06-05 | 14:02 | 2020-06-05 | 14:10 | 0:08 | 0 | 8 | [5 empty] | Tripped at ICCL end.
|  | 2020-06-08 | 14:58 | 2020-06-08 | 15:15 | 0:17 | 0 | 17 | [5 empty] | Tripped at ICCL end.
|  | 2020-06-12 | 18:31 | 2020-06-12 | 18:36 | 0:05 | 0 | 5 | [5 empty] | Tripped at ICCL end.
|  | 2020-06-12 | 18:40 | 2020-06-12 | 18:57 | 0:17 | 0 | 17 | [5 empty] | Tripped at ICCL end.
|  | 2020-07-04 | 15:14 | 2020-07-04 | 16:18 | 01:04 | 1 | 4 | [5 empty] | B PHASE GROUNDED
|  | 2020-07-08 | 16:42 | 2020-07-08 | 16:42 | 00:05 | 0 | 5 | [5 empty] | Tripped at mania end.
|  | 2020-07-25 | 01:33 | 2020-07-25 | 01:40 | 00:07 | 0 | 7 | [5 empty] | INCOMER FAIL
|  | 2020-08-04 | 14:22 | 2020-08-04 | 14:27 | 0:05 | 0 | 5 | [5 empty] | R PHASE GROUNDED
|  | 2020-08-14 | 12:44 | 2020-08-14 | 13:04 | 0:20 | 0 | 20 | [5 empty] | INCOMER FAIL
|  | 2020-08-22 | 16:21 | 2020-08-23 | 16:14 | 23:53 | 0 | 41 | [5 empty] | RY LINE FAULT
|  | 2020-08-31 | 12:16 | 2020-08-31 | 12:40 | 0:24 | 0 | 24 | [5 empty] | INCOMER FAIL
|  | 2021-01-12 | 00:53 | 2021-01-12 | 01:30 | 0:37 | 0 | 37 | [5 empty] | E/F
|  | 2021-01-16 | 07:15 | 2021-01-16 | 07:19 | 0:04 | 0 | 4 | [5 empty] | E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
385 | 132kV Mania- OCL |  |  |  |  | 1899-12-31 02:35 | 13 | 39 | [7 empty] | 4.063 | 8760 | 99.84% | 55.4599 | 35591.88
|  | 2020-05-11 | 5:33 | 2020-05-11 | 5:44 | 0:11 | 0 | 11 | [5 empty] | R PHASE GROUNDED
|  | 2020-06-05 | 14:02 | 2020-06-05 | 14:10 | 0:08 | 0 | 8 | [5 empty] | Tripped at ICCL end.
|  | 2020-06-08 | 14:58 | 2020-06-08 | 15:15 | 0:17 | 0 | 17 | [5 empty] | Tripped at ICCL end.
|  | 2020-06-12 | 18:31 | 2020-06-12 | 18:36 | 0:05 | 0 | 5 | [5 empty] | Tripped at ICCL end.
|  | 2020-06-12 | 18:40 | 2020-06-12 | 18:57 | 0:17 | 0 | 17 | [5 empty] | Tripped at ICCL end.
|  | 2020-07-04 | 15:14 | 2020-07-04 | 16:18 | 01:04 | 1 | 4 | [5 empty] | B PHASE GROUNDED
|  | 2020-07-08 | 16:42 | 2020-07-08 | 16:42 | 00:05 | 0 | 5 | [5 empty] | Tripped at mania end.
|  | 2020-07-25 | 01:33 | 2020-07-25 | 01:40 | 00:07 | 0 | 7 | [5 empty] | INCOMER FAIL
|  | 2020-08-04 | 14:22 | 2020-08-04 | 14:41 | 0:19 | 0 | 19 | [5 empty] | R PHASE GROUNDED
|  | 2020-08-14 | 12:44 | 2020-08-14 | 13:04 | 0:20 | 0 | 20 | [5 empty] | INCOMER FAIL
|  | 2020-08-22 | 16:21 | 2020-08-23 | 16:14 | 23:53 | 0 | 41 | [5 empty] | RY LINE FAULT
|  | 2020-08-31 | 12:16 | 2020-08-31 | 12:40 | 0:24 | 0 | 24 | [5 empty] | INCOMER FAIL
|  | 2021-01-12 | 00:53 | 2021-01-12 | 01:30 | 0:37 | 0 | 37 | [5 empty] | E/F
|  | 2021-01-16 | 07:15 | 2021-01-16 | 07:19 | 0:04 | 0 | 4 | [5 empty] | E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
386 | 132kV OCL-Salipur |  |  |  |  | 1899-12-31 02:24 | 12 | 47 | [7 empty] | 38.41 | 8760 | 99.85% | 491.0078 | 336471.6
|  | 2020-06-05 | 14:02 | 2020-06-05 | 14:10 | 0:08 | 0 | 8 | [5 empty] | Tripped at ICCL end.
|  | 2020-06-08 | 14:58 | 2020-06-08 | 15:15 | 0:17 | 0 | 17 | [5 empty] | Tripped at ICCL end.
|  | 2020-06-12 | 18:31 | 2020-06-12 | 18:36 | 0:05 | 0 | 5 | [5 empty] | Tripped at ICCL end.
|  | 2020-06-12 | 18:40 | 2020-06-12 | 18:57 | 0:17 | 0 | 17 | [5 empty] | Tripped at ICCL end.
|  | 2020-07-04 | 15:14 | 2020-07-04 | 16:18 | 01:04 | 0 | 38 | [5 empty] | B PHASE GROUNDED
|  | 2020-07-08 | 16:42 | 2020-07-08 | 16:42 | 00:05 | 0 | 5 | [5 empty] | Tripped at mania end.
|  | 2020-07-25 | 01:33 | 2020-07-25 | 01:40 | 00:07 | 0 | 7 | [5 empty] | INCOMER FAIL
|  | 2020-08-04 | 14:22 | 2020-08-04 | 14:41 | 0:19 | 0 | 19 | [5 empty] | R PHASE GROUNDED
|  | 2020-08-14 | 12:44 | 2020-08-14 | 13:04 | 0:20 | 0 | 20 | [5 empty] | INCOMER FAIL
|  | 2020-08-22 | 16:21 | 2020-08-23 | 16:14 | 23:53 | 0 | 41 | [5 empty] | RY LINE FAULT
|  | 2020-08-31 | 12:16 | 2020-08-31 | 12:40 | 0:24 | 0 | 24 | [5 empty] | INCOMER FAIL
|  | 2020-09-17 | 06:01 | 2020-09-17 | 13:47 | 07:46 | 0 | 45 | [5 empty] | Insulaors snapped at Loc.no.74(Y- phase)
|  | 2021-01-12 | 00:53 | 2021-01-12 | 01:30 | 0:37 | 0 | 37 | [5 empty] | E/F
|  | 2021-01-16 | 07:15 | 2021-01-16 | 07:19 | 0:04 | 0 | 4 | [5 empty] | E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
387 | 132kV Paradeep-Tirtol |  |  |  |  | 1899-12-31 10:01 | 13 | 14 | [7 empty] | 38.43 | 8760 | 99.85% | 508.557 | 336646.8
|  | 2020-05-01 | 13:20 | 2020-05-01 | 14:46 | 1:26 | 0 | 4 | [5 empty] | At Paradeep-Tripped, P/S restored from Cuttack end.
|  | 2020-05-01 | 15:16 | 2020-05-01 | 18:48 | 3:32 | 0 | 1 | [5 empty] | At Paradeep-Tripped, P/S restored from Cuttack end.
|  | 2020-05-06 | 6:07 | 2020-05-06 | 6:38 | 0:31 | 0 | 1 | [5 empty] | At Paradeep-Tripped, P/S restored from Cuttack end.
|  | 2020-05-09 | 0:37 | 2020-05-09 | 0:46 | 0:09 | 0 | 9 | [5 empty] | At Paradeep-Tripped,P/S restored from Cuttack end.
|  | 2020-05-24 | 14:47 | 2020-05-25 | 13:17 | 22:30 | 0 | 6 | [5 empty] | I/C power supplly failed from Paradeep end,P/S restored from Cuttack end.
|  | 2020-05-30 | 4:16 | 2020-05-30 | 4:55 | 0:39 | 0 | 1 | [5 empty] | I/C power supplly failed from Paradeep end with distance 2.1KM from Paradeep end,P/S restored from Cuttack end.
|  | 2020-06-28 | 15:06 | 2020-06-28 | 15:10 | 0:04 | 0 | 4 | [5 empty] | C-G, E/F, 1.9km at paradeep end.
|  | 2020-08-04 | 16:13 | 2020-08-04 | 18:51 | 2:38 | 0 | 12 | [5 empty] | ZONE-Z1 PHASE C TO N
|  | 2020-08-18 | 19:56 | 2020-08-18 | 20:03 | 0:07 | 0 | 7 | [5 empty] | E/F & O/C
|  | 2020-09-02 | 11:50 | 2020-09-02 | 12:05 | 0:15 | 0 | 15 | [5 empty] | E/F
|  | 2020-09-09 | 15:43 | 2020-09-09 | 17:53 | 2:10 | 0 | 14 | [5 empty] | At Paradeep-tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
388 | 132kV Tirtol- Jagatsinghpur |  |  |  |  | 0.54306 | 13 | 54 | [7 empty] | 29.26 | 8760 | 99.84% | 406.714 | 256317.6
|  | 2020-05-01 | 13:20 | 2020-05-01 | 14:46 | 1:26 | 0 | 4 | [5 empty] | At Paradeep-Tripped, P/S restored from Cuttack end.
|  | 2020-05-01 | 15:16 | 2020-05-01 | 18:48 | 3:32 | 0 | 1 | [5 empty] | At Paradeep-Tripped, P/S restored from Cuttack end.
|  | 2020-05-06 | 6:07 | 2020-05-06 | 6:38 | 0:31 | 0 | 1 | [5 empty] | At Paradeep-Tripped, P/S restored from Cuttack end.
|  | 2020-05-09 | 0:37 | 2020-05-09 | 0:46 | 0:09 | 0 | 9 | [5 empty] | At Paradeep-Tripped,P/S restored from Cuttack end.
|  | 2020-05-24 | 14:47 | 2020-05-25 | 13:17 | 22:30 | 0 | 6 | [5 empty] | I/C power supplly failed from Paradeep end,P/S restored from Cuttack end.
|  | 2020-05-30 | 4:16 | 2020-05-30 | 4:55 | 0:39 | 0 | 1 | [5 empty] | I/C power supplly failed from Paradeep end with distance 2.1KM from Paradeep end,P/S restored from Cuttack end.
|  | 2020-06-28 | 15:06 | 2020-06-28 | 15:10 | 0:04 | 0 | 4 | [5 empty] | C-G, E/F, 1.9km at paradeep end.
|  | 2020-07-26 | 13:50 | 2020-07-26 | 13:57 | 00:07 | 0 | 7 | [5 empty] | O/C at Tirtol end.
|  | 2020-08-04 | 16:13 | 2020-08-04 | 18:52 | 2:39 | 0 | 1 | [5 empty] | Incoming power suply to tirtol grid substation failed.
|  | 2020-08-18 | 19:57 | 2020-08-18 | 20:06 | 0:06 | 0 | 2 | [5 empty] | Tripped with relay indication o/c & E/f at tirtol end ,No relay indication at jagatsinghpur end.
|  | 2020-09-01 | 09:57 | 2020-09-01 | 11:16 | 1:19 | 0 | 2 | [5 empty] | Incoming power suply to tirtol grid substation failed from Paradeep due to burst of station transformer at Tirtol.
|  | 2020-09-02 | 11:50 | 2020-09-02 | 12:29 | 0:39 | 0 | 15 | [5 empty] | O/C(Y-Ph.),ZONE -1,IB-2.087 KA, DIST-12.08 KM
|  | 2020-09-02 | 12:29 | 2020-09-02 | 17:53 | 5:24 | 0 | 15 | [5 empty] | O/C(R-Ph.),ZONE -1,IA-2.341 KA, IB-2.343 KA
|  | 2020-09-09 | 15:43 | 2020-09-09 | 17:53 | 2:09 | 0 | 5 | [5 empty] | Incoming power suply failled from tirtol grid substation without any relay indication JSPUR end.
|  | 2020-11-20 | 05:40 | 2020-11-20 | 05:46 | 0:06 | 0 | 6 | [5 empty] | Tripped with relay Indication Y-Ph O/C at Tirtol End. No relay Indication at Jagatsinghpur End.
|  | 2020-12-20 | 07:35 | 2020-12-20 | 07:41 | 0:06 | 0 | 5 | [5 empty] | O/C(R-ph,Y-ph),E/F, IL1- 562.5A,IL2-477.5A
|  | 2021-03-27 | 18:17 | 2021-03-27 | 18:47 | 0:30 | 0 | 30 | [5 empty] | Tripped due to o/c in Y-ph,E/F. Dist.- 31.72 km.,Zone-2 Iy=2.710kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
389 | 132kVJagatsinghpur-Gorakhnath (T) |  |  |  |  | 1899-12-31 22:46 | 19 | 12 | [7 empty] | 16.53 | 8760 | 99.78% | 317.376 | 144802.8
|  | 2020-05-20 | 6:19 | 2020-05-20 | 06:42 | 0:23 | 0 | 23 | [5 empty] | Tripped on O/C in R-Y-B ph,E/F. IL1=0.01KA,IL2=2.36KA,IL3=0.01 KA
|  | 2020-05-20 | 8:35 | 2020-05-20 | 13:07 | 4:32 | 4 | 32 | [5 empty] | Tripped on O/C in R-Y-B ph,E/F. IL1=0.01KA,IL2=2.34KA,IL3=0.01 KA
|  | 2020-05-01 | 13:20 | 2020-05-01 | 14:46 | 1:26 | 0 | 4 | [5 empty] | At Paradeep-Tripped, P/S restored from Cuttack end.
|  | 2020-05-01 | 15:16 | 2020-05-01 | 18:48 | 3:32 | 0 | 1 | [5 empty] | At Paradeep-Tripped, P/S restored from Cuttack end.
|  | 2020-05-06 | 6:07 | 2020-05-06 | 6:38 | 0:31 | 0 | 1 | [5 empty] | At Paradeep-Tripped, P/S restored from Cuttack end.
|  | 2020-05-09 | 0:37 | 2020-05-09 | 0:46 | 0:09 | 0 | 9 | [5 empty] | At Paradeep-Tripped,P/S restored from Cuttack end.
|  | 2020-05-24 | 14:47 | 2020-05-25 | 13:17 | 22:30 | 0 | 6 | [5 empty] | I/C power supplly failed from Paradeep end,P/S restored from Cuttack end.
|  | 2020-05-30 | 4:16 | 2020-05-30 | 4:55 | 0:39 | 0 | 1 | [5 empty] | I/C power supplly failed from Paradeep end with distance 2.1KM from Paradeep end,P/S restored from Cuttack end.
|  | 2020-06-05 | 5:45 | 2020-06-05 | 9:50 | 5:17 | 0 | 5 | [5 empty] | Bidanasi End : Main-1 - B-pahae to Ground, Distance-11.17km, Z1 , Ib- 5.4kAmp. [Jumper snapped at Loc. No-69. ]
|  | 2020-06-28 | 15:06 | 2020-06-28 | 15:10 | 0:04 | 0 | 4 | [5 empty] | C-G, E/F, 1.9km at paradeep end.
|  | 2020-07-26 | 13:50 | 2020-07-26 | 13:57 | 00:07 | 0 | 7 | [5 empty] | O/C
|  | 2020-08-04 | 16:13 | 2020-08-04 | 18:52 | 2:39 | 0 | 1 | [5 empty] | Incoming power suply to tirtol grid substation failed.
|  | 2020-08-18 | 19:57 | 2020-08-18 | 20:06 | 0:06 | 0 | 2 | [5 empty] | Tripped with relay indication o/c & E/f at tirtol end ,No relay indication at jagatsinghpur end.
|  | 2020-09-01 | 09:57 | 2020-09-01 | 11:16 | 1:19 | 0 | 2 | [5 empty] | Incoming power suply to tirtol grid substation failed from Paradeep due to burst of station transformer at Tirtol.
|  | 2020-09-09 | 15:43 | 2020-09-09 | 17:53 | 2:09 | 0 | 5 | [5 empty] | Incoming power suply failled from tirtol grid substation without any relay indication JSPUR end.
|  | 2020-11-20 | 05:40 | 2020-11-20 | 05:46 | 0:06 | 0 | 6 | [5 empty] | Tripped with relay Indication Y-Ph O/C at Tirtol End. No relay Indication at Jagatsinghpur End.
|  | 2020-12-20 | 07:35 | 2020-12-20 | 07:41 | 0:06 | 0 | 5 | [5 empty] | O/C(R-ph,Y-ph),E/F, IL1- 562.5A,IL2-477.5A
|  | 2021-01-19 | 18:12 | 2021-01-19 | 19:00 | 0:48 | 0 | 48 | [5 empty] | Trip due to puncture Y-ph 33 kv Main bus Insulator & B-ph Station transformer PI (All power transformers were also pulled out)
|  | 2021-03-27 | 18:17 | 2021-03-27 | 18:47 | 0:30 | 0 | 30 | [5 empty] | Tripped due to o/c in Y-ph,E/F. Dist.- 31.72 km.,Zone-2 Iy=2.710kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
390 | 132kV Paradeep- IFFCO - I |  |  |  |  | 0.26042 | 5 | 10 | [7 empty] | 7.171 | 8760 | 99.94% | 37.0502 | 62817.96
|  | 2021-01-10 | 03:30 | 2021-01-10 | 09:45 | 6:15 | 5 | 10 | [5 empty] | O/C R-ph
391 | 132kV Paradeep- IFFCO - II |  |  |  |  | 0.21528 | 5 | 10 | [7 empty] | 7.171 | 8760 | 99.94% | 37.0502 | 62817.96
|  | 2021-01-10 | 03:30 | 2021-01-10 | 09:52 | 5:10 | 5 | 10 | [5 empty] | O/C R-ph
392 | 132kV Paradeep-PPL-I |  |  |  |  | 0.33958 | 2 | 51 | [7 empty] | 6.2 | 8760 | 99.97% | 17.67 | 54312
|  | 2020-12-30 | 03:30 | 2020-12-30 | 11:39 | 8:09 | 2 | 51 | [5 empty] | Tripped on O/C,R-ph
393 | 132kV Paradeep-PPL-II |  |  |  |  | 0.11875 | 2 | 51 | [7 empty] | 6.2 | 8760 | 99.97% | 17.67 | 54312
|  | 2020-12-30 | 03:30 | 2020-12-30 | 09:24 | 2:51 | 2 | 51 | [5 empty] | Tripped on O/C,R-ph
394 | 132kV Paradeep-PPT-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.65 | 8760 | 100% | 0 | 67014
395 | 132kV Paradeep-PPT-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.65 | 8760 | 100% | 0 | 67014
396 | 132kV Patnagarh-Padampur |  |  |  |  | 0.0069444 | 0 | 36 | [7 empty] | 44.24 | 8760 | 99.99% | 26.544 | 387542.4
|  | 2020-05-30 | 7:38 | 2020-05-30 | 7:48 | 0:10 | 0 | 10 | [5 empty] | Tripped on back up o/c and e/f.
|  | 2020-05-22 | 14:30 | 2020-05-22 | 14:56 | 0:26 | 0 | 26 | [5 empty] | 132KV POWER SUPPLY FAILED FROM 132/33KV PATNAGARH END DUE TO DISTANCE PROTECTION OPERATED.
397 | 132kV Padampur-Padampur Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.5 | 8760 | 100% | 0 | 91980
398 | 132 kV Purusottampur-Chatrapur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.45 | 8760 | 100% | 0 | 135342
399 | 132kV Rairakhole- Rairakhole RTSS |  |  |  |  | 0.13681 | 13 | 39 | [7 empty] | 3.5 | 8760 | 99.84% | 47.775 | 30660
|  | 2020-06-03 | 17:41 | 2020-06-03 | 17:55 | 0:14 | 0 | 14 | [5 empty] | O/C on R-phase, DP, 2426.2 A, 33.665 km, L1-N
|  | 2020-06-27 | 8:50 | 2020-06-27 | 9:01 | 0:11 | 0 | 11 | [5 empty] | Tripped at Boinda end.
|  | 2020-07-10 | 01:45 | 2020-07-10 | 01:55 | 0:10 | 0 | 10 | [5 empty] | Tripped at Boinda
|  | 2020-08-18 | 09:28 | 2020-08-18 | 09:36 | 0:08 | 0 | 8 | [5 empty] | Tripped [DUE TO CIRCUIT BREAKER PROBLEM AT BOINDA]
|  | 2020-08-20 | 07:38 | 2020-08-20 | 07:40 | 0:02 | 0 | 2 | [5 empty] | TRIPPED ON B/U RELAY INDICATING B-PHASE O/C & E/F AT RAIRAKHOL GRID END. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY]
|  | 2020-08-19 | 23:31 | 2020-08-19 | 23:36 | 0:05 | 0 | 5 | [5 empty] | Tripped at Angul end. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY AT RAIRAKHOL GRID END.]
|  | 2020-08-20 | 07:42 | 2020-08-20 | 07:49 | 0:07 | 0 | 7 | [5 empty] | O/C in Y-Phase, Fault Current(Y- PH)-1.06 KA and E/F.
|  | 2020-08-20 | 07:27 | 2020-08-20 | 07:40 | 0:13 | 0 | 6 | [5 empty] | Tripped at Angul end. [TRF-I & II TRIPPED ON 51N-E/F RELAY AND TRF-III TRIPPED ON LBB RELAY AT RAIRAKHOL GRID END.]
|  | 2020-08-25 | 14:25 | 2020-08-25 | 14:33 | 0:08 | 0 | 3 | [5 empty] | TRIPPED AT ANGUL END
|  | 2020-09-04 | 16:34 | 2020-09-04 | 16:41 | 0:07 | 0 | 7 | [5 empty] | Tripped at Rairakhol end.
|  | 2020-10-13 | 20:36 | 2020-10-13 | 20:42 | 0:06 | 0 | 6 | [5 empty] | Trig Signal- ZM01 Fault Abs Dist.- 26.915 KM Fault Loop- L3N, Fault current IR=231.47 A, IY= 385.90 A, IB= 3124.93 A
|  | 2020-10-29 | 15:17 | 2020-10-29 | 17:03 | 1:46 | 0 | 20 | [5 empty] | Tripped on E/F at both ends. [ one big mango tree has been uprooted by the railway authority which was in close proximity to 132 KV TTPS-Angul and 132 KV Chainpal-Angul double circuit
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
400 | 132kV Rajgangpur-OCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.5 | 8760 | 100% | 0 | 4380
401 | 132kV Rajgangapur-Rajgangapur (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.2 | 8760 | 100% | 0 | 36792
402 | 132kV Rajgangpur-Rourkela |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.1 | 8760 | 100% | 0 | 237396
403 | 132kV Ransinghpur-Badagada (Kesura) |  |  |  |  | 0.38125 | 15 | 13 | [7 empty] | 34.23 | 8760 | 99.83% | 520.8665 | 299854.8
|  | 2020-05-19 | 8:39 | 2020-05-19 | 9:08 | 0:29 | 0 | 29
|  | 2020-05-29 | 4:05 | 2020-05-29 | 4:59 | 0:54 | 0 | 54 | [5 empty] | Tripped at R.Singpur end.
|  | 2020-06-02 | 8:16 | 2020-06-02 | 15:45 | 7:29 | 0 | 41 | [5 empty] | DP Relay Operated
|  | 2020-06-30 | 9:03 | 2020-06-30 | 9:21 | 0:18 | 0 | 18 | [5 empty] | DP Relay Operated
|  | 2020-06-15 | 0:30 | 2020-06-15 | 0:53 | 0:23 | 0 | 23 | [5 empty] | DP Relay Operated
|  | 2020-06-29 | 13:21 | 2020-06-29 | 13:27 | 0:06 | 0 | 6 | [5 empty] | P/S failed from Chandaka Grid end
|  | 2020-08-31 | 15:44 | 2020-08-31 | 16:06 | 0:22 | 0 | 22 | [5 empty] | DP relay operated
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
404 | 132kV TS Alloys-Choudwar |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 22.6 | 8760 | 100% | 7.91 | 197976
|  | 2020-05-14 | 8:20 | 2020-05-14 | 8:23 | 0:04 | 0 | 4 | [5 empty] | O/C 'B'ph
|  | 2020-06-08 | 14:53 | 2020-06-08 | 15:10 | 0:17 | 0 | 17 | [5 empty] | O/C R,B at choudwar end ,E/F at T.S Alloys
405 | 132kV TS Alloys-Arati Steel |  |  |  |  | 0.24583 | 12 | 26 | [7 empty] | 17.28 | 8760 | 99.86% | 214.848 | 151372.8
|  | 2020-05-14 | 8:20 | 2020-05-14 | 13:22 | 5:02 | 0 | 4 | [5 empty] | E/F(Non closing of its own breaker)
|  | 2020-06-01 | 14:20 | 2020-06-01 | 14:47 | 0:27 | 0 | 15 | [5 empty] | Tripped on E/F
|  | 2020-06-08 | 14:53 | 2020-06-08 | 15:18 | 0:25 | 0 | 7 | [5 empty] | DP relay tripped at Arati end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
406 | 132kV Rayagada-Akhusingh |  |  |  |  | 0.05 | 12 | 40 | [7 empty] | 49.2 | 8760 | 99.86% | 623.2 | 430992
|  | 2020-05-18 | 13:31 | 2020-05-18 | 13.44 | 0:13 | 0 | 13 | [5 empty] | Tripped
|  | 2020-05-16 | 15:09 | 2020-05-16 | 15:18 | 0:09 | 0 | 6 | [5 empty] | Auto-tripped, R, B Phase fault, Z1 Trip
|  | 2020-10-03 | 14:47 | 2020-10-03 | 14:52 | 0:05 | 0 | 5 | [5 empty] | Tripped at Podagada
|  | 2020-10-15 | 19:04 | 2020-10-15 | 19:49 | 0:45 | 0 | 16 | [5 empty] | Tripped of Podagad end & JNR With O/C [Conductor y Phase CVT of JNR incoming side snapped at podagada end.]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
407 | 132kV Rayagada-Rayagada Traction |  |  |  |  | 0.025 | 13 | 57 | [7 empty] | 2.646 | 8760 | 99.84% | 36.9117 | 23178.96
|  | 2020-05-18 | 13:31 | 2020-05-18 | 13.44 | 0:13 | 0 | 13 | [5 empty] | Tripped
|  | 2020-05-27 | 9:13 | 2020-05-27 | 9:34 | 0:21 | 0 | 21 | [5 empty] | BGT
|  | 2020-07-30 | 14:46 | 2020-07-31 | 17:18 | 26:32:00 | 1 | 21 | [5 empty] | BG-T, Y- 6.1KAat Therubali end. [Y-Phase conductor snapped at Loc. No-65]
|  | 2020-10-20 | 17:41 | 2020-10-20 | 17:43 | 0:02 | 0 | 2 | [5 empty] | Tripped on O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
408 | 132kV Rayagada-VBC Ferro |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.3 | 8760 | 100% | 0 | 2628
409 | 132kV Rourkela-Bhalulata (T) |  |  |  |  | 1899-12-31 00:49 | 31 | 15 | [7 empty] | 23.89 | 8760 | 99.64% | 746.5625 | 209276.4
|  | 2020-06-08 | 14:16 | 2020-06-08 | 14:36 | 0:20 | 0 | 20 | [5 empty] | Backup Relay: O/C-Y Phase & E/F.
|  | 2020-09-08 | 01:10 | 2020-09-08 | 11:05 | 0:02 | 0 | 2 | [5 empty] | EARTHFAULT YPH (64X) [CT Y Phase Jumper Snapped at rourkela Grid ]
|  | 2020-09-25 | 20:19 | 2020-09-25 | 21:13 | 6:48 | 0 | 54 | [5 empty] | O/C- R Phase [R Phase Jumper from Breaker to Isolator snapped and 132kV Tarkera-
|  | 2020-12-17 | 16:47 | 2020-12-17 | 21:05 | 4:18 | 4 | 18 | [5 empty] | Tripped on E/F due to B-ph CT jumper snap at Nalda RTSS.
|  | 2020-12-19 | 07:43 | 2020-12-19 | 19:04 | 11:21 | 11 | 21 | [5 empty] | Tripped at RKL on E/F with following relay indications: Ia=345.7A; Ib=5.88kA; Ic=264.3A: In=5.273kA [Y-ph Jumper snapped at Loc-38 of RKL jurisdiction]
|  | 2021-01-27 | 03:10 | 2021-01-27 | 05:30 | 2:20 | 2 | 20 | [5 empty] | E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
410 | 132 kV New Bolangir - Bolangir Ckt - I |  |  |  |  | 0.22778 | 13 | 25 | [7 empty] | 3.78 | 8760 | 99.85% | 50.715 | 33112.8
|  | 24.04.20 | 5:16 | 24.04.20 | 5:23 | 0:07 | 0 | 7 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-05-28 | 16:22 | 2020-05-28 | 16:40 | 0:18 | 0 | 18 | [5 empty] | E/F
|  | 2020-06-12 | 14:30 | 2020-06-12 | 14:39 | 0:09 | 0 | 9 | [5 empty] | 132kV Kesinga Fdr tripped on E/F, B Phase and caused tripping of Bolangir Fdr simultaneously.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-02-02 | 16:28 | 2021-02-02 | 16:36 | 0:08 | 0 | 8 | [5 empty] | Tripped from Sadeipalli end on overload
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
411 | 132kV Bolangir- ACME |  |  |  |  | 0.35556 | 16 | 54 | [7 empty] | 21.62 | 8760 | 99.81% | 365.378 | 189391.2
|  | 08.04.20 | 16:28 | 08.04.20 | 16:33 | 0:05 | 0 | 5 | [5 empty] | Tripped on E/F at Bolangir end
|  | 08.04.20 | 16:49 | 08.04.20 | 16:57 | 0:08 | 0 | 8 | [5 empty] | Tripped on E/F at Bolangir end
|  | 24.04.20 | 5:16 | 24.04.20 | 5:23 | 0:07 | 0 | 7 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-05-06 | 0:51 | 2020-05-06 | 0:58 | 0:07 | 0 | 7 | [5 empty] | E/F
|  | 2020-05-07 | 3:45 | 2020-05-07 | 4:03 | 0:18 | 0 | 10 | [5 empty] | Tripped on Over voltage
|  | 2020-05-28 | 16:07 | 2020-05-28 | 16:12 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-05-28 | 16:22 | 2020-05-28 | 16:36 | 0:14 | 0 | 14 | [5 empty] | E/F
|  | 2020-05-29 | 17:17 | 2020-05-29 | 17:24 | 0:07 | 0 | 7
|  | 2020-06-12 | 14:30 | 2020-06-12 | 14:39 | 0:09 | 0 | 9 | [5 empty] | 132kV Kesinga Fdr tripped on E/F, B Phase and caused tripping of Bolangir Fdr simultaneously.
|  | 2020-07-04 | 21:24 | 2020-07-04 | 21:27 | 0:03 | 0 | 3 | [5 empty] | Due to LBB Operation at Tushra.
|  | 2020-07-31 | 15:33 | 2020-07-31 | 15:36 | 0:03 | 0 | 3 | [5 empty] | At Bolangir end: O/C, E/F.
|  | 2020-07-31 | 20:36 | 2020-07-31 | 20:38 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-31 | 21:30 | 2020-07-31 | 21:34 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-17 | 16:16 | 2020-07-17 | 16:20 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 0:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 0:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-07-30 | 08:39 | 2020-07-30 | 08:40 | 0:01 | 0 | 1 | [5 empty] | Tripped on directional o/c displayed on back up o/c and e/f relay.
|  | 2020-07-30 | 09:38 | 2020-07-30 | 09:41 | 0:03 | 0 | 3 | [5 empty] | Trpped at Bolangir due to O/L.
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-09-16 | 19:00 | 2020-09-16 | 19:03 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 20:21 | 2020-09-16 | 20:22 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 21:45 | 2020-09-16 | 21:47 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 0:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-09-28 | 19:12 | 2020-09-28 | 19:14 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 2020-09-29 | 20:00 | 2020-09-29 | 20:02 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-10-19 | 19:04 | 2020-10-19 | 19:06 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-19 | 20:12 | 2020-10-19 | 20:14 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-31 | 17:30 | 2020-10-31 | 17:34 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-11-11 | 03:13 | 2020-11-11 | 03:32 | 0:19 | 0 | 19 | [5 empty] | Tripped from Bolangir(Lal Tikira)on E/F
|  | 2020-11-18 | 17:49 | 2020-11-18 | 17:52 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-20 | 18:12 | 2020-11-20 | 18:13 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-12-04 | 18:20 | 2020-12-04 | 18:22 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:14 | 2020-12-06 | 17:16 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:47 | 2020-12-06 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:16 | 2020-12-06 | 18:19 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:31 | 2020-12-06 | 18:41 | 0:10 | 0 | 10 | [5 empty] | O/C
|  | 2020-12-06 | 18:54 | 2020-12-06 | 18:57 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-07 | 09:15 | 2020-12-07 | 09:20 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2020-12-28 | 16:38 | 2020-12-28 | 16:50 | 0:12 | 0 | 12 | [5 empty] | O/C
|  | 2020-12-29 | 18:09 | 2020-12-29 | 18:12 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-30 | 16:44 | 2020-12-30 | 16:48 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-31 | 19:05 | 2020-12-31 | 19:09 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-01-10 | 07:07 | 2021-01-10 | 07:09 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-11 | 07:22 | 2021-01-11 | 07:24 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-13 | 17:27 | 2021-01-13 | 17:30 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-18 | 18:46 | 2021-01-18 | 18:48 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-18 | 19:31 | 2021-01-18 | 19:33 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 17:57 | 2021-01-15 | 17:59 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 18:17 | 2021-01-15 | 18:19 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-17 | 06:53 | 2021-01-17 | 06:56 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-17 | 17:37 | 2021-01-17 | 17:39 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-21 | 18:19 | 2021-01-21 | 18:20 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-21 | 19:33 | 2021-01-21 | 19:35 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 17:00 | 2021-01-22 | 17:02 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 18:03 | 2021-01-22 | 18:05 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-26 | 18:24 | 2021-01-26 | 18:26 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-27 | 07:24 | 2021-01-27 | 07:27 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-31 | 17:47 | 2021-01-31 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-02-02 | 16:28 | 2021-02-02 | 16:36 | 0:08 | 0 | 8 | [5 empty] | Tripped from Sadeipalli end on overload
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
412 | 132 kV ACME - Tusura |  |  |  |  | 0.39861 | 17 | 49 | [7 empty] | 24.02 | 8760 | 99.8% | 427.9563 | 210415.2
|  | 08.04.20 | 16:28 | 08.04.20 | 16:33 | 0:05 | 0 | 5 | [5 empty] | Tripped on E/F at Bolangir end
|  | 08.04.20 | 16:49 | 08.04.20 | 16:57 | 0:08 | 0 | 8 | [5 empty] | Tripped on E/F at Bolangir end
|  | 24.04.20 | 5:16 | 24.04.20 | 5:23 | 0:07 | 0 | 7 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-05-06 | 0:51 | 2020-05-06 | 1:53 | 1:02 | 1 | 2 | [5 empty] | E/F
|  | 2020-05-07 | 3:45 | 2020-05-07 | 4:03 | 0:18 | 0 | 10 | [5 empty] | Tripped on Over voltage
|  | 2020-05-28 | 16:07 | 2020-05-28 | 16:12 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-05-28 | 16:22 | 2020-05-28 | 16:36 | 0:14 | 0 | 14 | [5 empty] | E/F
|  | 2020-05-29 | 17:17 | 2020-05-29 | 17:24 | 0:07 | 0 | 7
|  | 2020-06-12 | 14:30 | 2020-06-12 | 14:39 | 0:09 | 0 | 9 | [5 empty] | 132kV Kesinga Fdr tripped on E/F, B Phase and caused tripping of Bolangir Fdr simultaneously.
|  | 2020-07-04 | 21:24 | 2020-07-04 | 21:27 | 0:03 | 0 | 3 | [5 empty] | Due to LBB Operation at Tushra.
|  | 2020-07-31 | 15:33 | 2020-07-31 | 15:36 | 0:03 | 0 | 3 | [5 empty] | At Bolangir end: O/C, E/F.
|  | 2020-07-31 | 20:36 | 2020-07-31 | 20:38 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-31 | 21:30 | 2020-07-31 | 21:34 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-17 | 16:16 | 2020-07-17 | 16:20 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 0:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 0:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-07-30 | 08:39 | 2020-07-30 | 08:40 | 0:01 | 0 | 1 | [5 empty] | Tripped on directional o/c displayed on back up o/c and e/f relay.
|  | 2020-07-30 | 09:38 | 2020-07-30 | 09:41 | 0:03 | 0 | 3 | [5 empty] | Trpped at Bolangir due to O/L.
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-09-16 | 19:00 | 2020-09-16 | 19:03 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 20:21 | 2020-09-16 | 20:22 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 21:45 | 2020-09-16 | 21:47 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 0:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-09-28 | 19:12 | 2020-09-28 | 19:14 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 2020-09-29 | 20:00 | 2020-09-29 | 20:02 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-10-19 | 19:04 | 2020-10-19 | 19:06 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-19 | 20:12 | 2020-10-19 | 20:14 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-31 | 17:30 | 2020-10-31 | 17:34 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-11-11 | 03:13 | 2020-11-11 | 03:32 | 0:19 | 0 | 19 | [5 empty] | Tripped from Bolangir(Lal Tikira)on E/F
|  | 2020-11-18 | 17:49 | 2020-11-18 | 17:52 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-20 | 18:12 | 2020-11-20 | 18:13 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-12-04 | 18:20 | 2020-12-04 | 18:22 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:14 | 2020-12-06 | 17:16 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:47 | 2020-12-06 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:16 | 2020-12-06 | 18:19 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:31 | 2020-12-06 | 18:41 | 0:10 | 0 | 10 | [5 empty] | O/C
|  | 2020-12-06 | 18:54 | 2020-12-06 | 18:57 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-07 | 09:15 | 2020-12-07 | 09:20 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2020-12-28 | 16:38 | 2020-12-28 | 16:50 | 0:12 | 0 | 12 | [5 empty] | O/C
|  | 2020-12-29 | 18:09 | 2020-12-29 | 18:12 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-30 | 16:44 | 2020-12-30 | 16:48 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-31 | 19:05 | 2020-12-31 | 19:09 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-01-10 | 07:07 | 2021-01-10 | 07:09 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-11 | 07:22 | 2021-01-11 | 07:24 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-13 | 17:27 | 2021-01-13 | 17:30 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-18 | 18:46 | 2021-01-18 | 18:48 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-18 | 19:31 | 2021-01-18 | 19:33 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 17:57 | 2021-01-15 | 17:59 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 18:17 | 2021-01-15 | 18:19 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-17 | 06:53 | 2021-01-17 | 06:56 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-17 | 17:37 | 2021-01-17 | 17:39 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-21 | 18:19 | 2021-01-21 | 18:20 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-21 | 19:33 | 2021-01-21 | 19:35 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 17:00 | 2021-01-22 | 17:02 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 18:03 | 2021-01-22 | 18:05 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-26 | 18:24 | 2021-01-26 | 18:26 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-27 | 07:24 | 2021-01-27 | 07:27 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-31 | 17:47 | 2021-01-31 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-02-02 | 16:28 | 2021-02-02 | 16:36 | 0:08 | 0 | 8 | [5 empty] | Tripped from Sadeipalli end on overload
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
413 | 132 kV Tusura- Saintala |  |  |  |  | 0.44028 | 18 | 58 | [7 empty] | 22.38 | 8760 | 99.78% | 424.474 | 196048.8
|  | 08.04.20 | 16:28 | 08.04.20 | 16:33 | 0:05 | 0 | 5 | [5 empty] | Tripped on E/F at Bolangir end
|  | 08.04.20 | 16:49 | 08.04.20 | 16:57 | 0:08 | 0 | 8 | [5 empty] | Tripped on E/F at Bolangir end
|  | 24.04.20 | 5:16 | 24.04.20 | 5:23 | 0:07 | 0 | 7 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-05-06 | 0:51 | 2020-05-06 | 1:53 | 1:02 | 1 | 2 | [5 empty] | E/F
|  | 2020-05-07 | 3:45 | 2020-05-07 | 4:03 | 0:18 | 0 | 10 | [5 empty] | Tripped on Over voltage
|  | 2020-05-28 | 16:07 | 2020-05-28 | 16:12 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-05-28 | 16:22 | 2020-05-28 | 16:36 | 0:14 | 0 | 14 | [5 empty] | E/F
|  | 2020-05-29 | 17:17 | 2020-05-29 | 17:24 | 0:07 | 0 | 7
|  | 2020-06-12 | 14:30 | 2020-06-12 | 14:39 | 0:09 | 0 | 9 | [5 empty] | 132kV Kesinga Fdr tripped on E/F, B Phase and caused tripping of Bolangir Fdr simultaneously.
|  | 2020-07-04 | 21:24 | 2020-07-04 | 21:27 | 0:03 | 0 | 3 | [5 empty] | Due to LBB Operation at Tushra.
|  | 2020-07-31 | 15:33 | 2020-07-31 | 15:36 | 0:03 | 0 | 3 | [5 empty] | At Bolangir end: O/C, E/F.
|  | 2020-07-31 | 20:36 | 2020-07-31 | 20:38 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-31 | 21:30 | 2020-07-31 | 21:34 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-17 | 16:16 | 2020-07-17 | 16:20 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 0:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 0:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-07-30 | 08:39 | 2020-07-30 | 08:40 | 0:01 | 0 | 1 | [5 empty] | Tripped on directional o/c displayed on back up o/c and e/f relay.
|  | 2020-07-30 | 09:38 | 2020-07-30 | 09:41 | 0:03 | 0 | 3 | [5 empty] | Trpped at Bolangir due to O/L.
|  | 2020-08-14 | 15:12 | 2020-08-14 | 15:16 | 00:04 | 0 | 4 | [5 empty] | 132KV P/S FAILED FROM TUSHRA DUE TO LBB
|  | 2020-08-14 | 17:27 | 2020-08-14 | 17:29 | 00:02 | 0 | 2 | [5 empty] | 132KV P/S FAILED FROM TUSHRA DUE TO LBB
|  | 2020-08-18 | 08:22 | 2020-08-18 | 08:25 | 00:03 | 0 | 3 | [5 empty] | At Tushura-E/F
|  | 2020-08-17 | 08:24 | 2020-08-17 | 08:26 | 0:02 | 0 | 2 | [5 empty] | Local Breaker Backup (LBB) operation at Tushra Grid.
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-09-12 | 19:16 | 2020-09-12 | 19:18 | 0:02 | 0 | 2 | [5 empty] | Tripped from Tushra
|  | 2020-09-16 | 19:00 | 2020-09-16 | 19:03 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 20:21 | 2020-09-16 | 20:22 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 21:45 | 2020-09-16 | 21:47 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 0:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-09-28 | 19:12 | 2020-09-28 | 19:14 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 2020-09-29 | 20:00 | 2020-09-29 | 20:02 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-10-01 | 05:23 | 2020-10-01 | 05:36 | 0:13 | 0 | 13 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-04 | 00:24 | 2020-10-04 | 00:31 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-05 | 21:33 | 2020-10-05 | 21:35 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-07 | 23:07 | 2020-10-07 | 23:09 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-08 | 05:41 | 2020-10-08 | 05:48 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R .
|  | 2020-10-10 | 20:06 | 2020-10-10 | 20:07 | 0:01 | 0 | 1 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-15 | 03:32 | 2020-10-15 | 03:37 | 0:05 | 0 | 5 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-19 | 19:04 | 2020-10-19 | 19:06 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-19 | 20:12 | 2020-10-19 | 20:14 | 0:02 | 0 | 2
|  | 2020-10-21 | 04:52 | 2020-10-21 | 05:01 | 0:09 | 0 | 9 | [5 empty] | DUE TO OVERCURRENT AT TUSHRA GSS ALONG trippedTO 132KV KESINGA B/R ON E/F & 33/132 KV SOLAR B/R trippedON HV E/F.
|  | 2020-10-31 | 23:49 | 2020-10-31 | 23:51 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-31 | 17:30 | 2020-10-31 | 17:34 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-11-11 | 03:13 | 2020-11-11 | 03:32 | 0:19 | 0 | 19 | [5 empty] | Tripped from Bolangir(Lal Tikira)on E/F
|  | 2020-11-18 | 17:49 | 2020-11-18 | 17:52 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-20 | 18:12 | 2020-11-20 | 18:13 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-01 | 03:54 | 2020-11-01 | 04:02 | 0:08 | 0 | 8 | [5 empty] | Tripped From Tushra Grid on E/F
|  | 2020-12-04 | 18:20 | 2020-12-04 | 18:22 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:14 | 2020-12-06 | 17:16 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:47 | 2020-12-06 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:16 | 2020-12-06 | 18:19 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:31 | 2020-12-06 | 18:41 | 0:10 | 0 | 10 | [5 empty] | O/C
|  | 2020-12-06 | 18:54 | 2020-12-06 | 18:57 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-07 | 09:15 | 2020-12-07 | 09:20 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2020-12-28 | 16:38 | 2020-12-28 | 16:50 | 0:12 | 0 | 12 | [5 empty] | O/C
|  | 2020-12-29 | 18:09 | 2020-12-29 | 18:12 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-30 | 16:44 | 2020-12-30 | 16:48 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-31 | 19:05 | 2020-12-31 | 19:09 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-01-10 | 07:07 | 2021-01-10 | 07:09 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-11 | 07:22 | 2021-01-11 | 07:24 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-13 | 17:27 | 2021-01-13 | 17:30 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-18 | 18:46 | 2021-01-18 | 18:48 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-18 | 19:31 | 2021-01-18 | 19:33 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 17:57 | 2021-01-15 | 17:59 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 18:17 | 2021-01-15 | 18:19 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-17 | 06:53 | 2021-01-17 | 06:56 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-17 | 17:37 | 2021-01-17 | 17:39 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-21 | 18:19 | 2021-01-21 | 18:20 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-21 | 19:33 | 2021-01-21 | 19:35 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 17:00 | 2021-01-22 | 17:02 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 18:03 | 2021-01-22 | 18:05 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-26 | 18:24 | 2021-01-26 | 18:26 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-27 | 07:24 | 2021-01-27 | 07:27 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-31 | 17:47 | 2021-01-31 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-02-02 | 16:28 | 2021-02-02 | 16:36 | 0:08 | 0 | 8 | [5 empty] | Tripped from Sadeipalli end on overload
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
414 | 132kV Tusura -RTSS Deogaon road |  |  |  |  | 0.059028 | 13 | 25 | [7 empty] | 9.991 | 5460 | 99.75% | 134.0459 | 54550.86
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-09-12 | 19:16 | 2020-09-12 | 19:18 | 0:02 | 0 | 2 | [5 empty] | Tripped from Tushra
|  | 2020-09-16 | 19:00 | 2020-09-16 | 19:03 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 20:21 | 2020-09-16 | 20:22 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 21:45 | 2020-09-16 | 21:47 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 0:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-09-28 | 19:12 | 2020-09-28 | 19:14 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 2020-09-29 | 20:00 | 2020-09-29 | 20:02 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-10-01 | 05:23 | 2020-10-01 | 05:36 | 0:13 | 0 | 13 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-04 | 00:24 | 2020-10-04 | 00:31 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-05 | 21:33 | 2020-10-05 | 21:35 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-07 | 23:07 | 2020-10-07 | 23:09 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-08 | 05:41 | 2020-10-08 | 05:48 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R .
|  | 2020-10-10 | 20:06 | 2020-10-10 | 20:07 | 0:01 | 0 | 1 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-15 | 03:32 | 2020-10-15 | 03:37 | 0:05 | 0 | 5 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-19 | 19:04 | 2020-10-19 | 19:06 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-19 | 20:12 | 2020-10-19 | 20:14 | 0:02 | 0 | 2
|  | 2020-10-21 | 04:52 | 2020-10-21 | 05:01 | 0:09 | 0 | 9 | [5 empty] | DUE TO OVERCURRENT AT TUSHRA GSS ALONG trippedTO 132KV KESINGA B/R ON E/F & 33/132 KV SOLAR B/R trippedON HV E/F.
|  | 2020-10-31 | 23:49 | 2020-10-31 | 23:51 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-31 | 17:30 | 2020-10-31 | 17:34 | 0:04 | 0 | 4 | [5 empty] | O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
415 | 132kV Saintala- Kesinga |  |  |  |  | 0.53264 | 23 | 13 | [7 empty] | 32.8 | 8760 | 99.73% | 761.5067 | 287328
|  | 08.04.20 | 16:28 | 08.04.20 | 16:33 | 0:05 | 0 | 5 | [5 empty] | Tripped on E/F at Bolangir end
|  | 08.04.20 | 16:49 | 08.04.20 | 16:57 | 0:08 | 0 | 8 | [5 empty] | Tripped on E/F at Bolangir end
|  | 24.04.20 | 5:16 | 24.04.20 | 5:23 | 0:07 | 0 | 7 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-05-06 | 0:51 | 2020-05-06 | 1:38 | 0:47 | 0 | 47 | [5 empty] | E/F
|  | 2020-05-07 | 3:45 | 2020-05-07 | 4:03 | 0:18 | 0 | 10 | [5 empty] | Tripped on Over voltage
|  | 2020-05-28 | 16:07 | 2020-05-28 | 16:12 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-05-28 | 16:22 | 2020-05-28 | 16:36 | 0:14 | 0 | 14 | [5 empty] | E/F
|  | 2020-05-29 | 17:17 | 2020-05-29 | 17:24 | 0:07 | 0 | 7
|  | 2020-06-12 | 14:30 | 2020-06-12 | 14:39 | 0:09 | 0 | 9 | [5 empty] | 132kV Kesinga Fdr tripped on E/F, B Phase and caused tripping of Bolangir Fdr simultaneously.
|  | 2020-06-12 | 15:51 | 2020-06-12 | 16:06 | 0:15 | 0 | 15 | [5 empty] | Tripped from Saintala: O/C, B Phase.
|  | 2020-06-15 | 9:30 | 2020-06-15 | 9:33 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala
|  | 2020-06-29 | 11:57 | 2020-06-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Saintala end: Due to Circuit Overloading
|  | 2020-06-29 | 13:27 | 2020-06-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-06-29 | 17:17 | 2020-06-29 | 17:27 | 0:10 | 0 | 10 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-07-04 | 21:24 | 2020-07-04 | 21:27 | 0:03 | 0 | 3 | [5 empty] | Due to LBB Operation at Tushra.
|  | 2020-07-31 | 15:33 | 2020-07-31 | 15:36 | 0:03 | 0 | 3 | [5 empty] | At Bolangir end: O/C, E/F.
|  | 2020-07-31 | 20:36 | 2020-07-31 | 20:38 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-31 | 21:30 | 2020-07-31 | 21:34 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-17 | 16:16 | 2020-07-17 | 16:20 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 0:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 0:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-07-30 | 08:39 | 2020-07-30 | 08:40 | 0:01 | 0 | 1 | [5 empty] | Tripped on directional o/c displayed on back up o/c and e/f relay.
|  | 2020-07-30 | 09:38 | 2020-07-30 | 09:41 | 0:03 | 0 | 3 | [5 empty] | Trpped at Bolangir due to O/L.
|  | 2020-07-30 | 21:39 | 2020-07-30 | 21:45 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 23:00 | 2020-07-30 | 23:06 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala: O/C.
|  | 2020-08-12 | 19:38 | 2020-08-12 | 19:43 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala on Over load
|  | 2020-08-17 | 08:24 | 2020-08-17 | 08:26 | 0:02 | 0 | 2 | [5 empty] | Local Breaker Backup (LBB) operation at Tushra Grid.
|  | 2020-08-22 | 21:20 | 2020-08-22 | 21:26 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/L
|  | 2020-08-30 | 22:12 | 2020-08-30 | 22:17 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala
|  | 2020-09-02 | 19:15 | 2020-09-02 | 20:00 | 0:45 | 0 | 45 | [5 empty] | Tripped from saintala [Section isolator insulation punchure]
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-09-06 | 19:11 | 2020-09-06 | 19:21 | 0:10 | 0 | 10 | [5 empty] | Tripped From ACME
|  | 2020-09-12 | 19:16 | 2020-09-12 | 19:18 | 0:02 | 0 | 2 | [5 empty] | Tripped from Tushra
|  | 2020-09-13 | 19:18 | 2020-09-13 | 19:24 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala-Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-13 | 21:44 | 2020-09-13 | 21:50 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala- Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-14 | 20:13 | 2020-09-14 | 20:19 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/C B- Phase due to Ckt overloading
|  | 2020-09-16 | 09:41 | 2020-09-16 | 09:50 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-16 | 19:00 | 2020-09-16 | 19:03 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 20:21 | 2020-09-16 | 20:22 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 21:45 | 2020-09-16 | 21:47 | 00:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:32 | 2020-09-17 | 23:34 | 0:02 | 0 | 2 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:17 | 2020-09-17 | 23:19 | 0:02 | 0 | 2 | [5 empty] | DUE TO OVERCURRENT AT LALTIKIRA GRID.
|  | 2020-09-19 | 21:57 | 2020-09-19 | 22:03 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 0:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 00:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-09-28 | 19:12 | 2020-09-28 | 19:14 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 2020-09-29 | 20:00 | 2020-09-29 | 20:02 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-24 | 18:43 | 2020-09-24 | 18:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala-Tripped on E/F R-Phase
|  | 2020-10-01 | 05:23 | 2020-10-01 | 05:36 | 0:13 | 0 | 13 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-04 | 00:20 | 2020-10-04 | 0:24 | 0:04 | 0 | 4 | [5 empty] | Tripped From Saintala-Earth Fault on R-ph
|  | 2020-10-04 | 00:24 | 2020-10-04 | 00:31 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-05 | 21:33 | 2020-10-05 | 21:35 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-06 | 04:04 | 2020-10-06 | 04:10 | 0:06 | 0 | 6 | [5 empty] | Tripped From saintala
|  | 2020-10-07 | 23:07 | 2020-10-07 | 23:09 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-08 | 05:41 | 2020-10-08 | 05:48 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R .
|  | 2020-10-10 | 01:40 | 2020-10-10 | 01:45 | 0:05 | 0 | 5 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-10 | 20:06 | 2020-10-10 | 20:07 | 0:01 | 0 | 1 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-15 | 03:32 | 2020-10-15 | 03:37 | 0:05 | 0 | 5 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-16 | 20:10 | 2020-10-16 | 20:17 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala Grid- Earth Fault on B-Phase
|  | 2020-10-19 | 19:04 | 2020-10-19 | 19:06 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-19 | 20:12 | 2020-10-19 | 20:14 | 0:02 | 0 | 2
|  | 2020-10-21 | 04:52 | 2020-10-21 | 05:01 | 0:09 | 0 | 9 | [5 empty] | DUE TO OVERCURRENT AT TUSHRA GSS ALONG trippedTO 132KV KESINGA B/R ON E/F & 33/132 KV SOLAR B/R trippedON HV E/F.
|  | 2020-10-31 | 23:49 | 2020-10-31 | 23:51 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-31 | 17:30 | 2020-10-31 | 17:34 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-11-11 | 03:13 | 2020-11-11 | 03:32 | 0:19 | 0 | 19 | [5 empty] | Tripped from Bolangir(Lal Tikira)on E/F
|  | 2020-11-18 | 17:49 | 2020-11-18 | 17:52 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-20 | 18:12 | 2020-11-20 | 18:13 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-01 | 03:54 | 2020-11-01 | 04:02 | 0:08 | 0 | 8 | [5 empty] | Tripped From Tushra Grid on E/F
|  | 2020-11-03 | 01:30 | 2020-11-03 | 01:33 | 00:03 | 0 | 3 | [5 empty] | Tripped From Saintala Grid on Over Current B-Ph
|  | 2020-11-28 | 05:32 | 2020-11-28 | 05:39 | 00:07 | 0 | 7 | [5 empty] | Tripped From saintala on O/C R-ph
|  | 2020-11-16 | 16:13 | 2020-11-16 | 16:19 | 01:07 | 1 | 7 | [5 empty] | Tripped from Kesingadue to overloading.
|  | 2020-12-04 | 18:20 | 2020-12-04 | 18:22 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:14 | 2020-12-06 | 17:16 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:47 | 2020-12-06 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:16 | 2020-12-06 | 18:19 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:31 | 2020-12-06 | 18:41 | 0:10 | 0 | 10 | [5 empty] | O/C
|  | 2020-12-06 | 18:54 | 2020-12-06 | 18:57 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-07 | 09:15 | 2020-12-07 | 09:20 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2020-12-28 | 16:38 | 2020-12-28 | 16:50 | 0:12 | 0 | 12 | [5 empty] | O/C
|  | 2020-12-29 | 18:09 | 2020-12-29 | 18:12 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-30 | 16:44 | 2020-12-30 | 16:48 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-31 | 19:05 | 2020-12-31 | 19:09 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 16.12.20 | 17:21 | 16.12.20 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped on O/C R-ph from Saintala end.
|  | 2020-12-22 | 15:21 | 2020-12-22 | 15:25 | 0:04 | 0 | 4 | [5 empty] | Tripped on O/C B-ph from Saintala end.
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-01-10 | 07:07 | 2021-01-10 | 07:09 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-11 | 07:22 | 2021-01-11 | 07:24 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-13 | 17:27 | 2021-01-13 | 17:30 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-18 | 18:46 | 2021-01-18 | 18:48 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-18 | 19:31 | 2021-01-18 | 19:33 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 17:57 | 2021-01-15 | 17:59 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 18:17 | 2021-01-15 | 18:19 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-17 | 06:53 | 2021-01-17 | 06:56 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-17 | 17:37 | 2021-01-17 | 17:39 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-21 | 18:19 | 2021-01-21 | 18:20 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-21 | 19:33 | 2021-01-21 | 19:35 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 17:00 | 2021-01-22 | 17:02 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 18:03 | 2021-01-22 | 18:05 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-26 | 18:24 | 2021-01-26 | 18:26 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-27 | 07:24 | 2021-01-27 | 07:27 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-31 | 17:47 | 2021-01-31 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-02-02 | 16:28 | 2021-02-02 | 16:36 | 0:08 | 0 | 8 | [5 empty] | Tripped from Sadeipalli end on overload
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
416 | 132kV Kesinga-Khariar |  |  |  |  | 0.59375 | 26 | 54 | [7 empty] | 57.7 | 8760 | 99.69% | 1552.13 | 505452
|  | 08.04.20 | 16:28 | 08.04.20 | 16:33 | 0:05 | 0 | 5 | [5 empty] | Tripped on E/F at Bolangir end
|  | 08.04.20 | 16:49 | 08.04.20 | 16:57 | 0:08 | 0 | 8 | [5 empty] | Tripped on E/F at Bolangir end
|  | 24.04.20 | 5:16 | 24.04.20 | 5:23 | 0:07 | 0 | 7 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-05-06 | 2:11 | 2020-05-06 | 2:14 | 0:03 | 0 | 3 | [5 empty] | Tripped at Kesinga- on Overload
|  | 2020-05-06 | 5:29 | 2020-05-06 | 5:34 | 0:05 | 0 | 5 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 3:50 | 2020-05-06 | 3:58 | 0:08 | 0 | 8 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-19 | 15:44 | 2020-05-19 | 15:48 | 0:04 | 0 | 4 | [5 empty] | At Khariar-Tripped on Over Current B-Ph Fault
|  | 2020-05-19 | 16:49 | 2020-05-19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Khariar-Tripped on Over Current B-Ph Fault
|  | 2020-05-06 | 10:34 | 2020-05-06 | 10:38 | 0:04 | 0 | 4 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-21 | 15:02 | 2020-05-21 | 15:15 | 0:13 | 0 | 13 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-27 | 21:17 | 2020-05-27 | 21:23 | 0:06 | 0 | 6 | [5 empty] | Due to Over Current B-Ph Fault
|  | 2020-05-29 | 9:51 | 2020-05-29 | 10:57 | 1:06 | 1 | 6 | [5 empty] | At khariar-Tripped due to Due to Over loading at ACME
|  | 2020-05-29 | 11:57 | 2020-05-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Khariar end-Due to Circuit Overloading
|  | 2020-05-29 | 13:27 | 2020-05-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Due to Over Current B-Ph Fault
|  | 2020-05-06 | 5:29 | 2020-05-06 | 5:34 | 0:05 | 0 | 5 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 3:50 | 2020-05-06 | 3:58 | 0:08 | 0 | 8
|  | 2020-05-06 | 0:51 | 2020-05-06 | 1:38 | 0:47 | 0 | 47 | [5 empty] | E/F
|  | 2020-05-07 | 3:45 | 2020-05-07 | 4:03 | 0:18 | 0 | 10 | [5 empty] | Tripped on Over voltage
|  | 2020-05-28 | 16:07 | 2020-05-28 | 16:12 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-05-28 | 16:22 | 2020-05-28 | 16:36 | 0:14 | 0 | 14 | [5 empty] | E/F
|  | 2020-05-29 | 17:17 | 2020-05-29 | 17:24 | 0:07 | 0 | 7
|  | 2020-05-29 | 11:07 | 2020-05-29 | 11:10 | 0:03 | 0 | 3 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-19 | 15:43 | 2020-05-19 | 15:47 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-Tripped
|  | 2020-06-12 | 14:30 | 2020-06-12 | 14:39 | 0:09 | 0 | 9 | [5 empty] | 132kV Kesinga Fdr tripped on E/F, B Phase and caused tripping of Bolangir Fdr simultaneously.
|  | 2020-06-12 | 15:51 | 2020-06-12 | 16:06 | 0:15 | 0 | 15 | [5 empty] | Tripped from Saintala: O/C, B Phase.
|  | 2020-06-15 | 9:30 | 2020-06-15 | 9:33 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala
|  | 2020-06-29 | 11:57 | 2020-06-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Saintala end: Due to Circuit Overloading
|  | 2020-06-29 | 13:27 | 2020-06-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-06-29 | 17:17 | 2020-06-29 | 17:27 | 0:10 | 0 | 10 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-07-04 | 21:24 | 2020-07-04 | 21:27 | 0:03 | 0 | 3 | [5 empty] | Due to LBB Operation at Tushra.
|  | 2020-07-31 | 15:33 | 2020-07-31 | 15:36 | 0:03 | 0 | 3 | [5 empty] | At Bolangir end: O/C, E/F.
|  | 2020-07-31 | 20:36 | 2020-07-31 | 20:38 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-31 | 21:30 | 2020-07-31 | 21:34 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-15 | 14:09 | 2020-07-15 | 14:13 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-15 | 14:23 | 2020-07-15 | 14:26 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala.
|  | 2020-07-17 | 16:16 | 2020-07-17 | 16:20 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 17:08 | 2020-07-21 | 17:12 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 18:15 | 2020-07-21 | 18:20 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 19:10 | 2020-07-21 | 19:30 | 0:20 | 0 | 20 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 0:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 0:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-30 | 09:38 | 2020-07-30 | 09:41 | 0:03 | 0 | 3 | [5 empty] | Trpped at Bolangir due to O/L.
|  | 2020-07-30 | 19:24 | 2020-07-30 | 19:32 | 0:08 | 0 | 8 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 21:39 | 2020-07-30 | 21:45 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 23:00 | 2020-07-30 | 23:06 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala: O/C.
|  | 2020-08-30 | 17:24 | 2020-08-30 | 17:26 | 0:02 | 0 | 2 | [5 empty] | Tripped From Kesinga
|  | 2020-08-30 | 17:33 | 2020-08-30 | 17:35 | 0:02 | 0 | 2 | [5 empty] | Tripped From Kesinga
|  | 2020-08-30 | 18:08 | 2020-08-30 | 18:10 | 0:02 | 0 | 2 | [5 empty] | Tripped From Kesinga
|  | 2020-08-30 | 19:00 | 2020-08-30 | 19:09 | 0:09 | 0 | 9 | [5 empty] | Tripped From Kesinga
|  | 2020-08-12 | 19:38 | 2020-08-12 | 19:43 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala on Over load
|  | 2020-08-17 | 08:24 | 2020-08-17 | 08:26 | 0:02 | 0 | 2 | [5 empty] | Local Breaker Backup (LBB) operation at Tushra Grid.
|  | 2020-08-22 | 21:20 | 2020-08-22 | 21:26 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/L
|  | 2020-08-30 | 22:12 | 2020-08-30 | 22:17 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala
|  | 2020-09-02 | 19:15 | 2020-09-02 | 20:00 | 00:45 | 0 | 45 | [5 empty] | Tripped from saintala [Section isolator insulation punchure]
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 00:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-09-06 | 19:11 | 2020-09-06 | 19:21 | 00:10 | 0 | 10 | [5 empty] | Tripped From ACME
|  | 2020-09-10 | 11:13 | 2020-09-10 | 11:17 | 00:04 | 0 | 4 | [5 empty] | Tripped from Kesinga
|  | 2020-09-12 | 19:16 | 2020-09-12 | 19:18 | 00:02 | 0 | 2 | [5 empty] | Tripped from Tushra
|  | 2020-09-13 | 19:18 | 2020-09-13 | 19:24 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala-Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-13 | 21:44 | 2020-09-13 | 21:50 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala- Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-14 | 20:13 | 2020-09-14 | 20:19 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/C B- Phase due to Ckt overloading
|  | 2020-09-16 | 09:41 | 2020-09-16 | 09:50 | 00:09 | 0 | 9 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-16 | 19:00 | 2020-09-16 | 19:03 | 00:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 20:21 | 2020-09-16 | 20:22 | 00:01 | 0 | 1 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 21:45 | 2020-09-16 | 21:47 | 00:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:32 | 2020-09-17 | 23:34 | 00:02 | 0 | 2 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:17 | 2020-09-17 | 23:19 | 00:02 | 0 | 2 | [5 empty] | DUE TO OVERCURRENT AT LALTIKIRA GRID.
|  | 2020-09-19 | 21:57 | 2020-09-19 | 22:03 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 00:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 00:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-09-28 | 19:12 | 2020-09-28 | 19:14 | 00:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 2020-09-29 | 20:00 | 2020-09-29 | 20:02 | 00:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-24 | 18:43 | 2020-09-24 | 18:52 | 00:09 | 0 | 9 | [5 empty] | Tripped from Saintala-Tripped on E/F R-Phase
|  | 2020-10-01 | 05:23 | 2020-10-01 | 05:36 | 0:13 | 0 | 13 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-04 | 00:20 | 2020-10-04 | 0:24 | 0:04 | 0 | 4 | [5 empty] | Tripped From Saintala-Earth Fault on R-ph
|  | 2020-10-04 | 00:24 | 2020-10-04 | 00:31 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-05 | 21:33 | 2020-10-05 | 21:35 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-06 | 04:04 | 2020-10-06 | 04:10 | 0:06 | 0 | 6 | [5 empty] | Tripped From saintala
|  | 2020-10-07 | 23:07 | 2020-10-07 | 23:09 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-08 | 05:41 | 2020-10-08 | 05:48 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R .
|  | 2020-10-10 | 01:40 | 2020-10-10 | 01:45 | 0:05 | 0 | 5 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-10 | 20:06 | 2020-10-10 | 20:07 | 0:01 | 0 | 1 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-15 | 03:32 | 2020-10-15 | 03:37 | 0:05 | 0 | 5 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-16 | 20:10 | 2020-10-16 | 20:17 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala Grid- Earth Fault on B-Phase
|  | 2020-10-19 | 19:04 | 2020-10-19 | 19:06 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-19 | 20:12 | 2020-10-19 | 20:14 | 0:02 | 0 | 2
|  | 2020-10-21 | 04:52 | 2020-10-21 | 05:01 | 0:09 | 0 | 9 | [5 empty] | DUE TO OVERCURRENT AT TUSHRA GSS ALONG trippedTO 132KV KESINGA B/R ON E/F & 33/132 KV SOLAR B/R trippedON HV E/F.
|  | 2020-10-31 | 23:49 | 2020-10-31 | 23:51 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-31 | 17:30 | 2020-10-31 | 17:34 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-11-11 | 03:13 | 2020-11-11 | 03:32 | 0:19 | 0 | 19 | [5 empty] | Tripped from Bolangir(Lal Tikira)on E/F
|  | 2020-11-18 | 17:49 | 2020-11-18 | 17:52 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-20 | 18:12 | 2020-11-20 | 18:13 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-01 | 03:54 | 2020-11-01 | 04:02 | 0:08 | 0 | 8 | [5 empty] | Tripped From Tushra Grid on E/F
|  | 2020-11-03 | 01:30 | 2020-11-03 | 01:33 | 00:03 | 0 | 3 | [5 empty] | Tripped From Saintala Grid on Over Current B-Ph
|  | 2020-11-28 | 05:32 | 2020-11-28 | 05:39 | 00:07 | 0 | 7 | [5 empty] | Tripped From saintala on O/C R-ph
|  | 2020-11-16 | 16:13 | 2020-11-16 | 16:19 | 01:07 | 1 | 7 | [5 empty] | Tripped from Kesingadue to overloading.
|  | 2020-12-04 | 18:20 | 2020-12-04 | 18:22 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:14 | 2020-12-06 | 17:16 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:47 | 2020-12-06 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:16 | 2020-12-06 | 18:19 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:31 | 2020-12-06 | 18:41 | 0:10 | 0 | 10 | [5 empty] | O/C
|  | 2020-12-06 | 18:54 | 2020-12-06 | 18:57 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-07 | 09:15 | 2020-12-07 | 09:20 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2020-12-28 | 16:38 | 2020-12-28 | 16:50 | 0:12 | 0 | 12 | [5 empty] | O/C
|  | 2020-12-29 | 18:09 | 2020-12-29 | 18:12 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-30 | 16:44 | 2020-12-30 | 16:48 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-31 | 19:05 | 2020-12-31 | 19:09 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 16.12.20 | 17:21 | 16.12.20 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped on O/C R-ph from Saintala end.
|  | 2020-12-22 | 15:21 | 2020-12-22 | 15:25 | 0:04 | 0 | 4 | [5 empty] | Tripped on O/C B-ph from Saintala end.
|  | 2020-12-20 | 18:05 | 2020-12-20 | 18:15 | 0:10 | 0 | 10 | [5 empty] | Tripped From AB solar
|  | 2020-12-21 | 18:54 | 2020-12-21 | 18:58 | 0:04 | 0 | 4 | [5 empty] | Tripped From AB solar
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-01-10 | 07:07 | 2021-01-10 | 07:09 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-11 | 07:22 | 2021-01-11 | 07:24 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-13 | 17:27 | 2021-01-13 | 17:30 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-18 | 18:46 | 2021-01-18 | 18:48 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-18 | 19:31 | 2021-01-18 | 19:33 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 17:57 | 2021-01-15 | 17:59 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 18:17 | 2021-01-15 | 18:19 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-17 | 06:53 | 2021-01-17 | 06:56 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-17 | 17:37 | 2021-01-17 | 17:39 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-21 | 18:19 | 2021-01-21 | 18:20 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-21 | 19:33 | 2021-01-21 | 19:35 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 17:00 | 2021-01-22 | 17:02 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 18:03 | 2021-01-22 | 18:05 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-26 | 18:24 | 2021-01-26 | 18:26 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-27 | 07:24 | 2021-01-27 | 07:27 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-31 | 17:47 | 2021-01-31 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-02-02 | 16:28 | 2021-02-02 | 16:36 | 0:08 | 0 | 8 | [5 empty] | Tripped from Sadeipalli end on overload
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
417 | 132 kV Khariar - Kantabanji |  |  |  |  | 0.66597 | 26 | 27 | [7 empty] | 32.6 | 8760 | 99.7% | 862.27 | 285576
|  | 08.04.20 | 16:28 | 08.04.20 | 16:33 | 0:05 | 0 | 5 | [5 empty] | Tripped on E/F at Bolangir end
|  | 08.04.20 | 16:49 | 08.04.20 | 16:57 | 0:08 | 0 | 8 | [5 empty] | Tripped on E/F at Bolangir end
|  | 24.04.20 | 5:16 | 24.04.20 | 5:23 | 0:07 | 0 | 7 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-05-06 | 5:29 | 2020-05-06 | 5:34 | 0:05 | 0 | 5 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 3:50 | 2020-05-06 | 3:58 | 0:08 | 0 | 8 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-19 | 15:44 | 2020-05-19 | 15:48 | 0:04 | 0 | 4 | [5 empty] | At Khariar-Tripped on Over Current B-Ph Fault
|  | 2020-05-19 | 16:49 | 2020-05-19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Khariar-Tripped on Over Current B-Ph Fault
|  | 2020-05-06 | 10:34 | 2020-05-06 | 10:38 | 0:04 | 0 | 4 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-21 | 15:02 | 2020-05-21 | 15:15 | 0:13 | 0 | 13 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-27 | 21:17 | 2020-05-27 | 21:23 | 0:06 | 0 | 6 | [5 empty] | Due to Over Current B-Ph Fault
|  | 2020-05-29 | 9:51 | 2020-05-29 | 10:57 | 1:06 | 1 | 6 | [5 empty] | At khariar-Tripped due to Due to Over loading at ACME
|  | 2020-05-29 | 11:57 | 2020-05-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Khariar end-Due to Circuit Overloading
|  | 2020-05-29 | 13:27 | 2020-05-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Due to Over Current B-Ph Fault
|  | 2020-05-06 | 0:51 | 2020-05-06 | 1:38 | 0:47 | 0 | 47 | [5 empty] | E/F
|  | 2020-05-07 | 3:45 | 2020-05-07 | 4:03 | 0:18 | 0 | 10 | [5 empty] | Tripped on Over voltage
|  | 2020-05-28 | 16:07 | 2020-05-28 | 16:12 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-05-28 | 16:22 | 2020-05-28 | 16:36 | 0:14 | 0 | 14 | [5 empty] | E/F
|  | 2020-05-29 | 17:17 | 2020-05-29 | 17:24 | 0:07 | 0 | 7
|  | 2020-05-29 | 11:07 | 2020-05-29 | 11:10 | 0:03 | 0 | 3 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-19 | 15:43 | 2020-05-19 | 15:47 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-Tripped
|  | 2020-06-12 | 14:30 | 2020-06-12 | 14:39 | 0:09 | 0 | 9 | [5 empty] | 132kV Kesinga Fdr tripped on E/F, B Phase and caused tripping of Bolangir Fdr simultaneously.
|  | 2020-06-12 | 15:51 | 2020-06-12 | 16:06 | 0:15 | 0 | 15 | [5 empty] | Tripped from Saintala: O/C, B Phase.
|  | 2020-06-15 | 9:30 | 2020-06-15 | 9:33 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala
|  | 2020-06-29 | 11:57 | 2020-06-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Saintala end: Due to Circuit Overloading
|  | 2020-06-29 | 13:27 | 2020-06-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-06-29 | 17:17 | 2020-06-29 | 17:27 | 0:10 | 0 | 10 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-07-04 | 21:24 | 2020-07-04 | 21:27 | 0:03 | 0 | 3 | [5 empty] | Due to LBB Operation at Tushra.
|  | 2020-07-31 | 15:33 | 2020-07-31 | 15:36 | 0:03 | 0 | 3 | [5 empty] | At Bolangir end: O/C, E/F.
|  | 2020-07-31 | 20:36 | 2020-07-31 | 20:38 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-31 | 21:30 | 2020-07-31 | 21:34 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-15 | 14:09 | 2020-07-15 | 14:13 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-15 | 14:23 | 2020-07-15 | 14:26 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala.
|  | 2020-07-17 | 16:16 | 2020-07-17 | 16:20 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 17:08 | 2020-07-21 | 17:12 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 18:15 | 2020-07-21 | 18:20 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 19:10 | 2020-07-21 | 19:30 | 0:20 | 0 | 20 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 0:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 0:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-07-30 | 08:39 | 2020-07-30 | 08:40 | 0:01 | 0 | 1 | [5 empty] | Tripped on directional o/c displayed on back up o/c and e/f relay.
|  | 2020-07-30 | 09:38 | 2020-07-30 | 09:41 | 0:03 | 0 | 3 | [5 empty] | Trpped at Bolangir due to O/L.
|  | 2020-07-30 | 19:24 | 2020-07-30 | 19:32 | 0:08 | 0 | 8 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 21:39 | 2020-07-30 | 21:45 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 23:00 | 2020-07-30 | 23:06 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala: O/C.
|  | 2020-08-12 | 19:38 | 2020-08-12 | 19:43 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala on Over load
|  | 2020-08-17 | 08:24 | 2020-08-17 | 08:26 | 0:02 | 0 | 2 | [5 empty] | Local Breaker Backup (LBB) operation at Tushra Grid.
|  | 2020-08-22 | 21:20 | 2020-08-22 | 21:26 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/L
|  | 2020-08-30 | 22:12 | 2020-08-30 | 22:17 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala
|  | 2020-09-02 | 19:15 | 2020-09-02 | 20:00 | 0:45 | 0 | 45 | [5 empty] | Tripped from saintala [Section isolator insulation punchure]
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-09-06 | 19:11 | 2020-09-06 | 19:21 | 0:10 | 0 | 10 | [5 empty] | Tripped From ACME
|  | 2020-09-10 | 11:13 | 2020-09-10 | 11:17 | 0:04 | 0 | 4 | [5 empty] | Tripped from Kesinga
|  | 2020-09-12 | 19:16 | 2020-09-12 | 19:18 | 0:02 | 0 | 2 | [5 empty] | Tripped from Tushra
|  | 2020-09-13 | 19:18 | 2020-09-13 | 19:24 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala-Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-13 | 21:44 | 2020-09-13 | 21:50 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala- Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-14 | 20:13 | 2020-09-14 | 20:19 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/C B- Phase due to Ckt overloading
|  | 2020-09-16 | 09:41 | 2020-09-16 | 09:50 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-16 | 19:00 | 2020-09-16 | 19:03 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 20:21 | 2020-09-16 | 20:22 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 21:45 | 2020-09-16 | 21:47 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:32 | 2020-09-17 | 23:34 | 0:02 | 0 | 2 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:17 | 2020-09-17 | 23:19 | 0:02 | 0 | 2 | [5 empty] | DUE TO OVERCURRENT AT LALTIKIRA GRID.
|  | 2020-09-19 | 21:57 | 2020-09-19 | 22:03 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 0:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-09-28 | 19:12 | 2020-09-28 | 19:14 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 2020-09-29 | 20:00 | 2020-09-29 | 20:02 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-24 | 18:43 | 2020-09-24 | 18:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala-Tripped on E/F R-Phase
|  | 2020-10-01 | 05:23 | 2020-10-01 | 05:36 | 0:13 | 0 | 13 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-04 | 00:20 | 2020-10-04 | 0:24 | 0:04 | 0 | 4 | [5 empty] | Tripped From Saintala-Earth Fault on R-ph
|  | 2020-10-04 | 00:24 | 2020-10-04 | 00:31 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-05 | 21:33 | 2020-10-05 | 21:35 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-06 | 04:04 | 2020-10-06 | 04:10 | 0:06 | 0 | 6 | [5 empty] | Tripped From saintala
|  | 2020-10-07 | 23:07 | 2020-10-07 | 23:09 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-08 | 05:41 | 2020-10-08 | 05:48 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R .
|  | 2020-10-10 | 01:40 | 2020-10-10 | 01:45 | 0:05 | 0 | 5 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-10 | 20:06 | 2020-10-10 | 20:07 | 0:01 | 0 | 1 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-15 | 03:32 | 2020-10-15 | 03:37 | 0:05 | 0 | 5 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-16 | 20:10 | 2020-10-16 | 20:17 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala Grid- Earth Fault on B-Phase
|  | 2020-10-19 | 19:04 | 2020-10-19 | 19:06 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-19 | 20:12 | 2020-10-19 | 20:14 | 0:02 | 0 | 2
|  | 2020-10-21 | 04:52 | 2020-10-21 | 05:01 | 0:09 | 0 | 9 | [5 empty] | DUE TO OVERCURRENT AT TUSHRA GSS ALONG trippedTO 132KV KESINGA B/R ON E/F & 33/132 KV SOLAR B/R trippedON HV E/F.
|  | 2020-10-31 | 23:49 | 2020-10-31 | 23:51 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-31 | 17:30 | 2020-10-31 | 17:34 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-11-11 | 03:13 | 2020-11-11 | 03:32 | 0:19 | 0 | 19 | [5 empty] | Tripped from Bolangir(Lal Tikira)on E/F
|  | 2020-11-18 | 17:49 | 2020-11-18 | 17:52 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-20 | 18:12 | 2020-11-20 | 18:13 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-01 | 03:54 | 2020-11-01 | 04:02 | 0:08 | 0 | 8 | [5 empty] | Tripped From Tushra Grid on E/F
|  | 2020-11-03 | 01:30 | 2020-11-03 | 01:33 | 00:03 | 0 | 3 | [5 empty] | Tripped From Saintala Grid on Over Current B-Ph
|  | 2020-11-28 | 05:32 | 2020-11-28 | 05:39 | 00:07 | 0 | 7 | [5 empty] | Tripped From saintala on O/C R-ph
|  | 2020-11-16 | 16:13 | 2020-11-16 | 16:19 | 01:07 | 1 | 7 | [5 empty] | Tripped from Kesingadue to overloading.
|  | 2020-12-04 | 18:20 | 2020-12-04 | 18:22 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:14 | 2020-12-06 | 17:16 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:47 | 2020-12-06 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:16 | 2020-12-06 | 18:19 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:31 | 2020-12-06 | 18:41 | 0:10 | 0 | 10 | [5 empty] | O/C
|  | 2020-12-06 | 18:54 | 2020-12-06 | 18:57 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-07 | 09:15 | 2020-12-07 | 09:20 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2020-12-28 | 16:38 | 2020-12-28 | 16:50 | 0:12 | 0 | 12 | [5 empty] | O/C
|  | 2020-12-29 | 18:09 | 2020-12-29 | 18:12 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-30 | 16:44 | 2020-12-30 | 16:48 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-31 | 19:05 | 2020-12-31 | 19:09 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 16.12.20 | 17:21 | 16.12.20 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped on O/C R-ph from Saintala end.
|  | 2020-12-22 | 15:21 | 2020-12-22 | 15:25 | 0:04 | 0 | 4 | [5 empty] | Tripped on O/C B-ph from Saintala end.
|  | 2020-12-20 | 18:05 | 2020-12-20 | 18:15 | 0:10 | 0 | 10 | [5 empty] | Tripped From AB solar
|  | 2020-12-21 | 18:54 | 2020-12-21 | 18:58 | 0:04 | 0 | 4 | [5 empty] | Tripped From AB solar
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-01-10 | 07:07 | 2021-01-10 | 07:09 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-11 | 07:22 | 2021-01-11 | 07:24 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-13 | 17:27 | 2021-01-13 | 17:30 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-18 | 18:46 | 2021-01-18 | 18:48 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-18 | 19:31 | 2021-01-18 | 19:33 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 17:57 | 2021-01-15 | 17:59 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 18:17 | 2021-01-15 | 18:19 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-17 | 06:53 | 2021-01-17 | 06:56 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-17 | 17:37 | 2021-01-17 | 17:39 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-21 | 18:19 | 2021-01-21 | 18:20 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-21 | 19:33 | 2021-01-21 | 19:35 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 17:00 | 2021-01-22 | 17:02 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 18:03 | 2021-01-22 | 18:05 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-26 | 18:24 | 2021-01-26 | 18:26 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-27 | 07:24 | 2021-01-27 | 07:27 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-31 | 17:47 | 2021-01-31 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-02-02 | 16:28 | 2021-02-02 | 16:36 | 0:08 | 0 | 8 | [5 empty] | Tripped from Sadeipalli end on overload
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
418 | 132kV Kantabanji- Kantabanji Traction |  |  |  |  | 0.67153 | 26 | 35 | [7 empty] | 4 | 8760 | 99.7% | 106.3333 | 35040
|  | 08.04.20 | 16:28 | 08.04.20 | 16:33 | 0:05 | 0 | 5 | [5 empty] | Tripped on E/F at Bolangir end
|  | 08.04.20 | 16:49 | 08.04.20 | 16:57 | 0:08 | 0 | 8 | [5 empty] | Tripped on E/F at Bolangir end
|  | 24.04.20 | 5:16 | 24.04.20 | 5:23 | 0:07 | 0 | 7 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-05-06 | 5:29 | 2020-05-06 | 5:34 | 0:05 | 0 | 5 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 3:50 | 2020-05-06 | 3:58 | 0:08 | 0 | 8 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-19 | 15:44 | 2020-05-19 | 15:48 | 0:04 | 0 | 4 | [5 empty] | At Khariar-Tripped on Over Current B-Ph Fault
|  | 2020-05-19 | 16:49 | 2020-05-19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Khariar-Tripped on Over Current B-Ph Fault
|  | 2020-05-06 | 10:34 | 2020-05-06 | 10:38 | 0:04 | 0 | 4 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-21 | 15:02 | 2020-05-21 | 15:15 | 0:13 | 0 | 13 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-27 | 21:17 | 2020-05-27 | 21:23 | 0:06 | 0 | 6 | [5 empty] | Due to Over Current B-Ph Fault
|  | 2020-05-29 | 9:51 | 2020-05-29 | 10:57 | 1:06 | 1 | 6 | [5 empty] | At khariar-Tripped due to Due to Over loading at ACME
|  | 2020-05-29 | 11:57 | 2020-05-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Khariar end-Due to Circuit Overloading
|  | 2020-05-29 | 13:27 | 2020-05-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Due to Over Current B-Ph Fault
|  | 2020-05-06 | 0:51 | 2020-05-06 | 1:38 | 0:47 | 0 | 47 | [5 empty] | E/F
|  | 2020-05-07 | 3:45 | 2020-05-07 | 4:03 | 0:18 | 0 | 10 | [5 empty] | Tripped on Over voltage
|  | 2020-05-28 | 16:07 | 2020-05-28 | 16:12 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-05-28 | 16:22 | 2020-05-28 | 16:36 | 0:14 | 0 | 14 | [5 empty] | E/F
|  | 2020-05-29 | 17:17 | 2020-05-29 | 17:24 | 0:07 | 0 | 7
|  | 2020-05-29 | 11:07 | 2020-05-29 | 11:10 | 0:03 | 0 | 3 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-19 | 15:43 | 2020-05-19 | 15:47 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-Tripped
|  | 2020-06-12 | 14:30 | 2020-06-12 | 14:39 | 0:09 | 0 | 9 | [5 empty] | 132kV Kesinga Fdr tripped on E/F, B Phase and caused tripping of Bolangir Fdr simultaneously.
|  | 2020-06-12 | 15:51 | 2020-06-12 | 16:06 | 0:15 | 0 | 15 | [5 empty] | Tripped from Saintala: O/C, B Phase.
|  | 2020-06-15 | 9:30 | 2020-06-15 | 9:33 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala
|  | 2020-06-29 | 11:57 | 2020-06-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Saintala end: Due to Circuit Overloading
|  | 2020-06-29 | 13:27 | 2020-06-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-06-29 | 17:17 | 2020-06-29 | 17:27 | 0:10 | 0 | 10 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-07-04 | 21:24 | 2020-07-04 | 21:27 | 0:03 | 0 | 3 | [5 empty] | Due to LBB Operation at Tushra.
|  | 2020-07-31 | 15:33 | 2020-07-31 | 15:36 | 0:03 | 0 | 3 | [5 empty] | At Bolangir end: O/C, E/F.
|  | 2020-07-31 | 20:36 | 2020-07-31 | 20:38 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-31 | 21:30 | 2020-07-31 | 21:34 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-15 | 14:09 | 2020-07-15 | 14:13 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-15 | 14:23 | 2020-07-15 | 14:26 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala.
|  | 2020-07-17 | 16:16 | 2020-07-17 | 16:20 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 17:08 | 2020-07-21 | 17:12 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 18:15 | 2020-07-21 | 18:20 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 19:10 | 2020-07-21 | 19:30 | 0:20 | 0 | 20 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 0:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 0:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-07-30 | 08:39 | 2020-07-30 | 08:40 | 0:01 | 0 | 1 | [5 empty] | Tripped on directional o/c displayed on back up o/c and e/f relay.
|  | 2020-07-30 | 09:38 | 2020-07-30 | 09:41 | 0:03 | 0 | 3 | [5 empty] | Trpped at Bolangir due to O/L.
|  | 2020-07-30 | 19:24 | 2020-07-30 | 19:32 | 0:08 | 0 | 8 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 21:39 | 2020-07-30 | 21:45 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 23:00 | 2020-07-30 | 23:06 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala: O/C.
|  | 2020-08-12 | 19:38 | 2020-08-12 | 19:43 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala on Over load
|  | 2020-08-17 | 08:24 | 2020-08-17 | 08:26 | 0:02 | 0 | 2 | [5 empty] | Local Breaker Backup (LBB) operation at Tushra Grid.
|  | 2020-08-22 | 21:20 | 2020-08-22 | 21:26 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/L
|  | 2020-08-30 | 22:12 | 2020-08-30 | 22:17 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala
|  | 2020-09-02 | 19:15 | 2020-09-02 | 20:00 | 0:45 | 0 | 45 | [5 empty] | Tripped from saintala [Section isolator insulation punchure]
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-09-06 | 19:11 | 2020-09-06 | 19:21 | 0:10 | 0 | 10 | [5 empty] | Tripped From ACME
|  | 2020-09-10 | 11:13 | 2020-09-10 | 11:17 | 0:04 | 0 | 4 | [5 empty] | Tripped from Kesinga
|  | 2020-09-12 | 19:16 | 2020-09-12 | 19:18 | 0:02 | 0 | 2 | [5 empty] | Tripped from Tushra
|  | 2020-09-13 | 19:18 | 2020-09-13 | 19:24 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala-Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-13 | 21:44 | 2020-09-13 | 21:50 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala- Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-14 | 20:13 | 2020-09-14 | 20:19 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/C B- Phase due to Ckt overloading
|  | 2020-09-16 | 09:41 | 2020-09-16 | 09:50 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-16 | 19:00 | 2020-09-16 | 19:03 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 20:21 | 2020-09-16 | 20:22 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 21:45 | 2020-09-16 | 21:47 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:32 | 2020-09-17 | 23:34 | 0:02 | 0 | 2 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:17 | 2020-09-17 | 23:19 | 0:02 | 0 | 2 | [5 empty] | DUE TO OVERCURRENT AT LALTIKIRA GRID.
|  | 2020-09-19 | 21:57 | 2020-09-19 | 22:03 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 0:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-09-28 | 19:12 | 2020-09-28 | 19:14 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 2020-09-29 | 20:00 | 2020-09-29 | 20:02 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-24 | 18:43 | 2020-09-24 | 18:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala-Tripped on E/F R-Phase
|  | 2020-10-01 | 05:23 | 2020-10-01 | 05:36 | 0:13 | 0 | 13 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-04 | 00:20 | 2020-10-04 | 0:24 | 0:04 | 0 | 4 | [5 empty] | Tripped From Saintala-Earth Fault on R-ph
|  | 2020-10-04 | 00:24 | 2020-10-04 | 00:31 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-05 | 21:33 | 2020-10-05 | 21:35 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-06 | 04:04 | 2020-10-06 | 04:10 | 0:06 | 0 | 6 | [5 empty] | Tripped From saintala
|  | 2020-10-07 | 23:07 | 2020-10-07 | 23:09 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-08 | 05:41 | 2020-10-08 | 05:48 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R .
|  | 2020-10-10 | 01:40 | 2020-10-10 | 01:45 | 0:05 | 0 | 5 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-10 | 20:06 | 2020-10-10 | 20:07 | 0:01 | 0 | 1 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-15 | 03:32 | 2020-10-15 | 03:37 | 0:05 | 0 | 5 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-16 | 20:10 | 2020-10-16 | 20:17 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala Grid- Earth Fault on B-Phase
|  | 2020-10-19 | 19:04 | 2020-10-19 | 19:06 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-19 | 20:12 | 2020-10-19 | 20:14 | 0:02 | 0 | 2
|  | 2020-10-21 | 04:52 | 2020-10-21 | 05:01 | 0:09 | 0 | 9 | [5 empty] | DUE TO OVERCURRENT AT TUSHRA GSS ALONG trippedTO 132KV KESINGA B/R ON E/F & 33/132 KV SOLAR B/R trippedON HV E/F.
|  | 2020-10-31 | 23:49 | 2020-10-31 | 23:51 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-31 | 17:30 | 2020-10-31 | 17:34 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-11-11 | 03:13 | 2020-11-11 | 03:32 | 0:19 | 0 | 19 | [5 empty] | Tripped from Bolangir(Lal Tikira)on E/F
|  | 2020-11-18 | 17:49 | 2020-11-18 | 17:52 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-20 | 18:12 | 2020-11-20 | 18:13 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-01 | 03:54 | 2020-11-01 | 04:02 | 0:08 | 0 | 8 | [5 empty] | Tripped From Tushra Grid on E/F
|  | 2020-11-03 | 01:30 | 2020-11-03 | 01:33 | 00:03 | 0 | 3 | [5 empty] | Tripped From Saintala Grid on Over Current B-Ph
|  | 2020-11-28 | 05:32 | 2020-11-28 | 05:39 | 00:07 | 0 | 7 | [5 empty] | Tripped From saintala on O/C R-ph
|  | 2020-11-16 | 16:13 | 2020-11-16 | 16:19 | 01:07 | 1 | 7 | [5 empty] | Tripped from Kesingadue to overloading.
|  | 2020-12-04 | 18:20 | 2020-12-04 | 18:22 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:14 | 2020-12-06 | 17:16 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:47 | 2020-12-06 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:16 | 2020-12-06 | 18:19 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:31 | 2020-12-06 | 18:41 | 0:10 | 0 | 10 | [5 empty] | O/C
|  | 2020-12-06 | 18:54 | 2020-12-06 | 18:57 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-07 | 09:15 | 2020-12-07 | 09:20 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2020-12-28 | 16:38 | 2020-12-28 | 16:50 | 0:12 | 0 | 12 | [5 empty] | O/C
|  | 2020-12-29 | 18:09 | 2020-12-29 | 18:12 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-30 | 16:44 | 2020-12-30 | 16:48 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-31 | 19:05 | 2020-12-31 | 19:09 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 16.12.20 | 17:21 | 16.12.20 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped on O/C R-ph from Saintala end.
|  | 2020-12-22 | 15:21 | 2020-12-22 | 15:25 | 0:04 | 0 | 4 | [5 empty] | Tripped on O/C B-ph from Saintala end.
|  | 2020-12-20 | 18:05 | 2020-12-20 | 18:15 | 0:10 | 0 | 10 | [5 empty] | Tripped From AB solar
|  | 2020-12-21 | 18:54 | 2020-12-21 | 18:58 | 0:04 | 0 | 4 | [5 empty] | Tripped From AB solar
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-01-12 | 00:45 | 2021-01-12 | 00:50 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2021-01-12 | 04:00 | 2021-01-12 | 04:03 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-10 | 07:07 | 2021-01-10 | 07:09 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-11 | 07:22 | 2021-01-11 | 07:24 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-13 | 17:27 | 2021-01-13 | 17:30 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-18 | 18:46 | 2021-01-18 | 18:48 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-18 | 19:31 | 2021-01-18 | 19:33 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 17:57 | 2021-01-15 | 17:59 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 18:17 | 2021-01-15 | 18:19 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-17 | 06:53 | 2021-01-17 | 06:56 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-17 | 17:37 | 2021-01-17 | 17:39 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-21 | 18:19 | 2021-01-21 | 18:20 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-21 | 19:33 | 2021-01-21 | 19:35 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 17:00 | 2021-01-22 | 17:02 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 18:03 | 2021-01-22 | 18:05 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-26 | 18:24 | 2021-01-26 | 18:26 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-27 | 07:24 | 2021-01-27 | 07:27 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-31 | 17:47 | 2021-01-31 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-02-02 | 16:28 | 2021-02-02 | 16:36 | 0:08 | 0 | 8 | [5 empty] | Tripped from Sadeipalli end on overload
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
419 | 132 kV Khariar - Nuapara |  |  |  |  | 0.68542 | 27 | 10 | [7 empty] | 76.43 | 8760 | 99.69% | 2076.3483 | 669526.8
|  | 08.04.20 | 16:28 | 08.04.20 | 16:33 | 0:05 | 0 | 5 | [5 empty] | Tripped on E/F at Bolangir end
|  | 08.04.20 | 16:49 | 08.04.20 | 16:57 | 0:08 | 0 | 8 | [5 empty] | Tripped on E/F at Bolangir end
|  | 24.04.20 | 5:16 | 24.04.20 | 5:23 | 0:07 | 0 | 7 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-05-06 | 5:29 | 2020-05-06 | 5:34 | 0:05 | 0 | 5 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 3:50 | 2020-05-06 | 3:58 | 0:08 | 0 | 8 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-19 | 15:44 | 2020-05-19 | 15:48 | 0:04 | 0 | 4 | [5 empty] | At Khariar-Tripped on Over Current B-Ph Fault
|  | 2020-05-19 | 16:49 | 2020-05-19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Khariar-Tripped on Over Current B-Ph Fault
|  | 2020-05-06 | 10:34 | 2020-05-06 | 10:38 | 0:04 | 0 | 4 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-21 | 15:02 | 2020-05-21 | 15:15 | 0:13 | 0 | 13 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-27 | 21:17 | 2020-05-27 | 21:23 | 0:06 | 0 | 6 | [5 empty] | Due to Over Current B-Ph Fault
|  | 2020-05-29 | 9:51 | 2020-05-29 | 10:57 | 1:06 | 1 | 6 | [5 empty] | At khariar-Tripped due to Due to Over loading at ACME
|  | 2020-05-29 | 11:57 | 2020-05-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Khariar end-Due to Circuit Overloading
|  | 2020-05-29 | 13:27 | 2020-05-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Due to Over Current B-Ph Fault
|  | 2020-05-06 | 0:51 | 2020-05-06 | 1:38 | 0:47 | 0 | 47 | [5 empty] | E/F
|  | 2020-05-07 | 3:45 | 2020-05-07 | 4:03 | 0:18 | 0 | 10 | [5 empty] | Tripped on Over voltage
|  | 2020-05-28 | 16:07 | 2020-05-28 | 16:12 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-05-28 | 16:22 | 2020-05-28 | 16:36 | 0:14 | 0 | 14 | [5 empty] | E/F
|  | 2020-05-29 | 17:17 | 2020-05-29 | 17:24 | 0:07 | 0 | 7
|  | 2020-05-29 | 11:07 | 2020-05-29 | 11:10 | 0:03 | 0 | 3 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-19 | 15:43 | 2020-05-19 | 15:47 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-Tripped
|  | 2020-06-12 | 14:30 | 2020-06-12 | 14:39 | 0:09 | 0 | 9 | [5 empty] | 132kV Kesinga Fdr tripped on E/F, B Phase and caused tripping of Bolangir Fdr simultaneously.
|  | 2020-06-12 | 15:51 | 2020-06-12 | 16:06 | 0:15 | 0 | 15 | [5 empty] | Tripped from Saintala: O/C, B Phase.
|  | 2020-06-15 | 9:30 | 2020-06-15 | 9:33 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala
|  | 2020-06-29 | 11:57 | 2020-06-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Saintala end: Due to Circuit Overloading
|  | 2020-06-29 | 13:27 | 2020-06-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-06-29 | 17:17 | 2020-06-29 | 17:27 | 0:10 | 0 | 10 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-07-04 | 21:24 | 2020-07-04 | 21:27 | 0:03 | 0 | 3 | [5 empty] | Due to LBB Operation at Tushra.
|  | 2020-07-31 | 15:33 | 2020-07-31 | 15:36 | 0:03 | 0 | 3 | [5 empty] | At Bolangir end: O/C, E/F.
|  | 2020-07-31 | 20:36 | 2020-07-31 | 20:38 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-31 | 21:30 | 2020-07-31 | 21:34 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-15 | 14:09 | 2020-07-15 | 14:13 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-15 | 14:23 | 2020-07-15 | 14:26 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala.
|  | 2020-07-17 | 16:16 | 2020-07-17 | 16:20 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 17:08 | 2020-07-21 | 17:12 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 18:15 | 2020-07-21 | 18:20 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 19:10 | 2020-07-21 | 19:30 | 0:20 | 0 | 20 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 0:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 0:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-07-30 | 08:39 | 2020-07-30 | 08:40 | 0:01 | 0 | 1 | [5 empty] | Tripped on directional o/c displayed on back up o/c and e/f relay.
|  | 2020-07-30 | 09:38 | 2020-07-30 | 09:41 | 0:03 | 0 | 3 | [5 empty] | Trpped at Bolangir due to O/L.
|  | 2020-07-30 | 19:24 | 2020-07-30 | 19:32 | 0:08 | 0 | 8 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 20:59 | 2020-07-30 | 21:14 | 00:15 | 0 | 15 | [5 empty] | At Khariar end: O/C, Y Phase.
|  | 2020-07-30 | 21:39 | 2020-07-30 | 21:45 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 23:00 | 2020-07-30 | 23:06 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala: O/C.
|  | 2020-08-16 | 20:12 | 2020-08-16 | 20:20 | 0:08 | 0 | 8 | [5 empty] | Tripped from Khariar Tripped on Overcurrent on R-phase
|  | 2020-08-30 | 17:24 | 2020-08-30 | 17:26 | 0:02 | 0 | 2 | [5 empty] | Tripped From Kesinga
|  | 2020-08-30 | 17:33 | 2020-08-30 | 17:35 | 0:02 | 0 | 2 | [5 empty] | Tripped From Kesinga
|  | 2020-08-30 | 18:08 | 2020-08-30 | 18:10 | 0:02 | 0 | 2 | [5 empty] | Tripped From Kesinga
|  | 2020-08-30 | 19:00 | 2020-08-30 | 19:09 | 0:09 | 0 | 9 | [5 empty] | Tripped From Kesinga
|  | 2020-08-12 | 19:38 | 2020-08-12 | 19:43 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala on Over load
|  | 2020-08-17 | 08:24 | 2020-08-17 | 08:26 | 0:02 | 0 | 2 | [5 empty] | Local Breaker Backup (LBB) operation at Tushra Grid.
|  | 2020-08-22 | 21:20 | 2020-08-22 | 21:26 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/L
|  | 2020-08-30 | 22:12 | 2020-08-30 | 22:17 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala
|  | 2020-09-02 | 19:15 | 2020-09-02 | 20:00 | 0:45 | 0 | 45 | [5 empty] | Tripped from saintala [Section isolator insulation punchure]
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-09-06 | 19:11 | 2020-09-06 | 19:21 | 0:10 | 0 | 10 | [5 empty] | Tripped From ACME
|  | 2020-09-10 | 09:50 | 2020-09-10 | 09:55 | 0:05 | 0 | 5 | [5 empty] | Tripped from Khariar
|  | 2020-09-10 | 11:13 | 2020-09-10 | 11:17 | 0:04 | 0 | 4 | [5 empty] | Tripped from Kesinga
|  | 2020-09-12 | 19:16 | 2020-09-12 | 19:18 | 0:02 | 0 | 2 | [5 empty] | Tripped from Tushra
|  | 2020-09-13 | 19:18 | 2020-09-13 | 19:24 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala-Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-13 | 21:44 | 2020-09-13 | 21:50 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala- Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-14 | 20:13 | 2020-09-14 | 20:19 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/C B- Phase due to Ckt overloading
|  | 2020-09-16 | 09:41 | 2020-09-16 | 09:50 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-16 | 19:00 | 2020-09-16 | 19:03 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 20:21 | 2020-09-16 | 20:22 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 21:45 | 2020-09-16 | 21:47 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:32 | 2020-09-17 | 23:34 | 0:02 | 0 | 2 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:17 | 2020-09-17 | 23:19 | 0:02 | 0 | 2 | [5 empty] | DUE TO OVERCURRENT AT LALTIKIRA GRID.
|  | 2020-09-19 | 21:57 | 2020-09-19 | 22:03 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 0:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-09-28 | 19:12 | 2020-09-28 | 19:14 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 2020-09-29 | 20:00 | 2020-09-29 | 20:02 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-24 | 18:43 | 2020-09-24 | 18:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala-Tripped on E/F R-Phase
|  | 2020-10-01 | 05:23 | 2020-10-01 | 05:36 | 0:13 | 0 | 13 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-04 | 00:20 | 2020-10-04 | 0:24 | 0:04 | 0 | 4 | [5 empty] | Tripped From Saintala-Earth Fault on R-ph
|  | 2020-10-04 | 00:24 | 2020-10-04 | 00:31 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-05 | 21:33 | 2020-10-05 | 21:35 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-06 | 04:04 | 2020-10-06 | 04:10 | 0:06 | 0 | 6 | [5 empty] | Tripped From saintala
|  | 2020-10-07 | 23:07 | 2020-10-07 | 23:09 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-08 | 05:41 | 2020-10-08 | 05:48 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R .
|  | 2020-10-10 | 01:40 | 2020-10-10 | 01:45 | 0:05 | 0 | 5 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-10 | 20:06 | 2020-10-10 | 20:07 | 0:01 | 0 | 1 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-15 | 03:32 | 2020-10-15 | 03:37 | 0:05 | 0 | 5 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-16 | 20:10 | 2020-10-16 | 20:17 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala Grid- Earth Fault on B-Phase
|  | 2020-10-19 | 19:04 | 2020-10-19 | 19:06 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-19 | 20:12 | 2020-10-19 | 20:14 | 0:02 | 0 | 2
|  | 2020-10-21 | 04:52 | 2020-10-21 | 05:01 | 0:09 | 0 | 9 | [5 empty] | DUE TO OVERCURRENT AT TUSHRA GSS ALONG trippedTO 132KV KESINGA B/R ON E/F & 33/132 KV SOLAR B/R trippedON HV E/F.
|  | 2020-10-31 | 23:49 | 2020-10-31 | 23:51 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-31 | 17:30 | 2020-10-31 | 17:34 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-11-11 | 03:13 | 2020-11-11 | 03:32 | 0:19 | 0 | 19 | [5 empty] | Tripped from Bolangir(Lal Tikira)on E/F
|  | 2020-11-18 | 17:49 | 2020-11-18 | 17:52 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-20 | 18:12 | 2020-11-20 | 18:13 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-01 | 03:54 | 2020-11-01 | 04:02 | 0:08 | 0 | 8 | [5 empty] | Tripped From Tushra Grid on E/F
|  | 2020-11-03 | 01:30 | 2020-11-03 | 01:33 | 00:03 | 0 | 3 | [5 empty] | Tripped From Saintala Grid on Over Current B-Ph
|  | 2020-11-28 | 05:32 | 2020-11-28 | 05:39 | 00:07 | 0 | 7 | [5 empty] | Tripped From saintala on O/C R-ph
|  | 2020-11-16 | 16:13 | 2020-11-16 | 16:19 | 01:07 | 1 | 7 | [5 empty] | Tripped from Kesingadue to overloading.
|  | 2020-12-04 | 18:20 | 2020-12-04 | 18:22 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:14 | 2020-12-06 | 17:16 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:47 | 2020-12-06 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:16 | 2020-12-06 | 18:19 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:31 | 2020-12-06 | 18:41 | 0:10 | 0 | 10 | [5 empty] | O/C
|  | 2020-12-06 | 18:54 | 2020-12-06 | 18:57 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-07 | 09:15 | 2020-12-07 | 09:20 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2020-12-28 | 16:38 | 2020-12-28 | 16:50 | 0:12 | 0 | 12 | [5 empty] | O/C
|  | 2020-12-29 | 18:09 | 2020-12-29 | 18:12 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-30 | 16:44 | 2020-12-30 | 16:48 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-31 | 19:05 | 2020-12-31 | 19:09 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 16.12.20 | 17:21 | 16.12.20 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped on O/C R-ph from Saintala end.
|  | 2020-12-22 | 15:21 | 2020-12-22 | 15:25 | 0:04 | 0 | 4 | [5 empty] | Tripped on O/C B-ph from Saintala end.
|  | 2020-12-20 | 18:05 | 2020-12-20 | 18:15 | 0:10 | 0 | 10 | [5 empty] | Tripped From AB solar
|  | 2020-12-21 | 18:54 | 2020-12-21 | 18:58 | 0:04 | 0 | 4 | [5 empty] | Tripped From AB solar
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-01-10 | 07:07 | 2021-01-10 | 07:09 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-11 | 07:22 | 2021-01-11 | 07:24 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-13 | 17:27 | 2021-01-13 | 17:30 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-18 | 18:46 | 2021-01-18 | 18:48 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-18 | 19:31 | 2021-01-18 | 19:33 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 17:57 | 2021-01-15 | 17:59 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 18:17 | 2021-01-15 | 18:19 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-17 | 06:53 | 2021-01-17 | 06:56 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-17 | 17:37 | 2021-01-17 | 17:39 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-21 | 18:19 | 2021-01-21 | 18:20 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-21 | 19:33 | 2021-01-21 | 19:35 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 17:00 | 2021-01-22 | 17:02 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 18:03 | 2021-01-22 | 18:05 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-26 | 18:24 | 2021-01-26 | 18:26 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-27 | 07:24 | 2021-01-27 | 07:27 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-31 | 17:47 | 2021-01-31 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-02-02 | 16:28 | 2021-02-02 | 16:36 | 0:08 | 0 | 8 | [5 empty] | Tripped from Sadeipalli end on overload
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
420 | 132kV Nuapara-Nuapara RTSS |  |  |  |  | 0.68542 | 27 | 10 | [7 empty] | 4.528 | 8760 | 99.69% | 123.0107 | 39665.28
|  | 08.04.20 | 16:28 | 08.04.20 | 16:33 | 0:05 | 0 | 5 | [5 empty] | Tripped on E/F at Bolangir end
|  | 08.04.20 | 16:49 | 08.04.20 | 16:57 | 0:08 | 0 | 8 | [5 empty] | Tripped on E/F at Bolangir end
|  | 24.04.20 | 5:16 | 24.04.20 | 5:23 | 0:07 | 0 | 7 | [5 empty] | P/S failed from Bolangir New end
|  | 2020-05-06 | 5:29 | 2020-05-06 | 5:34 | 0:05 | 0 | 5 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-06 | 3:50 | 2020-05-06 | 3:58 | 0:08 | 0 | 8 | [5 empty] | At Therubali-Tripped Tripped at Kesinga- on Overload
|  | 2020-05-19 | 15:44 | 2020-05-19 | 15:48 | 0:04 | 0 | 4 | [5 empty] | At Khariar-Tripped on Over Current B-Ph Fault
|  | 2020-05-19 | 16:49 | 2020-05-19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Khariar-Tripped on Over Current B-Ph Fault
|  | 2020-05-06 | 10:34 | 2020-05-06 | 10:38 | 0:04 | 0 | 4 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-21 | 15:02 | 2020-05-21 | 15:15 | 0:13 | 0 | 13 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-27 | 21:17 | 2020-05-27 | 21:23 | 0:06 | 0 | 6 | [5 empty] | Due to Over Current B-Ph Fault
|  | 2020-05-29 | 9:51 | 2020-05-29 | 10:57 | 1:06 | 1 | 6 | [5 empty] | At khariar-Tripped due to Due to Over loading at ACME
|  | 2020-05-29 | 11:57 | 2020-05-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Khariar end-Due to Circuit Overloading
|  | 2020-05-29 | 13:27 | 2020-05-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Due to Over Current B-Ph Fault
|  | 2020-05-06 | 0:51 | 2020-05-06 | 1:38 | 0:47 | 0 | 47 | [5 empty] | E/F
|  | 2020-05-07 | 3:45 | 2020-05-07 | 4:03 | 0:18 | 0 | 10 | [5 empty] | Tripped on Over voltage
|  | 2020-05-28 | 16:07 | 2020-05-28 | 16:12 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 2020-05-28 | 16:22 | 2020-05-28 | 16:36 | 0:14 | 0 | 14 | [5 empty] | E/F
|  | 2020-05-29 | 17:17 | 2020-05-29 | 17:24 | 0:07 | 0 | 7
|  | 2020-05-29 | 11:07 | 2020-05-29 | 11:10 | 0:03 | 0 | 3 | [5 empty] | Due to Circuit Overloading
|  | 2020-05-19 | 15:43 | 2020-05-19 | 15:47 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-Tripped
|  | 2020-06-12 | 14:30 | 2020-06-12 | 14:39 | 0:09 | 0 | 9 | [5 empty] | 132kV Kesinga Fdr tripped on E/F, B Phase and caused tripping of Bolangir Fdr simultaneously.
|  | 2020-06-12 | 15:51 | 2020-06-12 | 16:06 | 0:15 | 0 | 15 | [5 empty] | Tripped from Saintala: O/C, B Phase.
|  | 2020-06-15 | 9:30 | 2020-06-15 | 9:33 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala
|  | 2020-06-29 | 11:57 | 2020-06-29 | 12:02 | 0:05 | 0 | 5 | [5 empty] | Tripped at Saintala end: Due to Circuit Overloading
|  | 2020-06-29 | 13:27 | 2020-06-29 | 13:31 | 0:04 | 0 | 4 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-06-29 | 17:17 | 2020-06-29 | 17:27 | 0:10 | 0 | 10 | [5 empty] | Tripped at Saintala end: Due to Over Current B-Ph Fault
|  | 2020-07-04 | 21:24 | 2020-07-04 | 21:27 | 0:03 | 0 | 3 | [5 empty] | Due to LBB Operation at Tushra.
|  | 2020-07-31 | 15:33 | 2020-07-31 | 15:36 | 0:03 | 0 | 3 | [5 empty] | At Bolangir end: O/C, E/F.
|  | 2020-07-31 | 20:36 | 2020-07-31 | 20:38 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-31 | 21:30 | 2020-07-31 | 21:34 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-15 | 14:09 | 2020-07-15 | 14:13 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-15 | 14:23 | 2020-07-15 | 14:26 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-16 | 14:08 | 2020-07-16 | 14:12 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala.
|  | 2020-07-17 | 16:16 | 2020-07-17 | 16:20 | 0:04 | 0 | 4 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 17:08 | 2020-07-21 | 17:12 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 18:15 | 2020-07-21 | 18:20 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 19:10 | 2020-07-21 | 19:30 | 0:20 | 0 | 20 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-21 | 17:39 | 2020-07-21 | 17:45 | 0:06 | 0 | 6 | [5 empty] | At Bolangir end: E/F.
|  | 2020-07-21 | 19:06 | 2020-07-21 | 19:14 | 0:08 | 0 | 8 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-21 | 19:17 | 2020-07-21 | 19:19 | 0:02 | 0 | 2 | [5 empty] | At Bolangir end: O/C.
|  | 2020-07-29 | 15:19 | 2020-07-29 | 15:22 | 0:03 | 0 | 3 | [5 empty] | Tripped on directional o/c and e/f at this end and on main-II DP relay operated at GSS Bargarh(New).
|  | 2020-07-30 | 08:39 | 2020-07-30 | 08:40 | 0:01 | 0 | 1 | [5 empty] | Tripped on directional o/c displayed on back up o/c and e/f relay.
|  | 2020-07-30 | 09:38 | 2020-07-30 | 09:41 | 0:03 | 0 | 3 | [5 empty] | Trpped at Bolangir due to O/L.
|  | 2020-07-30 | 19:24 | 2020-07-30 | 19:32 | 0:08 | 0 | 8 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 20:59 | 2020-07-30 | 21:14 | 00:15 | 0 | 15 | [5 empty] | At Khariar end: O/C, Y Phase.
|  | 2020-07-30 | 21:39 | 2020-07-30 | 21:45 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala due to Ckt. O/L.
|  | 2020-07-30 | 23:00 | 2020-07-30 | 23:06 | 00:06 | 0 | 6 | [5 empty] | Tripped from Saintala: O/C.
|  | 2020-08-16 | 20:12 | 2020-08-16 | 20:20 | 0:08 | 0 | 8 | [5 empty] | Tripped from Khariar Tripped on Overcurrent on R-phase
|  | 2020-08-30 | 17:24 | 2020-08-30 | 17:26 | 0:02 | 0 | 2 | [5 empty] | Tripped From Kesinga
|  | 2020-08-30 | 17:33 | 2020-08-30 | 17:35 | 0:02 | 0 | 2 | [5 empty] | Tripped From Kesinga
|  | 2020-08-30 | 18:08 | 2020-08-30 | 18:10 | 0:02 | 0 | 2 | [5 empty] | Tripped From Kesinga
|  | 2020-08-30 | 19:00 | 2020-08-30 | 19:09 | 0:09 | 0 | 9 | [5 empty] | Tripped From Kesinga
|  | 2020-08-12 | 19:38 | 2020-08-12 | 19:43 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala on Over load
|  | 2020-08-17 | 08:24 | 2020-08-17 | 08:26 | 0:02 | 0 | 2 | [5 empty] | Local Breaker Backup (LBB) operation at Tushra Grid.
|  | 2020-08-22 | 21:20 | 2020-08-22 | 21:26 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/L
|  | 2020-08-30 | 22:12 | 2020-08-30 | 22:17 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala
|  | 2020-09-02 | 19:15 | 2020-09-02 | 20:00 | 0:45 | 0 | 45 | [5 empty] | Tripped from saintala [Section isolator insulation punchure]
|  | 2020-09-06 | 01:43 | 2020-09-06 | 01:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Sadeipali on over load
|  | 2020-09-06 | 19:11 | 2020-09-06 | 19:21 | 0:10 | 0 | 10 | [5 empty] | Tripped From ACME
|  | 2020-09-10 | 09:50 | 2020-09-10 | 09:55 | 0:05 | 0 | 5 | [5 empty] | Tripped from Khariar
|  | 2020-09-10 | 11:13 | 2020-09-10 | 11:17 | 0:04 | 0 | 4 | [5 empty] | Tripped from Kesinga
|  | 2020-09-12 | 19:16 | 2020-09-12 | 19:18 | 0:02 | 0 | 2 | [5 empty] | Tripped from Tushra
|  | 2020-09-13 | 19:18 | 2020-09-13 | 19:24 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala-Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-13 | 21:44 | 2020-09-13 | 21:50 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala- Tripped on O/C B-Phase due to Ckt overloading
|  | 2020-09-14 | 20:13 | 2020-09-14 | 20:19 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala on O/C B- Phase due to Ckt overloading
|  | 2020-09-16 | 09:41 | 2020-09-16 | 09:50 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-16 | 19:00 | 2020-09-16 | 19:03 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 20:21 | 2020-09-16 | 20:22 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-16 | 21:45 | 2020-09-16 | 21:47 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:32 | 2020-09-17 | 23:34 | 0:02 | 0 | 2 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-17 | 23:17 | 2020-09-17 | 23:19 | 0:02 | 0 | 2 | [5 empty] | DUE TO OVERCURRENT AT LALTIKIRA GRID.
|  | 2020-09-19 | 21:57 | 2020-09-19 | 22:03 | 0:06 | 0 | 6 | [5 empty] | Tripped from Saintala [Due to Circuit Overloading.]
|  | 2020-09-27 | 10:03 | 2020-09-27 | 10:08 | 0:05 | 0 | 5 | [5 empty] | Tripped from Sadeipali [LA brust on Sadepali 220KV Ckt-ll incoming bay]
|  | 2020-09-28 | 10:55 | 2020-09-28 | 10:58 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir [LA of Sadeipali 220KV Ckt-ll incoming bay burst]
|  | 2020-09-28 | 19:12 | 2020-09-28 | 19:14 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 2020-09-29 | 20:00 | 2020-09-29 | 20:02 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir [Due to Circuit Overloading.]
|  | 2020-09-24 | 18:43 | 2020-09-24 | 18:52 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala-Tripped on E/F R-Phase
|  | 2020-10-01 | 05:23 | 2020-10-01 | 05:36 | 0:13 | 0 | 13 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-04 | 00:20 | 2020-10-04 | 0:24 | 0:04 | 0 | 4 | [5 empty] | Tripped From Saintala-Earth Fault on R-ph
|  | 2020-10-04 | 00:24 | 2020-10-04 | 00:31 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-05 | 21:33 | 2020-10-05 | 21:35 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-06 | 04:04 | 2020-10-06 | 04:10 | 0:06 | 0 | 6 | [5 empty] | Tripped From saintala
|  | 2020-10-07 | 23:07 | 2020-10-07 | 23:09 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-08 | 05:41 | 2020-10-08 | 05:48 | 0:07 | 0 | 7 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R .
|  | 2020-10-10 | 01:40 | 2020-10-10 | 01:45 | 0:05 | 0 | 5 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-10 | 20:06 | 2020-10-10 | 20:07 | 0:01 | 0 | 1 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R AND AISO PULLED OUT TUSHRA B/R AND ALSO TRIPPED 132/33KV SOLAR B/R .
|  | 2020-10-15 | 03:32 | 2020-10-15 | 03:37 | 0:05 | 0 | 5 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-16 | 13:38 | 2020-10-16 | 13:45 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala-Earth Fault on R-Phase
|  | 2020-10-16 | 20:10 | 2020-10-16 | 20:17 | 0:07 | 0 | 7 | [5 empty] | Tripped From saintala Grid- Earth Fault on B-Phase
|  | 2020-10-19 | 19:04 | 2020-10-19 | 19:06 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-10-19 | 20:12 | 2020-10-19 | 20:14 | 0:02 | 0 | 2
|  | 2020-10-21 | 04:52 | 2020-10-21 | 05:01 | 0:09 | 0 | 9 | [5 empty] | DUE TO OVERCURRENT AT TUSHRA GSS ALONG trippedTO 132KV KESINGA B/R ON E/F & 33/132 KV SOLAR B/R trippedON HV E/F.
|  | 2020-10-31 | 23:49 | 2020-10-31 | 23:51 | 0:02 | 0 | 2 | [5 empty] | DUE TO EARTHFAULT AT B- phase IN KESINGA B/R & ALSO PULLED OUT 132/33KV SOLAR B/R & 132KV SAINTALA B/R AT TUSHRA GSS .
|  | 2020-10-31 | 17:30 | 2020-10-31 | 17:34 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-11-11 | 03:13 | 2020-11-11 | 03:32 | 0:19 | 0 | 19 | [5 empty] | Tripped from Bolangir(Lal Tikira)on E/F
|  | 2020-11-18 | 17:49 | 2020-11-18 | 17:52 | 0:03 | 0 | 3 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-20 | 18:12 | 2020-11-20 | 18:13 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir(Lal Tikira) on E/F
|  | 2020-11-01 | 03:54 | 2020-11-01 | 04:02 | 0:08 | 0 | 8 | [5 empty] | Tripped From Tushra Grid on E/F
|  | 2020-11-03 | 01:30 | 2020-11-03 | 01:33 | 00:03 | 0 | 3 | [5 empty] | Tripped From Saintala Grid on Over Current B-Ph
|  | 2020-11-28 | 05:32 | 2020-11-28 | 05:39 | 00:07 | 0 | 7 | [5 empty] | Tripped From saintala on O/C R-ph
|  | 2020-11-16 | 16:13 | 2020-11-16 | 16:19 | 01:07 | 1 | 7 | [5 empty] | Tripped from Kesingadue to overloading.
|  | 2020-12-04 | 18:20 | 2020-12-04 | 18:22 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:14 | 2020-12-06 | 17:16 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2020-12-06 | 17:47 | 2020-12-06 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:16 | 2020-12-06 | 18:19 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-06 | 18:31 | 2020-12-06 | 18:41 | 0:10 | 0 | 10 | [5 empty] | O/C
|  | 2020-12-06 | 18:54 | 2020-12-06 | 18:57 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-07 | 09:15 | 2020-12-07 | 09:20 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 2020-12-28 | 16:38 | 2020-12-28 | 16:50 | 0:12 | 0 | 12 | [5 empty] | O/C
|  | 2020-12-29 | 18:09 | 2020-12-29 | 18:12 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2020-12-30 | 16:44 | 2020-12-30 | 16:48 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-31 | 19:05 | 2020-12-31 | 19:09 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
|  | 16.12.20 | 17:21 | 16.12.20 | 17:24 | 0:03 | 0 | 3 | [5 empty] | Tripped on O/C R-ph from Saintala end.
|  | 2020-12-22 | 15:21 | 2020-12-22 | 15:25 | 0:04 | 0 | 4 | [5 empty] | Tripped on O/C B-ph from Saintala end.
|  | 2020-12-20 | 18:05 | 2020-12-20 | 18:15 | 0:10 | 0 | 10 | [5 empty] | Tripped From AB solar
|  | 2020-12-21 | 18:54 | 2020-12-21 | 18:58 | 0:04 | 0 | 4 | [5 empty] | Tripped From AB solar
|  | 2021-01-01 | 09:22 | 2021-01-01 | 09:40 | 0:18 | 0 | 18 | [5 empty] | O/C & E/F
|  | 2021-01-10 | 07:07 | 2021-01-10 | 07:09 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-11 | 07:22 | 2021-01-11 | 07:24 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-13 | 17:27 | 2021-01-13 | 17:30 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-18 | 18:46 | 2021-01-18 | 18:48 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-18 | 19:31 | 2021-01-18 | 19:33 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 17:57 | 2021-01-15 | 17:59 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-15 | 18:17 | 2021-01-15 | 18:19 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-17 | 06:53 | 2021-01-17 | 06:56 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-17 | 17:37 | 2021-01-17 | 17:39 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-21 | 18:19 | 2021-01-21 | 18:20 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 2021-01-21 | 19:33 | 2021-01-21 | 19:35 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 17:00 | 2021-01-22 | 17:02 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-22 | 18:03 | 2021-01-22 | 18:05 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-26 | 18:24 | 2021-01-26 | 18:26 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 2021-01-27 | 07:24 | 2021-01-27 | 07:27 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-01-31 | 17:47 | 2021-01-31 | 17:50 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 2021-02-02 | 16:28 | 2021-02-02 | 16:36 | 0:08 | 0 | 8 | [5 empty] | Tripped from Sadeipalli end on overload
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
421 | 132kV Salipur-Kendrapara |  |  |  |  | 0.00625 | 0 | 6 | [7 empty] | 34 | 8760 | 100% | 3.4 | 297840
|  | 2020-10-14 | 06:29 | 2020-10-14 | 06:38 | 0:09 | 0 | 6 | [5 empty] | Tripeed On Differential Relay With M/R Due To 132Kv R -Ph CT Brust And Charged After Replacement Of New CT.
422 | 132kV Samagara-Puri |  |  |  |  | 0.62361 | 15 | 23 | [7 empty] | 3.99 | 8760 | 99.82% | 61.3795 | 34952.4
|  | 2020-07-04 | 07:21 | 2020-07-04 | 07:25 | 0:04 | 0 | 4 | [5 empty] | E/F, Ia=0.267kA, Ib=0.271kA,Ic,=0.180kA,Ig=0.131k A at Shamuka end.
|  | 2020-07-04 | 08:04 | 2020-07-04 | 08:10 | 0:06 | 0 | 6 | [5 empty] | E/F, Ia=0.255kA, Ib=0.259kA, Ic,=0.173kA,Ig=0.125kA, at Shamuka end.
|  | 2020-07-27 | 10:32 | 2020-07-27 | 10:35 | 0:03 | 0 | 3 | [5 empty] | E/F, Ia=1.131kA, Ib=0.205kA, Ic=0.306kA, Ig= 0.724kA at Shamuka end.
|  | 2020-07-03 | 12:10 | 2020-07-03 | 12:17 | 0:07 | 0 | 7 | [5 empty] | Source Failure
|  | 2020-07-04 | 11:25 | 2020-07-04 | 11:34 | 0:09 | 0 | 9 | [5 empty] | Source Failure
|  | 2020-07-15 | 13:05 | 2020-07-15 | 18:29 | 0:53 | 0 | 53 | [5 empty] | DP operate, Cphase-G, Distance= - 5.2 km,Zone- Z1,Ia=363.036A,Ib=704.279A, Ic=470.334A, In=14499.373A at Shamuka end.
|  | 2020-07-27 | 17:07 | 2020-07-27 | 17:38 | 0:31 | 0 | 31 | [5 empty] | Tripped at Shamuka end.
|  | 2020-08-03 | 03:40 | 2020-08-03 | 03:44 | 0:04 | 0 | 4 | [5 empty] | At Shamuka end. E/F, Ia=0.250kA, Ib=0.256kA,Ic,=0.171kA,Ig=0.124k A
|  | 2020-08-05 | 02:03 | 2020-08-05 | 02:04 | 0:01 | 0 | 1 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-05 | 02:07 | 2020-08-05 | 02:08 | 0:01 | 0 | 1 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-05 | 02:16 | 2020-08-05 | 02:22 | 0:06 | 0 | 6 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-13 | 14:42 | 2020-08-13 | 15:06 | 0:02 | 0 | 2 | [5 empty] | At Shamuka end. DP Relay operate.Zone- Z1, Bphase- G, Distance= 26.9km, Ia=564.648A, Ib=458.075A,Ic,=389.975A,Ig=1404 .703A. Heavy rain and Lightning
|  | 2020-08-19 | 20:41 | 2020-08-19 | 20:43 | 0:02 | 0 | 2 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain and Lightning.
|  | 2020-09-18 | 11:55 | 2020-09-18 | 12:15 | 00:19 | 0 | 19 | [5 empty] | ON DP RELAY -NOT OPERATE. ON BACK UP RELAY- 50/51 G TRIP ,MASTER TRIP RLY-86.2 OPERATED ,MASTER TRIP SUPN.RLY 95-B OPERATED. Ia-0.26 KA,Ib-0.33 KA,Ic-0.09 KA; Vab-120.67KV,Vbc-118.84 KV,Vca- 95.61 KV. Puri end: ON BACK UP RELAY- PICKED UP, ON DP
|  | 2020-09-30 | 10:11 | 2020-09-30 | 10:28 | 0:17 | 0 | 17 | [5 empty] | DP, Rph-2.4 kA, Yph-2.1 kA, 54.73 km
|  | 2020-10-01 | 05:49 | 2020-10-01 | 18:15 | 12:32 | 0 | 10 | [5 empty] | DP, Rph & Yph, 2.4 kA, 2.2 kA, 54.83 km
|  | 2020-10-03 | 14:04 | 2020-10-03 | 14:18 | 00:14 | 0 | 14 | [5 empty] | DP, Yph & Bph, 3.7 kA, 7.5 kA, 7.11 km
|  | 2020-10-07 | 12:35 | 2020-10-07 | 12:42 | 00:07 | 0 | 7 | [5 empty] | DP, Yph-N, 2.34 kA, 42.88 km
|  | 2020-10-17 | 02:31 | 2020-10-17 | 02:38 | 00:07 | 0 | 7 | [5 empty] | DP, Yph-N, 1.95 kA, 54.6 km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
423 | 132kV Samagara-Satasankha Ckt-I |  |  |  |  | 0.62361 | 14 | 51 | [7 empty] | 28.07 | 6684 | 99.78% | 416.8395 | 187619.88
|  | 2020-07-04 | 07:21 | 2020-07-04 | 07:25 | 0:04 | 0 | 4 | [5 empty] | E/F, Ia=0.267kA, Ib=0.271kA,Ic,=0.180kA,Ig=0.131k A at Shamuka end.
|  | 2020-07-04 | 08:04 | 2020-07-04 | 08:10 | 0:06 | 0 | 6 | [5 empty] | E/F, Ia=0.255kA, Ib=0.259kA, Ic,=0.173kA,Ig=0.125kA, at Shamuka end.
|  | 2020-07-27 | 10:32 | 2020-07-27 | 10:35 | 0:03 | 0 | 3 | [5 empty] | E/F, Ia=1.131kA, Ib=0.205kA, Ic=0.306kA, Ig= 0.724kA at Shamuka end.
|  | 2020-07-03 | 12:10 | 2020-07-03 | 12:17 | 0:07 | 0 | 7 | [5 empty] | Source Failure
|  | 2020-07-04 | 11:25 | 2020-07-04 | 11:34 | 0:09 | 0 | 9 | [5 empty] | Source Failure
|  | 2020-07-15 | 13:05 | 2020-07-15 | 18:29 | 0:53 | 0 | 21 | [5 empty] | DP operate, Cphase-G, Distance= - 5.2 km,Zone- Z1,Ia=363.036A,Ib=704.279A, Ic=470.334A, In=14499.373A at Shamuka end.
|  | 2020-07-27 | 17:07 | 2020-07-27 | 17:38 | 0:31 | 0 | 31 | [5 empty] | Tripped at Shamuka end.
|  | 2020-08-03 | 03:40 | 2020-08-03 | 03:44 | 0:04 | 0 | 4 | [5 empty] | At Shamuka end. E/F, Ia=0.250kA, Ib=0.256kA,Ic,=0.171kA,Ig=0.124k A
|  | 2020-08-05 | 02:03 | 2020-08-05 | 02:04 | 0:01 | 0 | 1 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-05 | 02:07 | 2020-08-05 | 02:08 | 0:01 | 0 | 1 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-05 | 02:16 | 2020-08-05 | 02:22 | 0:06 | 0 | 6 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-13 | 14:42 | 2020-08-13 | 15:06 | 0:02 | 0 | 2 | [5 empty] | At Shamuka end. DP Relay operate.Zone- Z1, Bphase- G, Distance= 26.9km, Ia=564.648A, Ib=458.075A,Ic,=389.975A,Ig=1404 .703A. Heavy rain and Lightning
|  | 2020-08-19 | 20:41 | 2020-08-19 | 20:43 | 0:02 | 0 | 2 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain and Lightning.
|  | 2020-09-18 | 11:55 | 2020-09-18 | 12:15 | 00:19 | 0 | 19 | [5 empty] | ON DP RELAY -NOT OPERATE. ON BACK UP RELAY- 50/51 G TRIP ,MASTER TRIP RLY-86.2 OPERATED ,MASTER TRIP SUPN.RLY 95-B OPERATED. Ia-0.26 KA,Ib-0.33 KA,Ic-0.09 KA; Vab-120.67KV,Vbc-118.84 KV,Vca- 95.61 KV. Puri end: ON BACK UP RELAY- PICKED UP, ON DP
|  | 2020-09-30 | 10:11 | 2020-09-30 | 10:28 | 0:17 | 0 | 17 | [5 empty] | DP, Rph-2.4 kA, Yph-2.1 kA, 54.73 km
|  | 2020-10-01 | 05:49 | 2020-10-01 | 18:15 | 12:32 | 0 | 10 | [5 empty] | DP, Rph & Yph, 2.4 kA, 2.2 kA, 54.83 km
|  | 2020-10-03 | 14:04 | 2020-10-03 | 14:18 | 00:14 | 0 | 14 | [5 empty] | DP, Yph & Bph, 3.7 kA, 7.5 kA, 7.11 km
|  | 2020-10-07 | 12:35 | 2020-10-07 | 12:42 | 00:07 | 0 | 7 | [5 empty] | DP, Yph-N, 2.34 kA, 42.88 km
|  | 2020-10-17 | 02:31 | 2020-10-17 | 02:38 | 00:07 | 0 | 7 | [5 empty] | DP, Yph-N, 1.95 kA, 54.6 km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
424 | 132kV Samagara-Satasankha Ckt-II |  |  |  |  | 0.62361 | 14 | 51 | [7 empty] | 28.07 | 6684 | 99.78% | 416.8395 | 187619.88
|  | 2020-07-04 | 07:21 | 2020-07-04 | 07:25 | 0:04 | 0 | 4 | [5 empty] | E/F, Ia=0.267kA, Ib=0.271kA,Ic,=0.180kA,Ig=0.131k A at Shamuka end.
|  | 2020-07-04 | 08:04 | 2020-07-04 | 08:10 | 0:06 | 0 | 6 | [5 empty] | E/F, Ia=0.255kA, Ib=0.259kA, Ic,=0.173kA,Ig=0.125kA, at Shamuka end.
|  | 2020-07-27 | 10:32 | 2020-07-27 | 10:35 | 0:03 | 0 | 3 | [5 empty] | E/F, Ia=1.131kA, Ib=0.205kA, Ic=0.306kA, Ig= 0.724kA at Shamuka end.
|  | 2020-07-03 | 12:10 | 2020-07-03 | 12:17 | 0:07 | 0 | 7 | [5 empty] | Source Failure
|  | 2020-07-04 | 11:25 | 2020-07-04 | 11:34 | 0:09 | 0 | 9 | [5 empty] | Source Failure
|  | 2020-07-15 | 13:05 | 2020-07-15 | 18:29 | 0:53 | 0 | 21 | [5 empty] | DP operate, Cphase-G, Distance= - 5.2 km,Zone- Z1,Ia=363.036A,Ib=704.279A, Ic=470.334A, In=14499.373A at Shamuka end.
|  | 2020-07-27 | 17:07 | 2020-07-27 | 17:38 | 0:31 | 0 | 31 | [5 empty] | Tripped at Shamuka end.
|  | 2020-08-03 | 03:40 | 2020-08-03 | 03:44 | 0:04 | 0 | 4 | [5 empty] | At Shamuka end. E/F, Ia=0.250kA, Ib=0.256kA,Ic,=0.171kA,Ig=0.124k A
|  | 2020-08-05 | 02:03 | 2020-08-05 | 02:04 | 0:01 | 0 | 1 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-05 | 02:07 | 2020-08-05 | 02:08 | 0:01 | 0 | 1 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-05 | 02:16 | 2020-08-05 | 02:22 | 0:06 | 0 | 6 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-13 | 14:42 | 2020-08-13 | 15:06 | 0:02 | 0 | 2 | [5 empty] | At Shamuka end. DP Relay operate.Zone- Z1, Bphase- G, Distance= 26.9km, Ia=564.648A, Ib=458.075A,Ic,=389.975A,Ig=1404 .703A. Heavy rain and Lightning
|  | 2020-08-19 | 20:41 | 2020-08-19 | 20:43 | 0:02 | 0 | 2 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain and Lightning.
|  | 2020-09-18 | 11:55 | 2020-09-18 | 12:15 | 00:19 | 0 | 19 | [5 empty] | ON DP RELAY -NOT OPERATE. ON BACK UP RELAY- 50/51 G TRIP ,MASTER TRIP RLY-86.2 OPERATED ,MASTER TRIP SUPN.RLY 95-B OPERATED. Ia-0.26 KA,Ib-0.33 KA,Ic-0.09 KA; Vab-120.67KV,Vbc-118.84 KV,Vca- 95.61 KV. Puri end: ON BACK UP RELAY- PICKED UP, ON DP
|  | 2020-09-30 | 10:11 | 2020-09-30 | 10:28 | 0:17 | 0 | 17 | [5 empty] | DP, Rph-2.4 kA, Yph-2.1 kA, 54.73 km
|  | 2020-10-01 | 05:49 | 2020-10-01 | 18:15 | 12:32 | 0 | 10 | [5 empty] | DP, Rph & Yph, 2.4 kA, 2.2 kA, 54.83 km
|  | 2020-10-03 | 14:04 | 2020-10-03 | 14:18 | 00:14 | 0 | 14 | [5 empty] | DP, Yph & Bph, 3.7 kA, 7.5 kA, 7.11 km
|  | 2020-10-07 | 12:35 | 2020-10-07 | 12:42 | 00:07 | 0 | 7 | [5 empty] | DP, Yph-N, 2.34 kA, 42.88 km
|  | 2020-10-17 | 02:31 | 2020-10-17 | 02:38 | 00:07 | 0 | 7 | [5 empty] | DP, Yph-N, 1.95 kA, 54.6 km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
425 | 132kV Sambalpur-Shyam DRI |  |  |  |  | 0.022917 | 0 | 33 | [7 empty] | 28.91 | 8760 | 99.99% | 15.9005 | 253251.6
|  | 2021-01-28 | 12:59 | 2021-01-28 | 13:32 | 0:33 | 0 | 33 | [5 empty] | Trip on DP relay,Zone1,B-ph
426 | 132kV Shamuka-Puri |  |  |  |  | 0.62361 | 15 | 23 | [7 empty] | 16.9 | 8760 | 99.82% | 259.9783 | 148044
|  | 2020-07-04 | 07:21 | 2020-07-04 | 07:25 | 0:04 | 0 | 4 | [5 empty] | E/F, Ia=0.267kA, Ib=0.271kA,Ic,=0.180kA,Ig=0.131k A at Shamuka end.
|  | 2020-07-04 | 08:04 | 2020-07-04 | 08:10 | 0:06 | 0 | 6 | [5 empty] | E/F, Ia=0.255kA, Ib=0.259kA, Ic,=0.173kA,Ig=0.125kA, at Shamuka end.
|  | 2020-07-27 | 10:32 | 2020-07-27 | 10:35 | 0:03 | 0 | 3 | [5 empty] | E/F, Ia=1.131kA, Ib=0.205kA, Ic=0.306kA, Ig= 0.724kA at Shamuka end.
|  | 2020-07-03 | 12:10 | 2020-07-03 | 12:17 | 0:07 | 0 | 7 | [5 empty] | Source Failure
|  | 2020-07-04 | 11:25 | 2020-07-04 | 11:34 | 0:09 | 0 | 9 | [5 empty] | Source Failure
|  | 2020-07-15 | 13:05 | 2020-07-15 | 18:29 | 0:53 | 0 | 53 | [5 empty] | DP operate, Cphase-G, Distance= - 5.2 km,Zone- Z1,Ia=363.036A,Ib=704.279A, Ic=470.334A, In=14499.373A at Shamuka end.
|  | 2020-07-27 | 17:07 | 2020-07-27 | 17:38 | 0:31 | 0 | 31 | [5 empty] | Tripped at Shamuka end.
|  | 2020-08-03 | 03:40 | 2020-08-03 | 03:44 | 0:04 | 0 | 4 | [5 empty] | At Shamuka end. E/F, Ia=0.250kA, Ib=0.256kA,Ic,=0.171kA,Ig=0.124k A
|  | 2020-08-05 | 02:03 | 2020-08-05 | 02:04 | 0:01 | 0 | 1 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-05 | 02:07 | 2020-08-05 | 02:08 | 0:01 | 0 | 1 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-05 | 02:16 | 2020-08-05 | 02:22 | 0:06 | 0 | 6 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain Outside.
|  | 2020-08-13 | 14:42 | 2020-08-13 | 15:06 | 0:02 | 0 | 2 | [5 empty] | At Shamuka end. DP Relay operate.Zone- Z1, Bphase- G, Distance= 26.9km, Ia=564.648A, Ib=458.075A,Ic,=389.975A,Ig=1404 .703A. Heavy rain and Lightning
|  | 2020-08-19 | 20:41 | 2020-08-19 | 20:43 | 0:02 | 0 | 2 | [5 empty] | No Relay indication, Breaker trip at shamuka end. Heavy Rain and Lightning.
|  | 2020-09-18 | 11:55 | 2020-09-18 | 12:15 | 00:19 | 0 | 19 | [5 empty] | ON DP RELAY -NOT OPERATE. ON BACK UP RELAY- 50/51 G TRIP ,MASTER TRIP RLY-86.2 OPERATED ,MASTER TRIP SUPN.RLY 95-B OPERATED. Ia-0.26 KA,Ib-0.33 KA,Ic-0.09 KA; Vab-120.67KV,Vbc-118.84 KV,Vca- 95.61 KV. Puri end: ON BACK UP RELAY- PICKED UP, ON DP
|  | 2020-09-30 | 10:11 | 2020-09-30 | 10:28 | 0:17 | 0 | 17 | [5 empty] | DP, Rph-2.4 kA, Yph-2.1 kA, 54.73 km
|  | 2020-10-01 | 05:49 | 2020-10-01 | 18:15 | 12:32 | 0 | 10 | [5 empty] | DP, Rph & Yph, 2.4 kA, 2.2 kA, 54.83 km
|  | 2020-10-03 | 14:04 | 2020-10-03 | 14:18 | 00:14 | 0 | 14 | [5 empty] | DP, Yph & Bph, 3.7 kA, 7.5 kA, 7.11 km
|  | 2020-10-07 | 12:35 | 2020-10-07 | 12:42 | 00:07 | 0 | 7 | [5 empty] | DP, Yph-N, 2.34 kA, 42.88 km
|  | 2020-10-17 | 02:31 | 2020-10-17 | 02:38 | 00:07 | 0 | 7 | [5 empty] | DP, Yph-N, 1.95 kA, 54.6 km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
427 | 132kV Shyam DRI-Aryan Ispat |  |  |  |  | 0.041667 | 1 | 0 | [7 empty] | 4.2 | 8760 | 99.99% | 4.2 | 36792
|  | 2021-01-10 | 01:07 | 2021-01-10 | 01:34 | 0:27 | 0 | 27 | [5 empty] | trip due to damage of insulator
|  | 2021-01-28 | 12:59 | 2021-01-28 | 13:32 | 0:33 | 0 | 33 | [5 empty] | Trip on DP relay,Zone1,B-ph
428 | 132kV Aryan Ispat - Lapanga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.9 | 8760 | 100% | 0 | 34164
429 | 132kV Lapanga-SMC Power |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.7 | 8760 | 100% | 0 | 41172
430 | 132kV SMC Power-Kuchinda |  |  |  |  | 0.94792 | 13 | 5 | [7 empty] | 52.53 | 8760 | 99.85% | 687.2675 | 460162.8
|  | 2020-05-04 | 8:31 | 2020-05-04 | 8:59 | 0:28 | 0 | 28 | [5 empty] | Tripped at SMC end
|  | 2020-05-24 | 15:09 | 2020-05-24 | 15:29 | 0:20 | 0 | 1 | [5 empty] | (Incomer)tripped at SMC end
|  | 2020-07-22 | 19:13 | 2020-07-22 | 19:18 | 00:05 | 0 | 2 | [5 empty] | started phase A B N, Tripped ph A B C, Distance trip Z1, fault distance - 8.339 ms, relay trip time - 80.05ms, fault location X Y -31.42KM, IA-208.5 MA , IB-165.8 MA , IC-279 MA , Van-6.992 V, Vbn-73.63V, Vcn-69.5 V, Fault resistance xy -20.13 ohm
|  | 2020-08-03 | 15:15 | 2020-08-03 | 15:36 | 00:21 | 0 | 10 | [5 empty] | started phase B C, IA=IB=IC=0.0A Fault in Zone None
|  | 2020-10-08 | 14:12 | 2020-10-09 | 12:09 | 21:57 | 0 | 24 | [5 empty] | Tripped at SMC end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
431 | 132kV Soro-Bhadrak |  |  |  |  | 0.054167 | 0 | 53 | [7 empty] | 45.62 | 8760 | 99.99% | 40.2977 | 399631.2
|  | 2021-02-02 | 13:22 | 2021-02-02 | 14:40 | 1:18 | 0 | 53 | [5 empty] | At Balasore end: Siemens B/U relay: B-Ph O/C, E/F, Fault current: IL3=1.33KA
432 | 132kV Sunabeda-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.6 | 8760 | 100% | 0 | 110376
433 | 132kV Sunabeda-HAL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.7 | 8760 | 100% | 0 | 6132
434 | 132kV Sunabeda-Pottangi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33 | 8760 | 100% | 0 | 289080
435 | 132kV Tarkera-Kalunga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.48 | 8760 | 100% | 0 | 135604.8
436 | 132kV Tarkera-Budhipadar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 109 | 8760 | 100% | 0 | 954840
437 | 132kV Tarkera-Chhend-I |  |  |  |  | 0.036806 | 13 | 8 | [7 empty] | 6.165 | 8760 | 99.85% | 80.967 | 54005.4
|  | 2020-06-23 | 19:09 | 2020-06-23 | 19:49 | 0:40 | 0 | 40 | [5 empty] | DP Relay ( Loop- A_G, Distance- 8.96 Kms , Ia-5.34 kA , In-4.84 kA) at Tarkera end.
|  | 2020-07-14 | 00:36 | 2020-07-14 | 00:49 | 0:13 | 0 | 13 | [5 empty] | At Tarkera end, DP Relay- Tripped Phase- AGT, , Zone- 1, Fault location- 3.77 km, IA=6430A, IN=6187A,IG=6191 A; Master Trip operated. [Heavy rain & Lightening with thunderstorm.]
|  | 2020-08-01 | 19:22 | 2020-08-01 | 19:37 | 00:15 | 0 | 15 | [5 empty] | DP - Loop-A_G , Distance- 7.96 Kms , Ia- 5.76 kA , In-5.27 kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
438 | 132kV Tarkera-Chhend-II |  |  |  |  | 0.063889 | 0 | 28 | [7 empty] | 6.165 | 8760 | 99.99% | 2.877 | 54005.4
|  | 2020-07-14 | 00:36 | 2020-07-14 | 00:49 | 0:15 | 0 | 13 | [5 empty] | At Tarkera end, DP Relay- Tripped Phase- AGT, , Zone- 1, Fault location- 3.45 km, IA=7167A, IN=6942A,IG=6946A; Master Trip operated.
|  | 2020-08-01 | 19:22 | 2020-08-01 | 0.86042 | 1:17 | 0 | 15 | [5 empty] | DP - Loop-A_G , Distance- 7.96 Kms , Ia- 5.76 kA , In-5.27 kA
439 | 132kV Tarkera-Rajgangpur-I |  |  |  |  | 0.052778 | 0 | 2 | [7 empty] | 24.1 | 8760 | 100% | 0.80333 | 211116
|  | 2020-05-30 | 0:18 | 2020-05-30 | 1:34 | 1:16 | 0 | 2 | [5 empty] | DP OPERATED AGT ZONE-1 LOC- 0.59KM IA-4298A IG-4807A
440 | 132kV Tarkera-Rajgangpur-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.1 | 8760 | 100% | 0 | 211116
441 | 132kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
442 | 132kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
443 | 132kV Tarkera-Rourkela-I |  |  |  |  | 0.90694 | 15 | 51 | [7 empty] | 3 | 8760 | 99.82% | 47.55 | 26280
|  | 2020-06-08 | 14:16 | 2020-06-08 | 14:36 | 0:20 | 0 | 20 | [5 empty] | Backup Relay: O/C-Y Phase & E/F.
|  | 2020-09-08 | 01:10 | 2020-09-08 | 05:16 | 4:06 | 0 | 17 | [5 empty] | EARTHFAULT YPH (64X) [CT Y Phase Jumper Snapped at rourkela Grid ]
|  | 2020-09-25 | 20:19 | 2020-09-25 | 23:47 | 14:57 | 0 | 54 | [5 empty] | O/C- R Phase [R Phase Jumper from Breaker to Isolator snapped and 132kV Tarkera-
|  | 2021-01-27 | 03:10 | 2021-01-27 | 05:33 | 2:23 | 2 | 20 | [5 empty] | E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
444 | 132kV Tarkera-Rourkela-II |  |  |  |  | 0.39792 | 15 | 20 | [7 empty] | 3 | 8760 | 99.82% | 46 | 26280
|  | 2020-06-08 | 14:16 | 2020-06-08 | 14:37 | 0:21 | 0 | 20 | [5 empty] | Backup Relay: O/C-Y Phase & E/F.
|  | 2020-09-08 | 01:10 | 2020-09-08 | 1:12 | 0:02 | 0 | 2 | [5 empty] | EARTHFAULT YPH (64X) [CT Y Phase Jumper Snapped at rourkela Grid ]
|  | 2020-09-25 | 20:19 | 2020-09-25 | 21:13 | 6:48 | 0 | 54 | [5 empty] | O/C- R Phase [R Phase Jumper from Breaker to Isolator snapped and 132kV Tarkera-
|  | 2021-01-27 | 03:10 | 2021-01-27 | 05:32 | 2:22 | 2 | 20 | [5 empty] | E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
445 | 132kV Tarkera-Rourkela-III |  |  |  |  | 1899-12-31 15:21 | 4 | 28 | [7 empty] | 3 | 8760 | 99.95% | 13.4 | 26280
|  | 2020-09-08 | 01:10 | 2020-09-09 | 14:11 | 37:01 | 2 | 8 | [5 empty] | EARTHFAULT YPH (64X) [CT Y Phase Jumper Snapped at rourkela Grid ]
|  | 2021-01-27 | 03:10 | 2021-01-27 | 05:30 | 2:20 | 2 | 20 | [5 empty] | E/F
446 | 132kV Jayapatna- Dabugaon |  |  |  |  | 0.10278 | 14 | 21 | [7 empty] | 65.59 | 3300 | 99.57% | 941.2165 | 216447
|  | 2020-11-30 | 09:19 | 2020-11-30 | 11:28 | 2:09 | 2 | 9 | [5 empty] | tripped due to overfluxing
|  | 2020-12-15 | 11:10 | 2020-12-15 | 11:15 | 0:05 | 0 | 5 | [5 empty] | pulled out with above fault and Tripped at Jaypatna end
|  | 2021-03-16 | 11:37 | 2021-03-16 | 11:40 | 0:03 | 0 | 3 | [5 empty] | Tripped at Jayapatna end.
|  | 2021-03-16 | 11:48 | 2021-03-16 | 11:59 | 0:11 | 0 | 4 | [5 empty] | Tripped at Jayapatna end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
447 | 132kV Dabugaon -Umerkote |  |  |  |  | 0.59236 | 17 | 17 | [7 empty] | 45.49 | 8760 | 99.8% | 786.2188 | 398492.4
|  | 2020-05-02 | 18:41 | 2020-05-02 | 18:54 | 0:13 | 0 | 13 | [5 empty] | Tripped from Tentulikhunti
|  | 2020-05-12 | 10:08 | 2020-05-12 | 20:27 | 10:19 | 1 | 30 | [5 empty] | B Phase CT burst. (Jayanagar, Tentulikhunti affected due to damage to the Reserve Bus isolator)
|  | 2020-05-29 | 11:44 | 2020-05-29 | 11:50 | 0:06 | 0 | 6 | [5 empty] | At Jayanagar-Tripped
|  | 2020-05-29 | 17:25 | 2020-05-29 | 17:37 | 0:12 | 0 | 12 | [5 empty] | Tripped on over current [due to 33KV Indravati feeder backup relay operated and CB not tripped]
|  | 2020-10-21 | 10:49 | 2020-10-21 | 11:22 | 0:33 | 0 | 33 | [5 empty] | Tripped on LBB [due to DC Failure]
|  | 2020-11-30 | 09:19 | 2020-11-30 | 11:28 | 2:09 | 2 | 9 | [5 empty] | tripped due to overfluxing
|  | 2020-12-15 | 11:10 | 2020-12-15 | 11:15 | 0:05 | 0 | 5 | [5 empty] | pulled out with above fault and Tripped at Jaypatna end
|  | 2021-02-12 | 12:55 | 2021-02-12 | 13:17 | 0:22 | 0 | 22 | [5 empty] | Tripped
|  | 2021-03-16 | 11:37 | 2021-03-16 | 11:40 | 0:03 | 0 | 3 | [5 empty] | Tripped at Jayapatna end.
|  | 2021-03-16 | 11:48 | 2021-03-16 | 11:59 | 0:11 | 0 | 4 | [5 empty] | Tripped at Jayapatna end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
448 | 132kV Tentulikhunti-Dabugaon ckt |  |  |  |  | 0.58264 | 17 | 10 | [7 empty] | 42.8 | 8760 | 99.8% | 734.7333 | 374928
|  | 2020-05-02 | 18:41 | 2020-05-02 | 18:54 | 0:13 | 0 | 13 | [5 empty] | Tripped from Tentulikhunti
|  | 2020-05-12 | 10:08 | 2020-05-12 | 20:27 | 10:19 | 1 | 30 | [5 empty] | B Phase CT burst. (Jayanagar, Tentulikhunti affected due to damage to the Reserve Bus isolator)
|  | 2020-05-29 | 11:44 | 2020-05-29 | 11:50 | 0:06 | 0 | 6 | [5 empty] | At Jayanagar-Tripped
|  | 2020-05-29 | 17:25 | 2020-05-29 | 17:37 | 0:12 | 0 | 12 | [5 empty] | Tripped on over current [due to 33KV Indravati feeder backup relay operated and CB not tripped]
|  | 2020-10-21 | 10:49 | 2020-10-21 | 11:22 | 0:33 | 0 | 33 | [5 empty] | Tripped on LBB [due to DC Failure]
|  | 2020-11-30 | 09:19 | 2020-11-30 | 11:28 | 2:09 | 2 | 9 | [5 empty] | tripped due to overfluxing
|  | 2020-12-15 | 11:10 | 2020-12-15 | 11:15 | 0:05 | 0 | 5 | [5 empty] | pulled out with above fault and Tripped at Jaypatna end
|  | 2021-02-12 | 12:55 | 2021-02-12 | 13:17 | 0:22 | 0 | 22 | [5 empty] | Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
449 | 132kV Tentulikhunti-Vento Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.192 | 8760 | 100% | 0 | 36721.92
450 | 132kV Therubali-IMFA |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2 | 8760 | 100% | 0 | 17520
451 | 132kV Therubali-JK Pur |  |  |  |  | 0.03125 | 0 | 45 | [7 empty] | 9.68 | 8760 | 99.99% | 7.26 | 84796.8
|  | 2020-10-17 | 06:18 | 2020-10-17 | 07:03 | 0:45 | 0 | 45 | [5 empty] | Back up operated with B-Phase over current at Therubali end. Under voltage relay operated at JK end
452 | 132kV Therubali-Rayagada |  |  |  |  | 1899-12-31 02:45 | 1 | 34 | [7 empty] | 19.6 | 8760 | 99.98% | 30.7067 | 171696
|  | 2020-05-18 | 13:31 | 2020-05-18 | 13.44 | 0:13 | 0 | 13 | [5 empty] | Tripped
|  | 2020-07-30 | 14:46 | 2020-07-31 | 17:18 | 26:32 | 1 | 21 | [5 empty] | BG-T, Y- 6.1KAat Therubali end. [Y-Phase conductor snapped at Loc. No-65]
453 | 132kV TTPS-Angul |  |  |  |  | 0.079861 | 1 | 31 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 15.6 | 8760 | 99.99% | 23.66 | 136656
|  | 2020-10-29 | 15:17 | 2020-10-29 | 17:03 | 1:46 | 1 | 22 | [5 empty] | Tripped on E/F at both ends. [ one big mango tree has been uprooted by the railway authority which was in close proximity to 132 KV TTPS-Angul and 132 KV Chainpal-Angul double circuit
|  | 2021-03-11 | 18:55 | 2021-03-12 | 16:04 | 0:09 | 0 | 9 | [5 empty] | TRIPPED DUE TO SNAPPING OF R-PH CONDUCTOR OF MAIN BUS TO SI
454 | 132kV TTPS-Chainpal-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
455 | 132kV TTPS-Chainpal-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
456 | 132kV TTPS-Chainpal-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
457 | 132kV TTPS-Jabamayee FAlloys |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.276 | 8760 | 100% | 0 | 668177.76
458 | 132kV TTPS-OPCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31 | 8760 | 100% | 0 | 271560
459 | 132kV Tusura-Vento Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.8 | 8760 | 100% | 0 | 129648
(17): 7841.9171; (20): 92272.6795; (21): 138597535.8 | 0.00066576
ICTs / AUTOS
1 | New Duburi 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
2 | New Duburi 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
3 | Lapanga 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
4 | Lapanga 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 3876 | 100% | 0 | 3052350
5 | Meramundali 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
6 | Meramundali 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
7 | Mendhasal 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
8 | Mendhasal 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
9 | Mendhasal 315MVA ICT – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
10 | Aska New 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
11 | Aska New 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
12 | Atri 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
13 | Atri 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
14 | Balasore 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
15 | Balasore 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
16 | Balasore 160MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
17 | Baragarh New 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
18 | Baragarh New 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
19 | Bidanasi 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
20 | Bidanasi 100MVA Auto - II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
21 | Bidanasi 160MVA Auto - III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
22 | Bhadrak 100MVA Auto – I |  |  |  |  | 0.0034722 | 0 | 5 | [6 empty] | 100 |  | 8760 | 100% | 20.8333 | 2190000
|  | 2020-08-12 | 16:41 | 2020-08-12 | 16:46 | 0:05 | 0 | 5 | [5 empty] | LBB protection.
23 | Bhadrak 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
24 | Bhadrak 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
25 | Bhadrak 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
26 | New Bolangir 160MVA Auto I |  |  |  |  | 0.19653 | 0 | 13 | [6 empty] | 160 |  | 8760 | 100% | 86.6667 | 3504000
|  | 2020-12-28 | 16:36 | 2020-12-28 | 21:19 | 4:43 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
27 | New Bolangir 160 MVA Auto II |  |  |  |  | 0.0090278 | 0 | 13 | [6 empty] | 160 |  | 8760 | 100% | 86.6667 | 3504000
|  | 2020-12-28 | 16:36 | 2020-12-28 | 16:49 | 0:13 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
28 | New Bolangir 160 MVA Auto III |  |  |  |  | 0.028472 | 12 | 31 | [6 empty] | 160 |  | 8760 | 99.86% | 5006.6667 | 3504000
|  | 2020-05-01 | 15:29 | 2020-05-01 | 15:37 | 0:08 | 0 | 8 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-05-30 | 7:38 | 2020-05-30 | 7:58 | 0:20 | 0 | 10 | [5 empty] | Tripped on earth fault displayed on o/c and e/f relay.
|  | 2020-12-28 | 16:36 | 2020-12-28 | 16:49 | 0:13 | 0 | 13 | [5 empty] | Tripped on differential protection due to puncture of 220KV R-Phase LA.Total grid black out occurred.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
29 | Bhanjanagar 160MVA Auto – I |  |  |  |  | 0.35278 | 0 | 57 | [6 empty] | 160 |  | 8760 | 99.99% | 380 | 3504000
|  | 2020-05-20 | 10:02 | 2020-05-20 | 17:55 | 7:53 | 0 | 22 | [5 empty] | BPH O E/F
|  | 2020-08-01 | 12:34 | 2020-08-01 | 13:09 | 0:35 | 0 | 35 | [5 empty] | B PH TO E/F, IB= 896.7A
30 | Bhanjanagar 160MVA Auto – II |  |  |  |  | 0.041667 | 0 | 57 | [6 empty] | 160 |  | 8760 | 99.99% | 380 | 3504000
|  | 2020-05-20 | 10:02 | 2020-05-20 | 10:24 | 0:22 | 0 | 22 | [5 empty] | Tripped due to bird fault.
|  | 2020-08-01 | 12:34 | 2020-08-01 | 13:12 | 0:38 | 0 | 35 | [5 empty] | B PH TO E/F, IB= 801.0A
31 | Budhipadar 160MVA Auto – I |  |  |  |  | 0.23403 | 0 | 40 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 2021-02-05 | 09:26 | 2021-02-05 | 15:03 | 5:37 | 0 | 40 | [5 empty] | Tripped at Both end with O/C Y&B- Ph.
32 | Budhipadar 160MVA Auto – II |  |  |  |  | 0.24236 | 0 | 40 | [6 empty] | 160 |  | 8760 | 99.99% | 266.6667 | 3504000
|  | 2021-02-05 | 09:26 | 2021-02-05 | 15:15 | 5:49 | 0 | 40 | [5 empty] | Tripped at Both end with with O/C Y&B-Ph and auto Transformer declared Faulty on dt 06.02.2021 due to Y ph 132KV side bushing lead damaged.
33 | Chandaka 100MVA Auto – I |  |  |  |  | 0.0076389 | 0 | 9 | [6 empty] | 100 |  | 8760 | 100% | 37.5 | 2190000
|  | 2020-06-30 | 9:04 | 2020-06-30 | 9:15 | 0:11 | 0 | 9 | [5 empty] | Tripped.
34 | Chandaka 160MVA Auto – II |  |  |  |  | 0.00625 | 0 | 9 | [6 empty] | 160 |  | 8760 | 100% | 60 | 3504000
|  | 2020-06-30 | 9:04 | 2020-06-30 | 9:13 | 0:09 | 0 | 9 | [5 empty] | Tripped.
35 | Chandaka 100MVA Auto – III |  |  |  |  | 0.0076389 | 0 | 9 | [6 empty] | 100 |  | 8760 | 100% | 37.5 | 2190000
|  | 2020-06-30 | 9:04 | 2020-06-30 | 9:15 | 0:11 | 0 | 9 | [5 empty] | Tripped.
36 | Chandaka 160MVA Auto – IV |  |  |  |  | 0.0076389 | 0 | 9 | [6 empty] | 160 |  | 8760 | 100% | 60 | 3504000
|  | 2020-06-30 | 9:04 | 2020-06-30 | 9:15 | 0:11 | 0 | 9 | [5 empty] | Tripped.
37 | Chandaka-B 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
38 | Chandaka-B 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
39 | Cuttack 160MVA Auto – I |  |  |  |  | 0.0041667 | 0 | 6 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 2020-04-25 | 11:18 | 2020-04-25 | 11:24 | 0:06 | 0 | 6 | [5 empty] | Tripped on V/F trip,V/F warn,86A&86B trip
40 | Cuttack 100MVA Auto – II |  |  |  |  | 0 | 0 | 6 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
|  | 2020-04-25 | 11:18 | 2020-04-25 | 11:26 | 0:08 | 0 | 6 | [5 empty] | Tripped on V/F trip,V/F warn,86A&86B trip
41 | Duburi 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
42 | Duburi 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
43 | Duburi 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
44 | Goda 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 7344 | 100% | 0 | 2937600
45 | Goda 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 7344 | 100% | 0 | 2937600
46 | Jayanagar 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
47 | Jayanagar 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
48 | Jayapatna 160MVA Auto – I |  |  |  |  | 0.089583 | 2 | 9 | [6 empty] | 160 |  | 6300 | 99.97% | 860 | 2520000
|  | 2020-11-30 | 09:19 | 2020-11-30 | 11:28 | 2:09 | 2 | 9 | [5 empty] | tripped due to overfluxing
49 | Jayapatna 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
50 | Joda 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
51 | Joda 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 5832 | 100% | 0 | 2332800
52 | Joda 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
53 | Katapalli 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
54 | Katapalli 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
55 | Katapalli 160MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
56 | Kesinga 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 5064 | 100% | 0 | 2025600
57 | Kesinga 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 3360 | 100% | 0 | 1344000
58 | Lapanga 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
59 | Lapanga 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
60 | Mendhasal 100MVA Auto – I |  |  |  |  | 0.011111 | 0 | 9 | [6 empty] | 100 |  | 8760 | 100% | 37.5 | 2190000
|  | 2020-06-15 | 0:31 | 2020-06-15 | 0:47 | 0:16 | 0 | 9 | [5 empty] | Tripped
61 | Mendhasal 100MVA Auto – II |  |  |  |  | 0.03125 | 0 | 9 | [6 empty] | 100 |  | 8760 | 100% | 37.5 | 2190000
|  | 2020-06-15 | 0:31 | 2020-06-15 | 0:45 | 0:45 | 0 | 9 | [5 empty] | Tripped
62 | Meramundali 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
63 | Meramundali 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
64 | Meramundali 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
65 | Narendrapur 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
66 | Narendrapur 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
67 | Narendrapur 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
68 | Paradeep 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
69 | Paradeep 160 MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
70 | Paradeep 160 MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
71 | Samagara 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
72 | Samagara 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
73 | Tarkera 100MVA Auto – I |  |  |  |  | 0.077083 | 0 | 31 | [6 empty] | 100 |  | 8760 | 99.99% | 129.1667 | 2190000
|  | 2020-06-08 | 14:16 | 2020-06-08 | 14:23 | 1:40 | 0 | 20 | [5 empty] | Backup Relay: O/C-Y Phase & E/F.
|  | 2020-09-08 | 01:10 | 2020-09-08 | 01:21 | 0:11 | 0 | 11 | [5 empty] | EARTH FAULT (64X)
74 | Tarkera 100MVA Auto – II |  |  |  |  | 0.0125 | 0 | 18 | [6 empty] | 100 |  | 8760 | 100% | 79.1667 | 2190000
|  | 2020-09-08 | 01:10 | 2020-09-08 | 01:28 | 0:18 | 0 | 18 | [5 empty] | EARTHFAULT AND MASTERTRIP(ABB)
75 | Tarkera 100MVA Auto – III |  |  |  |  | 0.013194 | 0 | 19 | [6 empty] | 100 |  | 8760 | 100% | 79.1667 | 2190000
|  | 2020-06-08 | 14:16 | 2020-06-08 | 14:25 | 0:09 | 0 | 9 | [5 empty] | Backup Relay: O/C-Y Phase & E/F.
|  | 2020-09-08 | 01:10 | 2020-09-08 | 01:20 | 0:10 | 0 | 10 | [5 empty] | NUMERICAL BACKUP EARTHFAULT IB-2.452KA, IN MEASURED- 2.226KA IN DERIVED-2.215KA
76 | Tarkera 100MVA Auto – IV |  |  |  |  | 0.0090278 | 0 | 13 | [6 empty] | 100 |  | 8760 | 100% | 54.1667 | 2190000
|  | 2020-06-08 | 14:16 | 2020-06-08 | 14:29 | 0:13 | 0 | 13 | [5 empty] | Backup Relay: O/C-Y Phase & E/F.
77 | Therubali 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
78 | Therubali 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
79 | Therubali 160MVA Auto –III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
12475
(16): Sub-total (ICTs / Autos); (20): 7699.1667; (21): 262429950 | 2.9338e-05 | 99.9971
[15 empty] | TOTAL (Lines, ICTs & Autos) |  |  |  | 99971.8461 | 401027485.8
[11 empty] | NAFY |  | [ Σ ( OH l x Cktkm l x NSC l ) + Σ ( OH t x MVA t x 2.5 )] [THY x { Σ (Cktkm l x NSC l ) +Σ (MVA t x 2.5 ) } ] | [5 empty] | 0.00024929
[13 empty] | 100 - (100 X NAFY) | [5 empty] | 99.9751