## Page-1
A. POWER SUPPLY SECURITY
Format-A1
Load Restriction due to non availability of Generation
Year | Quarter | Month | Total Hrs. | * Duration of restriction (in HRs.) | Percentage of time load restricted
1 | 2 | 3 | 4 | 5 | 6
2025-26 | 2nd | JULY | 744 | 0 | 0
|  | AUGUST | 744 | 0 | 0
|  | SEPTEMBER | 720 | 0 | 0
Total |  |  | 2208 | 0 | 0
* SLDC is preparing the drawal schedule for discom considering the availability of power from all sources.
Load restriction is being done by the discom as and when required on rotation basis to curtail the demand.

## Page-2
Format-A2
Particulars of Generating Station which failed to meet forcasted requirement at the time of load restriction
(In relation to Format: A-1)
Year | Quarter | Month | Hour | Name of Generating Station | *Duration of failure to meet forecasted requirement (HRs.) Date Time Total |  |  |  | Quantum/ Percentage of Load Restriction Imposed
1 | 2 | 3 | 4 | 5 |  | 6 | 7 | 8
2025-26 | 2nd | JULY | 744 | - | - | - |  | - | -
|  | AUGUST | 744 | - | - | - | - | - | -
|  | SEPTEMBER | 720 | - | - | - | - | - | -
* Load restriction imposed in the state on rotation basis to curtail the demand(During evening peak hour).

## Page-3
Format-A3
Particulars of demand curtailed and areas affected due to failure of Generating Station to meet forcasted requirement at the time of load restriction
(In relation to Format: A-1)
Name of Gen. Station | Year | Quarter | Month | Hour | Duration of failure to meet forecasted requirement (HRs.) Date From To Total |  |  |  | L.R. Imposed in MW | Area / Consumer categories affected
1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 9 | 10 | 11
- | 2025-26 | 2nd | JULY | 744 | - | - | - | - | - | Load restriction imposed in the state on rotation basis to curtail the demand.
|  |  | AUGUST | 744 | - | - | - | - | -
|  |  | SEPTEMBER | 720 | 09.09.25 | 20:00 | 24:00 | 4 Hrs | 350
* Load restriction imposed in the state on rotation basis to curtail the demand(During evening peak hour).

## Page-4
B. TRANSMISSION SECURITY
Format-B1
Load Restriction due to non availability of Transmission Capacity, (Percentage of time)
(even though Generation was available)
Year | Quarter | Month | Total Hrs. of the month | Duration of restriction (in Hrs.) | Duration of failure to meet forecasted requirement (HRs.) Date From To Total |  |  | L.R. Imposed in MW | Remark | Percentage of time load restricted [=(5/4) *100]
1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 10 |  | 6
[5 empty] | - | - | - | -
2025-26 | 2nd | JULY | 744 | 0 | [5 empty] | 0
|  | AUGUST | 744 | 0 | [5 empty] | 0
|  | SEPTEMBER | 720 | 0 | [5 empty] | 0
Total |  |  | 2208 | 0 | [5 empty] | 0

## Page-5
B. TRANSMISSION SECURITY
Format-B2
Rescheduling of Generation due to non availability of Transmission Capacity, (Percentage of time)
(even though load restriction was not required)
Year | Quarter | Month | Total Hrs. | Duration of Generation rescheduled (HRs.) | Percentage of time Gen.rescheduled [=(5/4) *100]
1 | 2 | 3 | 4 | 5 | 6
2025-26 | 2nd | JULY | 744 | - | -
|  | AUGUST | 744 | - | -
|  | SEPTEMBER | 720 | - | -
Total |  |  | 2208 | NIL | NIL

## Page-6-59
Particulars of Transmission elements not available resulting in loss of Transmission capacity and Grid Sub-stations affected.
Sl. No. | Substation | Date | From | To | Duration | Transmission element (Line / Tfr. / CB etc.)not available | Reason for non-availability of Transmission element (schedule maintenance outage / forced outage*)with details | Grid Sub-stations affected (it can be more than one) | Interruption time (Hr. Min.) | Extent of Generation Rescheduling required |  | Energy lost in MU | Remarks | Feeders Affected
[10 empty] | MW rescheduled or estimated capacity restriction affected | Time: This should match with hours of non-availability in a month in Format B-2 as the case may be
1 | Meramundali | 30.06.25 | 8:24 | 01.07.25 16:30 | 28:10 | 220kV Meramundali-BSL CKT-I | At Meramundali end: Ir-29.15 kA, Iy-1.73 kA, Ib-1.48 kA, 0.3 KM At BSL end: Ir-8.69 kA, Iy-1.73 kA, Ib-1.48 kA, 3 KM | - | - | - | - | - | Insulator puncture at loc no-05 | -
2 | Bhawanipatna | 01.07.25 | 1:13 | 1:17 | 0:04 | 132kV Bhawanipatna-Bhawanipatna RTSS Feeder | O/C | Bhawanipatna RTSS | 0:05 | - | - | 2.3647e-05 | - | -
|  |  | 2:00 | 2:01 | 0:01
3 | Polasponga | 01.07.25 | 15:07 | 15:10 | 0:03 | 132kV Polasponga-Kendujhargarh RTSS Feeder | O/C, Ir- 301.2A, Iy- 221.1A, Ib- 114.6A | Kendujhargarh RTSS | 0:03 | - | - | 0.00041103 | - | -
4 | Kalarangi | 02.07.25 | 10:00 | 10:32 | 0:32 | 132kV Kalarangi-Duburi (old) Feeder | At Kalarangi end: R-N, Zone 1, Dist- 15.88km, Ir- 2.753kA At Duburi end: R-N, Zone 1, Dist- 17.39km, Ir- 3.975kA | - | - | - | - | - | - | -
5 | Balugaon | 02.07.25 | 10:59 | 10:59 | 0:00 | 132kV Balugaon-Chatrapur Feeder | At Balugaon end: Zone 1, Dist- 9.26km, Ib- 1.391kA At Chatrapur end: B-N, Zone 1, Dist- 46.78km, Ib- 1.797kA | - | - | - | - | - | A/R successful at both ends | -
| Balugaon | 02.07.25 | 11:01 | 15:47 | 4:46 | 132kV Balugaon-Chatrapur Feeder | At Balugaon end: B-N, Zone 1, Dist- 9.27km, Ib- 1.357kA At Chatrapur end: B-N, Zone 1, Dist- 46.75km, Ib- 1.77kA
6 | Rajgangpur | 02.07.25 | 13:20 | 13:50 | 0:30 | 132kV Rajgangpur-Kutra Feeder | Y-N, Zone 1, Dist- 4.3km, Iy- 5.048kA | - | - | - | - | - | - | -
7 | Bargarh New | 02.07.25 | 14:14 | 18:22 | 4:08 | 220kV Bargarh New-Bolangir New Feeder | At Bargarh New end: R-N, Zone 2, Dist- 38.2km, ir- 1.7kA | - | - | - | - | - | - | -
8 | Mendhasal | 02.07.25 | 14:43 | 15:05 | 0:22 | 220kV Mendhasal-Nayagarh Feeder | Ib-3.08kA, Distance-43.6km, Z-1 | - | - | - | - | - | AR successful at Nayagarh end | -
9 | Chatrapur | 02.07.25 | 15:48 | 18:39 | 2:51 | 132kV Chatrapur Balugaon Feeder | At Chatrapur end: B-N, Zone 1, Dist-46.87km, Ib- 1.78kA At Balugaon end: B-N, Zone 1, Dist- 9.13km, Ib- 1.364kA | - | - | - | - | - | Weather condition:Rainy | -
10 | Lapanga | 02.07.25 | 16:05 | 03.07.25 11:45 | 19:40 | 132kV Lapanga-Burla PH CKT-II | At Lapanga end: Y-B, Zone 1, Iy- 5.32kA, Ib- 7.94kA, Dist- 12.9km | - | - | - | - | - | Y-ph jumper snapped at location 106. | -
11 | Paradeep | 02.07.25 | 22:42 | 23:23 | 0:41 | 220kV Paradeep-Duburi New CKT-II | At Paradeep end: O/C on R-Ph to G, Zone 1, Dist - 43.6 KM, Ir=2.3 kA , Iy=364.6 A, Ib=438.05 A At Duburi New end: R-N, Dist-47.7 KM, Ir-3.35 KA, Zone-1 | - | - | - | - | - | - | -
12 | Budhipadar | 03.07.25 | 6:03 | 7:35 | 1:32 | 220kV Budhipadar-Kuarmunda Feeder | R-N, Zone 1, Dist- 2.878km, Ir- 22.56kA | - | - | - | - | - | A/R successful at Kuarmunda end | -
13 | Paralakhemendi | 03.07.25 | 6:34 | 6:38 | 0:04 | 132kV Paralakhemendi-Akhusingh Feeder | Tripped on Fault | - | - | - | - | - | - | -
14 | Bhubaneswar | 03.07.25 | 14:24 | 14:24 | 0:00 | 132kV Bhubaneswar-Chandaka CKT-II | O/C | - | - | - | - | - | - | -
15 | Udala | 04.07.25 | 15:30 | 16:36 | 1:06 | 132kV Udala-Balasore Feeder | Ia:0.72kA, Ib:0.10kA, Ic:0.14kA, Distance: 56.5km | - | - | - | - | - | Source Failure | -
16 | Kalimela | 04.07.25 | 15:53 | 16:12 | 0:19 | 220kV Balimela-Kalimela CKT-II | DUE TO FAULT | - | - | - | - | - | - | -
17 | Budhipadar | 05.07.25 | 22:30 | 06.07.25 00:45 | 2:15 | 220kV Budhipadar AAL CKT-I | Zone1, A-ph-N Fault,11.08km, 53.28ms,I=(10.48kA,10.58A,7.70A) | - | - | - | - | - | - | -
|  |  |  | 22:53 | 0:23 | 220kV Lapanga-Budhipadar CKT-II | R-N, Zone 3, Dist: -114.8km, Ir- 1.45kA
18 | Budhipadar | 05.07.25 | 22:54 | 22:54 | 0:00 | 132kV Budhipadar Kalunga Feeder | At Kalunga end: R-N, Zone 1, Dist- 27.08km, Ir- 3.22kA | - | - | - | - | - | A/R Successful at Kalunga end | -
19 | Budhipadar | 05.07.25 | 23:08 | 23:38 | 0:30 | 132kV Lapanga-Budhipadar Feeder | R-Y-B, Dist- 17.6km, Ir- 5.97kA, Iy- 6.36kA, Ib- 6.18kA | Budhipadar Sundargarah, MSP Brajarajnagar, Belpahar RTSS, Jharsuguda, Lakhanpur Kechhobahal RTSS MCL | 00:25 00:32 00:30 00:31 01:19 | - | - | 0.073009 | Jumper snapped in between loc-58-59 at Budhipadar end and R-ph conductor snapped from gantry point with LA falling from structure at Budhipadar end | -
|  |  |  | 07.07.25 23:00 | 47:52 | 132kV Budhipadar Kalunga Feeder | Tripped ph- R-N, Zone-1, Fault duration-0ms,, Fault Loc-18.69 km, Ir-4.167 KA,Iy-159.9 A,Ib-130.8 A,
|  |  |  | 23:37 | 0:29 | 132kV Brajrajnagar-Budhipadar Feeder | Failure From Source
|  |  |  | 23:46 | 0:38 | 132kV Brajrajnagar-Lakhanpur Feeder | Failure From Source
|  |  |  | 23:32 | 0:24 | 160MVA Auto TRF-I | P14D,B/U 132kV side, I=(5.580kA,5.048kA, 5.025kA,1.021kA) 220kV side-RYB-ph O/C
|  |  |  | 06.07.25 00:20 | 1:12 | 160MVA Auto TRF-II | P14I,B/U 132kV side,I_f=(5.636kA,534.6A, 5.392kA,5.901kA) 220kV side,RYB-ph O/C
|  |  | 23:10 | 06.07.25 00:10 | 1:00 | 132kV Lakhanpur-Budhipadar Feeder | Ia=5.58kA, Ib=5.04kA, Ic=5.025kA, In=1.021kA, Trip Time-240ms
|  |  |  | 23:46 | 0:36 | 132kV Brajrajnagar-Lakahanpur Feeder | Ia=5.636kA, Ib=4.6kA, Ic=5.392kA, In=5.90kA, Trip Time-240ms
|  |  |  | 06.07.25 00:42 | 1:32 | 132kV Jharsuguda-Budhipadar CKT-II | Rph-Bph,Zone-1,Distance=2.294km,Ir= 2.268kA, Iy= 850.4A, Ib= 2.249kA
|  |  |  | 06.07.25 01:24 | 2:14 | 132kV Jharsuguda-Budhipadar CKT-I | Rph-Bph,Zone-1,Distance=km, Ir= 2.001kA, Iy= 227.0A, Ib= 2.005kA
|  |  | 23:20 | 23:34 | 0:14 | 132kV Budhipadar-Sundergarh CKT-I & II | H/T for restoration of 132kV/33kV system
|  |  |  | 08.07.25 13:14 | 61:54 | 132kV Budhipadar-Bamra Feeder
|  |  |  | 23:33 | 0:13 | 20MVA TRF-I
|  |  |  | 23:38 | 0:18 | 132kV Budhipadar - Lapanga Feeder
|  |  |  | 06.07.25 00:25 | 1:05 | 132kV Budhipadar-Jharsuguda CKT-I
|  |  |  | 06.07.25 02:30 | 3:10 | 132kV Budhipadar-Jharsuguda CKT-II
|  |  |  | 23:37 | 0:17 | 132kV Budhipadar - Remja Feeder
|  |  |  | 06.07.25 00:43 | 1:23 | 12.5MVA TRF-II
|  |  |  | 23:40 | 0:20 | 132kV Budhipadar - MSP Feeder
|  |  | 23:43 | 06.07.25 01:45 | 2:02 | 132kV Budhipadar - MCL Feeder | Zone1, R-N, Dist- 13.39km, Ir- 3.868kA
|  |  | 23:46 | 06.07.25 00:10 | 0:24 | 220kV Budhipadar IB CKT-III | R-N, Zone 1, Dist- 11.46km, Ir- 9.742kA
|  |  | 23:50 | 06.07.25 00:11 | 0:21 | 220kV Budhipadar IB CKT-IV | R-N, Zone 1, Dist- 9.328km, Ir- 11.37kA
|  | 06.07.25 | 0:19 | 12:02 | 11:43 | 132kV Lapanga-Budhipadar Feeder | At Lapanga end: B-N, Dist- 5.3km At Budhipadar end: Zone 1, B-N, Dist- 12.7km
|  |  | 0:28 | 0:28 | 0:00 | 220kV Budhipadar IB CKT-II | R-N, Zone 1, Dist- 13.31km, Ir- 8.278kA
|  |  | 0:29 | 0:49 | 0:20 | 220kV Budhipadar IB CKT-III | R-N, Zone 1, Dist- 9.08km, Ir- 11.56kA
20 | Bolangir New | 05.07.25 | 23:28 | 23:46 | 0:18 | 132kV Bolangir New-Patnagarh CKT-II | Tripped On operation of DP Relay. | - | - | - | - | - | - | -
21 | Kantabanji | 06.07.25 | 1:35 | 1:37 | 0:02 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 596 A | Kantabanji RTSS | 0:02 | - | - | 0.0001316 | - | -
22 | Jharsuguda | 06.07.25 | 2:38 | 7:27 | 4:49 | 132kV Jharsuguda-Budhipadar CKT-II | R-Y-B, Zone 1, Dist- 2.832km, Ir- 3.631kA, Iy- 4.015kA, Ib- 3.812kA | - | - | - | - | - | - | -
23 | Budhipadar | 06.07.25 | 2:38 | 6:24 | 3:46 | 132kV Budhipadar - MCL Feeder | R-N, Zone 1, Dist- 13.39km, Ir- 0.273kA | MCL | 3:46 | - | - | 0.0714 | - | -
24 | Kantabanji | 06.07.25 | 7:20 | 7:25 | 0:05 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 600 A | Kantabanji RTSS | 0:05 | - | - | 0.00032901 | - | -
25 | Paradeep | 06.07.25 | 7:31 | 7:45 | 0:14 | 132kV Paradeep-Kendrapada Feeder | Tripped on O/C on B-Ph, Ir=183 A , Iy=144.8 A, Ib=489.5 A | Kendrapada Salipur | 00:14 00:05 | - | - | 0.0087366 | TRANSIENT FAULT | -
|  |  |  | 8:00 | 0:29 | 132kV Marshaghai-Kendrapada Feeder | O/C OPERATED IL1=.44 KA. IL2=0.43 KA, IL3=0.86 KA | [5 empty] | 132kV Paradeep-Marshaghai Feeder was in service
|  |  |  | 7:45 | 0:14 | 132kV Kendrapada-Salipur Feeder | Incomer failure from Kendrapada end | [5 empty] | P/S was availed from ICCL end on 132kV Bahugram - Salipur at 07:36 Hrs
|  |  |  | 7:54 | 0:23 | 132kV Kendrapada-Pattamundai Feeder | At Kendrapada end: E/F, IR=133A, IY=93.2KA, IB=294A No tripping at Pattamundai end | [5 empty] | -
26 | Meramundali | 06.07.25 | 7:45 | 17:35 | 9:50 | 400kV Meramundali-JSPL CKT-II | At Meramundali end: A/R unsuccessful, M1 - Z1B, SOTF, L1E, IL1 - 10.4 kA, 30.5 KM At JSPL end: A/R unsuccessful, IL1 - 12.14 KA, 4.56 KM | - | - | - | - | - | Insulator puncture at loc no 111 | -
27 | Paralakhemendi | 06.07.25 | 8:29 | 8:33 | 0:04 | 132kV Paralakhemendi-Akhusingh Feeder | Incomer Failed | - | - | - | - | - | - | -
28 | Sunabeda | 06.07.25 | 15:04 | 15:46 | 0:42 | 132kV Sunabeda-Jayanagar CKT-I | Fault located at location No. 35 of 132kV Jayanagar-Sunabeda CKT-II | Sunabeda HAL Potangi | 00:42 01:30 00:49 | - | - | 0.019077 | - | -
|  |  |  | 07.07.25 18:02 | 26:58 | 132kV Sunabeda-Jayanagar CKT-II
|  |  |  | 15:53 | 0:49 | 132kV Sunabeda-Potangi Feeder
29 | Balasore | 06.07.25 | 16:18 | 19:59 | 3:41 | 132kV Balasore-Balasore RTSS Feeder | Fault report: Dist R-ph OPTD,Zone-1,Dist-2.13KM,fault current:Ir=8.9KA,In=8.9 KA. | Balasore RTSS | 3:41 | - | - | 0.029873 | R-ph LA at Railway end is brust. | -
30 | Chandikhol | 06.07.25 | 19:56 | 08.07.25 12:34 | 40:38 | 132kV Chandikhol-MTPCL CKT-I | TRIPPED ON R PH O/C , E/F (Zone 1,DIST-9.9KM,IL1-2.2KA) AT CHANDIKHOLE GSS end WITH DP RELAY OPERATED. | - | - | - | - | - | - | -
31 | Bargarh New | 07.07.25 | 2:13 | 7:02 | 4:49 | 220kV Bargarh New-Katapali Feeder | MAIN-I DP(Z-2, A-G, LOC;-52.1 KM ), MAIN-II DP( Z-2, A-N, Loc-56.3 km, fault durat-393.7ms, Relay trip time-80.07ms,Ia-2.068KA,Ib-100.7A,& Ic-218A, ) | - | - | - | - | - | - | -
32 | Sambalpur | 07.07.25 | 2:17 | 11:39 | 9:22 | 132kV Katapali-Sambalpur Feeder | At Katapali end: Zone-2 in Y Phase OPTD, Ir=4.897A , Iy=5.097KA, Ib=5.295A, dis- 16.6km At Sambalpur end: Y-ph E/F, Ia=4.84 A, Ib=4.079 KA,Ic=5.29 A | Sambalpur | 1:18 | - | - | 0.065101 | - | -
|  |  | 3:35 | 14:18 | 10:43 | 31.5MVA TRF-I | Tripped due to 33KV IOCL feeder Breaker mechanical problem.
|  |  |  | 4:57 | 1:22 | 31.5MVA TRF-II
|  |  |  | 4:53 | 1:18 | 40MVA TRF-III
|  |  |  | 4:53 | 1:18 | 40MVA TRF-IV
33 | Lapanga | 07.07.25 | 4:11 | 12:38 | 8:27 | 220kV Lapanga-Katapali CKT-II | At Lapanga end: Zone-1, L3-E, DIST-12.5KM, IL2=9.23kA At Katapali end: Zone-2, FD=32.52KM, IB-2.8KA, L3-E | - | - | - | - | - | Rph Jumper snapped at loc no 40 OF CKT-II | -
|  |  | 4:38 | 8:55 | 4:17 | 400kV Lapanga-VAL CKT-I | AT Lapanga end: Zone-2, L3-E, DIST-13.8KM, IL1=0.792kA, IL2=4.05KA, IL3=20.92KA
|  |  | 4:48 | 15:13 | 10:25 | 400kV Lapanga-VAL CKT-II | AT Lapanga end: Zone-1, L1-E, DIST-4.38KM, IL1=15.71kA, IL2=1.61KA, IL3=1.99KA At VAL end: Zone-2, DIST=10.9KM, IR=12.3KA
|  |  | 4:48 | 6:21 | 1:33 | 400kV Reactor 2 | AT Lapanga end: Zone-1, DIST-346.6KM, IL1=43.79A, IL2=101.1A, IL3=104.5A
|  |  | 5:15 | 6:00 | 0:45 | 400kV Reactor 1 | AT Lapanga end: Zone-1, IL1=20.20A, IL2=102.2A, IL3=100.2A
|  |  | 5:15 | 5:15 | 0:00 | 400kV Lapanga-Meramundali CKT-I | A/R successful M1: L1E, Z1B, IL1- 1.92 kA M2: L1E, Z1B, IL1-1.92 kA
34 | Nimapara | 07.07.25 | 8:42 | 12:44 | 4:02 | 132kV Nimapara-Pratapsasan Feeder | At Nimapara end : BCN, Z1,D=16.07KM, Ia=7A, Ib=3.15KA, Ic=2.59KA At Pratapsasan end: CN, Z1,D=24.28KM, Ia=78.6A, Ib=67.5A, Ic=1.5KA ,AR Successful | - | - | - | - | - | - | -
35 | Kantabanji | 07.07.25 | 10:50 | 10:55 | 0:05 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 592 A | Kantabanji RTSS | 0:05 | - | - | 0.00032901 | - | -
36 | Meramundali | 07.07.25 | 14:02 | 14:53 | 0:51 | 100MVA Auto TRF-I | 220kV: OLTC/Bucholz/OSR indication 132kV: Inter tripping | - | - | - | - | - | Charged after isolating faulty cable | -
37 | Akhusingh | 07.07.25 | 20:03 | 20:07 | 0:04 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
| Akhusingh | 07.07.25 | 23:21 | 23:25 | 0:04 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | [6 empty] | -
38 | Lapanga | 08.07.25 | 3:45 | 15:44 | 11:59 | 400kV Lapanga-VAL CKT-I | At Lapanga end: L3-E, Zone-2, DIST-16.12KM, IL1-1.080KA, IL2-2.085kA, IL3-12.43KA At VAL end: z1,dist=13.98km, IL3=25.96KA | - | - | - | - | - | B Ph INSULATOR DAMAGED at location 13 SO TRIPPED IN FAULT | -
39 | Bhubaneswar | 08.07.25 | 14:10 | 14:10 | 0:00 | 132kV Bhubaneswar-Phulnakhara Feeder | IA=789.86A,IB=102.74A,IC=71.98A,In-642.29 | - | - | - | - | - | - | -
40 | Bargarh New | 08.07.25 | 23:38 | 09.07.25 00:24 | 0:46 | 220kV Bargarh New-Katapali Feeder | MAIN-I DP(Z-2, A-G, LOC;-64.6 KM ), MAIN-II DP( Z-2, A-N, Loc-64.68 km, fault durat-391.8ms, Relay trip time-80.03ms,Ia-1.422KA,Ib-130.6A,& Ic-299.8A, Fault resistance;-1.003ohm) | - | - | - | - | - | - | -
41 | Narendrapur | 09.07.25 | 17:42 | 17:44 | 0:02 | 132kV Narendrapur-Narendrapur RTSS Feeder | Tripped on R-ph & B-ph O/C. (Ir=1.02KA,Ib=1.02KA) | Narendrapur RTSS | 0:02 | - | - | 0.00017216 | - | -
42 | Barbil | 09.07.25 | 21:49 | 10.07.25 23:42 | 25:53 | 132kV Barbil-KSP(RML) Feeder | At Barbil GSS end: ABC(Over voltage),Zone-II, Dist=31.51KM,Ia=62.42A,Ib=2.697kA,Ic=169.7A At KSP end: ABC(Over voltage),Zone-I, Dist=5.2KM,Fault Current: Ia=99.12A,Ib=159.3A,Ic=86.16A | KSP(RML) | 2:22 | - | - | 0.026384 | On dt.10.07.2025 at 00:11Hrs 132kV Barbil-KSP(RML) Feeder was idle charged from Barbil GSS end. | -
43 | Rairakhol | 09.07.25 | 22:58 | 23:11 | 0:13 | 132kV Rairakhol-Maneswar Feeder | At Rairakhol end-Distance -35.87KM, IL1-130.5A, IL2-99.15A, IL3-155.7A, fault loop- ABC , Zone-1 At Maneswar end- Distance -22.6KM, IL3-2.61KA, IL3-E, Zone-1 | Rairakhol, Rairakhol RTSS | 0:13 | - | - | 0.0022634 | Power supply availed from Maneswar Grid end at 23:11 hrs . | -
44 | Duburi New | 10.07.25 | 5:21 | 11.07.25 16:04 | 34:43 | 400kV Duburi New-Pandibil Feeder | Main-1(7SA52A)-IL2-3.47KA,Loop-L2-E,fault Distance-84.9 Km,Zone-1,Main-2(REL670)- IL2-3.85KA,Loop-L2-E,fault Distance-83.13Km,Zone-1 | - | - | - | - | - | one of the insulator string of Y phase conductor was broken at LOC-665 (Tension Tower) | -
45 | Balasore | 10.07.25 | 13:41 | 13:41 | 0:00 | 132kV Balasore-Udala Feeder | Fault report: Dist B-ph OPTD,Zone-1,Carrier send,A/R OPTD,Dist-10.98KM,fault current:Ib=0.4KA. | - | - | - | - | - | A/R was opertaed successfully. | -
| Udala | 10.07.25 | 13:41 | 13:42 | 0:01 | 132kV Balasore-Udala-Betanati Feeder | A/R operated and Closed at Balasore grid end. | [5 empty] | Source Failure | -
46 | Budhipadar | 10.07.25 | 15:42 | 17:33 | 1:51 | 220kV Budhipadar-AAL CKT-II | D/P 1- (Areva p442):Zone 1, Fault loop- R-N, Fault Distance- 5.791 km, IL1-14.92KA, IL2- 9.185A, IL3- 7.341A, Fault resistance-1.282Ohm,Fault Duration-50.06ms D/P 2- (Areva p442): Fault loop- L1-E, Fault Distance- 5.7km,Zone 1, IL1-15.37KA,IL2-8.421A,IL3-6.785A,fault duration-48.39ms,fault resistance-1.092ohm | - | - | - | - | - | weather-Lightening & Rain | -
47 | Akhusingh | 11.07.25 | 1:21 | 1:24 | 0:03 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
48 | Meramundali-B | 11.07.25 | 8:07 | 8:25 | 0:18 | 220kV Meramundali B-Duburi Feeder | Transient fault. Z3, Dist.- 98.43 KM, Ir- 1.652 KA | - | - | - | - | - | - | -
49 | Therubali | 11.07.25 | 13:06 | 17:30 | 4:24 | 220kV Therubali-Aska New Feeder | At Therubali end: YB,Ir-296.4A,Iy-1.5kA,Ib-1.2kA At Aska New end: YB,Z-1,36.9KM,Ir-295.9A,Iy-3.476kA,Ib-3.635kA | - | - | - | - | - | - | -
50 | Goda | 11.07.25 | 13:26 | 16:44 | 3:18 | 220kV Goda -Duburi Feeder | At Goda end: E/F, Ir-201.2A,Iy-189.9A,Ib-1.782kA,Dist-30.67kM,Zone-1 At Duburui end: E/F, Ir-208.0A,Iy-186.9A,Ib-7.743kA,Dist-7.769kM,Zone-1 | - | - | - | - | - | Weather condition : Heavey rain & lighting | -
51 | Rourkela | 11.07.25 | 14:55 | 16:37 | 1:42 | 132kV Rourkela-Tarkera CKT-II |  | - | - | - | - | - | - | -
52 | Duburi New | 11.07.25 | 16:18 | 12.07.25 14:40 | 22:22 | 220kV Duburi New- Jindal Feeder2 | Main-1: DP RELAY (7SA52) – Fault Loop-L1-E, Fault distance-1.2 KM, IL1-16.99 KA, Zone-1,IL1=16.99KA, IL2=0.26 KA,IL3=0.4 KA Main-2: DP RELAY (P444) – R ph Trip,Fault Loop-A-N, Fault distance-865.8M, IL1-15.4 KA, IL2=0.272 KA,IL3=0.374 KA , Zone-1 | - | - | - | - | - | The Earth Wire between tower loc no.4 & 5 has snapped during OPGW stringing work . | -
53 | Paralakhemendi | 12.07.25 | 1:19 | 1:22 | 0:03 | 132kV Paralakhemendi-Akhusingh Feeder | Tripped on Fault | - | - | - | - | - | - | -
54 | Polasponga | 12.07.25 | 7:56 | 7:58 | 0:02 | 132kV Polasponga-Kendujhargarh RTSS Feeder | Back up relay,O/C, IA=299.3A, IB=257.5A, IC=47.2A, INM=7.520A, IND=5.892A | Kendujhargarh RTSS | 0:02 | - | - | 0.00027402 | - | -
55 | Rajgangpur | 12.07.25 | 10:59 | 11:22 | 0:23 | 132kV Rajgangpur-Tarkera CKT-II | At Rajgangpur end: A/R SUCCESSFUL, CGT, DISTANCE=19.67 KM, IA=54 A, IB=63 A,IC=650 A At Tarkera end: L3-N,Zone-2,DISTANCE=-1 KM, IL1=5.33 A,IL2=5.88 A,IL3=1966.8 A | - | - | - | - | - | - | -
56 | Mendhasal | 12.07.25 | 11:36 | 11:36 | 0:00 | 220kV Mendhasal-Nayagarh Feeder | At Mendhasal end: Ib-4.06KA, Dist-10.7KM, Zone-1 At Nayagarh end: Ib-1.419kA, Dist-51.14km, Zone-3 | - | - | - | - | - | AR successful at both end | -
57 | Therubali | 12.07.25 | 12:08 | 13:02 | 0:54 | 220kV Therubali-Aska New Feeder | At Therubali end: BN,Z-1,150.7KM,Ir-196.4A,Iy-201.4A,Ib-199.7A At Aska New end: BN,Z-1, 56.8KM,Ir-78.45A,Iy-79.19A,Iy-201.4A,Ib-3KA,AR-Lockout. | - | - | - | - | - | - | -
58 | Narasinghpur | 12.07.25 | 13:11 | 16:42 | 3:31 | 220kV Narasinghpur-Bhanjanagar CKT-II | At Narasinghpur end: Zone-1,Distance-38.67km Ir-2.736kA,Iy-2.539kA,Ib-206.2A At Bhanjanagar end: Zone-1,Distance-43.76km Ir-3.447kA,Iy-3.63kA,Ib-197.6A | - | - | - | - | - | - | -
59 | Balasore | 12.07.25 | 14:05 | 14:05 | 0:00 | 220kV Balasore-Bhadrak Feeder | Balasore end : Main-I: Dist B-ph protn optd,carrier send,A/R Optd,dist-4.24KM,Fault current ,Ir-377.5A,Iy-530.6A,Ib-3.8KA,Zone-1. Main-II:Dist B-ph optd,carrier send,A/R optd,Dist-4.1KM,Fault current Ir-264.5A,Iy-534A,Ib-2947A. Bhadrak end: Main-1:Trip Phase-C,Zone-2,Dist-69.29 KM,Ia-99.90A,Ib-378.4A,Ic-1.979 KA. Main-II: Trip phase-C,Dist-49.46KM,Zone-2,Fault current Ia-102.1A,Ib-375.5A,Ic-1.972 KA. | - | - | - | - | - | A/R operated sucessfully. | -
60 | Joda | 12.07.25 | 14:19 | 15:53 | 1:34 | 220kV Joda-TTPS CKT-II | At 14:19Hrs 220kV Joda-TTPS CKT-II Feeder tripped at both end and A/R operated at Joda end but again Tripped with following relay details. AT Joda end:- Event -0,DP Relay Tripped DP Main –I,Start ph-ABN Zone-02,AR LOCKOUT SHOT Fault Distance: 138.5KM Trip Phase-ABC,AT Joda end:- Event -01,DP Relay Tripped DP Main –I,DP Main-II AT Joda end:- Event -0,DP Relay Tripped Event -1,DP Relay Tripped Relay at TTPS end:-D.P Relay Zone-01,Trip ph-ABC Fault Distance=3.442KM | - | - | - | - | - | NO FAULT FOUND | -
61 | Telkoi | 12.07.25 | 14:20 | 16:29 | 2:09 | 220kV Telkoi-TTPS Feeder | Tripped due to CN fault | - | - | - | - | - | E/F | -
62 | Jaleswar | 12.07.25 | 14:37 | 15:09 | 0:32 | 132kV Baripada PG-Jaleswar Feeder | Tripped from both end. | - | - | - | - | - | - | -
63 | Aska New | 12.07.25 | 14:49 | 14:49 | 0:00 | 220kV Aska New-Theruvali Feeder | A/R optd on B-Ph E/F ,Z1,A/R close,D=41.7km,IB=2.49KA | - | - | - | - | - | - | -
64 | Baripada | 12.07.25 | 14:50 | 16:21 | 1:31 | 132kV Baripada-Baripada(PG) Feeder | Relay indication details from Baripada grid end : DP relay indication details : A/R success ,Zone -I ,Active group -I ,Y-Phase trip ,satarted phase -YN,Tripped phase -RYB ,Fault duration- 51.61ms ,Relay trip time -79.91ms, fault location -7.857KM , IR=433A, IY=346.8A, IB=262.2A, VRN=75.36KV, VYN=6.784KV, VBN=75.72KV . Relay indication details from PGCIL grid end : DP relay operated ,Y-G fault ,IR=406A, IY=8.55KA, IB=244.3A, VRN=43.62KV, VYN=38.83KV, VBN=98.51KV ,Zone- I . | Baripada Betanati | 01:13 00:10 | - | - | 0.03358 | There was no P/S at BARIPADA GSS either from PGCIL or Betanati GSS due to tripping of single source 132kV BARIPADA-PGCIL Line from PGCIL grid end .A/R was success at BARIPADA grid end of the mentioned line .Weather condition :- Heavy rain and thundersterm . | -
|  |  |  | 16:03 | 1:13 | 132kV Baripada-Betanati Feeder | SOURCE FAILURE due to tripping 132kV BARIPADA -PGCIL Line from PGCIL grid end . Relay indication details from Baripada grid end : DP relay indication details : A/R success ,Zone -I ,Active group -I ,Y-Phase trip ,satarted phase -YN,Tripped phase -RYB ,Fault duration- 51.61ms ,Relay trip time -79.91ms, fault location -7.857KM , IR=433A, IY=346.8A, IB=262.2A, VRN=75.36KV, VYN=6.784KV, VBN=75.72KV . Relay indication details from PGCIL grid end : DP relay operated ,Y-G fault ,IR=406A, IY=8.55KA, IB=244.3A, VRN=43.62KV, VYN=38.83KV, VBN=98.51KV ,Zone- I .
65 | Bhograi | 12.07.25 | 15:10 | 16:40 | 1:30 | 132kV Bhograi-Baripada(PG) Feeder | At Bhograi end: B-G,Z-2,FL-107.7KM,IR-20.9A,IY-20.3A,IB-368.9A At Baripada PG end: B-G,Z-1,FL-13.58KM,IR-98.35A,IY-130.2A,IB-2.640KA | - | - | - | - | - | - | -
66 | Jaleswar | 12.07.25 | 15:10 | 17:02 | 1:52 | 132kV Baripada PG-Jaleswar Feeder | Tripped from both end. | - | - | - | - | - | - | -
67 | Therubali | 12.07.25 | 15:40 | 20:30 | 4:50 | 220kV Therubali-Aska New Feeder | At Therubali end: BN,Z-1,168.5KM,Ir-81A,Iy-85A,Ib-82A,SOTF,AR Lockout. At Aska New end: BN,Z-1, 33.15KM,Ir-210A,Iy-301.5A,Ib-3.024KA,AR-Close | - | - | - | - | - | - | -
68 | BC Mohanty Sw. Stn. | 12.07.25 | 15:41 | 15:53 | 0:12 | 132kV BC Mohanty-Tomka RTSS Feeder | B/U relay optd. Ia=237.1A, Ic=239.8A Van=74.41KV, Vbn=76.43KV, Vcn=76.72KV | Tomka RTSS | 0:12 | - | - | 0.00095831 | - | -
69 | Akhusingh | 12.07.25 | 17:08 | 17:11 | 0:03 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
70 | Hinjili GIS | 12.07.25 | 18:00 | 18:53 | 0:53 | 132kV Aska New - Hinjili Feeder | At Hinjili end: B-ph E/F, Zone-1, Dist. : 2.682 KM, Ia = 138.2 A, Ib = 704.5 A, Ic = 352.0 A At Aska New end: B-ph E/F, Zone-2, Dist. : 22.67 KM, Ir = 123.7 A, Iy = 696.7 A, Ib = 3036 A | Hinjili | 0:53 | - | - | 0.0067934 | - | -
|  |  |  | 19:04 | 1:04 | 132kV Berhampur - Hinjili Feeder | At Hinjili end: B-ph E/F, Zone-1, Dist. : 1.573 KM, Ia = 136 A, Ib = 643.6 A, Ic = 227.6 A At Berhampur end: B-ph E/F, Zone-1, Dist. : 15.69 KM, Ir = 135.4 A, Iy = 638.1 A, Ib = 3223 A
71 | Rourkela | 13.07.25 | 5:29 | 6:08 | 0:39 | 132kV Rourkela-Bhalulata- Jaganath Steel Feeder | TRIPPED ON AGT, LOC= 25.95, IA=3.1KA, IB= 16A, IC= 27A, IN= 0, IG= 3.18KA, GROUP 2, Zone-1. | Bhalulata RTSS | 7:55 | - | - | 0.032051 | - | -
|  |  | 6:09 | 7:56 | 1:47 |  | TRIPPED ON AGT, LOC= 25.86, IA= 3171A, IB= 16A, IC= 12A, IN=0, IG= 3188A, GROUP-2, Zone-1.
|  |  | 8:48 | 9:17 | 0:29 |  | TRIPPED ON CGT, LOC= 41.75, IA= 18A, IB= 16A, IC= 2069A, IN=0, IG= 2075A, Zone-1.
|  |  | 10:57 | 15:57 | 5:00 |  | TRIPPED ON BGT, LOCATION= 38.25A, Zone-1, GROUO-2, IA= 14A, IB= 2193A, IC= 8A, IN=0A, IG= 2206A.
72 | Joda | 13.07.25 | 9:55 | 10:44 | 0:49 | 220kV Joda-Ramchandrapur Feeder | AT Joda end: Started phase-BN, Zone-01, Dist: 6.190KM, IA=425.6A, Ib=4.534KA, Ic=299.3A At Ramchandrapur end: Zone-2, Trip ph-BG, Distance=129.9KM, Ia=.51kA, Ib=1.50kA, Ic=.30KA | - | - | - | - | - | NO FAULT FOUND | -
73 | Kantabanji | 13.07.25 | 9:58 | 10:05 | 0:07 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 400A | Kantabanji RTSS | 0:07 | - | - | 0.00046061 | - | -
74 | Aska New | 13.07.25 | 11:22 | 11:22 | 0:00 | 220kV Aska New-Theruvali Feeder | A/R optd on B-Ph E/F ,Z1,A/R close,D=44.8km,IB=2.26KA | - | - | - | - | - | - | -
75 | Duburi | 13.07.25 | 13:42 | 15:31 | 1:49 | 132kV Duburi - BRPL Feeder | Tripped on DP relay. | - | - | - | - | - | - | -
76 | Narendrapur | 13.07.25 | 16:25 | 16:25 | 0:00 | 220kV Narendrapur-Aska New Feeder | At Narendrapur end: A to G trip, Ia=1719, Ib=127A, Ic=101A, Z1, Loc=55.06km At Aska New end: Zone-I,A/R close , Fault location- 14.10Km,Ir=4.22KA | - | - | - | - | - | Heavy Thunderstorm and lightening. | -
77 | Kantabanji | 13.07.25 | 17:19 | 17:22 | 0:03 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 360A | Kantabanji RTSS | 0:03 | - | - | 0.0001974 | - | -
78 | Jayapatna | 13.07.25 | 23:33 | 23:55 | 0:22 | 220kV Jayapatna-Kasipur Feeder | O/C (Y-Ph), Ir- 0.602kA, Iy- 0.635kA, Ib- 0.629kA | Jayapatna, Megalift Dabugaon | 00:22 00:10 | - | - | 0.0048469 | - | -
[6 empty] | 220kV Jayapatna-Indravati Feeder | No 220kV and 132kV incoming power supply to GSS,Jayapatna due to tripping of 220kV Kasipur Feeder CB at both end, 220kV Indravati Feeder CB at Indravati end & 132kV Tentulikhunti-Dabugaon Feeder CB tripped at Tentulikhunti end
160MVA AUTO TRF-I & TRF-II
132kV Jayapatna-Dabugaon Feeder
132kV Jayapatna-Megalift CKT-I & II
132kV Jayapatna-Megalift CKT-II
40MVA TRF-I & TRF-II
|  |  |  | 23:43 | 0:10 | 132kV Tentulikhunti- Dabugaon Feeder | Distance Protection,AR Lockout Zone 1
79 | G.Udayagiri | 14.07.25 | 4:11 | 4:19 | 0:08 | 132kV Bhanjanagar-G.Udaygiri Feeder | At Bhanjanagar end: Zone-1 , D-8.885KM, IL1-263.4Amp, IL2-5.81KA & IL3-150.8Amp, A/R operated successfully. At G.Udayagiri end: Zone-1 , D-37.3KM, IL1-0.28KA, IL2-0.20KA & IL3-0.17KA. | G.Udayagiri Phulbani | 00:08 00:13 | - | - | 0.0033442 | - | -
[6 empty] | 132kV G.Udaygiri-Phulbani Feeder | At Bhanjanagar end: Zone-1 , D-8.885KM, IL1-263.4Amp, IL2-5.81KA & IL3-150.8Amp, A/R operated successfully. At G.Udayagiri end: Zone-1 , D-37.3KM, IL1-0.28KA, IL2-0.20KA & IL3-0.17KA.
80 | Joda | 14.07.25 | 4:18 | 4:58 | 0:40 | 220kV Joda-Telkoi Feeder | At Joda end: Zone-1, Dist- 75.78KM, Ia=1.711KA, Ib=1.719kA, Ic=447.5A At Telkoi end: Zone-I, Dist- 18.73KM, Ia= 2.479KA, Ib=2.480kA, Ic= 428.8A | Telkoi | 0:40 | - | - | 0.0012099 | Weather condition: Heavy rain & thunderstorm, NO FAULT FOUND | -
|  |  |  | 5:09 | 0:51 | 220kV Joda-TTPS Feeder | At Joda end: Zone-1, Dist- 76.23KM, Ia=1.490KA, Ib=1.711kA, Ic=2.720KA At TTPS end: Zone-I, Dist. = 66.30KM, Ia= 3.415KA, Ib=3.897kA, Ic= 4.289kA
81 | Kalunga | 14.07.25 | 5:00 | 5:00 | 0:00 | 132kV Kalunga-Budhipadar Feeder | Tripped ph- R-N, Zone-1, Fault duration-154.9 ms,, Fault Loc-77.57 km, Ir-1.267 KA,fault resistance-1.096 ohm, | - | - | - | - | - | Auto-recloser successful at Kalunga end and stood ok. (heavy Lightening & raining). | -
82 | Rourkela | 14.07.25 | 5:16 | 13:58 | 8:42 | 132kV Rourkela-Tarkera CKT-II |  | - | - | - | - | - | - | -
83 | Rajgangpur | 14.07.25 | 6:59 | 6:59 | 0:00 | 132kV Rajgangpur-Bamra Feeder | At Rajgangpur end: A/R SUCCESSFUL, A-N,Zone-1, DISTANCE=13.22 KM, IA=3252 A At Bamra end: A/R SUCCESSFUL, L1-N, Zone-1, DIST- 28.83 KM, IA=2151 A | - | - | - | - | - | HEAVY LIGHTENING & RAINFALL. | -
84 | Kalunga | 14.07.25 | 7:13 | 7:13 | 0:00 | 132kV Kalunga-Budhipadar Feeder | Tripped ph- R-N, Zone-1, Fault duration-59.96 ms,, Fault Loc-59.12 km, Ir-1.399 KA, | - | - | - | - | - | Auto-recloser successful at Kalunga end and stood ok. (heavy Lightening & raining). | -
85 | Joda | 14.07.25 | 10:15 | 10:56 | 0:41 | 220kV Joda-TTPS CKT-II | No indication and alaram at Joda end AT TTPS end: Z4 fault, VT fail alarm, IA=125A, IB=125A, IC=127A | - | - | - | - | - | - | -
86 | Kesinga | 14.07.25 | 12:41 | 13:20 | 0:39 | 132kV Kesinga-Lanjigarh Feeder | Distance protection relay operated,Zone-1,distance-49.72 KM,R-67.5 A,Y-149.4 A,B-1.5 KA | - | - | - | - | - | - | -
87 | Kamakhyanagar | 14.07.25 | 12:43 | 13:29 | 0:46 | 132kV Kamakhyanagar-OPCL Feeder | Zone-1,IA-2.26kA,IB-131.3A,IC-48.01KA,DISTANCE-17.71KM | - | - | - | - | - | - | -
88 | Akhusingh | 14.07.25 | 17:53 | 17:55 | 0:02 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
89 | Bhawanipatna | 14.07.25 | 19:06 | 19:09 | 0:03 | 132kV Bhawanipatna-Lanjigarh RTSS Feeder | TRIPPED ON O/C | Lanjigarh RTSS | 0:03 | - | - | 0.00036737 | - | -
90 | Rayagada | 15.07.25 | 6:21 | 6:27 | 0:06 | 132kV Rayagada-Podagada Feeder | Incomer Rayagada -podagada Feeder supply failure | - | - | - | - | - | Changeover of supply from Machkund supply to Pottangi supply due to Machkund supply fail. | -
132kV Rayagada-Akhusingh Feeder
91 | Jayanagar | 15.07.25 | 6:46 | 7:22 | 0:36 | 132kV Machhkund-Jayanagar Feeder | O/C | Jayanagar Podagada Rayagada | 00:41 00:13 00:06 | - | - | 0.012148 | - | -
92 | Paradeep | 15.07.25 | 10:38 | 13:35 | 2:57 | 220kV Paradeep-Duburi New CKT-I | Tripped on O/C on B-Ph to G, Zone 1, Dist - 56.4 KM, Ir=0 kA , Iy=0 kA, Ib=2.04 kA | - | - | - | - | - | DUE TO VEHICLE MOVEMENT BY NHAI AT LOC 194 ACCIDENTALLY TOUCHED THE CONDUCTOR | -
93 | Kalunga | 15.07.25 | 11:53 | 11:53 | 0:00 | 132kV Kalunga-Budhipadar Feeder | Tripped ph- B-N, Zone-1, Fault duration-60.05ms,, Fault Loc-59.12 km, Ib-2.541 KA, fault resistance-8.452 ohm | - | - | - | - | - | Auto-recloser successful at Kalunga end and stood ok. | -
94 | Bamra | 15.07.25 | 12:13 | 12:13 | 0:00 | 132kV Budhipadar-Bamra Feeder | At Budhipadar end: Zone 2, Fault loop- C-N, Fault Distance- 45.73 km, IL1- 10.84A, IL2-11.27A, IL3- 2.004KAA/R Successful. | Bamra | 0:53 | - | - | 0.005145 | - | -
|  |  |  | 13:06 | 0:53 | 132kV Rajgangpur-Bamra Feeder | At Rajgangpur end: B-N, Zone-2, DIST- 41.26 KM, Ib- 2052 A At Bamra end: Zone-1, DISTANCE=8.779 KM, Ib- 3123A
95 | Mendhasal | 15.07.25 | 12:15 | 12:15 | 0:00 | 220kV Mendhasal-Nayagarh Feeder | At Mendhasal end: Ib-3.24KA,Dist-42.5KM,Zone-1 At Nayagarh end: Ib-1.71KA,Dist-23.20km | - | - | - | - | - | AR successful at both end | -
96 | Atri | 15.07.25 | 12:57 | 12:57 | 0:00 | 220kV Atri- Narendrapur CKT-II | At Atri end: B phase-N, Zone-1, IB= 3.63 kA,Dist= 35.64 km At Narendrapur end: B phase-N, Zone-1,IB= 1.30 kA, Dist= 96.4 km | - | - | - | - | - | A/R successful from both the ends | -
97 | Narendrapur | 15.07.25 | 23:00 | 23:00 | 0:00 | 220kV Narendrapur-Atri CKT-II | At Narendrapur end: C to N, Z1, Ia=28.21A, Ib=36.68A, Ic=1.308KA At Atri end : A/R successful, C-ph to N, Z1, Ia=28.65A,Ib=47.59A,Ic= 3.63KA, Loc=35.54Km | - | - | - | - | - | Heavy Thunderstorm & Lightning | -
98 | Gondia | 16.07.25 | 5:13 | 5:30 | 0:17 | 132kV Gondia-JFAL Feeder | Tripped from JFAL end | JFAL | - | - | - | - | - | -
99 | Polasponga | 16.07.25 | 7:45 | 11:40 | 3:55 | 132kV Joda-Polasponga Feeder |  | - | - | - | - | - | - | -
100 | Jayanagar | 16.07.25 | 11:40 | 13:09 | 1:29 | 132kV Machhkund-Jayanagar Feeder | Y-G,Z-2,Dist-35.3Km,If-1.566KA | Jayanagar Podagada | 00:15 00:18 | - | - | 0.0052251 | - | -
101 | Meramundali | 16.07.25 | 13:04 | 13:04 | 0:00 | 220kV Meramundali-Narsinghpur Feeder | At Meramundali end: A/R successful, R-N, Z1, 26.09 KM, Ir- 5.36 KA At Narsinghpur end: A/R successful, R-N, Z1, 31.9 KM, Ir-1.06 KA | - | - | - | - | - | - | -
102 | Joda | 16.07.25 | 14:01 | 17:06 | 3:05 | 220kV Joda-Ramchandrapur Feeder | At 14:01Hrs 220kV Joda-Ramchandrapur Feeder tripped at both ends and A/R operated at Joda end but again tripped with following relay indication At Joda end:-EVENT-0,DP Relay Tripped DP Main –I: Start ph –BN,Trip ph –B Zone-01,Fault Distance: 1.411KM EVENT -01:DP Relay Tripped DP Main –I: Start ph –BN Trip ph –B Zone-01,Fault Distance: 1.769KM DP Main-II,Fault Distance=1.53KM Faulty Phase: BGT,Zone-01 At Ramchandrapur end: DP relay: Zone- 2,Trip ph- BG,Dist=122.9KM Fault current: Ia-0.65KA,Ib-1.78KA,Ic-0.27KA,. | - | - | - | - | - | No fault found | -
103 | Tarkera | 16.07.25 | 14:08 | 15:43 | 1:35 | 132kV Tarkera-Kalunga Feeder | DP Relay :- Loop : B-N, Dist=1.883 km, Zone-1, IA=144.45 A, IB=11983.2 A, IC=79.0 A, IN=12013 A | - | - | - | - | - | A CUTTING TREE FALL TOWARS THE LINE | -
104 | Chainpal | 16.07.25 | 14:32 | 14:44 | 0:12 | 132kV Chainpal-Angul Feeder | Feeder tripped in DP relay in Rphase fault distance 8.4km, fault current 5.8KA | - | - | - | - | - | - | -
105 | Jayanagar | 16.07.25 | 15:17 | 15:22 | 0:05 | 132kV Machhkund-Jayanagar Feeder | O/C | - | - | - | - | - | - | -
106 | Polasponga | 17.07.25 | 7:35 | 11:20 | 3:45 | 132kV Joda-Polasponga Feeder |  | - | - | - | - | - | - | -
107 | Rayagada | 17.07.25 | 11:17 | 11:27 | 0:10 | 132kV Rayagada-Podagada Feeder | E/F, B-Phase, Zone-1,Distaance-21Km from Podagada end. | Rayagada | 0:10 | - | - | 0.0018769 | - | -
132kV Rayagada-Akhusingh Feeder
108 | Podagada | 17.07.25 | 11:23 | 13:14 | 1:51 | 132kV Podagada-Rayagada Feeder | Distance Protection relay optd. , Zone-1, Distance= 36.7 KM, Trip time= 750mS, Pickup Time= 830mS, IL1= 0.01 KA,IL2=0.01 KA,IL3=0.75 KA. | - | - | - | - | - | - | -
109 | Kharagprasad | 17.07.25 | 12:22 | 13:10 | 0:48 | 132kV Kharagprasad-MGM Feeder | Tripped over O/C on B-Ph Ib=158.3A , SLDC switch On code-SN-08 | MGM | 0:48 | - | - | 1.3656e-07 | O/C | -
110 | Kalunga | 17.07.25 | 12:32 | 12:32 | 0:00 | 132kV Kalunga-Budhipadar Feeder | Tripped ph- B-N, Zone-1, Fault duration-158.4ms,, Fault Loc-73.14 km, Ib-1.201 KA, fault resistance-14.89 ohm | - | - | - | - | - | - | -
|  |  | 12:48 | 16:00 | 3:12 |  | R-B-N, Zone-1, location-22.94 km, Ir-3.784KA, Iy- 22.0A, Ib- 4.353KA
111 | Rajgangpur | 17.07.25 | 12:51 | 13:41 | 0:50 | 132kV Rajgangpur-Rajgangpur RTSS Feeder1 | RTT=34 ms,AGT,IA=9034.8 A, IB=58.8 A, IC=0.4 A,IG=9084.4 A, MT OPERATED | - | - | - | - | - | - | -
112 | Rajgangpur | 17.07.25 | 20:47 | 21:27 | 0:40 | 132kV Rajgangpur-Tarkera CKT-II | At Rajgangpur end: A/R BLOCK,Zone-1, DISTANCE=3.26 KM, IA=214 A,IB=6877 A, IC=6136 A At Tarkera end: L2-L3,Zone-2,DISTANCE=23.98 KM, IL1=201.1 A,IL2=4054 A,IL3=3513A | - | - | - | - | - | 132kV Y-PH CT burst at Rajgangpur GSS | -
|  |  |  | 18.07.25 18:57 | 22:10 | 40MVA TRF-I | HS1 TRIP,FD=85 ms,OT=80 ms,RTT=0 ms,IA=126.5 A,IB=4192 A,IC=126.3 A, IAdiff=7.889 PU,IBdiff=15.78 PU,ICdiff=7.890 PU,IAbias=3.945 PU,IBbias=7.892 PU,ICbias=3.945 PU,
113 | Mendhasal | 18.07.25 | 5:57 | 8:22 | 2:25 | 132kV Mendhasal-Chandaka Feeder | At Mendhasal end: Z4 trip, AR- Block, Ir-4.13KA, Dist-0.1km At Chandaka end: Z2, Dist-27.67km,Il1-6.01a,Il2-5.33A,Il3-5.18A | - | - | - | - | - | monkey fault | -
|  |  |  | 18:30 | 12:33 | 100MVA Auto TRF-I | 220kV side Buchholz alarm ,Master trip operated ,IL1-2.01KA,IL2-0.33KA,IL3-0.26KA Dir-O/C pick up, Diff-Pick up,132kV Master trip operated,IL1-3.94KA,IL2-1.19KA,IL3-1.03KA,O/C trip, E/F pick up.
|  |  |  | 8:03 | 2:06 | 100MVA Auto TRF-II | 22oKV side of AUTO 2 relay details Master trip operated,IL1-1.27KA,IL2-0.09KA IL3-0.11KA 132kV side Master trip operated
114 | Katapali | 18.07.25 | 10:07 | 10:18 | 0:11 | 220kV Lapanga-Katapali CKT-II | AT Lapanga end: Zone-1, DIST=0.8KM, IB=16.37kA | - | - | - | - | - | - | -
[6 empty] | 132kV side Auto TRF-III | 132kV side tripped on O/c &E/F
115 | Jaleswar | 18.07.25 | 10:08 | 13:42 | 3:34 | 132kV Jaleswar-Baripada PG Feeder | Dimond arrangment of earth wire by Construction Div. Balasore | - | - | - | - | - | - | -
116 | Choudwar | 18.07.25 | 12:20 | 12:50 | 0:30 | 132kV Choudwar-TS Alloys Feeder | At Choudwar end: O/C Y phase, B phase, Zone 4, dist 9.78km, Ia-2.19kA, Ib-2.08kA, Ic-2.19kAr At TS Alloys end: No tripping | T S Alloys, BPPL, Ultratech, Beekay Steel | 0:30 | - | - | 0.013721 | - | -
[6 empty] | 132kV TS Alloys-Ultratech Feeder | At TS Alloys end: O/C Y phase, B phase, Zone 2, dist 21.72km, Ia-0.061kA, Ib-2.922kA, Ic-2.88kAr At Ultratech end: O/C Y phase, B phase, Zone 1, dist 7.8km, Ia-0.05kA, Ib-0.31kA, Ic-0.36kA
117 | Meramundali-B | 18.07.25 | 12:55 | 16:10 | 3:15 | 500MVA ICT-II | Tripped on SPR optd. The cable from SPR to MB found faulty. | - | - | - | - | - | - | -
118 | Kantabanji | 18.07.25 | 13:36 | 13:39 | 0:03 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 366A | Kantabanji RTSS | 0:03 | - | - | 0.0001974 | - | -
119 | Thuapali | 18.07.25 | 17:01 | 18:06 | 1:05 | 132kV Thuapali-Bargarh Feeder | E/F in B - phase trip ,Zone -1 ,FD-32.7 Km | - | - | - | - | - | - | -
120 | Pattamundai | 18.07.25 | 19:02 | 19:43 | 0:41 | 132kV Olaver-Pattamundai CKT-II | At Pattamundai end :- Distance prot. operated , Z1 trip,Ir=0.224kA,Iy=3.867kA, Ib=0.088kA, distance= 0.12km | - | - | - | - | - | Monkey Fault | -
121 | Therubali | 19.07.25 | 1:58 | 21.07.25 17:01 | 63:03 | 220kV Therubali-Gunupur Feeder | At Therubali end: E/F (B/U relay)Ir-275.8A,Iy-357.4A,Ib-352.4A At Gunupur end: BN,Z-1, 56.8KM,Ir-78.45A,Iy-79.19A,Iy-201.4A,Ib-3KA,AR-Lockout. | - | - | - | - | - | - | -
122 | Digapahandi | 19.07.25 | 7:20 | 7:38 | 0:18 | 132kV Digapahandi-Mohana Feeder | At Digapahandi end: Y-B-N, Zone-1, Dist- 78.52km, Iy- 1.536kA, Ib- 1.495kA | Mohana | 0:18 | - | - | 0.0017498 | - | -
|  |  |  | 16:55 | 16:55 | 132kV Mohana-Akhusingh Feeder | E/F (Y-B)
123 | Nimapara | 19.07.25 | 11:04 | 11:16 | 0:12 | 132kV Nimapara-Samangara Feeder | At Nimapara end: AN, Z1,D=12.30KM, Ia=2.48KA, Ib=86A, Ic=106A , AR Successful At Samangara end: AN, Z1, D=11.6KM, Ia=3.21KA, AR Block | - | - | - | - | - | - | -
124 | Digapahandi | 19.07.25 | 12:17 | 12:23 | 0:06 | 132kV Digapahandi-Mohana Feeder | digapahandi end.Back up Relay,B Phase earth fault,ia-0.02ka,ib-0.06ka,ic-0.75ka | Mohana | 0:06 | - | - | 0.00058328 | - | -
125 | Rairangpur | 19.07.25 | 12:38 | 12:38 | 0:00 | 132kV Karanjia-Rairangpur Feeder | Zone-1, AR Close, B-Phase, Distance-44.26 KM, Ia=194.9 A, Ib=98.02 A, Ic=1.153KA | - | - | - | - | - | - | -
126 | Aska New | 19.07.25 | 14:03 | 14:03 | 0:00 | 132kV Aska New-Chatrapur Feeder | A/R optd on R-Ph E/F ,Z1,A/R close,D=31.33km,IR=2.08KA | - | - | - | - | - | - | -
127 | Meramundali | 19.07.25 | 14:24 | 14:45 | 0:21 | 100MVA Auto TRF-I | 220kV : backup relay, M/T Ir - 401.8 A, Iy - 418.8 A, Ib - 383.7 A 132kV : M/T | Dhenkanal, Joranda RTSS Kharagprasad, Jaganath Power & Infra Ltd, NBVL, Meramundali RTSS, MGM, BRG RUNGTA MLR, RUNGTA DSP Chainpal, Talcher Fert. Ltd, Global, Heavy water Chainpal RTSS Khuntuni, Shree cement | 01:09 00:26 00:38 00:16 00:21 00:49 | - | - | 0.096177 | 132kV Bus dead | -
|  |  |  | 15:31 | 1:07 | 100MVA Auto TRF-II | 220kV - Winding temperature high trip & M/T 132kV - M/T
|  |  |  | 15:33 | 1:09 | 132kV Dhenkanal-Meramundali Feeder | Source failed from GSS Meramundali end due to tripping of all 3 auto transformer at Meramundali end
|  |  |  | 15:08 | 0:44 | 132KV Chainpal-Meramundali CKT-II
|  |  |  | 15:22 | 0:58 | 132KV Chainpal-Meramundali CKT-I
|  |  |  | 15:14 | 0:50 | 132kV Chainpal-TFL-GLOBAL-HWB
|  |  |  | 15:13 | 0:49 | 132kV Khuntuni-Dhenkanal Feeder
|  |  |  | 14:50 | 0:26 | 132kV Kharagprasad-Meramundali CKT-I & II
128 | Balasore | 19.07.25 | 15:57 | 17:35 | 1:38 | 160MVA Auto TRF-II | Indication:Main tank PRV Trip. | - | - | - | - | - | - | -
129 | Rourkela | 19.07.25 | 17:14 | 17:32 | 0:18 | 132kV Rourkela-Bhalulata- Jaganath Steel Feeder | Zone-1, BGT, LOCATION= 69.12, IA= 28A, IB= 1247A, IC= 40A, IN=0, IG= 1264A. | Bhalulata RTSS, Jaganath Steel | 0:18 | - | - | 0.0016237 | - | -
130 | Kesinga | 19.07.25 | 18:20 | 18:35 | 0:15 | 132kV Kesinga-Khariar Feeder | Distance protection relay operated,Zone-1,distance-26.36 KM,R-143.3 A,Y-436.2 A,B-2.794 KA | Khariar, Kantabanji, Kantabanji RTSS | 0:15 | - | - | 0.0087527 | - | -
131 | Bolangir New | 19.07.25 | 18:45 | 19:15 | 0:30 | 132kV Bolangir New-Birmaharajpur Feeder | Tripped On operation of DP Relay. | Birmaharajpur | 0:30 | - | - | 0.0040966 | - | -
132 | Balasore | 20.07.25 | 7:27 | 7:32 | 0:05 | 132kV Balasore-Balasore RTSS Feeder | Fault report: O/C,R-ph ,B-ph OPTD fault current:Ir=291A,Iy=290A. | Balasore RTSS | 0:05 | - | - | 0.00067586 | - | -
133 | Rajgangpur | 20.07.25 | 11:57 | 12:07 | 0:10 | 132kV Rajgangpur-Rajgangpur RTSS Feeder1 | RTT=16.520 s,O/C,IA=364.4 A, IB=364 A, IC=0 A,IG=0 A, MT OPERATED | - | - | - | - | - | - | -
134 | Bargarh New | 20.07.25 | 12:31 | 17:06 | 4:35 | 220kV Bargarh New-Katapali Feeder | MAIN-I DP(Z-1, C-G, LOC;-44.2 KM ), MAIN-II DP( Z-1, C-N, Loc-NONE km, fault durat-55.02ms, ,Ic-2.016A,) | - | - | - | - | - | - | -
135 | BC Mohanty Sw. Stn. | 20.07.25 | 15:31 | 15:50 | 0:19 | 132kV BC Mohanty-Tomka RTSS Feeder | B/U relay optd. Ia=237.8A, Ic=240.0A Van=73.75KV, Vbn=75.65KV, Vcn=76.01KV | Tomka RTSS | 0:19 | - | - | 0.0015173 | - | -
136 | Birmaharajapur | 20.07.25 | 18:45 | 21.07.25 19:15 | 24:30 | 132kV Bolangir New-Birmaharajpur Feeder | DP relay Tripped on O/C (Bph), Zone-1, Dist-1 KM Ir-149 A ,Iy-261A & Ib-1.574 KA | - | - | - | - | - | 132kV Sonepur-Birmaharajpur Feeder WAS IN SERVICE | -
137 | Jaleswar | 21.07.25 | 7:31 | 7:38 | 0:07 | 132kV Jaleswar-Jaleswar RTSS Feeder | Tripped on over load | Jaleswar RTSS | 0:07 | - | - | 0.00088352 | - | -
138 | Tarkera | 21.07.25 | 9:37 | 11:37 | 2:00 | 220kV Tarkera-Bisra PGCIL CKT I | DP2:- E/F TRIP, IA=0, IB=246.0 A, IC=232.4 A, FAULT DURATION=22.02 SEC, BROKEN CONDUCTOR ALARM | - | - | - | - | - | - | -
139 | Therubali | 21.07.25 | 11:45 | 15:55 | 4:10 | 220kV Therubali-Indravati CKT-II | At Therubali end: E/F (B/U relay)Ir-154.8A,Iy-154.3A,Ib-32.69A At Indravati end: RN,Z-1, 39.79KM,Ir-156.9A,Iy-159.4A,Ib-132A | - | - | - | - | - | - | -
140 | Meramundali | 21.07.25 | 12:22 | 16:53 | 4:31 | 400kV Meramundali-JSPL CKT-I | At Meramundali end: B-N, Ib - 11.65 KA, Z1, 13.5 KM At JSPL end: Z2, Ib - 3.4 KA, 31 KM | - | - | - | - | - | Line charged after clearance form JSPL patrolling team | -
141 | Salipur | 21.07.25 | 12:52 | 18:42 | 5:50 | 132kV Kendrapada-Salipur Feeder | Tripped at Kendrapada end on DP relay. Fault current: Ir=1.19 kA, Iy=928.6 A. Ib=87.99 A | Salipur | 0:10 | - | - | 0.004001 | P/S was availed from ICCL end on 132kV Bahugram - Salipur at 13:02 Hrs | -
|  |  |  | 13:02 | 0:10 | 20MVA TRF-I, II & III | Incomer failure from Kendrapada end
142 | Rourkela | 21.07.25 | 15:10 | 15:53 | 0:43 | 132kV Rourkela-Bhalulata- Jaganath Steel Feeder | CGT, LOCATION= 35.26, IA= 36A, IB= 15A, IC= 2234A, IN=0, IG= 2271A, GROUP-2, Zone-1. | Bhalulata RTSS | 0:43 | - | - | 0.0029015 | - | -
143 | Kalunga | 21.07.25 | 16:25 | 16:25 | 0:00 | 132kV Kalunga-Budhipadar Feeder | Tripped ph- R-N, Zone-1, Fault duration-53.99 ms,, Fault Loc-47.02 km, Ir-1.962 KA,fault resistance-3.345 ohm, | - | - | - | - | - | Auto-recloser successful at Kalunga end and stood ok. . | -
144 | Jayanagar | 21.07.25 | 17:00 | 19:33 | 2:33 | 220kV Jayanagar-Govindpally Feeder | Z1,R-Y-B-G,Ir-3.7KA,Iy-4KA,Ib-3.8KA,Dist-46.47Km | - | - | - | - | - | - | -
145 | Budhipadar | 21.07.25 | 17:14 | 17:14 | 0:00 | 220kV Budhipadar Korba CKT-II | At Budhipadar end: Y-N, Dist- 110km, Iy- 1.627kA At Korba end: Zone 1, Dist- 64.27km, Iy- 2.513kA | - | - | - | - | - | A/R- successful | -
146 | Akhusingh | 22.07.25 | 9:36 | 9:38 | 0:02 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
147 | Godisahi | 22.07.25 | 10:22 | 14:14 | 3:52 | 220kV Godisahi-Mendhasal Feeder | At Godisahi end: Ir=2.606KA, Iy=239.6A, Ib=317.8A, Zone-1, Distance= 14.74KM At Mendhasal end: Ir- 5.39kA, Zone 1, Dist- 20.2km | - | - | - | - | - | - | -
148 | Akhusingh | 22.07.25 | 10:33 | 10:44 | 0:11 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
149 | Mendhasal | 22.07.25 | 11:25 | 16:01 | 4:36 | 220kV Mendhasal-Chandaka GIS Feeder | At Mendhasal end: B-N, Zone 1, Dist- 2.1km, Ib- 14.8kA At Chandaka B end: B-N, Dist- 19.4km, Ib- 1.8kA | - | - | - | - | - | AR unsuccessful | -
150 | Therubali | 22.07.25 | 11:35 | 14:37 | 3:02 | 220kV Therubali-Upper kolab Feeder | At Theribali end: BG,Z-1,73.57KM,Ib-1.749kA,AR-NAAt Kolab end: BG,Z-1,64.66KM,Ib-1.992kA,AR-Lockout | - | - | - | - | - | - | -
151 | Dhenkanal | 22.07.25 | 12:01 | 12:12 | 0:11 | 132kV Dhenkanal-Meramundali Feeder | LBB operated due to malfunction of DC MCB of TBC | Khuntuni, Shree cement | 0:07 | - | - | 0.0018527 | Y-Ph LA was bursted at ICCL end.(132kV Khuntuni-ICCL Feeder was in charging condition from Khuntuni end only and Breaker of this Feeder tripped at Khuntuni end.) SLDC S/ON Code-SN-29 | -
132kV Dhenkanal-Khajuriakata-Nuapatana T- Feeder
132kV Dhenkanal-Khuntuni Feeder
132kV Dhenkanal-Joranda RTSS Feeder
40MVA TRF -I & III
152 | Therubali | 22.07.25 | 14:18 | 14:29 | 0:11 | 220kV Therubali-Laxmipur CKT-II | At Therubali end: BG,Z-1,9.35KM,Ib-4.618kA,AR-NA At Laxmipur end: BG,Z-1,35.5KM,Ib-2.7kA,AR-Success | - | - | - | - | - | - | -
153 | Joda | 22.07.25 | 14:44 | 15:43 | 0:59 | 220kV Joda-Ramchandrapur Feeder | At Joda end: Y-N, Zone 1, Dist- 101.5km, Iy- 1.241kA At Ramchandrapur end: Y-N, Zone 1, Dist- 32.7km, Iy- 2.38kA | - | - | - | - | - | No fault found | -
154 | Budhipadar | 22.07.25 | 14:45 | 16:01 | 1:16 | 220kV Budhipadar-Raigarh Feeder | At Budhipadar end: B-N, Ib- 2.302kA, Dist- 57.68km, A/R- successful At Raigarh end: B-N, Ib- 3.555kA, Dist- 34.268km, A/R- successful | - | - | - | - | - | - | -
155 | Chend | 22.07.25 | 15:22 | 15:31 | 0:09 | 132kV Chend-Kuarmunda Feeder | Tripped on O/C, Fault loop-AB,Tripp time-20.696ms,IL1-397.5A,IL2-393.2A,IL3-283.5A,IN-5.417A | - | - | - | - | - | At that time 132kV Tarkera-Chend-CKT-I &2 are in L/C condition. | -
156 | Kantabanji | 22.07.25 | 15:34 | 15:37 | 0:03 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 603A | Kantabanji RTSS | 0:03 | - | - | 0.0001974 | - | -
157 | Chend | 22.07.25 | 16:24 | 16:45 | 0:21 | 132kV Chend-Nuagaon RTSS Feeder | Tripped on DP- ABT,Zone-1,IL1-5348A,IL2-5009 A,IL3-0A,IN-0A, IG-2911A,Distance-19.47KM | Nuagaon RTSS | 0:21 | - | - | 0.0011852 | - | -
158 | Budhipadar | 22.07.25 | 16:27 | 16:27 | 0:00 | 132kV Budhipadar-Kalunga Feeder | D/P - (ALSTOM micom p444):Zone 1, Fault loop- A-N, Fault Distance- 47.02 km, IL1- 1.962kA, IL2-95.30A, IL3- 131.2A, Fault resistance-3.345ohm,Fault Duration-53.29ms A/R Successful. | - | - | - | - | - | weather-Clear | -
159 | Rayagada | 22.07.25 | 17:39 | 17:54 | 0:15 | 132kV Rayagada-Podagada Feeder | At Podagada end: R-N, E/F, Dist- 70.9km | Rayagada | 0:17 | - | - | 0.0031907 | - | -
160 | Meramundali | 22.07.25 | 21:28 | 21:41 | 0:13 | 100MVA Auto TRF-I | 220kV : backup relay, M/T, Ir - 417.5 A, Iy - 449.5A, Ib - 399.9 A 132kV : M/T | Dhenkanal Joranda RTSS, Meramundali RTSS Khajuriakata Kharagprasad, Jaganath Power & Infra Ltd, MGM, NAVA Chainpal, TFL, Chainpal RTSS, Global, Heavy water BRG Rungta MLR, Rungta MInes | 00:21 00:52 00:24 00:26 00:09 00:36 00:43 | - | - | 0.061542 | 132kV Bus dead | -
|  |  |  | 22:54 | 1:26 | 100MVA Auto TRF-II | 220kV - Winding temperature high trip & M/T 132kV - M/T
|  |  |  | 22:08 | 0:40 | 132kV Dhenkanal-Meramundali Feeder | 132kV Bus pull out at Meramundali grid end due to overloading of auto transformer-II
|  |  |  | 23:06 | 1:38 | 132kV Dhenkanal-Khajuriakata-Nuapatana T- Feeder
|  |  |  | 21:49 | 0:21 | 132kV Dhenkanal-Khuntuni Feeder
|  |  |  | 22:20 | 0:52 | 132kV Dhenkanal-Joranda RTSS Feeder
|  |  |  | 21:57 | 0:29 | 132kV Kharagprasad-Meramundali CKT-I
|  |  |  | 21:54 | 0:26 | 132kV Kharagprasad-Meramundali CKT-II
|  |  |  | 21:54 | 0:26 | 132kV Kharagprasad-NAVA CKT-I & II
|  |  |  | 21:54 | 0:26 | 132kV Kharagprasad-MGM Feeder
|  |  |  | 21:54 | 0:26 | 132kV Kharagprasad-JPIPL Feeder
|  |  |  | 22:20 | 0:52 | 132kV Kharagprasad-Meramundali RTSS Feeder
|  |  |  | 21:36 | 0:08 | 132kV Chainpal-Chainpal RTSS Feeder
|  |  |  | 22:54 | 1:26 | 132kV Chainpal-Meramundali CKT-I & II
|  |  |  | 21:47 | 0:19 | 132kV Chainpal-TFL-Global Feeder
161 | Joda | 23.07.25 | 12:04 | 12:20 | 0:16 | 220kV Joda-TTPS CKT-II | At Joda end: B-N, Zone 1, Dist- 85.95km, Ib- 1.384kA, A/R successful At TTPS end: B-N, Zone 1, Dist- 57.1km, Ib- 3kA | - | - | - | - | - | - | -
162 | Nuapatana | 23.07.25 | 13:11 | 13:28 | 0:17 | 132kV Nuapatna-Arati Feeder | At Nuapatna end: Y-B-N, Zone 1, Dist- 45km, Iy- 1.5kA, Ib- 1.5kA At Arati end: B-N, Dist- 19km, Ib -72.6A | - | - | - | - | - | Tripped due to bad weather | -
163 | Chandikhol | 23.07.25 | 13:39 | 13:45 | 0:06 | 132kV Chandikhol-MTPCL CKT-II | TRIPPED ON R PH O/C , E/F (IB-603 A) AT MTPCL end WITH VECTOR SERGE RELAY OPERATED. | - | - | - | - | - | - | -
164 | Duburi | 23.07.25 | 13:40 | 14:09 | 0:29 | 132kV Duburi-Jakhapura RTSS Feeder | Tripped on DP relay. | Jakhapura RTSS | 0:29 | - | - | 0.0054697 | - | -
165 | Balugaon | 23.07.25 | 14:57 | 21:13 | 6:16 | 132kV Balugaon-Chandpur Feeder | At Balugaon end: R-N, Zone 1, Dist- 33.55km, Ir- 1.032kA At Chandpur end: R-N, Zone 1, Dist- 2.4km, Ir- 2.49kA | Chandpur | 1:30 | - | - | 0.026473 | Tripped due to insulator got punctured at location no 114 | -
166 | Joda | 23.07.25 | 15:08 | 15:36 | 0:28 | 132kV Joda-Kenduposi Feeder | At Joda end: B-N, Zone 1, Dist- 29.95km, Ib- 1.495kA No tripping at Kenduposi end | - | - | - | - | - | - | -
167 | Kuarmunda | 23.07.25 | 15:22 | 15:31 | 0:09 | 132kV Kuarmunda-Chend Feeder | TRIPPED ON O/C ,R-YPH AT Kuarmunda end. | Chend, Nuagaon RTSS | 0:09 | - | - | 0.0071628 | - | -
168 | Budhipadar | 23.07.25 | 15:43 | 18:37 | 2:54 | 220kV Budhipadar Korba I | At Budhipadar end: R-N, Dist- 53.27km, Ir- 2.859kA At Korba end: R-N, Zone 1, Dist- 104.4km, Ir- 1.716kA | - | - | - | - | - | Weather: Rain & lightening | -
169 | Lapanga | 23.07.25 | 16:38 | 19:47 | 3:09 | 220kV Lapanga-Budhipadar CKT-II | At Lapanga end: R-N, Zone 1, Ir- 15.23kA, Dist- 3.5km At Budhipadar end: R-N, Zone 1, Ir- 9.307kA, Dist-12.51km | - | - | - | - | - | INSULATOR DAMAGED AT LOC NO 130-A | -
|  |  |  | 24.07.25 14:49 | 22:11 | 132kV Lapanga-Budhipadar Feeder | At Lapanga end: R-Y-B-N, Zone 1, Ir- 13.21kA, Iy- 11.04kA, Ib- 11.03kA, Dist-0.6km At Budhipadar end: B-N, Zone 1, Ib- 5.73kA, Dist- 14.1km
|  |  |  | 24.07.25 14:46 | 22:08 | 132kV Lapanga-Jharsuguda Feeder | At Lapanga end: Y-B, Zone 1, Ir- 0.53kA, Iy- 11.19kA, Ib- 14.32kA, Dist-0.2km At Jharsuguda end: Y-B, Iy- 2.86kA, Ib- 2.07kA
170 | Rourkela | 23.07.25 | 17:21 | 18:39 | 1:18 | 132kV Rourkela-Bhalulata- Jaganath Steel Feeder | ABCT, LOCATION= 62.50, IA= 1870A, IB= 2051A, IC= 1922A, IN=0, IG= 178A, Zone-1. | Bhalulata RTSS, Jaganath Steel | 1:18 | - | - | 0.007036 | - | -
171 | Lapanga | 23.07.25 | 17:28 | 17:53 | 0:25 | 132kV Lapanga-Burka PH CKT-II | At Lapanga end: Y-N, Zone 1, Iy- 4.27kA, Dist- 33.3km | - | - | - | - | - | - | -
172 | Duburi New | 23.07.25 | 17:58 | 18:09 | 0:11 | 220kV Duburi New-Paradeep CKT-I | Tripped only 86 relay operated | - | - | - | - | - | - | -
173 | Rairakhol | 23.07.25 | 18:42 | 18:54 | 0:12 | 132kV Rairakhol-Maneswar Feeder | At Rairakhol end: Dist- 31.33km, Ir- 175.3A, Iy- 117.7A, Ib- 161.4A, Zone 1 At Maneswar end- Dist- 22.5km, Iy-2.58KA, Zone-1 | Rairakhol, Rairakhol RTSS, Maneswar Boinda, Boinda RTSS | 00:12 00:13 | - | - | 0.006675 | - | -
|  |  |  | 18:55 | 0:13 | 132kV Boinda-Rairakhol Feeder | Source failure from Rairakhol end
174 | Deogarh | 23.07.25 | 19:31 | 24.07.25 18:13 | 22:42 | 220kV Deogarh-Rengali Feeder | Y-φ Suspension insulator snapped at Location no.-252. | - | - | - | - | - | - | -
175 | Narendrapur | 23.07.25 | 19:36 | 25.07.25 19:15 | 47:39 | 220kV Atri CKT-I | At Narendrapur end: R-N, Ir- 2.857kA, Zone 1, Dist- 31.79km At Atri end: Y-N, Zone 1, Iy- 1.573kA, Dist- 104.4km, A/R successful | - | - | - | - | - | R-ph conductor snapped | -
176 | Kalunga | 23.07.25 | 21:05 | 21:05 | 0:00 | 132kV Kalunga-Budhipadar | Tripped ph- R-N, Zone-1, Fault duration-55.04 ms,, Fault Loc-41.72 km, Ir-2.034 KA,fault resistance-5.7 ohm, | - | - | - | - | - | Auto-recloser successful at Kalunga end and stood ok. . (heavy Lightening & raining) | -
177 | Budhipadar | 23.07.25 | 21:28 | 22:39 | 1:11 | 132kV Budhipadar-Kalunga | D/P - (ALSTOM micom p444):Zone 1, Fault loop- A-C-N, Fault Distance- 63.48 km, IL1- 1.924kA, IL2-226.5A, IL3- 2.216kA, Fault resistance-46.87ohm,Fault Duration-63.33ms A/R Successful. | - | - | - | - | - | - | -
178 | Gondia | 24.07.25 | 5:13 | 5:30 | 0:17 | 132kV Gondia-TTPS Feeder | Tripped from Gondia end. | - | - | - | - | - | - | -
179 | Rourkela | 24.07.25 | 8:58 | 17:20 | 8:22 | 132kV Rourkela-Tarkera CKT-II |  | - | - | - | - | - | - | -
|  |  |  | 16:52 | 7:54 | 132kV Rourkela-Tarkera CKT-III
180 | Akhusingh | 24.07.25 | 9:19 | 9:22 | 0:03 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
181 | Meramundali | 24.07.25 | 13:30 | 14:20 | 0:50 | 132kV Meramundali-RUNGTA Mines Feeder | Tripped without any indication due to faulty cable | RUNGTA Mines | 0:50 | - | - | 0.0090885 | Faulty cable replaced | -
182 | Anandpur | 24.07.25 | 15:56 | 15:56 | 0:00 | 132kV Anandapur- Agarpada Feeder | Zone-1, 'B' PhaseFault location-31.19Km, IA-180.4A IB-185.0A IC-2.015KA | - | - | - | - | - | A/R successful | -
183 | Duburi | 24.07.25 | 16:46 | 18:23 | 1:37 | 132kV Duburi -Mishrilal Feeder | Tripped on DP relay. | Mishrilal | 1:37 | - | - | 0.017244 | - | -
184 | Duburi New | 24.07.25 | 17:01 | 19:16 | 2:15 | 132kV Duburi - BRPL Feeder | Tripped on DP relay. | BRPL | 0:14 | - | - | 0.002778 | - | -
185 | Duburi New | 24.07.25 | 17:10 | 18:18 | 1:08 | 132kV Duburi-Jakhapura RTSS Feeder | Tripped on DP relay. | Jakhapura RTSS | 1:08 | - | - | 0.012826 | - | -
186 | Kalunga | 24.07.25 | 17:43 | 17:43 | 0:00 | 132kV Kalunga-Budhipadar Feeder | Tripped ph- R-B-N, Zone-1, Fault duration-71.70 ms,, Fault Loc-17.44 km, Ir-4.5332 KA,fault resistance-1.402 ohm, | - | - | - | - | - | A/R Successful. | -
187 | Kalunga | 24.07.25 | 17:49 | 17:49 | 0:00 | 132kV Kalunga-Budhipadar Feeder | Tripped ph- R-B-N, Zone-1, Fault duration-53.37 ms,, Fault Loc-15.93 km, Ir-5.094 KA,fault resistance-295.3 mohm, | - | - | - | - | - | A/R Successful. | -
188 | Jharsuguda | 24.07.25 | 17:58 | 19:53 | 1:55 | 132kV Jharsuguda-Ultratech Feeder | Bph-G,Zone-1,Distance=4.024km, Ir= 104.9A, Iy= 135.6A,Ib=7.428kA | Ultratech | 1:55 | - | - | 0.014674 | - | -
189 | Joda | 24.07.25 | 18:28 | 18:56 | 0:28 | 132kV Joda-Kenduposi Feeder | At Joda end: R-N, Zone 2, Dist- 42.01km, Ir- 2.249kA At Kenduposi end: Ir- 0.26kA, Iy- 0.2kA, Ib- 0.27kA | - | - | - | - | - | - | -
190 | Gondia | 24.07.25 | 19:18 | 19:31 | 0:13 | 132kV Gondia-JFAL Feeder | Tripped at Both end. | - | - | - | - | - | - | -
191 | Barkote | 24.07.25 | 21:56 | 25.07.25 14:17 | 16:18 | 220kV Barkote-Bonai Feeder | TRIPPED ON DP RELAY | - | - | - | - | - | DURING INTURRPTION BARKOTE GSS AVAIL POWER SUPPLY FROM DEOGARH GSS end & BONAI GSS AVAIL SUPPLY FROM Tarkera GSS end. | -
192 | Rairakhol | 25.07.25 | 10:25 | 10:32 | 0:07 | 132kV Rairakhol-Maneswar Feeder | 132kV P/S failed from Maneswar grid end due to source failure | Rairakhol, Rairakhol RTSS Boinda | 00:07 00:05 | - | - | 0.0022746 | - | -
193 | Jharsuguda | 26.07.25 | 1:05 | 12:42 | 11:37 | 132kV Jharsuguda-Budhipadar CKT-II | Rph-G,Zone-1,Distance=3.891km,Fault Current Ir= 2.909kA, Iy= 864.2A, Ib= 674.9A, Fault duration=58.34ms, Fault resistance=1.514ohm, Relay make-MiCOM P442 | - | - | - | - | - | R phase insulator burst at loc no. 178 | -
194 | Lapanga | 26.07.25 | 7:15 | 7:36 | 0:21 | 132kV Lapanga-Rengali RTSS Feeder | Lapanga end DETAILS MAIN RELAY-1:- AT Lapanga end: FAULT LOOP-L1-E Zone-1,IL1-8.0KA,IL3-0.2KA DIST-7.68KM FD-525ms | Rengali RTSS | 0:21 | - | - | 0.0024684 | - | -
195 | Lapanga | 26.07.25 | 7:15 | 14:06 | 6:51 | 132kV Lapanga -Aryan Feeder | Lapanga end DETAILS MAIN RELAY-1(SIEMENS):- AT Lapanga end: FAULT LOOP-L2-E,Zone-1 IL1-0.35KA,IL2-17.40KA,IL3-0.25KA DIST- KM FD-20ms | - | - | - | - | - | JUMPER SNAPPED AT LOCATION 130 | -
196 | Bhubaneswar | 26.07.25 | 9:50 | 13:35 | 3:45 | 132kV Bhubaneswar-Chandaka CKT-I | IA=4.856KA,IB=342.18A,IC=378.24A, Zone-1, Distance-2.96KM | - | - | - | - | - | - | -
197 | Akhusingh | 26.07.25 | 18:16 | 18:18 | 0:02 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
198 | Gondia | 27.07.25 | 11:08 | 11:25 | 0:17 | 132kV Gondia-JFAL Feeder | Tripped from JFAL end | - | - | - | - | - | - | -
199 | Therubali | 27.07.25 | 11:16 | 11:25 | 0:09 | 220kV Therubali-Bhanjanagar CKT-II | At Therubali end: BG,Z-1,119.8KM,Ib-1.085kA,AR-NA At Bhanjanagar end: BG,Z-1,43.57KM,Ib-2.696kA,AR-success | - | - | - | - | - | - | -
200 | Polasponga | 27.07.25 | 15:47 | 15:50 | 0:03 | 132kV Polasponga-Kendujhargarh RTSS Feeder | Back up relay,O/C, IA=299.5A, IB=246.5A, IC=58.2A, INM=6.89A, IND=5.08A | Kendujhargarh RTSS | 0:03 | - | - | 0.00041103 | - | -
201 | Angul | 27.07.25 | 10:34 | 11:18 | 0:44 | 132kV TTPS-Angul Feeder | Tripped on DP Relay,Fault Loop -L3N,fault current 2.2KA. | Angul, MCL Boinda, Boinda RTSS | 00:28 00:19 | - | - | 0.03136 | - | -
|  |  |  | 11:02 | 0:28 | 132kV Chainpal- Angul Feeder | O/C(B-PH)& E/F,fault current 2.162KA.
202 | Chatrapur | 27.07.25 | 14:03 | 17:44 | 3:41 | 132KV Chatrapur-IRE-2 | DP Relay,A/R Operated ,Z-1 Fault,RGT, distance=23.3m,IR=7.359KA,IY=59.5A,IB=87.42A A/R Lock out ,Z-1 Fault,CGT, distance=80.32m,IR=8.186KA,IY=180.5A,IB=88.43A | - | - | - | - | - | - | -
203 | Jayanagar | 28.07.25 | 13:04 | 13:20 | 0:16 | 132kV Jayanagar-Jeypore RTSS Feeder | Z1,R-B,Dist-100.9Km,Ir-1.4KA,Ib-1.5KA | Jeypore RTSS | 0:16 | - | - | 0.0030126 | - | -
204 | Akhusingh | 28.07.25 | 23:43 | 23:47 | 0:04 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
205 | Gunupur | 29.07.25 | 17:37 | 18:40 | 1:03 | 220kV Gunupur-Therubali Feeder | E/F | - | - | - | - | - | - | -
206 | Gondia | 30.07.25 | 3:50 | 4:07 | 0:17 | 132kV Gondia-JFAL Feeder | Tripped from JFAL end | - | - | - | - | - | - | -
207 | Chandabali GIS | 30.07.25 | 11:33 | 31.07.25 13:20 | 25:47 | 132kV Dhamra-Chandbali CKT-I | At Chandabali end: Zone-1, phase-B, , fault location-14.03 KMs, Ia=167.2A,Ib=146.2A, Ic=3.13KA No Tripping at balimunda end | - | - | - | - | - | B-Phase jumper snapped | -
208 | Pratapsasan | 30.07.25 | 13:53 | 15:25 | 1:32 | 132kV Pratapsasan-Phulnakhara CKT-II | Tripped ( Zone-1, C-ph, Fault current: 3.953KA, Distance:11.05KM) | - | - | - | - | - | - | -
209 | Narendrapur | 30.07.25 | 14:04 | 14:26 | 0:22 | 220kV Narendrapur-Tata CKT-II | Started phase N, Earth fault 1, Start IN1>1,Over power Start1 B C, Trip 1 B C, ,Ia=55.77A,Ib=59.77A,Ic=83.80A | Tata | 0:22 | - | - | 0.006926 | - | -
210 | Therubali | 31.07.25 | 10:53 | 11:04 | 0:11 | 220kV Therubali-Bhanjanagar CKT-I | At Therubali end: RG,Z-1,122.6KM,Ir-1.391kA At Bhanjanagar end: RG,Z-1,44.94KM,Ir-1.085kA, AR-Success | - | - | - | - | - | - | -
211 | Jajpur Town | 31.07.25 | 13:25 | 16:33 | 3:08 | 132kV Jajpur Town- Jajpur Road Feeder | Tripped on DP relay but no fault found after line patrolling | - | - | - | - | - | - | -
212 | Akhusingh | 31.07.25 | 15:50 | 15:50 | 0:00 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
213 | Therubali | 31.07.25 | 16:42 | 17:01 | 0:19 | 220kV Therubali-Laxmipur CKT-I | At Therubali end: RG,Z-1,25.65KM,Ir-2.861kA At Laxmipur end :R-PH,Z-1,DIST-36.7KM,If-1.3KA, A/R operated | - | - | - | - | - | - | -
214 | Akhusingh | 31.07.25 | 17:08 | 17:08 | 0:00 | 132kV Rayagada-Akhusingh Feeder | Incoming failed | - | - | - | - | - | - | -
215 | Gondia | 01.08.25 | 4:43 | 4:47 | 0:04 | 132kV Gondia-JFAL Feeder | Tripped from JFAL end | Gondia | 0:04 | - | - | 0.00048961 | - | -
216 | Bhadrak | 01.08.25 | 9:43 | 9:47 | 0:04 | 132kV Bhadrak-Bhadrak RTSS Feeder | O/C Y&B Phase IL2=0.27KA,IL3=0.27KA | Bhadrak RTSS | 0:04 | - | - | 0.00058915 | - | -
217 | Kalunga | 01.08.25 | 11:12 | 13:05 | 1:53 | 132kV Budhipadar-Kalunga Feeder | At Kalunga end: R-Y-N, Zone-1, Dist-12.38 km, Ir-4.743 kA, Iy- 5.020 KA, Ib- 251.6A At Budhipadar end: R-Y, Zone-1, Dist-98.87 km, Ir-1.475KA,Iy-1.465KA | - | - | - | - | - | - | -
218 | Therubali | 01.08.25 | 11:18 | 11:29 | 0:11 | 220kV Therubali-Bhanjanagar CKT-II | At Therubali end: BG,Z-2,145.2KM,Ir-111A,Iy-359.8A,Ib-1.095kA At Bhanjanagar end: BG,Z-1,2.22KM,Ib-2.834kA,AR-Success | - | - | - | - | - | - | -
219 | Akhusingh | 01.08.25 | 13:26 | 13:34 | 0:08 | 132kV Rayagada-Akhusingh Feeder | Rayagada incoming failed | - | - | - | - | - | - | -
220 | Therubali | 01.08.25 | 14:29 | 14:39 | 0:10 | 220kV Therubali-Bhanjanagar CKT-I | At Therubali end: RG,Z-1,125.1KM,Ir-1.399kA,Iy-168.3A,Ib-333.3A At Bhanjanagar end: RG,Z-1,46.44KM,Ir-2.148kA ,AR-Success | - | - | - | - | - | - | -
221 | Jaleswar | 01.08.25 | 14:45 | 15:48 | 1:03 | 132kV Baripada PG-Jaleswar Line | A/R successful from Jaleswar end. | - | - | - | - | - | - | -
222 | Akhusingh | 01.08.25 | 17:52 | 17:59 | 0:07 | 132kV Rayagada-Akhusingh Feeder | Rayagada incoming failed | Rayagada, Rayagada RTSS | 0:07 | - | - | 0.002164 | - | -
223 | Aska New | 01.08.25 | 19:12 | 19:12 | 0:00 | 132kV Aska New-Digapahandi CKT-II | A/R optd,R-Ph E/F,Z1,IR=7.006KA,D=4.1km | - | - | - | - | - | - | -
224 | Gondia | 01.08.25 | 19:19 | 19:32 | 0:13 | 132kV Gondia-JFAL Feeder | Tripped from JFAL end | Gondia | 0:13 | - | - | 0.0015912 | - | -
225 | Aska New | 01.08.25 | 19:24 | 19:24 | 0:00 | 132kV Aska New-Chatrapur Feeder | A/R optd,R-Ph E/F,Z1,IR=6.4KA,D=5.11km | - | - | - | - | - | - | -
226 | Rairangpur | 01.08.25 | 19:58 | 19:58 | 0:00 | 132kV Bangriposi-Rairangpur Feeder | Zone-1, AR Close, B-Phase, Distance-5.08 KM, Ia=217.4 A, Ib=1.257KA, Ic=242.7A | - | - | - | - | - | - | -
227 | Rayagada | 01.08.25 | 13:26 | 13:30 | 0:04 | 132kV Rayagada-Podagada Feeder | B-Phase Earth Fault, the relay indication Ib= 0.41Ka at Podagada GSS end. | - | - | - | - | - | - | -
228 | Joda | 02.08.25 | 11:54 | 12:41 | 0:47 | 220kV Joda-Ramchandrapur Feeder | At Joda end: Y-N, Zone 1, Dist- 24.55km, Iy- 2.678kA At Ramchandrapur end: Y-N, Zone 1, Dist- 13.7km | - | - | - | - | - | NO FAULT FOUND | -
229 | Therubali | 02.08.25 | 12:43 | 12:50 | 0:07 | 220kV Therubali-Bhanjanagar CKT-I | At Therubali end: RG,Z-1,122.5KM,Ir-1.46kA,Iy-146.7A,Ib-276.3A At Bhanjanagar end: RG,Z-1,42.29KM,Ir-2.6kA, AR-Success | - | - | - | - | - | - | -
230 | Bangiriposi | 02.08.25 | 14:36 | 14:36 | 0:00 | 132kV Bangiriposi-Rairangpur Feeder | A/R successful | - | - | - | - | - | - | -
231 | Gondia | 03.08.25 | 5:12 | 5:22 | 0:10 | 132kV Gondia-TTPS Feeder | Tripped from Gondia end. | - | - | - | - | - | - | -
232 | Marshaghai | 03.08.25 | 12:09 | 12:26 | 0:17 | 132kV Marshaghai-Kendrapada RTSS Feeder | O/C OPERATED IL1=.44 KA. IL2=0.43 KA, IL3=0.86 KA | Kendrapada RTSS | 0:17 | - | - | 0.00081017 | - | -
233 | Balasore | 03.08.25 | 21:46 | 21:50 | 0:04 | 132kV Balasore-Balasore RTSS Feeder | Fault report: O/C,R-ph ,B-ph OPTD fault current:Ir=305A,Iy=304A. | Balasore RTSS | 0:04 | - | - | 0.00054508 | - | -
234 | Polasponga | 03.08.25 | 23:05 | 23:52 | 0:47 | 132kV Polasponga-Kendujhargarh RTSS Feeder | Back up relay,O/C, IA=301.01A, IB=261.5A, IC=45.2A, INM=7.04A, IND=5.7A | Kendujhargarh RTSS | 0:47 | - | - | 0.006549 | - | -
235 | Jajpur Town | 04.08.25 | 3:08 | 4:32 | 1:24 | 132kV Jajpur Town- Bhadrak Feeder | Tripped from both end after line patrolling no physical fault found on the tansmission line | - | - | - | - | - | - | -
236 | Katapali | 04.08.25 | 8:12 | 17:40 | 9:28 | 132kV Katapali-Thuapali Feeder | Tripped with Back up relay operated Ia=515.9Amp, Ib=531.8Amp and Ic=548.4Amp | - | - | - | - | - | - | -
237 | Therubali | 04.08.25 | 12:31 | 12:41 | 0:10 | 220kV Therubali-Laxmipur CKT-I | At Therubali end: RG,Z-1,26.25KM,Ir-3.156kA,Iy-151A,Ib-74.28A At Laxmipur end: RG,Z-1,41.8KM,Ir-1.31kA,Iy-161.8A,Ib-55.62A,AR-Success | - | - | - | - | - | - | -
238 | Polasponga | 04.08.25 | 18:07 | 18:09 | 0:02 | 132kV Polasponga-Kendujhargarh RTSS Feeder | Back up relay,O/C, IA=298.9A, IB=217.1A, IC=96.8A, INM=6.9A, IND=7.8A | Kendujhargarh RTSS | 0:02 | - | - | 0.00027868 | - | -
239 | Bhadrak | 05.08.25 | 4:25 | 4:31 | 0:06 | 132kV Bhadrak-Bhadrak RTSS Feeder | O/C Y&B Phase IL2=0.27KA,IL3=0.27KA | Bhadrak RTSS | 0:06 | - | - | 0.00088372 | - | -
240 | Meramundali | 05.08.25 | 12:30 | 16:06 | 3:36 | 220kV Meramundali-Bhanjanagar Feeder | At Meramundali end: Z1, Ib-3.09 kA, 55.43 KM At Bhanjanagar end: B-N, Z1, Ib-1.37KA, 109.8 KM | - | - | - | - | - | - | -
241 | Joda | 05.08.25 | 13:22 | 13:57 | 0:35 | 220kV Joda-Ramchandrapur Feeder | At Joda end: R-N, Zone 1, Dist- 74.14km, Ir- 1.854kA At Ramchandrapur end: R-N, Zone 1, Dist-51.3km, Ir- 3.22kA | - | - | - | - | - | - | -
242 | Mendhasal | 05.08.25 | 15:36 | 17:38 | 2:02 | 100MVA Auto TRF-I | Master trip relay 86.1and 86.2opt Il1=0.14KA,IL2=0.18KA,IL3=0.18KA | - | - | - | - | - | 132kV B-Phase LA of Khurdha Feeder burst and simuntaneously 132kV BUS pulled out. | -
|  |  |  | 18:43 | 3:07 | 100MVA Auto TRF-II | Master trip relay 86.2opt Il1=0.11KA,IL2=0.08KA,IL3=1.22KA
|  |  |  | 18:51 | 3:15 | 132kV Mendhasal-Khurda Feeder | Loop L3-E, IL3=9.24KA, Dist=0.1KM, zone-1
|  |  |  | 18:42 | 3:06 | 132kV Mendhasal-Chandaka Feeder | IL3=3.88KA,Dist=0.1KM
243 | Kesinga | 06.08.25 | 3:12 | 3:31 | 0:19 | 132kV Kesinga-Khariar Feeder | Distance protection relay operated,zone-1,distance-23.84 KM,R-146.9 A,Y-477.8 A,B-2.813KA | Khariar, Kantabanji, Kantabanji RTSS | 0:19 | - | - | 0.012575 | - | -
244 | Kalunga | 06.08.25 | 6:21 | 6:21 | 0:00 | 132kV Budhipadar-Kalunga Feeder | At Kalunga end: R-N, Zone-1, Dist-52.01 km, Ir-1.303 kA, Iy- 46.47A, Ib- 152.6A At Budhipadar end: R-N, Zone-1, Dist-37.84 km, Ir-2.207KA,Iy-22.78A,Ib-158.8 A | - | - | - | - | - | Auto-recloser successful at Kalunga end and stood ok | -
245 | Lapanga | 06.08.25 | 11:21 | 17:22 | 6:01 | 400KV Lapanga-Vedant CKT-I | At Lapanga end: ZONE-1, L1-E, DIST-7.2KM, IL1=19.15kA At Vedant end: Zone-1 FD=7.7KM, IB-2.8KA, L3-E | - | - | - | - | - | Jumper snapped at LOC No-32 | -
246 | Angul | 06.08.25 | 13:10 | 13:37 | 0:27 | 132kV Angul-TTPS Feeder | O/C(R-PH)& E/F,fault current IR-997.85A,IN-1.25KA. | Angul, MCL Boinda | 00:27 00:21 | - | - | 0.032456 | Weather condition :- Heavyrain and severe lightning | -
|  |  |  | 13:27 | 0:17 | 132kV Chainpal-Angul Feeder | At Chainpal end: O/C (R Ph) & E/F, Ir- 1.985kA, Zone 2, Dist- 15.1km
247 | Jayanagar | 06.08.25 | 13:24 | 13:29 | 0:05 | 220kV Jayanagar-Laxmipur CKT-I | Tripped on D/P. Z2,B-G,Dist-66KM,If-2.4KA | - | - | - | - | - | - | -
248 | Balasore | 06.08.25 | 13:39 | 13:53 | 0:14 | 132kV Balasore-Balasore RTSS Feeder | Fault report: O/C,R-ph ,B-ph OPTD fault current:Ir=282A,Iy=281A. | Balasore RTSS | 0:14 | - | - | 0.0019078 | - | -
249 | Angul | 06.08.25 | 13:49 | 07.08.25 16:17 | 26:28 | 132kV Angul-TTPS Feeder | O/C(Y-PH)& E/F,fault current IY-1.334KA,IN-1.820KA. | - | - | - | - | - | - | -
250 | Meramundali | 06.08.25 | 13:58 | 13:58 | 0:00 | 220kV Meramundali-Bhanjanagar Feeder | At Meramundali end: R-E, Z1, Ir-7.83 kA, 18.73 KM At Bhanjanagar end: Ir - 1.33 kA, Z1, 101 KM | - | - | - | - | - | A/R successful at both end | -
251 | Mendhasal | 06.08.25 | 15:36 | 18:42 | 3:06 | 132kV Mendhasal-Chandaka Feeder | At Mendhasal end: Ir- 4.16kA, Dist- 9.9km, Zone 1 | - | - | - | - | - | 132kV B-Phase LA of Khurdha Feeder burst and simuntaneously 132kV BUS pulled out and 132kV Chandaka,Khurdha,Auto TRF-Iand Auto TRF-II tripped. | -
252 | Sundargarh | 06.08.25 | 15:47 | 18:57 | 3:10 | 132kV Budhipadar-Sundargarh CKT-I | At Sundargarh end: ABT, Zone-1, Dist. 23.93 Km, Ia=2614 A, Ib=2329 A At Budhipadar end: RY-E, Dist. 8.7 Km, Ir=7.93 KA, Iy=8.84 KA, Ib= 0.09 KA | - | - | - | - | - | - | -
253 | Rayagada | 06.08.25 | 16:02 | 16:18 | 0:16 | 132kV Rayagada-Akhusingh Feeder | Zone-1, distance= 44.77KM, Ia=151A, Ib=597.7A, Ic=46.39A | - | - | - | - | - | - | -
254 | Akhusingh | 06.08.25 | 23:25 | 23:27 | 0:02 | 132kV Rayagada-Akhusingh Feeder | Rayagada incoming failed | - | - | - | - | - | - | -
255 | Telkoi | 07.08.25 | 4:48 | 5:09 | 0:21 | 220kV Telkoi-TTPS Feeder | Tripped from TTPS only due to AN fault, AR success at Telkoi end. | - | - | - | - | - | - | -
256 | Jayanagar | 07.08.25 | 9:55 | 13:01 | 3:06 | 132kV Jayanagar-Meenakshi Feeder | Tripped on D/P.Z-1,R-G,If-8.16KA,Dist-3.86Km | Megalift | 3:06 | - | - | 1.5833e-06 | - | -
257 | Meramundali | 07.08.25 | 10:58 | 10:58 | 0:00 | 220kV Meramundali-Kaniha CKT-II | At Meramundali end: R-E, Ir-2.79 kA, Z1, 31.53 KM At Kaniha end: R-E, Ir - 4.55 kA, 16.3 KM | - | - | - | - | - | A/R successful at both ends | -
258 | Podagada | 07.08.25 | 13:26 | 13:33 | 0:07 | 132kV Podagada-Rayagada Feeder | Distance Protection relay optd. , Distance= 115 KM, Fault loop = L3-E, IL1= 0.03KA,IL2=0.03KA,IL3=0.41KA. | - | - | - | - | - | - | -
259 | Atri | 07.08.25 | 15:08 | 15:08 | 0:00 | 220kV Atri- Narendrapur CKT-II | At Atri end: R-N, Zone 1, Dist- 96.14km, Ir- 1.206kA At Narendrapur end: R-N, Zone 1, Dist- 42.46km, Ir- 2.163kA | - | - | - | - | - | A/R successful from both the ends | -
260 | Atri | 07.08.25 | 15:29 | 15:29 | 0:00 | 132kV Atri- Shamuka Feeder | At Atri end: B-N, Zone 1, Dist- 22.93km, Ib- 3.632kA At Shamuka end: B-N, Zone 1, Dist- 31.6km, Ir- 0.242kA | - | - | - | - | - | A/R successful from both the ends | -
261 | Birmaharajapur | 07.08.25 | 15:49 | 19:52 | 4:03 | 132kV Sonepur-Birmaharajpur Feeder | E/F (R Ph), Zone 1, Dist- 50.37km, Ir- 0.565kA | Birmaharajapur | 4:03 | - | - | 0.046048 | - | -
262 | Atri | 07.08.25 | 16:18 | 16:18 | 0:00 | 220kV Atri- Mendhasal Feeder | At Atri end: R-N, Zone 1, Dist- 6.397km, Ir- 7.433kA At Mendhasal end: R-N, Zone 1, Dist- 16.5km, Ir- 5.54kA | - | - | - | - | - | A/R successful from Atri GSS end | -
263 | Sadeipali | 07.08.25 | 16:31 | 18:16 | 1:45 | 160MVA Auto TRF-III | Tripped on OSR Trip. | - | - | - | - | - | - | -
264 | Gondia | 07.08.25 | 19:44 | 19:53 | 0:09 | 132kV Gondia-JFAL Feeder | Tripped at Both end. | Gondia | 0:09 | - | - | 0.0011016 | - | -
265 | Polasponga | 08.08.25 | 3:34 | 6:49 | 3:15 | 132kV Polasponga-Turumunga Feeder | At Polasponga end: Zone-2,Ia-26A,Ib-25A,Ic-796A,Distance-94.18km At Turumunga end: Zone-1, Location-7.043km,Ia-314.8A,Ib-109.5A,Ic-4.126KA | - | - | - | - | - | - | -
266 | Polasponga | 08.08.25 | 6:49 | 13:29 | 6:40 | 132kV Polasponga-Turumunga Feeder | Turumunga end - Ia-25.68A,Ib-844A,Ic-24.84A | - | - | - | - | - | - | -
267 | Rayagada | 08.08.25 | 07:52 | 08:15 | 0:23 | 132kV Transfer BUS Rayagada | Fault report on relay- fault duration= 160msec, Ia=66.52A, Ib=579A, Ic=52.6A, In=522.7A and In(derived)= 524.7 | Rayagada | 0:23 | - | - | 0.0043994 | - | -
268 | Paradeep | 08.08.25 | 7:55 | 9:42 | 1:47 | 132kV Paradeep-PPL CKT II | Tripped on O/C on B-Ph to G, Zone 1, Dist - 4.53 KM, Ir-0 kA, Iy-0 kA , Ib- 3.06KA | - | - | - | - | - | TRANSIENT FAULT | -
269 | Akhusingh | 08.08.25 | 9:34 | 9:38 | 0:04 | 132kV Rayagada-Akhusingh Feeder | Rayagada incoming failed | - | - | - | - | - | - | -
|  |  | 9:39 | 9:54 | 0:15
270 | Polasponga | 08.08.25 | 13:29 | 14:15 | 0:46 | 132kV Polasponga-Turumunga Feeder | Turumunga end - Ia-25.49A,Ib-84801A,Ic-26.44A,SOTF operated | - | - | - | - | - | Flash in 132kV LA(Y-phase) | -
|  |  | 14:15 | 18:54 | 4:39 |  | Polasponga end-DP relay: Zone-1,BG T,Ia-23A,Ib-3297A,Ic-25A,In-0,Ig-3318A,3I2-3324A,Distance-0.21km
271 | Kantabanji | 08.08.25 | 17:45 | 17:47 | 0:02 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 331 A | Kantabanji RTSS | 0:02 | - | - | 0.00011075 | - | -
272 | Narendrapur | 09.08.25 | 11:00 | 19:25 | 8:25 | 220kV Narendrapur-Gunupur Feeder | At Narendrapur end: R-N, Zone 1, Dist- 66.11km, Ir- 1.248kA At Gunupur end: Zone 1, SOTF, Dist- 87.63km, Ir- 0.963kA | - | - | - | - | - | - | -
273 | Dhenkanal | 09.08.25 | 11:06 | 11:35 | 0:29 | 132kV Dhenkanal-Khajuriakata-Nuapatana T- Line | At Dhenkanal end: Z-2, Dist=39.56, C-N, Ic=494A At Khajuriakata end: Bph-E/F,Ib-500A,BPh-E/F | - | - | - | - | - | - | -
274 | Kendrapada | 09.08.25 | 11:21 | 11:47 | 0:26 | 132kV Kendrapada-RAMCO Feeder | AT Kendrapada END:[DP OPERATED, ZONE-1, DISTANCE: 20.22Kms , BACKUP O/C OPERATED, Ir=45.9A,Iy=664A,Ib=2.3kA,In=2.3kA] AT RAMCO END: BREAKER DID NOT TRIP | RAMCO | 0:26 | - | - | 0.0018155 | - | -
275 | Bidanasi | 09.08.25 | 11:56 | 15:54 | 3:58 | 132kV Bidanasi-Brajabiharipur Feeder | At Bidanasi end: E/F (Y-N), Zone 1, Dist- 0.291km, Iy- 10.45kA At Brajabiharipur end: Y-N, Zone 1, Iy- 2.75kA, Dist- 5.5km | - | - | - | - | - | - | -
276 | Budhipadar | 09.08.25 | 12:46 | 16:34 | 3:48 | 220kV Budhipadar-Korba-I Feeder | At Budhipadar end: B-N, Zone 1, Dist- 154.7 km, Ib- 1.004kA At Korba end: B-N, Zone 1, Dist- 3.03km, Ib- 12.885kA | - | - | - | - | - | - | -
277 | Duburi-New | 09.08.25 | 13:17 | 17:29 | 4:12 | 220kV Duburi New-JINDAL-1(B-Y-R) | DP-1&2 operated | - | - | - | - | - | - | -
278 | Meramundali | 09.08.25 | 13:20 | 13:20 | 0:00 | 220kV Meramundali-Kaniha CKT-II | At Meramundali end: R-E, Ir - 4.173 kA, Z2, 40.59 KM At Kaniha end: R-E, Z3, 24 KM | - | - | - | - | - | A/R successful at both ends | -
279 | Kamakhyanagar | 09.08.25 | 13:29 | 13:52 | 0:23 | 132kV OPCL-Kamakhyanagar Feeder | At Kamakhyanagar end: ZONE-1,IA-1.93kA,IB-144.7A,IC-25.31A,DISTANCE-24.19KM At OPCL end: ZONE-1,IA-1.89kA,IB-144.1A,IC-15.67A,DISTANCE-36.34KM | - | - | - | - | - | Transient Fault | -
280 | Bhadrak | 09.08.25 | 15:17 | 15:19 | 0:02 | 132kV Bhadrak-Bhadrak RTSS Feeder |  | Bhadrak RTSS | 0:02 | - | - | 0.00029457 | - | -
281 | Duburi-New | 09.08.25 | 17:49 | 10.08.25 16:28 | 22:39 | 220kV Duburi New-Dhamra Feeder | O/C (R Ph), Zone 1, Ir- 1.254kA | - | - | - | - | - | - | -
|  |  |  | 17:49 | 0:00 | 220kV Duburi New-Bhadrak Feeder | DP-1&2 operated
282 | Bhadrak | 09.08.25 | 18:20 | 18:22 | 0:02 | 132kV Bhadrak-Bhadrak RTSS Feeder |  | Bhadrak RTSS | 0:02 | - | - | 0.00029457 | - | -
283 | Narendrapur | 10.08.25 | 10:56 | 10:56 | 0:00 | 220kV Narendrapur-Gunupur Feeder | At Narendrapur end: R-N, Zone 1, Dist-93.43km, Ir- 1.033kA At Gunupur end: Zone 1, Dist- 41.9km, Ir- 0.731kA | - | - | - | - | - | - | -
284 | Balugaon | 11.08.25 | 8:36 | 8:50 | 0:14 | 132kV Balugaon-Solari RTSS Feeder | If- 0.27kA | Solari RTSS | 0:14 | - | - | 0.00090616 | - | -
285 | Podagada | 11.08.25 | 9:55 | 10:17 | 0:22 | 132kV Podagada-Potangi Feeder | Distance Protection relay optd. , Zone-1, Distance= 33.97 KM, Fault loop = L3-E, IL1= 10.75A,IL2= 10.53A,IL3= 635.7A. | - | - | - | - | - | - | -
286 | Kendrapada | 11.08.25 | 10:49 | 11:05 | 0:16 | 132kV Kendrapada-RAMCO Feeder | AT Kendrapada END:[DP OPERATED, ZONE-1, DISTANCE: 20.9Kms , BACKUP E/F OPERATED, Ir=37.24A,Iy=55A,Ib=2.3kA,In=2.2kA] AT RAMCO END: BREAKER DID NOT TRIP | RAMCO | 0:16 | - | - | 0.0011172 | - | -
287 | Purushottampur | 11.08.25 | 12:36 | 12:36 | 0:00 | 132kV Aska (Old)-Purusottampur Feeder | A/R operated, DP operated, in B ph, zone-1, L3-E loop, IL1=0.08 ka, IL2=0.20 ka, IL3=2.11 ka,Distance-11.0 km | - | - | - | - | - | A/R operated successfully | -
288 | Jayanagar | 11.08.25 | 13:02 | 16:10 | 3:08 | 220kV Jayanagar-Laxmipur CKT-II | Tripped on D/P.Z2,Y-B-G,Iy-2.508kA,Ib-2.313kA,Dist-69.05KM | - | - | - | - | - | - | -
289 | Duburi-New | 11.08.25 | 13:35 | 12.08.25 12:58 | 23:23 | 220kV Duburi New-JINDAL-2 Feeder | DP-1&2 operated | - | - | - | - | - | - | -
290 | Balasore | 11.08.25 | 17:00 | 17:32 | 0:32 | 220kV Balasore-Bhadrak Feeder | At Balasore end: R-N, Zone 2, Dist- 97.4km, Ir- 1.9kA.No breaker tripping at Bhadrak end | Bhadrak, Facor, Bhadrak RTSS Dhamra Port RTSS Dhamra Port Jajpur Town | 00:23 00:28 00:31 00:09 | - | - | 0.034964 | Line cvt brust in Bhadrak GSS | -
|  |  |  | 17:23 | 17:23 | 220kV Duburi New-Bhadrak(B-Y-R) | DP-1&2 operated
|  |  |  | 23:58 | 23:58 | 132kV Soro- Bhadrak Line | At Soro end: Zone-2, Distance-37.23KM, EVENT-B to G, IA=63A, IB=926KA, IC=244A At Bhadrak end: Zone-1, IA=90.30A, IB=10.76KA, IC=2.98KA
291 | Marshaghai | 12.08.25 | 2:53 | 3:07 | 0:14 | 132kV Paradeep-Marshaghai Feeder | Source failure | Marshaghai, Kendrapada RTSS | 0:25 | - | - | 0.0077399 | - | -
|  |  |  | 2:53 | 0:00 | 132kV Kendrapada-Salipur Feeder
|  |  | 3:09 | 3:20 | 0:11 | 132kV Paradeep-Marshaghai Feeder
292 | Bhadrak | 12.08.25 | 10:07 | 10:09 | 0:02 | 132kV Bhadrak-Bhadrak RTSS Feeder |  | Bhadrak RTSS | 0:02 | - | - | 0.00029457 | - | -
293 | Tarkera | 12.08.25 | 11:28 | 12:01 | 0:33 | 220kV Tarkera-Rengali Feeder | At Tarkera end: E/F TRIP, IA=266.8 A, IB=106.5 A, IC=81.59 A At Rengali end: AGT, IA=958.9 A, 76.1 A, IC=43.9 A | - | - | - | - | - | TRANSIENT FAULT | -
294 | Katapali | 12.08.25 | 11:46 | 11:58 | 0:12 | 132kV Katapali-Burla PH CKT-I | Tripped without indication | - | - | - | - | - | - | -
295 | Boinda | 12.08.25 | 12:24 | 12:48 | 0:24 | 132kV Boinda-Angul Feeder | At Angul end: E/F (Y Ph), Iy- 0.89kA No tripping at Boinda end | Boinda, Boinda RTSS Rairakhol, Rairakhol RTSS | 00:24 00:25 | - | - | 0.011885 | - | -
|  |  |  | 12:49 | 0:25 | 132kV Rairakhol-Boinda Feeder | Source failure from Angul grid end.
296 | Sambalpur | 12.08.25 | 12:30 | 18:01 | 5:31 | 132kV Sambalpur-Burla PH Feeder | Tripped at BPH end with Yph E/F, 860 Optd, fault current=548A & not tripped at SBP end | - | - | - | - | - | - | -
297 | Cuttack | 12.08.25 | 13:12 | 16:11 | 2:59 | 220kV Cuttack-Pratapsasan CKT-II | Tripped ( Zone-1, Y-ph to B-Ph, Fault current: Iy-2.72KA,Ib-2.6KA Distance:37.05KM) | - | - | - | - | - | - | -
298 | Anandpur | 12.08.25 | 16:33 | 18:26 | 1:53 | 132kV Anandapur- Agarpada Feeder | Zone-1, Dist- 2.63km, Iy- 5.126kA, Ib- 4.982kA | Agarpada | 0:06 | - | - | 0.00097898 | - | -
299 | Rairangpur | 12.08.25 | 18:00 | 18:15 | 0:15 | 132kV Rairangpur-Karanjia Feeder | Zone-2, R-Phase, Distance-63.48 KM, Ia=992.4A, Ib=290.6A, Ic=128.9A | - | - | - | - | - | - | -
300 | Podagada | 12.08.25 | 19:14 | 19:24 | 0:10 | 132kV Podagada-Rayagada Feeder | Distance Protection relay optd. , Zone-2, Distance= 70.4 KM, Fault loop = L1-E, IL1= 0.79KA,IL2=0.02KA,IL3=0.01KA. | Rayagada | 0:10 | - | - | 0.0019128 | - | -
301 | Chandabali GIS | 12.08.25 | 19:53 | 13.08.25 16:24 | 20:31 | 132kV Dhamra-Chandbali CKT-II | Y-phase jumper snapped | - | - | - | - | - | - | -
302 | Angul | 12.08.25 | 21:32 | 22:15 | 0:43 | 132kV Angul-TTPS Feeder | Tripped on DP Relay,Fault Abs. Dist=10.24KM,Fault Loop -L1N,fault current 2.54KA. | Angul, MCL Boinda, Boinda RTSS Rairakhol, Rairakhol RTSS | 00:08 00:13 00:06 | - | - | 0.013116 | Heavy rain and severe lightning | -
|  |  |  | 21:40 | 0:08 | 132kV Rairakhol-Boinda Feeder | Source failure from Angul grid end
303 | Meramundali | 12.08.25 | 21:37 | 21:37 | 0:00 | 400kV Meramundali-Kaniha CKT-II | A/R successful M1: L1-N, IL1-10.43 kA, Z1, 23.1 KM M2: L1-N, IL1-10.5 kA, Z1, 20 KM | - | - | - | - | - | - | -
304 | Meramundali | 12.08.25 | 21:45 | 22:14 | 0:29 | 132kV Meramundali-Dhenkanal Feeder | At Meramundali end: A/R successful, Z1, IL2 - 8.43 kA, In - 8.078 KA, 8.96 KM At Dhenkanal end: Iy - 899.5 A, Z2, 32.23 KM | Dhenkanal | 0:29 | - | - | 0.016143 | - | -
305 | Rayagada | 12.08.25 | 19:15 | 19:25 | 0:10 | 132kV Rayagada-Podagada Feeder | R-Phase , Zone-2, distance =70.4KM from Podagada GSS,Fault Current= .79KA at Podagada end. | Rayagada | 0:10 | - | - | 0.0019128 | - | -
306 | Kalunga | 13.08.25 | 1:04 | 1:04 | 0:00 | 132kV Budhipadar-Kalunga Feeder | At Kalunga end: R-N, Zone-1, Dist-60.741 km, Ir-1.106 kA, Iy- 87.97A, Ib- 206.3A | - | - | - | - | - | Auto-recloser successful at Kalunga end | -
307 | Hirakud | 13.08.25 | 1:54 | 2:42 | 0:48 | 132kV Hirakud-Burla P.H Feeder | P/S Fail | Hirakud | 0:48 | - | - | 0.0032632 | - | -
308 | Paradeep | 13.08.25 | 2:53 | 3:18 | 0:25 | 132kV Paradeep-Kendrapada Feeder | Tripped on O/C on B-Ph Ir=214 A, Iy=280 A Ib=843 A | Kendrapada, Marsaghai, Kendrapada RTSS | 0:25 | - | - | 0.020514 | DUE TO OVERLOADING | -
|  |  |  | 3:18 | 0:25 | 132kV Paradeep-Marshaghai Feeder | Tripped on O/C on R,Y & B-Ph Ir=576 A, Iy=596 A Ib=473 A
|  |  |  | 3:30 | 0:37 | 132kV Kendrapada-Chandikhol Feeder | AT Kendrapada END: [DP OPERATED , ZONE-2, DISTANCE=29.08Kms, Ir=6.9A,Iy=7.9A,Ib=1.4kA] AT Chandikhol END: BREAKER DID NOT TRIP
309 | Jaleswar | 13.08.25 | 8:41 | 14:52 | 6:11 | 132kV Basta-Jaleswar Feeder | Tripped from both end. | - | - | - | - | - | - | -
310 | BC Mohanty | 13.08.25 | 12:45 | 12:54 | 0:09 | 132kV BC Mohanty-Tomka RTSS Feeder | Ir- 0.238kA, Ib- 0.24kA, O/C | Tomka RTSS | 0:09 | - | - | 0.00075379 | - | -
311 | Sonepur | 13.08.25 | 12:49 | 13:18 | 0:29 | 132kV Sonepur -Bolangir Feeder | 132kV Sonepur -Bolangir CKT tripped at Bolangir end. | Sonepur, Boudh, Birmaharajapur | 0:29 | - | - | 0.025153 | - | -
312 | Mendhasal | 13.08.25 | 13:35 | 15:46 | 2:11 | 220kV Mendhasal-Godisahi Feeder | At Mendasal end: AG FAULT,ZONE-1,DIST-9.9KM,Ia=7.47KA At Godisahi end: Ia-2.6kA, Ib-208.1A,Ic-281.0A,Dist-11.83KM | - | - | - | - | - | - | -
313 | Kesinga | 13.08.25 | 15:55 | 16:15 | 0:20 | 132kV Kesinga-Lanjigarh Feeder | Over current,Earth fault,R-1.09KA | - | - | - | - | - | - | -
314 | Balasore | 13.08.25 | 16:12 | 18:15 | 2:03 | 160MVA Auto TRF-II | TRF tripped due to mechanical problem in breaker(220kV side). | - | - | - | - | - | - | -
315 | Jharsuguda | 13.08.25 | 19:38 | 14.08.25 20:21 | 24:43 | 132kV Jharsuguda-Lapanga Feeder | At Jharsuguda end: Bph-G,Zone-1,Distance=4.559 km, Ir= 3.38A, Iy= 2.790A, Ib= 6.157kA At Lapanga end: B-ph-G,Distance=13.6km, Ib= 8.50kA | Jharsuguda | 0:25 | - | - | 0.010003 | B-phase jumper snapped at loc. No-138 | -
|  |  |  | 20:17 | 0:39 | 132kV Budhipadar-Lapanga Feeder | B/U relay:- B ph
|  |  |  | 14.08.25 03:53 | 8:15 | 220kV Budhipadar-BPSL-II Feeder | zone 1, A-N, Distance- 7.840 km, IL1- 9.409kA, IL2-742A, IL3- 909.1A
316 | Gondia | 13.08.25 | 22:41 | 23:18 | 0:37 | 132kV Gondia-TTPS Feeder | Tripped at Both end. | - | - | - | - | - | Feeder was Connected to OPCL through TTPS BUS-II. | -
317 | Akhusingh | 14.08.25 | 7:59 | 8:02 | 0:03 | 132kV Rayagada-Akhusingh Feeder | Rayagada incoming failed | - | - | - | - | - | - | -
| Akhusingh | 14.08.25 | 10:12 | 10:14 | 0:02 | 132kV Rayagada-Akhusingh Feeder | Rayagada incoming failed
318 | Tarkera | 14.08.25 | 12:24 | 13:52 | 1:28 | 132kV Tarkera-Kalunga CKT | DP RELAY :- Loop : L1-L3, Dist=7.28 km, Zone-1, IA=7935.65 A, IB=1.02 A, IC=7925.33 A | - | - | - | - | - | THE Feeder WAS AVAILED SHUTDOWN BY Kalunga GSS BUT FIRST CHARGED AT TARKERA GSS AFTER COMPLETION OF SHUTDOWN BUT TRIPPED ON SWITCH ON TO FAULT. | -
319 | Bhawanipatna | 14.08.25 | 16:05 | 16:07 | 0:02 | 132kV Bhawanipatna-Lanjigarh RTSS Feeder | O/C | Lanjigarh RTSS | 0:02 | - | - | 0.00023949 | - | -
320 | Polasponga | 14.08.25 | 19:11 | 19:13 | 0:02 | 132kV Polasponga-Kendujhargarh RTSS Feeder | Back up relay,O/C, IA=299.0A, IB=205A, IC=106.0A, INM=7.07A, IND=6.68A | Kendujhargarh RTSS | 0:02 | - | - | 0.00027868 | - | -
321 | Gondia | 14.08.25 | 20:26 | 20:42 | 0:16 | 132kV Gondia-TTPS Feeder | Tripped at Both end. | - | - | - | - | - | Feeder was Connected to OPCL through TTPS BUS-II. | -
322 | Tarkera | 15.08.25 | 16:16 | 21:14 | 4:58 | 220kV Tarkera-Bamra Feeder | ONLY MASTER TRIP RELAY OPERATED | - | - | - | - | - | FUSE BLOWN OUT | -
323 | Polasponga | 15.08.25 | 16:40 | 16:42 | 0:02 | 132kV Polasponga-Kendujhargarh RTSS Feeder | Back up relay,O/C, IA=299.7A, IB=246.3A, IC=77A, INM=6.43A, IND=6.02A | Kendujhargarh RTSS | 0:02 | - | - | 0.00027868 | - | -
324 | Rairangpur | 15.08.25 | 18:12 | 18:25 | 0:13 | 132kV Rairangpur-Karanjia Feeder | Zone-2, R-Phase, Distance-63.04 KM, Ia=1.030KA, Ib=281.8A, Ic=154.2A | - | - | - | - | - | - | -
325 | Rayagada | 15.08.25 | 19:32 | 19:49 | 0:17 | 132kV Rayagada-Podagada Feeder | R-Phase ,E/F, O/V -1, Zone-1, distance =47.95KM,Ia=122.8A,Ib=79.51A, Ic=201.3A Van=10.6KV, Vbn= 77.89KV and Vcn= 72.20KV at Rayagada end. | Rayagada, Akhusingh | 0:17 | - | - | 0.005264 | Power avail from 132kV Therubali BTH P/S. | -
326 | Mania | 16.08.25 | 4:00 | 4:00 | 0:00 | 132kV Mania-ICCL Feeder | At Mania end: ZONE 1, LOCATION 9.90KM, IA=377A,IB=882A, IC=290A At ICCL end: ZONE 1, LOCATION 11.98KM, IA=362A,IB=4.479KA, IC=273.4A | - | - | - | - | - | MANIA GSS WAS AVAILING SUPPLY FROM ICCL THROUGH SALIPUR GSS AND OCL SS. | AUTO RECLOSURE WAS SUCCESS AT MANIA GSS
327 | Kantabanji | 16.08.25 | 9:35 | 9:44 | 0:09 | 132kV Khariar-Kantabanji Feeder | TRIPPED AT GSS Kantabanji ON OVER LOAD SOURCE | Kantabanji, Kantabanji RTSS | 0:09 | - | - | 0.0027824 | - | -
328 | Therubali | 16.08.25 | 10:51 | 14:07 | 3:16 | 220kV Therubali-Laxmipur CKT-II | At Therubali end: BN,Z-1,26.87KM,Ib-3.173kA At Laxmipur end: BN,Z-1,23.6KM,Ib-2.09kA,AR-Lockout | - | - | - | - | - | - | -
329 | Akhusingh | 16.08.25 | 10:57 | 11:00 | 0:03 | 132kV Rayagada-Akhusingh Feeder | Rayagada incoming failed | - | - | - | - | - | - | -
330 | Kalunga | 16.08.25 | 13:47 | 13:47 | 0:00 | 132kV Budhipadar-Kalunga Feeder | At Kalunga end: R-N, Zone-1, Dist-49.30 km, Ir-1.339 kA, Iy-162.0A, Ib- 314.1A At Budhipadar end: R-N, Zone-1, Dist-41.49 km, Ir-1.991KA,Iy-319.1A,Ib-166.7A | - | - | - | - | - | Auto-recloser successful at Kalunga end and stood ok | -
331 | Therubali | 16.08.25 | 14:53 | 19:33 | 4:40 | 220kV Therubali-Laxmipur CKT-II | At Therubali end: BN,Z-1,28.15KM,Ib-3.02kA At Laxmipur end: BN,Z-1,26.55KM,Ib-3.05kA,AR-Lockout | - | - | - | - | - | - | -
332 | Jayanagar | 16.08.25 | 15:37 | 15:38 | 0:01 | 220kV Jayanagar-Laxmipur CKT-I | Tripped on D/P.Z1,R-G,If-2.356KA,Dist-49.96Km | - | - | - | - | - | - | -
333 | Kantabanji | 16.08.25 | 18:39 | 18:42 | 0:03 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 400 A | Kantabanji RTSS | 0:03 | - | - | 0.00016612 | - | -
334 | Budhipadar | 16.08.25 | 20:13 | 22:49 | 2:36 | 220kV Budhipadar-Korba-I Feeder | At Budhipadar end: Zone 1, R-N, Dist- 53.79km, Ir- 2.937kA At Korba end: R-N, Zone 1, Dist- 105.84km, Ir- 1.654kA | - | - | - | - | - | - | -
335 | Jaleswar | 16.08.25 | 23:55 | 17.08.25 00:52 | 0:57 | 132kV Baripada PG-Jaleswar Feeder | Tripped from both end. | - | - | - | - | - | - | -
336 | Jaleswar | 17.08.25 | 10:20 | 10:50 | 0:30 | 132kV Bhograi-Jaleswar Line | Tripprd frpm Jaleswar end | - | - | - | - | - | - | -
337 | Duburi | 17.08.25 | 10:29 | 10:38 | 0:09 | 132kV Duburi- Jakhapura RTSS Feeder | Tripped on Directional O/C MT(86) Operated. | Jakhapura RTSS | 0:09 | - | - | 0.0017802 | - | -
338 | Balasore | 17.08.25 | 12:20 | 12:20 | 0:00 | 132kV Balasore-Udala Feeder | At Balasore end: B-N, Zone 1, Dist- 10.8km, Ib- 5.4kA | - | - | - | - | - | A/R operated successfully from Balasore end | -
339 | Meramundali | 17.08.25 | 12:30 | 12:30 | 0:00 | 220kV Meramundali-Bhanjanagar Feeder | At Meramundali end: B-N, Ib - 1.951 kA, Z1, 89.01 KM At Bhanjanagar end: B-N, Ib - 2.6 kA, Z1, 51.9 KM | - | - | - | - | - | A/R successful | -
340 | Tarkera | 17.08.25 | 12:56 | 17:56 | 5:00 | 220kV Tarkera-Bamra Feeder | ONLY MASTER TRIP RELAY OPERATED | - | - | - | - | - | FUSE BLOWN OUT | -
341 | Therubali | 17.08.25 | 16:26 | 20:24 | 3:58 | 220kV Therubali-Aska New | At Therubali end: BG,Z-1,153.2KM,Ir-80.73A,Iy-328.5A,Ib-1.118kA,AR-Lockout At Aska New end: BG,Z-1,37.65KM,Ir-81.65A,Iy-86.7A,Ib-3.171kA,AR-Lockout | - | - | - | - | - | - | -
342 | Kantabanji | 17.08.25 | 20:51 | 20:54 | 0:03 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 382A | Kantabanji RTSS | 0:03 | - | - | 0.00016612 | - | -
343 | Tarkera | 18.08.25 | 1:41 | 9:14 | 7:33 | 132kV Tarkera-Rourkela CKT II | B/U Relay :- IA=453.9 A, IB=1494 A, IC=1149 A | Rourkela Bhalulata RTSS | 05:28 06:59 | - | - | 0.22707 | 33 KV BUS FAULT AT Rourkela GRID END | -
|  |  |  | 8:29 | 6:48 | 132kV Tarkera-Rourkela CKT III | CGT, DIST=3.72 KM, IA=878 A, IB=802 A, IC=4004 A
|  |  |  | 8:42 | 7:01 | 132kV Rourkela-Bhalulata- Jaganath Steel Feeder
|  |  |  | 2:53 | 1:12 | 100 MVA AUTO-I | ONLY 132kV SIDE TRIPPED
|  |  |  | 2:55 | 1:14 | 100 MVA AUTO-III | 132kV SIDE: IA- 184.57 A, IB=290.039 A, IC=2622.656A
|  |  | 1:44 | 20.08.25 12:13 | 58:29 | 100 MVA AUTO-IV | 132kV Side :- IA=255 A, IB=463.2 A, IC=3115.8 A
344 | Rourkela | 18.08.25 | 10:32 | 19.08.25 18:22 | 31:50 | 132kV Rourkela-Tarkera CKT-II |  | - | - | - | - | - | - | -
345 | Padampur | 18.08.25 | 15:21 | 16:12 | 0:51 | 132kV Patnagarh-Padampur CKT-I | DP Operated, Zone3, Ia=1.71KA, Ib=1.031KA(At GSS Patnagarh) | - | - | - | - | - | - | -
|  |  |  | 15:41 | 0:20 | Padampur-Nuapada Line-II | DP Operated, Zone1,Dist=45.3KM, Ia=71.66A, Ib=8.92A, Ic=70.44A(At GSS Nuapada)
346 | Kuchinda | 18.08.25 | 16:22 | 17:00 | 0:38 | 132kV Kuchinda-SMC Feeder | Y-N, E/F, Zone 1, Dist- 34.75km, Iy- 0.938kA | - | - | - | - | - | Heavy wind and rain fall | -
347 | Bidanasi | 18.08.25 | 17:08 | 17:20 | 0:12 | 160MVA Auto TRF-III | Tripped due DC Interruption, 96 operated. | - | - | - | - | - | - | -
348 | Duburi-New | 18.08.25 | 17:30 | 17:30 | 0:00 | 220kV Duburi New-Bhadrak Feeder | DP-1&2 operated | - | - | - | - | - | - | -
349 | Gondia | 18.08.25 | 19:14 | 19:36 | 0:22 | 132kV Gondia-TTPS Feeder | Tripped from Gondia end. | - | - | - | - | - | Feeder was Connected to OPCL through TTPS BUS-II. | -
350 | Duburi | 18.08.25 | 22:53 | 23:25 | 0:32 | 220kV Duburi - Meramundali-B Feeder | Tripped on DP & Back-up relay. | - | - | - | - | - | - | -
351 | Joda | 19.08.25 | 10:50 | 11:20 | 0:30 | 220kV Joda-Telkoi Feeder, 220kV Joda-TTPS Feeder | BUS BAR PROTECTION RELAY:- 96.1 TSIL AUXILARY RELAY,96.2 RAMACHANDRAPUR RELAY,96.3 TTPS-02,96.4 TTPS-01,96.8 JSPL RELAY | Joda, Bansapani RTSS FAP TSL TSLP Bolani, Barbil, ARYA Steel, BRPL, IMTCPL, Karakolha, Nalda, Jaganath Steel Polasponga, ESIL, MSP, OSISL, Kendujhargarh RTSS | 00:30 00:35 01:00 00:38 00:24 00:20 | - | - | 0.071993 | Due to operation of BUS-Bar protection at GSS,Joda to all 220kV Incomer Feeder tripped | -
|  |  |  | 11:18 | 0:28 | 220kV Joda-Ramchandrapur Feeder
|  |  |  | 11:24 | 0:34 | 220kV Joda -JSPL Feeder
|  |  |  | 11:24 | 0:34 | 220kV Joda- TSIL Feeder
|  |  |  | 11:24 | 0:34 | 220kV Joda-TSL Feeder
|  |  |  | 11:19 | 0:29 | 160MVA Auto TRF-I, II & III
|  |  |  | 11:14 | 0:24 | 132kV Bolani-Barbil Feeder | Source Failure due to operation of Bus bar protection at Joda end.
|  |  |  | 13:06 | 13:06 | 132kV Joda-Polasponga Feeder
|  |  |  | 11:10 | 0:20 | 132kV Polasponga-Turumunga Feeder | Turumunga end - Ia-435.2A,Ib-440.8A,Ic-395.4A, Inm-9.253A,Ind-9.008A
|  |  | 10:55 | 11:25 | 0:30 | 132kV Joda -Barbil Feeder | Failure due to operation of Bus bar protection at Joda end
|  |  |  | 11:25 | 0:30 | 132kV Joda- Bansapani Feeder
|  |  |  | 11:25 | 0:30 | 132kV Joda-Kenduposi Feeder
|  |  |  | 11:30 | 0:35 | 132kV Joda -FAP Feeder
|  |  |  | 11:25 | 0:30 | 20MVA TRF-II, IV, V & 40MVA TRF VI
352 | Joda | 19.08.25 | 12:12 | 13:27 | 1:15 | 220kV Joda-Telkoi Feeder, 220kV Joda-TTPS Feeder | BUS BAR PROTECTION RELAY:- 96.1 TSIL AUXILARY RELAY,96.2 RAMACHANDRAPUR RELAY,96.3 TTPS-02,96.4 TTPS-01,96.8 JSPL RELAY | Joda, Bansapani RTSS FAP TSL TSLP | 01:01 01:29 01:21 01:30 | - | - | 0.075916 | Due to operation of BUS-Bar protection at GSS,Joda to all 220kV Incomer Feeder tripped | -
|  |  |  | 13:27 | 1:15 | 220kV Joda-Ramchandrapur Feeder
|  |  |  | 13:20 | 1:08 | 220kV Joda -JSPL Feeder
|  |  |  | 13:27 | 1:15 | 220kV Joda- TSIL Feeder
|  |  |  | 13:27 | 1:15 | 220kV Joda-TSL Feeder
|  |  |  | 18:21 | 6:09 | 160MVA Auto TRF-I, II & III
|  |  | 12:18 | 13:19 | 1:01 | 132kV Joda -Polasponga Feeder
132kV Joda -Barbil Feeder
132kV Joda- Bansapani Feeder
132kV Joda-Kenduposi Feeder
|  |  |  | 13:47 | 1:29 | 132kV Joda -FAP Feeder
353 | Aska New | 19.08.25 | 12:33 | 12:33 | 0:00 | 132kV Aska New-Digapahandi CKT-I | A/R close optd,Y-Ph E/F,Z1,IY=4.505KA,D=12.21km | - | - | - | - | - | - | -
354 | Narendrapur | 19.08.25 | 13:04 | 13:04 | 0:00 | 220kV Narendrapur-Atri CKT-I | At Narendrapur end: R-N, Zone 1, Dist- 42.46km, Ir- 2.163kA At Atri end: R-N, Zone 1, Dist- 96.14km, Ib- 1.206kA, A/R successful | - | - | - | - | - | A/R successful from both the ends | -
[6 empty] | 220kV Narendrapur-Atri CKT-II | At Narendrapur end: B-N, Zone 1, Dist- 42.56km, Ib- 2.175kA At Atri end: B-N, Zone 1, Dist- 110.3km, Ib- 1.327kA, A/R successful
355 | Jharsuguda | 19.08.25 | 14:19 | 16:32 | 2:13 | 132kV Jharsuguda-Budhipadar CKT-I | At Jharsuguda end: R-N, Zone-1, Dist- 5.011km, Ir= 810.3A At Budhipadar end: B-N, Zone-1, Dist- 4.086km, Ib- 11.47kA | - | - | - | - | - | AR successful at Budhipadar end. | -
356 | Tarkera | 20.08.25 | 0:18 | 0:43 | 0:25 | 220kV Tarkera-Bamra Feeder | ONLY MASTER TRIP RELAY OPERATED | - | - | - | - | - | FUSE BLOWN OUT | -
357 | Bhograi | 20.08.25 | 7:37 | 8:21 | 0:44 | 132kV Bhograi-Baripada PG Feeder | At Bhograi end: R-N, Dist- 1.9km, Ir- 1.819kA At Baripada end: R-N, Zone 1, Dist- 78.03km, Ir- 0.963kA | - | - | - | - | - | - | -
358 | Paradeep | 20.08.25 | 10:39 | 13:18 | 2:39 | 220kV Paradeep-Duburi New CKT-I | Tripped on O/C on Y & B-Ph to G, Zone 1, Dist - 28.1 KM, Iy=3.14KA, Ib=2.51KA ,AR BLOCKED | - | - | - | - | - | TRANSIENT FAULT | -
359 | Therubali | 20.08.25 | 12:41 | 15:43 | 3:02 | 220kV Therubali-Upper Kolab | At Therubali end: YN,Z-1,95.24KM,Iy-1.275kA At Kolab end: YN,Z-1,31KM,Iy-3.56kA | - | - | - | - | - | - | -
360 | Jajpur Town | 20.08.25 | 14:40 | 18:27 | 3:47 | 132kV Jajpur Town- Bhadrak Feeder | Tripped on DP relay but no fault found after line patrolling | - | - | - | - | - | - | -
361 | BC Mohanty | 21.08.25 | 2:59 | 4:19 | 1:20 | 132kV BC Mohanty-Daitari Feeder | At BC Mohanty end:Zone 1, Dist- 10.7km, Ir- 5.94kA, Iy- 5.65kA, Ib- 0.51kA At Daitari end:Zone 1, Dist- 16.39km, Ir- 0.44kA, Iy- 0.45kA, Ib- 0.45kA | Daitari TATA FAP Bamnipal | 01:20 01:24 | - | - | 0.0026511 | - | -
362 | Rourkela | 21.08.25 | 4:35 | 5:33 | 0:58 | 132kV Rourkela-Bhalulata- Jaganath Steel Feeder | BGT, LOC= 57.48, IA= 33A, IB= 2245A, IC= 2265A, IN=0, IG= 7A, GROUP2, ZONE-1. | Bhalulata RTSS | 13:48 | - | - | 0.065171 | - | -
|  |  | 5:35 | 18:24 | 12:49 | 132kV Rourkela-Bhalulata- Jaganath Steel Feeder | CGT, IA= 14A, IB= 15A, IC= 1019A, IN= 0A, IG= 1027A, ZONE-1, LOC= 59.53A.
363 | Nayagarh | 21.08.25 | 8:00 | 11:17 | 3:17 | 220kV Nayagarh-Bhanjanagar Feeder | DP Relay 2 Maloperation | - | - | - | - | - | - | -
364 | Narendrapur | 21.08.25 | 10:13 | 10:15 | 0:02 | 132kV Narendrapur-Narendrapur RTSS Feeder | O/C (R-B), Ir- 1.03kA, Ib- 1.04kA | Narendrapur RTSS | 0:02 | - | - | 0.0002004 | - | -
365 | Karanjia | 21.08.25 | 12:19 | 22.08.25 12:15 | 23:56 | 132kV Karanjia-Rairangpur Line | At Karanjia End: Zone 1, IL1-0.27KA,IL2-0.20KA,IL3-2.35KA, Dist- 0.1km At Rairangpur End: B-Phase, Zone-2, IL1-299.8A,IL2-245.1A,IL3-1.008KA, Dist- 70.98km | - | - | - | - | - | B Ph LA burst at Karanjia end. At the time of breakdown, Karanjia & Dhenkikote GSS avail power supply from Turumunga GSS | -
366 | Bhadrak | 21.08.25 | 12:40 | 13:04 | 0:24 | 132kV Bhadrak-Dhamra Port Feeder |  | Dhamra Port | 0:24 | - | - | 0.003164 | - | -
367 | Brajarajnagar | 22.08.25 | 5:24 | 8:39 | 3:15 | 132kV Brajarajnagar-Belpahar RTSS Feeder2 | zone - 1, A - N, 8.914 km, 66.71 ms, Ia = 5.588 kA | - | - | - | - | - | Heavy lightening and rain, 132kV RTSS Belpahar I Feeder was in service | -
368 | Therubali | 22.08.25 | 9:10 | 12:28 | 3:18 | 132kV Therubali-Bhalumaska RTSS Feeder | BG,Z-1,14.96KM,Ir-58.75A,Ib-4.059kA | Bhalumaska RTSS | 3:18 | - | - | 0.0085131 | - | -
369 | Budhipadar | 22.08.25 | 9:30 | 12:28 | 2:58 | 220kV Budhipadar-Korba-II Feeder | D/P(ABB REL):- IL1-0.27A, IL2-0.27A, IL3-52.66A, IN-52.24A | - | - | - | - | - | - | -
370 | Kalarangi | 22.08.25 | 9:47 | 9:55 | 0:08 | 12.5MVA TRF-I, 20MVA TRF-III | Tripped due to 33kV feeder fault | Kalarangi | 0:08 | - | - | 0.00072968 | - | -
371 | Meramundali | 22.08.25 | 10:40 | 11:17 | 0:37 | 220kV Meramundali-NALCO-1 | Tripped without any indication | - | - | - | - | - | - | -
| Meramundali | 22.08.25 | 10:43 | 11:22 | 0:39 | 220kV Meramundali-TTPS CKT-II | Tripped without any indication | [6 empty] | -
| Meramundali | 22.08.25 | 10:46 | 11:23 | 0:37 | 220kV Meramundali-Kaniha CKT-II | Tripped without any indication | [6 empty] | -
372 | Budhipadar | 22.08.25 | 12:48 | 14:54 | 2:06 | 220kV Budhipadar-Korba-II Feeder | D/P(ABB REL):- IL1-0.15A, IL2-0.25A, IL3-0.94A, IN-1.17A,AR block | - | - | - | - | - | - | -
373 | Potangi | 22.08.25 | 14:21 | 14:28 | 0:07 | 132kV Sunabeda-Potangi Feeder | Incoming p/s failed from Sunabeda end | Potangi | 0:07 | - | - | 0.00037279 | - | -
374 | Rajnagar | 23.08.2025 | 21:52 | 21:52 | 0:00 | 132kV Pattamundai-Rajnagar CKT-I Feeder. | A/R was successful | - | - | - | - | - | Weather: Heavy thunderstorm | -
375 | Kantabanji | 23.08.25 | 6:57 | 6:58 | 0:01 | 132kV Kantabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 600A | Kantabanji RTSS | 0:01 | - | - | 5.5374e-05 | - | -
376 | Balichandrapur | 23.08.25 | 21:41 | 24.08.25 23:40 | 25:59 | 220kV Paradeep-Balichandrapur Feeder | Tripped on O/C on B-Ph to G, Zone-I,Dist-39.50 KM , Ir=280 A, Iy=516 A, Ib=2.397 Ka | Balichandrapur | 25:59 | - | - | 0.045775 | CONDUCTOR SNAPPED AT LOC NO. 220-221 | -
377 | Pattamundai | 23.08.25 | 21:52 | 21:52 | 0:00 | 132kV Pattamundai-Rajnagar CKT-I | At Pattamundai end: Zone 1, Ib- 2.78kA, dist- 8.5km At Rajnagar end: Zone 1, Ib- 0.81kA, dist- 9.4km | - | - | - | - | - | Heavy thunderstorm | -
378 | Kantabanji | 23.08.25 | 22:29 | 22:54 | 0:25 | 132kV Khariar Kantabanji Feeder | TRIPPED FROM KESINGA END | Khariar, Kantabanji, Kantabanji RTSS | 0:25 | - | - | 0.016547 | - | -
379 | Joda | 23.08.25 | 22:30 | 22:57 | 0:27 | 220kV Joda-TTPS CKT-II | At Joda end: B-N, Zone 1, Dist- 113.9km, Ib- 1.29kA | - | - | - | - | - | NO FAULT FOUND | -
380 | Kesinga | 23.08.25 | 22:30 | 23:18 | 0:48 | 132kV Kesinga-Powmex Feeder | Master Trip Relay Operated | - | - | - | - | - | - | -
381 | Joda | 24.08.25 | 5:05 | 5:40 | 0:35 | 220kV Joda-TTPS CKT-II | At Joda end: B-N, Zone 1, Dist- 113.5km, Ib- 1.313kA At TTPS end: Zone 1, Dist- 29.67km, ib- 4.938kA | - | - | - | - | - | - | -
382 | Duburi-New | 24.08.25 | 21:40 | 25.08.25 00:26 | 2:46 | 220kV Duburi New-Paradeep CKT-I | DP-1&2 operated | - | - | - | - | - | - | -
383 | Bhadrak | 25.08.25 | 1:49 | 1:52 | 0:03 | 132kV Bhadrak-Bhadrak RTSS Feeder |  | Bhadrak RTSS | 0:03 | - | - | 0.00044186 | - | -
384 | Polasponga | 25.08.25 | 1:50 | 1:50 | 0:00 | 132kV Polasponga-Turumunga Feeder | At Polasponga end-Zone-1,Ia-42A,Ib-1119A,Ic-215A,Distance-67.52km | - | - | - | - | - | A/R operated successfully | -
385 | Tentulikhunti | 25.08.25 | 1:55 | 3:36 | 1:41 | 20MVA TRF-I, II & III | Tripped due to fault at 33KV Indravati Feeder | Tentulikhunti | 1:41 | - | - | 0.011894 | - | -
386 | Atri | 25.08.25 | 15:05 | 17:44 | 2:39 | 132kV Atri- Shamuka Feeder | At Atri end: Y-B, Zone 1, Dist- 4.53km, Iy- 5.26kA, Ib- 9.73kA No tripping at Shamuka end | Shamuka | 0:30 | - | - | 0.013641 | - | -
|  |  |  | 15:05 | 0:00 | 132kV Atri- Khurda CKT-I | At Atri end: Y-N, Zone 1, Dist- 2.51km, Iy- 7.44kA, A/R success At Khurda end: Y-N, Zone 3, Dist- 17.52km, Iy- 3.48kA
|  |  |  | 16:50 | 1:45 | 132kV Atri- Khurda CKT-II | At Atri end: Y-N, Zone 1, Iy- 4.13kA No tripping at Khurda end
387 | Polasponga | 25.08.25 | 20:38 | 21:01 | 0:23 | 132kV Polasponga-Turumunga Feeder | Polasponga end-DP relay: Zone-2,Ia-26A,Ib-798A,Ic-26A,In-0,Ig-823A,3I2-819A,Distance-92.10km | - | - | - | - | - | - | -
388 | Bonai | 26.08.25 | 1:42 | 12:02 | 10:20 | 220kV Bonai-Tarkera Feeder | At Bonai end: Zone 1, Y-N, Dist- 33.37km, Iy- 0.991kA | - | - | - | - | - | - | -
389 | Polasponga | 26.08.25 | 5:08 | 5:38 | 0:30 | 132kV Polasponga-Turumunga Feeder | Polasponga end-DP relay: Zone-2,Ia-26A,Ib-808A,Ic-26A,In-0,Ig-834A,3I2-830A,Distance-92.14km | - | - | - | - | - | - | -
390 | Joda | 26.08.25 | 13:02 | 13:29 | 0:27 | 220kV Joda-TTPS CKT-II | At Joda end: B-N, Zone 1, Dist- 116.5km, Ir- 1.799kA At TTPS end: Zone 1, Ir- 0.543kA | - | - | - | - | - | NO FAULT FOUND | -
391 | Kesinga | 26.08.25 | 13:11 | 14:15 | 1:04 | 220kV Bolangir PG-Kesinga Feeder | Distance protection relay operated,Zone-1,distance-58.7 KM,R-1.6 KA | - | - | - | - | - | - | -
392 | Kesinga | 26.08.25 | 13:13 | 13:55 | 0:42 | 132kV Kesinga-Lanjigarh Feeder | Distance protection relay operated,,distance-57.39 KM,R-1.34 KA,Y-70.23 A,B-226.7A | - | - | - | - | - | - | -
393 | Berhampur | 26.08.25 | 13:25 | 13:53 | 0:28 | 132kV Berhampur-Hinjili Feeder | At Berhampur end: B-N, Zone 2, Ib- 3.211kA, Dist- 13.81km At Hinjili end: B-ph E/F, Zone-1, Dist. : 1.691 KM, Ic = 2785 A | Hinjili | 0:28 | - | - | 0.0036944 | - | -
|  |  |  | 13:51 | 0:26 | 132kV Narendrapur-Berhampur CKT-I & II | At Narendrapur end: E/F (B-N) No tripping at Berhampur end
394 | Joda | 26.08.25 | 15:40 | 15:49 | 0:09 | 220kV Joda-TSL Feeder | NO RELAY OPERATED | TSL | 0:09 | - | - | 0.0016844 | NO FAULT FOUND | -
395 | Lapanga | 26.08.25 | 16:25 | 17:23 | 0:58 | 400KV Lapanga-OPGC CKT-II | At Lapanga end: R-Y, Zone 1, Dist- 8.493km, Ir- 16.3kA, Iy- 16.71kA | - | - | - | - | - | - | -
396 | Kalunga | 26.08.25 | 16:37 | 16:37 | 0:00 | 132kV Budhipadar-Kalunga Feeder | At Kalunga end: R-N, Zone-1, Dist-65.74 km, Ir-996.3A, Iy-105.8A, Ib- 134.7A At Budhipadar end: R-N, Zone-1, Dist-27.03 km, Ir-2.68KA,Iy-115A,Ib-137.7A | - | - | - | - | - | Auto-recloser successful at Kalunga end and stood ok | -
397 | Joda | 26.08.25 | 22:33 | 22:50 | 0:17 | 220kV Joda-TSL Feeder | NO RELAY OPERATED | TSL | 0:17 | - | - | 0.0031816 | NO FAULT FOUND | -
398 | Gondia | 27.08.25 | 3:23 | 3:33 | 0:10 | 132kV Gondia-TTPS Feeder | Tripped from Gondia end. | - | - | - | - | - | - | -
|  |  | 5:04 | 5:23 | 0:19
399 | Paradeep | 27.08.25 | 8:45 | 11:07 | 2:22 | 132kV Paradeep-PPT CKT-II | Tripped on O/C on B-Ph ,Zone-I ,DIST= 3.43KM, Ir=132.64 A , Iy = 292.275 A , Ib=9.356 kA | - | - | - | - | - | TRANSIENT FAULT | -
400 | Therubali | 27.08.25 | 11:33 | 11:41 | 0:08 | 220kV Therubali-Laxmipur CKT-I | At Therubali end: RG, Z-1,24.88KM, Ir-3.1kA, Iy-168.2A, Ib-64.74A At Laxmipur end: RG,Z-1,34.5KM,Ir-1.36kA,AR-Success | - | - | - | - | - | - | -
401 | Jayanagar | 27.08.25 | 13:48 | 14:36 | 0:48 | 132kV Transfer BUS Jayanagar |  | Jeypore RTSS Sunabeda, HAL Potangi | 00:54 00:51 00:47 | - | - | 0.026101 | 132KV Railway fdr,132KV Boriguma fdr,132KV Tentulikhunti fdr,132KV Sunabeda-1&2 fdr interrupted. During the shutdown period only Sunabeda GSS was in complete blackout condition rest GSS were having alternate supply from other connected fdrs to them | -
|  |  |  | 14:36 | 0:48 | 132kV Main BUS Jayanagar
|  |  |  | 14:36 | 0:48 | 132kV Tentulikhunti-Jayanagar Feeder | Tripped on D/P. Z4-Reverse Zone,If-600A
|  |  |  | 14:36 | 0:48 | 160MVA Auto TRF-I & II | Tripped on O/C. B-G,If-5.2KA
|  |  |  | 19:32 | 5:44 | 132kV Jayanagar-Meenakshi Feeder | Before tripping of CB of Meenakshi feeder the AUTO Trf-1&2 tripped as the snapped jumper touched the reserve bus which was in charged condition.
|  |  |  | 14:35 | 0:47 | 132kV Sunabeda-Potangi SC Line | I/C Failure
|  |  |  | 14:39 | 0:51 | 132kV Sunabeda-HAL Feeder | I/C Failure
|  |  |  | 14:48 | 1:00 | 132kV Sunabeda-Jayanagar CKT-I | 132kV Main Bus breakdown at GSS Jayanagar end
|  |  |  | 14:42 | 0:54 | 132kV Sunabeda-Jayanagar CKT-II | 132kV Main Bus breakdown at GSS Jayanagar end
402 | Joda | 27.08.25 | 16:01 | 16:11 | 2:23 | 220kV Joda-TSL Feeder | NO RELAY OPERATED | TSL | 3:27 | - | - | 0.038741 | DP RELAY WIRE BURST | -
|  |  | 18:27 | 18:34 | 0:07
|  |  | 18:38 | 21:48 | 3:10
403 | Sonepur | 27.08.25 | 18:53 | 19:09 | 0:16 | 20MVA TRF-I, 40MVA TRF-II & TRF-III | Due to heavy sparking seen at 33KV main Bus | Sonepur, Boudh, Birmaharajapur | 0:16 | - | - | 0.013877 | - | -
404 | Umerkote | 28.08.25 | 11:56 | 12:06 | 0:10 | 132kV Dabugaon-Umerkote Feeder | Incomer Failed | Umerkote | 0:10 | - | - | 0.0030249 | - | -
405 | Gondia | 28.08.25 | 21:11 | 21:25 | 0:14 | 132kV Gondia-JFAL Feeder | Tripped at Both end. | - | - | - | - | - | - | -
406 | Khariar | 29.08.25 | 1:00 | 1:24 | 0:24 | 132kV Kesinga-Khariar Feeder | Zone-1,distance-36.6 KM,R-154 A,Y-421 A,B-2.07KA | Khariar, Kantabanji, Kantabanji RTSS | 0:24 | - | - | 0.015885 | - | -
407 | Tarkera | 29.08.25 | 7:01 | 20:23 | 13:22 | 220kV Tarkera-Bamra Feeder | ONLY MASTER TRIP RELAY OPERATED | - | - | - | - | - | FUSE BLOWN OUT | -
408 | Rajgangpur | 29.08.25 | 8:57 | 9:08 | 0:11 | 132kV Rajgangpur- RTSS Feeder 1 | RTT=16.734 s,O/C,IA=357.2 A,IB=356 A,IC=0 A,IG=0.8 A | - | - | - | - | - | - | -
409 | Paradeep | 29.08.25 | 10:41 | 11:15 | 0:34 | 220kV Paradeep-Balichandrapur Feeder | Tripped on O/C on B-Ph to G, Zone I1, Dist - 53.76 KM,Ir=277.9 A Iy=521.074 A, Ib=1.71 kA ,AR BLOCKED | Paradeep, AMNS, IFFCO, IOCL, PPL, PPT, Siju RTSS Kendrapada, Pattamundai, Marshaghai, Kendrapada RTSS | 00:34 00:10 | - | - | 0.066835 | DUE TO TREE TOUCHING | -
|  |  |  | 10:48 | 0:07 | 132kV Kendrapada-Pattamundai Feeder | Source failure
|  |  |  | 11:20 | 0:39 | 132kV Kendrapada-Paradeep Feeder.
|  |  |  | 10:51 | 0:10 | 132kV Kendrapada-Marshaghai Feeder
|  |  |  | 11:22 | 0:41 | 132kV Paradeep-Marshaghai Feeder
410 | Meramundali | 29.08.25 | 11:05 | 11:05 | 0:00 | 220kV Meramundali-Bhanjanagar Feeder | At Meramundali end: B-N, Ib - 1.951 kA, Z1, 83.74 KM At Bhanjanagar end: B-N, Ib - 1.73 kA, Z1, 73.41 KM | - | - | - | - | - | A/R successful | -
411 | Paradeep | 29.08.25 | 13:22 | 17:07 | 3:45 | 132kV Paradeep-PPT CKT-I | Tripped on O/C on R & Y-Ph ,Zone-I ,DIST= 0.561 KM,Ir=7.64 kA , Iy = 7.63kA , Ib=172 A | - | - | - | - | - | DUE TO JUMPER CONDUCTOR SNAPPED AT LOC NO. 5 | -
412 | Rourkela | 29.08.25 | 14:37 | 15:22 | 0:45 | 132kV Rourkela-Tarkera CKT-I | BGT, LOC= 0.42, IA= 589A, IB= 4662A, IC= 477A, IN= 0A, IG= 3606A. GROUP-1, ZONE=3 | Rourkela Bhalulata RTSS Jaganath Steel Chend | 00:46 05:35 00:05 00:01 | - | - | 0.054421 | 132kV Joda Feeder JUMPER SNAPPED AT Rourkela GRID END | -
|  |  |  | 15:49 | 1:12 | 132kV Rourkela-Tarkera CKT-III
|  |  |  | 15:43 | 1:06 | 35MVA TRF-I | IL1= 0.47KA, IL2= 0.34KA, IL3= 0.3KA.
|  |  |  | 15:23 | 0:46 | 40MVA TRF-II | O/C, IA= 477.6A, IB= 316A, IC= 450A, IN= 1.152KA.
|  |  |  | 15:43 | 1:06 | 35MVA TRF-III | IL1= 0.47KA, IL2= 0.35KA, IL3= 0.3KA.
|  |  |  | 20:12 | 5:35 | 132kV Rourkela-Bhalulata- Jaganath Steel Feeder | BGT, LOC= 0.79, IA= 90A, IB= 9069A, IC= 85A, IN= 1A, IG= 8986A, GROUP-2, ZONE-1.
|  |  |  | 14:55 | 0:18 | 100 MVA AUTO-I at Tarkera | ONLY 132kV SIDE TRIPPED. B/U Relay :- 202.7 A, IB=2.706 KA, IC=213.0 A
|  |  |  | 14:57 | 0:20 | 100 MVA AUTO-III at Tarkera | ONLY 132kV SIDE TRIPPED. B/U Relay :- 120.703A, IB=2752.734 A, IC=247.266 A
|  |  |  | 15:13 | 0:36 | 100 MVA AUTO-IV at Tarkera | 132kV Side :- IA=311.4 A, IB=3177.6 A, IC=270 A
|  |  | 14:48 | 15:46 | 0:58 | 132kV Chend-Kuarmunda Feeder | Tripped on DP- ABC,Zone-2,IL1-2.655A,IL2-2.066A,IL3-1.318KA,Distance-12.84KM
413 | Gondia | 29.08.25 | 19:56 | 20:04 | 0:08 | 132kV Gondia-TTPS Feeder | Tripped from Gondia end. | - | - | - | - | - | - | -
414 | Kantabanji | 30.08.25 | 4:20 | 4:40 | 0:20 | 132kV Khariar Kantabanji Feeder | Zone-1,distance-13.24 KM,R-93.79 A,Y-334.1 A,B-3.82KA | Khariar, Kantabanji, Kantabanji RTSS | 0:20 | - | - | 0.013237 | - | -
415 | Gondia | 30.08.25 | 5:14 | 5:19 | 0:05 | 132kV Gondia-TTPS Feeder | Tripped from Gondia end. | - | - | - | - | - | - | -
416 | Barbil | 30.08.25 | 8:06 | 8:28 | 0:22 | 132kV Barbil-Bolani Feeder | At Barbil end: O/C, Ir- 0.278kA, Iy- 0.256kA, Ib- 0.4kA | Bolani, ARYA Steel, BRPL, IMTCPL, Karakolha, Nalda Jaganath Steel, Bhalulata RTSS | 00:21 00:25 | - | - | 0.011472 | Bolani GSS,Bolani SAIL, Arya s/s,PTCL s/s, Karakhendra s/s, Nalda RTSS, Jagannath steel s/S. | -
417 | Baripada | 30.08.25 | 10:49 | 11:47 | 0:58 | 132kV Baripada-Betanati Feeder | B-N, Ir- 0.14kA, Iy- 0.24kA, Ib- 2.06kA | - | - | - | - | - | - | -
418 | Kharagprasad | 30.08.25 | 13:33 | 13:39 | 0:06 | 20MVA TRF-I, II | E/F, Ir- 1.6kA | Kharagprasad | 0:06 | - | - | 0.00032132 | - | -
419 | Jagatsinghpur | 30.08.25 | 16:18 | 18:13 | 1:55 | 132kV Jagatsinghpur-Tirtol Feeder | No Relay Indication at Jagatsinghpur end At Tirtol end: Zone 1, Yph-N, Dist- 5.816Km, Iy- 200.9Amp, Ir-285.9Amp,Ib=200.9Amp | Tirtol | 0:14 | - | - | 0.0040258 | At 16:32 Hrs, Tirtol GSS availed Power supply from Paradeep | -
420 | Jaleswar | 30.08.25 | 17:50 | 17:54 | 0:04 | 132kV Jaleswar-Jaleswar RTSS Feeder | Tripped on over load. | Jaleswar RTSS | 0:04 | - | - | 0.00052016 | - | -
421 | Meramundali | 30.08.25 | 18:33 | 19:27 | 0:54 | 400kV Meramundali-Duburi CKT-I | DTT | - | - | - | - | - | - | -
422 | Joda | 30.08.25 | 20:22 | 20:32 | 0:10 | 220kV Joda-TSL Feeder | NO RELAY OPERATED | TSL | 0:14 | - | - | 0.0026202 | - | -
|  |  | 23:46 | 23:50 | 0:04
423 | Chend | 31.08.25 | 4:30 | 4:44 | 0:14 | 132kV Chend-Nuagaon RTSS Feeder | Y-N, ZONE-1, LOC-11.83KM, Iy- 5.974kA | Nuagaon RTSS | 0:14 | - | - | 0.00086807 | - | -
424 | Kuchinda | 31.08.25 | 5:15 | 5:37 | 0:22 | 132kV Kuchinda-SMC Feeder | R-N, E/F, Zone 1, Dist- 34.99km, Ir- 0.89kA | - | - | - | - | - | Heavy wind and rain fall | -
425 | Budhipadar | 31.08.25 | 6:09 | 6:48 | 0:39 | 132kV Budhipadar-Brajarajnagar Feeder | D/P - (Schneider micom p442):zone 1, Fault loop- A-N, Fault Distance- 8.408 km, IL1- 4.621kA, IL2-141.3A, IL3- 343.4A, Fault resistance-1.981ohm,Fault Duration-78.38ms. | MSP Lakhanpur | 00:50 01:06 | - | - | 0.014365 | weather-Lightening | -
|  |  | 6:09 | 6:59 | 0:50 | 132kV Budhipadar-MSP Feeder | B/U (Schneider P141):-E/F,M/T operated.
|  |  | 6:10 | 6:10 | 0:00 | 132kV Budhipadar-Lakhanpur Feeder | D/P - (Areva P441):zone 1, Fault loop- A-N, Fault Distance- 13.23 km, IL1- 6.45kA, IL2-161.6A, IL3- 156.8A, Fault resistance-189.1mohm,Fault Duration-56.70ms. AR-Successful
|  |  | 6:11 | 6:52 | 0:41 | 132kV Brajarajnagar- Jurabanga MCL Feeder | Dp operated: Siemens, zone 1, L1 - E, 3.0 km, 65 ms, Ia = 4.09 kA, Ib(y) = 0, Ic = 0
|  |  | 6:21 | 16:01 | 9:40 | 220kV Budhipadar-AAL CKT-II | D/P-I: - (Areva P442):zone 1, Fault loop- A-N, Fault Distance- 4.711 km, IL1- 11.88kA, IL2-0A, IL3- 0A, Fault resistance-3.975ohm,Fault Duration-75.13ms. D/P-II: - (Areva P442):zone 1, Fault loop- A-N, Fault Distance- 4.507 km, IL1- 11.90kA, IL2-0A, IL3- 0A, Fault resistance-3.979ohm,Fault Duration-75.12ms.
426 | Rourkela | 31.08.25 | 7:49 | 13:59 | 6:10 | 132kV Rourkela-Bhalulata- Jaganath Steel Feeder | AGT, LOC=26.03, IA= 3088A, ZONE-1. | Bhalulata RTSS | 6:10 | - | - | 0.029122 | - | -
427 | Kalarangi | 31.08.25 | 10:05 | 10:06 | 0:01 | 12.5MVA TRF-I | Black out due to pulled out of TFR-1 by 33KV Kaliapani Feeder fault when TFr-3 is on Shutdown | Kalarangi | 0:01 | - | - | 9.121e-05 | - | -
428 | Kendrapada | 31.08.25 | 10:37 | 12:32 | 1:55 | 132kV Kendrapada-RAMCO Feeder | AT Kendrapada END: ZONE-1, DISTANCE: 4.32Kms , Ir=11.95A,Iy=11.81A,Ib=3.9kA AT RAMCO END: BREAKER TRIPPED ON E/F. | RAMCO | 1:55 | - | - | 0.0080301 | - | -
429 | Bhadrak | 31.08.25 | 13:14 | 14:04 | 0:50 | 132kV Bhadrak-Dhamra Port RTSS Feeder |  | Dhamra Port RTSS | 0:50 | - | - | 0.0028068 | - | -
430 | Budhipadar | 31.08.25 | 13:53 | 13:53 | 0:00 | 132kV Budhipadar-Lakhanpur Feeder | D/P - (Areva P441):zone 1, Fault loop- C-N, Fault Distance- 7.107 km, IL1- 80.39A, IL2-118.6A, IL3- 11.83KA, Fault resistance-1.978ohm,Fault Duration-59.79ms. AR-Successful | - | - | - | - | - | - | -
431 | Dhenkanal | 31.08.25 | 15:23 | 15:35 | 0:12 | 132kV Dhenkanal-Khuntuni Feeder | Z-1, Dist=12.99, B-N, Ib=2.983KA | Khuntuni, Shree Cement | 0:12 | - | - | 0.0033143 | - | -
432 | Bhanjanagar | 31.08.25 | 16:22 | 16:25 | 0:03 | 132kV Bhanjanagar-G.Udayagiri Feeder | B-N, Zone 1, Dist- 40.19km, Ib- 2.247kA | G.Udayagiri Phulbani | 00:03 00:12 | - | - | 0.002687 | - | -
|  |  |  | 16:34 | 0:12 | 132kV G.Udayagiri - Phulbani Feeder | Incomer Power Supply Failure From G.Udayagiri GSS
433 | Meramundali | 31.08.25 | 18:29 | 18:29 | 0:00 | 132kV Meramundali-Khajuriakata Feeder | At Meramundali end: A/R successful, B-E, Ib - 7.25 KA, 11.75 KM , Z1 At Khajuriakata end: A/R successful, B-E, Ib - 0.98 kA, 16.53 KM | - | - | - | - | - | - | -
434 | Kalunga | 31.08.25 | 19:09 | 19:09 | 0:00 | 132kV Budhipadar-Kalunga Feeder | At Kalunga end: R-N, Zone-1, Dist-36.59 km, Ir-2.171KA, Iy-47.21A, Ib- 24.08A At Budhipadar end: R-N, Zone-1, Dist-54 km, Ir-1.68 KA,Iy-191.8A,Ib-168.8A | - | - | - | - | - | Auto-recloser successful at Kalunga end and stood ok | -
435 | Bhawanipatna | 31.08.25 | 20:18 | 20:21 | 0:03 | 132kV Bhawanipatna-Bhawanipatna RTSS Feeder | O/C | Bhawanipatna RTSS | 0:07 | - | - | 2.8432e-05 | - | -
|  |  | 20:39 | 20:43 | 0:04
436 | Jharsuguda | 01.09.25 | 2:18 | 3:17 | 0:59 | 132kV Jharsuguda- Ultratech Feeder | Bph-G, Zone-1, Dist=5.509 km, Ib= 6.848kA | Ultratech | 0:59 | - | - | 0.007715 | - | -
437 | Polasponga | 01.09.25 | 6:36 | 6:36 | 0:00 | 132kV Polasponga-Turumunga Feeder | At Polasponga end: E/F, Y-N, Zone-1, Iy- 2.27kA, Dist- 16km At Turumunga end: A/R successful, Y-N, Zone 1, Dist- 80.80km, Iy- 1.116kA | - | - | - | - | - | A/R operated successfully at both end | -
438 | Rourkela | 01.09.25 | 9:21 | 10:32 | 1:11 | 132kV Rourkela-Bhalulata-Jaganath Steel Feeder | Y-N, Zone 1, Dist- 2.38km, Iy- 6.3kA | Bhalulata | 8:19 | - | - | 0.00060053 | - | -
|  |  | 10:32 | 17:40 | 7:08 |  | Iy- 7.05kA
439 | Tarkera | 01.09.25 | 10:34 | 10:57 | 0:23 | 132kV Tarkera-Rourkela CKT-I | Tripped from Tarkera end only due to fault in 132kV Rourkela-Joda Feeder | - | - | - | - | - | - | -
|  |  |  | 12:04 | 1:30 | 132kV Tarkera-Rourkela CKT-III
440 | Mendhasal | 01.09.25 | 12:14 | 12:14 | 0:00 | 400kV Mendhasal-Meramundali CKT-I | R-N, Zone 1, Dist- 0.05km, Ir- 12.92kA | - | - | - | - | - | AR successful at both end. | -
441 | Budhipadar | 01.09.25 | 13:37 | 15:47 | 2:10 | 220kV Budhipadar Korba I | At Budhipadar end: Zone 1, Fault loop - A-N, Fault Dist - 53.50km, Ia- 2.878kA, Ib- 181.4A, Ic- 354.9A, A/R successful At Korba end: Zone 1, Fault loop- A-N, Ia- 17.77kA, Ib- 142A, Ic- 346A, In- 14.85kA | - | - | - | - | - | A/R successful at Budhipadar end. Feeder had tripped from Korba end. | -
442 | Polasponga | 01.09.25 | 14:39 | 14:41 | 0:02 | 132kV Polasponga-Kendujhargarh RTSS Feeder | O/C, IA=303.8A, IB=260.9A, IC=56.13A | Kendujhargarh RTSS | 0:02 | - | - | 0.00027741 | OVER CURRENT | -
443 | Rourkela | 01.09.25 | 15:32 | 15:44 | 0:12 | 132kV Rourkela-Tarkera CKT-II |  | - | - | - | - | - | - | -
|  |  | 15:40 | 16:00 | 0:20 | 132kV Rourkela-Tarkera CKT-III | IL1= 0.06KA, IL2= 0.01KA, IL3= 0.09KA
|  |  | 15:46 | 16:53 | 1:07 | 35MVA TRF-III
444 | Rourkela | 01.09.25 | 18:12 | 18:41 | 0:29 | 132kV Rourkela-Bhalulata-Jaganath Steel Feeder |  | Bhalulata | 0:29 | - | - | 3.4901e-05 | - | -
445 | Sambalpur | 01.09.25 | 18:41 | 19:04 | 0:23 | 132kV BurlaPH-Sambalpur Feeder | At Burla end: Tripped on Y ph O/C with IR=318.1 A, IY=399.6 A,IB=369.3 A, Ig=7.455 A No tripping at Sambalpur end | Sambalpur Rairakhol, Rairakhol RTSS, Boinda, Boinda RTSS Maneswar, Maneswar RTSS | 00:13 00:29 00:14 | - | - | 0.02618 | blackout at SBP GSS, 132kV SBP-ShyamDRI Feeder was in H/T condition prior to fault. | -
|  |  |  | 20:19 | 1:38 | 132kV Sambalpur-Katapali Feeder | At Katapali end: Y ph O/C, Ia= 536 A, Ib=728 A, Ic=655 A No tripping at Sambalpur end
|  |  |  | 19:10 | 0:29 | 132kV Rairakhol-Maneswar Feeder | Source failure from Sambalpur side
|  |  |  | 18:55 | 0:14 | 132kV Sambalpur-Maneswar Feeder
446 | Paradeep | 02.09.25 | 4:06 | 11:22 | 7:16 | 220kV Paradeep-Duburi New CKT-II | Tripped on O/C on Y-Ph to G, Zone 1, Dist - 15.5km, Ir-0 kA, Iy-3.8 kA , Ib- 0 kA | - | - | - | - | - | FAULT FOUND AS HANGER FAILURE AT LOC NO. 351 | -
447 | Kalunga | 02.09.25 | 0:05 | 0:05 | 0:00 | 132kV Tarkera-Kalunga Feeder | B-N, Zone-1, Dist- 2.265 km, Ib- 2.722KA | - | - | - | - | - | Auto-recloser successful at kalunga end and stood ok. | -
448 | Balasore | 02.09.25 | 4:06 | 03.09.25 12:42 | 32:36 | 220kV Balasore-Balimunda Feeder | At Balasore end: R-N, Zone 1, Dist- 4.24km, Ir- 7.424kA At Balimunda end: R-N, Zone 1, Dist- 65.3km, Ir- 1.307kA | - | - | - | - | - | R-Ph disc insulator at Dist no 434 is punctured.. | -
449 | Duburi-New | 02.09.25 | 4:06 | 11:22 | 7:16 | 220kV Duburi New-Paradeep Feeder | At Paradeep end: Y-N, Dist- 15.5km, Zone 1, Iy- 4.4kA | - | - | - | - | - | - | -
450 | Kalunga | 02.09.25 | 8:41 | 8:41 | 0:00 | 132kV Budhipadar-Kalunga Feeder | At Budhipadar end: R-N, Zone-1, Dist-40.53 km, Ir-2.157 KA,Iy-175.9A,Ib-110.4 A At Kalunga end: R-N, Zone-1, Dist-50.88 km, Ir-1.589 kA, Iy- 160.7A, Ib- 98.19A | - | - | - | - | - | E/F | -
451 | Malkangiri | 02.09.25 | 10:01 | 11:02 | 1:01 | 220kV Malkangiri-Kalimela Feeder | R-Y-B Phase Pickup, Zone-2 OPTD, E/F Pickup, A/R Lockout., Dist- 53.8km | - | - | - | - | - | - | -
452 | Rairakhol | 02.09.25 | 10:51 | 11:07 | 0:16 | 132kV Sambalpur-Rairakhol Feeder | Zone 1, DIST- 27.9KM, R-PHASE O/C, IL1=2.11KA | - | - | - | - | - | - | -
453 | Kalimela | 02.09.25 | 371:33 | 373:37 | 2:04 | 220kV Balimela-Kalimela Feeder | DUE TO FAULT | - | - | - | - | - | - | -
454 | Polasponga | 02.09.25 | 12:19 | 12:22 | 0:03 | 132kV Polasponga-Kendujhargarh RTSS Feeder | O/C, IA=298.6A, IB=225.3A, IC=107.6A | Kendujhargarh RTSS | 0:03 | - | - | 0.00041611 | OVER CURRENT | -
455 | BC Mohanty | 02.09.25 | 12:24 | 12:35 | 0:11 | 132kV BC Mohanty-Tomka RTSS Feeder | O/C, B/U relay optd. Ia=237.5A, Ic=239.6A Van=75.71KV, Vbn=77.82KV, Vcn=77.89KV | Tomka RTSS | 0:11 | - | - | 0.00088301 | - | -
456 | Kantabanji | 02.09.25 | 14:23 | 14:28 | 0:05 | 132kV Kanatabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 448 A | Kantabanji RTSS | 0:05 | - | - | 0.00029227 | - | -
457 | Tarkera | 02.09.25 | 15:30 | YET NOT CHARGED | - | 100MVA Auto TRF-I | 220kV Y-PH BUSHING INSULATOR RUPTURED | - | - | - | - | - | - | -
458 | Kharagprasad | 02.09.25 | 18:20 | 18:27 | 0:07 | 132kV Kharagprasad-NAVA Feeder-I | Tripped on LBB Trip during NAVA Feeder-I CT testing. | - | - | - | - | - | - | -
459 | Gondia | 02.09.25 | 20:30 | 20:41 | 0:11 | 132kV Gondia-JFAL Feeder | Tripped at Both end. | Gondia | 0:11 | - | - | 0.0013303 | - | -
460 | Budhipadar | 03.09.25 | 22:46 | 04.09.25 00:41 | 1:55 | 132kV Budhipadar Sundergarh II | At Budhipadar end: Zone 1, A-G, Fault Dist- 6.35km, Ia- 6.742kA At Sundargarh end: A-G, Dist - 19.69km, Ia- 955A, Ib- 69A, Ic- 133A, A/R successful | - | - | - | - | - | - | -
461 | Bhadrak | 04.09.25 | 12:27 | 14:41 | 2:14 | 132kV Bhadrak-Dhamra Port Feeder1 | At Bhadrak end: B-N, Zone 1, Dist- 34.34km, Ib- 2.377kA At DPCL-I end: Ia=189 A,Ib=271A,Ic=292 A | Dhamra Port | 2:14 | - | - | 0.0195 | - | -
462 | Balugaon | 04.09.25 | 14:23 | 17:53 | 3:30 | 132kV Balugaon- Chatrapur Line | At Balugaon end: Zone 2, Dist- 46.86km, Iy- 1.019kA, Ib- 1.01kA At Chatrapur end: Zone 1, Dist- 14.72km, Iy- 4.457kA, ib- 4.394kA | - | - | - | - | - | From Loc-348 to Loc-347 a Tree fell on to the line due to cutting of trees by villagers | -
463 | Angul | 04.09.25 | 14:32 | 14:54 | 0:22 | 132kV TTPS-Angul Feeder | Tripped on DP Relay,Fault Abs. Dist=3.4KM,Fault Loop -L2N,fault current 4.2KA | - | - | - | - | - | Heavy rain and sever lightning | -
|  |  |  | 15:24 | 0:52 | 132kV Chainpal-TTPS CKT-II | O/C B phase & E/F Ib: 2.7 KA, Zone 3
464 | Barkote | 04.09.25 | 15:46 | 18:49 | 3:03 | 220kV Barkote-Deogarh Feeder | At Deogarh end: Tripped Ph-ABC,Zone-1,Ia-2.89 KA,Ib-4.36KA,Ic-0.04KA,Fault Dist-11.9 Kms At Barkote end: Tripped ph- AB Dist- 10.61Km Ia-2105KA, Ib- 2.773KA, Ic- 19.17A Fault resistance- 1.195ohm Zone-I | - | - | - | - | - | - | POWER SUPPLY NOT INTERRUPTED DUE TO BOTH GRID (Barkote WAS FED FROM BONAI & Deogarh WAS FED FROM RENGALI) end.
465 | Brajarajnagar | 04.09.25 | 23:48 | 05.09.25 00:39 | 0:51 | 132kV Brajrajnagar - Jorabaga MCL Feeder | DP operated : Dist - 12.8 km, trip time - 44ms, L1 - E, IL1 - 4.10 KA, Zone 1 | - | - | - | - | - | a. Weather : Heavy Lightening & Rain b. The Feeder was idle charged from Brajrajnagar end. | -
466 | Govindapally | 05.09.25 | 1:26 | 9:08 | 7:42 | 220kV Balimela-Govindpalli CKT-III | Zone-2 Fault at 41.3KM Towards Balimela cause of Trip was Jumped snap and Over Voltage | - | - | - | - | - | - | -
467 | Aska New | 05.09.25 | 10:17 | 14:13 | 3:56 | 220kV Aska New-Bhanjanagar CKT-I | Tripped on B-Ph E/F,Z2,D=52.7Km,IB=4.08KA, A/R Lockout | - | - | - | - | - | A/R close optd at GSS Bhanjanagar end.Not tripped at remote end. | -
468 | Therubali | 05.09.25 | 12:49 | 16:08 | 3:19 | 220kV Therubali-Bhanjanagar CKT-II | At Therubali end: B/U relay details: O/C, BG, Ib=790A At Bhanjanagar end: BG, Z-2, 81.64KM, Ib=1.027KA | - | - | - | - | - | - | -
469 | Gondia | 05.09.25 | 19:24 | 19:38 | 0:14 | 132kV Gondia-OPCL Feeder | Tripped at Both end. | - | - | - | - | - | - | -
470 | Podagada | 05.09.25 | 21:06 | 22:17 | 1:11 | 132kV Podagada-Potangi Feeder | Zone-1, Dist= 29.44 KM, IA= 1.280kA | Potangi | 1:11 | - | - | 0.0054377 | - | -
|  |  |  | 06.09.25 17:00 | 19:54 | 132kV Sunabeda-Potangi Feeder | IL1 : 2.86 KA, IL2 : 0.07 KA, IL3 : 0.53 KA, Dist- 10.6km
471 | Paradeep | 06.09.25 | 9:48 | 13:08 | 3:20 | 132kV Paradeep-PPT CKT-I | Tripped on O/C on R-Ph to G, Zone 1, Dist - 3.37 KM, Ir-7.4 kA, Iy-116 A , Ib- 245 A | - | - | - | - | - | DUE TO HEAVY LIGHTNING AND RAINFALL | -
472 | Malkangiri | 06.09.25 | 1:27 | 2:15 | 0:48 | 220kV Malkangiri-Balimela Feeder | R-Y-B, Zone-2, Dist- 26.7km | Malkangiri, Kalimela Balimela | 00:48 00:51 | - | - | 0.017293 | - | -
|  |  |  | 2:18 | 0:51 | 220kV Balimela-Kalimela Feeder | DUE TO SUPPLY FAIL
|  |  |  | 2:15 | 0:48 | 220kV Malkangiri-Kalimela Feeder | DUE TO SUPPLY FAIL
473 | Balasore | 06.09.25 | 9:22 | 9:34 | 0:12 | 132kV Balasore-Balasore RTSS Feeder | O/C,R-ph ,B-ph OPTD fault current:Ir=337A,Iy=334A. | Balasore RTSS | 0:12 | - | - | 0.0016759 | - | -
474 | Kesinga | 06.09.25 | 12:16 | 17:49 | 5:33 | 220kV Bolangir New-Kesinga Feeder | Dist protection relay operated,Zone-1,Dist-52.24 KM,R-73.07 A,Y-150.07 A,B-933.4 A | Bolangir New, Bolangir Sonepur, Boudh, Birmaharajpur Nuapada, Nuapada RTSS, Tusura, Deogaon RTSS Padampur, Patnagarh, ACME BEL, ORDNANCE | 00:28 00:37 00:25 00:33 00:08 | - | - | 0.093827 | - | -
|  |  |  | 12:38 | 0:22 | 132kV Kesinga-Vento Power Solar-II | Source failure from Bolangir New end
|  |  |  | 12:53 | 0:37 | 132kV Sonepur -Bolangir Feeder
|  |  |  | 12:50 | 0:34 | 132kV Sonepur-Birmaharajpur Feeder
|  |  |  | 17:49 | 5:33 | 220kV Bolangir New-Kesinga Feeder
|  |  |  | 12:25 | 0:09 | 132kV Saintala-Tusura Feeder
|  |  |  | 12:44 | 0:28 | 132kV Bolangir- Bolangir New CKT-I, II
475 | Laxmipur | 06.09.25 | 12:34 | 13:05 | 0:31 | 220kV laxmipur-aditya CKT-II | B-N, Zone 1, Dist- 8.41km, A/R successful | - | - | - | - | - | - | -
476 | Kalunga | 06.09.25 | 13:10 | 13:10 | 0:00 | 132kV Budhipadar-Kalunga Feeder | R-Y-N, Zone-1, Dist-74.98km, Ir-1.705 kA, Iy- 1.521KA, Ib- 170.7A | - | - | - | - | - | - | -
477 | Budhipadar | 06.09.25 | 13:23 | 13:23 | 0:00 | 132kV Budhipadar-Bamra Feeder | Zone 1, R-N, Dist- 31.32 km, Ir- 2.799kA, A/R Successful | - | - | - | - | - | - | -
478 | Polasponga | 06.09.25 | 13:46 | 20:05 | 6:19 | 132kV Polasponga-Turumunga Feeder | Polasponga end-DP relay: AG T,Zone-2,Ia-761A,Ib-24A,Ic-26A,In-0,Ig-786A,Dist-94.1km Turumunga end - DP relay,Zone-1, Dist-8.195km,Ia-4.211KA,Ib-288.3A,Ic-86.18KA | - | - | - | - | - | EARTH FAULT | -
479 | Joda | 06.09.25 | 17:13 | 17:13 | 0:00 | 220kV Joda-Telkoi Feeder | At Joda end: DP MAIN-01 Started ph –AN, Tripped ph –A A/R OPERATED,Zone –01,Dist-73.9KM DP MAIN-02,Event-AGT,A/R operted Zone –01,Dist-68.191KM At Telkoi end:Zone-1 ,Tripped phase-AN Dist-46.69KM, DP MAIN-02,Event-AG,A/R operted Zone –01,Dist-46.8KM | - | - | - | - | - | - | -
| Joda | 06.09.25 | 17:13 | 17:44 | 0:31 | 220kV Joda-TTPS Feeder | At 17:13 Hrs. 220kV Joda –TTPS CKT-II Feeder tripped at TTPS ends and A/R success at Joda end with following fault details. At Joda end:DP MAIN-01,Started ph –AN, Tripped ph –A,A/R OPERATED Zone –01,Dist-77.11KM DP MAIN-02,Event-AGT,A/R operted Zone –01,Dist-70.57KM At TTPS end:Zone-1 ,Tripped phase-AN Dist-110.2KM
| Telkoi | 06.09.25 | 17:19 | 17:19 | 0:00 | 220kV Telkoi-Joda Feeder | 220kV Telkoi-Joda Tripped from both ends and AR sucessful from both ends. Relay details at Telkoi end. DP Main-1 (i) Started phase AN, Trip phase A (ii) Zone-1 , AR successful (iii) Dist =46.69 KM ,(iv) Ia= 1.302 KA , Ib=68.23 A , Ic=221.8 A (v) Van=43.19 KV, Vbn=148.9 KV, Vcn=148.5 KV DP Main -2 (i) Fault type AG , (ii) Zone-1 ,(iii) Dist =46.8 KM ,(v) Ia= 1.171 KA , Ib= 94.437 A , Ic=204.769 A, In= 1.005 KA (vi) Van=37.571 KV, Vbn=149.070 KV, Vcn=144.230 KV
480 | Jayanagar | 06.09.25 | 01:27 | 02:08 | 0:41 | 220kV Balimela PH-Govinpalli-Jayanagar Feeder | Dist,Zone-2,B phase to Ground ,Ib=1.67KA,Dist-112.3Km | - | - | - | - | - | - | -
481 | Jayanagar | 06.09.25 | 12:33 | 13:52 | 1:19 | 132kV Jayanagar-Jeypore RTSS Feeder | Y-B-G,Z-1,y-4.2KA,Ib-4.2KA,Dist-19Km, | Jeypore RTSS | 1:19 | - | - | 0.014676 | - | -
482 | Kantabanji | 07.09.25 | 6:07 | 6:09 | 0:02 | 132kV Kanatabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 400 A | Kantabanji RTSS | 0:02 | - | - | 0.00011691 | - | -
483 | Nuapatana | 07.09.25 | 11:21 | 13:34 | 2:13 | 132kV Nuapatna-Arati Feeder | At Nuapatna end:Y and B-phase O/C Zone-1 ,Dist-40.55 KM ,Iy-1.52 kA Ib-1.603 kA At Arati end: R and Y-ph O/C ,Dist-25.63 KM , Ir-2.246 kA Iy-2.126 kAH/T | - | - | - | - | - | - | -
484 | Narendrapur | 07.09.25 | 11:59 | 11:59 | 0:00 | 220kV Narendrapur-Gunupur Feeder | At Narendrapur end: A/R operated, R-N, Dist- 72.53km, Ir- 0.853kA At Gunupur end: A/R Operated, R-N, Zone 1, Dist- 97.7km, Ir- 0.823kA | - | - | - | - | - | - | -
485 | Kesinga | 07.09.25 | 12:26 | 12:53 | 0:27 | 132kV Kesinga-Junagarh Feeder | At Kesinga end: Dist protection relay operated,Dist-33.7 KM,R-249 A,Y-2.11 KA,B-170.7 A At Junagarh end: DP relay operated: Zone 1, Fault Dist=18.8km, Y ph E/F. Current not shown. | - | - | - | - | - | - | -
486 | Kuchinda | 07.09.25 | 18:40 | 19:30 | 0:50 | 132kV Kuchinda-SMC Feeder | R-N,E/F, 2) Zone -01, 3) Dist : 12.83 KM, 4) IR=1.047 KA | - | - | - | - | - | Lightning and rain fall | -
487 | Kesinga | 08.09.25 | 10:36 | 13:09 | 2:33 | 160 MVA Auto TRF-II | OSR operated. | - | - | - | - | - | - | -
488 | Kesinga | 08.09.25 | 19:16 | 19:30 | 0:14 | 132kV Kesinga-Khariar Line | Dist protection relay operated,Dist-51.62 KM,R-1.6 KA,B-199A,B-320A. | Khariar, kantabanji, Kantabanji RTSS | 0:14 | - | - | 0.0092877 | - | -
489 | Kantabanji | 09.09.25 | 0:55 | 1:14 | 0:19 | 132kV Khariar Kantabanji Feeder | TRIPPED FROM Kesinga end | Khariar, kantabanji, Kantabanji RTSS | 0:19 | - | - | 0.012605 | - | -
490 | Lapanga | 09.09.25 | 9:13 | 16:45 | 7:32 | 132kV Lapanga-Burla PH CKT-II | AT Lapanga end:DP RELAY,Zone-1, L1-L2 DIST-5.5KM, | - | - | - | - | - | - | -
491 | Katapali | 09.09.25 | 9:14 | 9:15 | 0:01 | 100MVA Auto TRF-II | 132kV side Back up relay-tripped with O/C ,Ir=0.78KA , Iy=0.82KA, Ib=0.78KA, | - | - | - | - | - | - | -
492 | Rayagada | 09.09.25 | 16:11 | 16:22 | 0:11 | 132kV Rayagada-Podagada Feeder | Incomer Rayagada -podagada Feeder supply failure | Podagada, Rayagada, Rayagada RTSS | 0:13 | - | - | 0.0052076 | supply failed at MKD generation end.. | -
|  |  |  | 16:30 | 0:19 | 132kV Rayagada-Akhusingh Feeder
493 | Jayanagar | 09.09.25 | 19:51 | 21:36 | 1:45 | 220kV Jayanagar-Balimela PH CKT-I | Y-G,Z-1, Iy-3.136,Dist-44.54KM | Balimela, Malkangiri, Kalimela | 1:50 | - | - | 0.038639 | - | -
|  |  |  | 21:29 | 1:38 | 220kV Balimela PH-Balimela-Jayanagar CKT-II | R-Y-G,Ir-5.329KA,Iy-5.506KA,40.81KM
|  |  |  | 20:06 | 0:15 | (206) OHPC Balimela-Govindpalli CKT-III (LILO at GSS,Govindpalli) | Ir- 0.89kA, Iy- 0.9A, Ib- 0.88kA
|  |  |  | 10.09.25 08:15 | 12:24 | 220kV Malkangiri-Balimela Feeder | Incomer failure from Power House Balimela
|  |  |  | 21:41 | 1:50 | 220kV Balimela-Kalimela CKT-II | DUE TO SUPPLY FAIL
|  |  |  | 21:41 | 1:50 | 220kV Malkangiri-Kalimela Feeder | DUE TO SUPPLY FAIL
494 | Anandpur | 09.09.25 | 19:56 | 20:22 | 0:26 | 132kV Jajpur Road-Anandapur CKT-I & CKT-II | Power supply failed from Duburi and Jajpur Road end due overloading and under frequency issue. | Anandpur | 0:26 | - | - | 0.0037402 | - | -
495 | Somnathpur | 09.09.25 | 20:02 | 20:19 | 0:17 | 132kV Somnathpur-Imami Feeder | Source Fail | Somnathpur, Imami, Stork | 0:17 | - | - | 0.0083441 | - | -
132kV FAP Tata steel
12.5MVA TRF-I, II
496 | Soro | 09.09.25 | 20:09 | 11.09.25 14:55 | 42:46 | 132kV Soro-Bhadrak Feeder | Soro Grid end Relay Details: Master trip relay , Dist protection relay: Zone -I, Dist -1.37km, Event-A G T, Ia-191A, Ib - 277A, Ic - 475A , IG - 636A , Group- 1, shot -0. Bhadrak Grid end Realay Details: 1st event- started phase -A N , Zone - 1 , Fault Duration - 61.65 ms, Ia - 5.55KA , Ib - 286.4A , Ic - 503.5A , Van - 30.72KV, Vbn - 72.20KV, Vcn - 70.02KV, Fault resistance -611.6Mohm 2nd event- started phase -A N, Active Group-1, tripped Phase -ABC, SOTF Trip, A/R look out, Fault dutation- 79.49ms, Ia - 5.87KA , Ib - 10.8KA , Ic - 9.376KA , Van - 29.6KV, Vbn - 74.12KV, Vcn - 72.17KV, Fault resistance -215.6.6Mohm | Soro | 00:09 | - | - | 0.0060427 | 132kV Soro-Bhadrak line conductor snapped at Loc No - 30 & 31. Before the Incident the Chandipur GSS was P/S availed from Soro grid end. Soro Grid was getting P/S from Bhadrak Grid through 132kV Soro-Bhadrak Line . 132kV Soro-Bhadrak Line Tripped at 20:09 Hr at Bhadrak Grid only Soro Grid end Breaker charged through Auto Recloser At-20:09 Hr Dated 9/09/2025. Soro Grid power availed from Chanipur grid end at 20:24 Hr. Soro Grid black out from 20:09 Hr dated 09/09/2025 to 20:24 Hr dated 09/09/2025. 132kV Soro-Bhadrak line L/C taken 22:10Hrs 09/09/2025 & 132kV Soro-Bhadrak line charged at Bhadrak grid end 14:55 Hrs at 11/09/2025. Soro grid availed Power supply both Bhadrak & Chandipur Grid . | -
497 | Khariar | 10.09.25 | 0:54 | 1:13 | 0:19 | 132kV Kesinga-Khariar Feeder | Tripped from Kesinga | Khariar, Kantabanji, Kantabanji RTSS | 0:19 | - | - | 0.012605 | - | -
498 | Balasore | 10.09.25 | 9:23 | 9:29 | 0:06 | 132kV Balasore-Balasore RTSS Feeder | Fault report: O/C,R-ph ,B-ph OPTD fault current:Ir=303A,Iy=302A. | Balasore RTSS | 0:12 | - | - | 0.0016759 | - | -
|  |  | 9:32 | 9:38 | 0:06 |  | Fault report: O/C,R-ph ,B-ph OPTD fault current:Ir=327A,Iy=326A.
499 | Barbil | 10.09.25 | 9:50 | 9:51 | 0:01 | 132kV Barbil-ARYA Feeder | 132kV ARYA Feeder Side Incoming Failure and avail from Nalda(Rourkela) end. | - | - | - | - | - | - | -
500 | Bhanjanagar | 10.09.25 | 11:57 | 12:05 | 0:08 | 220kV Bhanjanagar-Therubali CKT-II | A/R Close, CN, Zone-1, D= 118.4Km, IC= 999.1A | - | - | - | - | - | - | -
501 | Mendhasal | 10.09.25 | 12:53 | 18:15 | 5:22 | 220kV Mendhasal-Nayagarh Feeder | At Mendhasal end: Ib-3.37kA, Dist- 10.2km, Zone 1 At Nayagarh end: Ib- 1.451kA, Dist- 45.8km | - | - | - | - | - | Fault tripping(AR unsuccessful at both end) | -
502 | Narendrapur | 10.09.25 | 13:03 | 16:06 | 3:03 | 220kV Narendrapur-Atri CKT-II | At Atri end: R-Y, Zone 1, Ir- 4.903kA, Iy- 4.866kA, Dist- 33.97km At Narendrapur end: R-Y, Zone 1, Ir- 1.532kA, Iy- 1.557kA, Dist- 106.5km | - | - | - | - | - | - | -
503 | Barbil | 10.09.25 | 13:55 | 13:56 | 0:01 | 132kV Nalda Feeder | 132kV Nalda Feeder Side Incoming Failure and avail from Arya(Joda) end. | - | - | - | - | - | - | -
504 | Kalunga | 10.09.25 | 15:28 | 17:52 | 2:24 | 132kV Budhipadar-Kalunga Feeder | At Budhipadar end: R-Y-N, Zone-1, Dist-69.09 km, Ir-2.382 KA,Iy-1.760 KA,Ib-206.2 A At kalunga end: -R-Y-N, Zone-1, Dist-39.33 km, Ir-2.667 KA, Iy- 2.305 KA, Ib- 201.6A | - | - | - | - | - | E/F | -
505 | Jayanagar | 10.09.25 | 16:58 | 17:15 | 0:17 | 132kV Jayanagar-Meenakshi Feeder | B-G,Z-1,Ib=2.6KA,Dist-34KM | Megalift | 0:23 | - | - | 2.4278e-07 | - | -
506 | Kesinga | 11.09.25 | 0:54 | 1:14 | 0:20 | 132kV Kesinga-Khariar Line | Dist protection relay operated,Dist-45.57 KM,Zone-2,Y-1.926 A | Khariar, Kantabanji, Kantabanji RTSS | 0:20 | - | - | 0.013268 | - | -
507 | Pratapsasan | 11.09.25 | 2:40 | 4:33 | 1:53 | 220kV Pratapsasan-Pandiabil CKT-II | 220kV Main Bus Y-Ph Bus PT Burst | - | - | - | - | - | - | -
|  |  |  | 4:10 | 1:30 | 160MVA Auto TRF-II
|  |  |  | 4:35 | 1:55 | 220kV Pratapsasan-Cuttack CKT-II
508 | Duburi | 11.09.25 | 4:17 | 14:50 | 10:33 | 132kV Duburi - BRPL Feeder | Tripped on DP relay. | - | - | - | - | - | Insulator puncture and conductor snap at Loc. No. 14. | -
509 | Bolangir New | 11.09.25 | 7:12 | 9:31 | 2:19 | 33KV Aftab Solar | Tripped On operation of Backup O/C & E/F Relay. | Aftab Solar | 2:19 | - | - | 0.0020775 | - | -
510 | Mendhasal | 11.09.25 | 11:25 | 15:39 | 4:14 | 220kV Mendhasal-Chandaka Feeder | At Mendhasal end: Mainn-1= Ir-0.03KA,Iy-6.41KA,Ib-5.73KA,D-14.9KM,Zone-1 At Chandaka end: YBN trip,Ib-2.3KA, dist-2.3KM. | - | - | - | - | - | - | -
511 | Infocity-II GIS | 11.09.25 | 11:40 | 12:00 | 0:20 | 220kV Mendhasal-Infocity-II Feeder | Y-B ph directional O/C | - | - | - | - | - | - | -
512 | Gunupur | 11.09.25 | 11:45 | 18:33 | 6:48 | 220kV Narendrapur-Gunupur Feeder | Zone-1,R-Ph,Dist-102.7KM | - | - | - | - | - | - | -
513 | Lapanga | 11.09.25 | 11:49 | 15:04 | 3:15 | 220kV Lapanga- Budhipadar CKT-II | AT Lapanga end: Y-N, Zone 1, Dist- 0.6km, iy- 23.53kA | - | - | - | - | - | Jumper snappes at LOC 50/4 | -
|  |  |  | 12.09.25 08:11 | 20:22 | 220kV Lapanga- Budhipadar CKT-I | AT Lapanga end: Y-N, Zone 1, Dist- 10.3km, iy- 16.16kA
|  |  |  | 12:40 | 0:51 | 220kV Budhipadar-BPSL-I
514 | Therubali | 11.09.25 | 12:39 | 17:29 | 4:50 | 220kV Therubali-Aska New Feeder | At Therubali end: RYB, Ir=1.66KA, Iy=1.032KA, Ib=1.752KA At Aska New end: B-N, Z-2, 100.3KM, Ib=721.7A | - | - | - | - | - | - | -
|  |  | 12:42 | 17:21 | 4:39 | 220kV Therubali-Indravati CKT-II | At Therubali end: YG, Z-4, 22.05KM, Iy=1.198KA At Indravati end: YG, Z-2, 72.42KM, Iy=670.6A
515 | Budhipadar | 11.09.25 | 13:42 | 13:42 | 0:00 | 220kV Budhipadar-Raigarh Feeder | C-N, Fault Dist-57.87km,IL1-30.71A, IL2-32.65A, IL3-2.608KA | - | - | - | - | - | - | -
516 | Budhipadar | 11.09.25 | 18:15 | 19:05 | 0:50 | 132kV Budhipadar-MCL Feeder | D/P -I (ALSTOM micom p444):Zone 2, Fault loop- A-N, Fault Dist-17.28km,IL1-5.11KA, IL2-76.36A, IL3-1.817KA, Fault resistance-1.336ohm. | MCL | 0:50 | - | - | 0.017441 | - | -
517 | Brajarajnagar | 11.09.25 | 18:15 | 18:15 | 0:00 | 132kV Brajrajnagar - Jorabaga MCL Feeder | DP operated : Dist - 11.3 km, trip time - 66 ms, Ia - 3.99 kA,R ph, Zone 1 Autoreclosure successful | - | - | - | - | - | Heavy Lightening & Rain | -
518 | Kalunga | 11.09.25 | 18:22 | 18:22 | 0:00 | 132kV Budhipadar-Kalunga Feeder | tripped at kalunga end D.P.RELAY- Micom p444- tripped ph-R-N, Zone-1, Fault duration- 53.38 ms, Relay trip time- 80.07 ms, Dist- 62.02 km, Ir-1.281 kA, Iy- 22.52 A, Ib- 22.05 A, Fault resistance- 13.04 ohm | - | - | - | - | - | - | -
519 | Joda | 11.09.25 | 19:06 | 12.09.25 00:35 | 5:29 | 220kV Joda -Ramchandrapur Feeder | At Joda end: R-Y-B, Zone 2, Dist- 125.9km, Ir- 1.443kA, Iy- 1.679kA, Ib- 0.268kA At Ramchandrapur end: Zone 1, R-Y-B, Dist- 1.5km, Ir- 1.5kA, Iy- 1.69kA, Ib- 1.77kA | - | - | - | - | - | ICT -02 CT BURST AT RAMACHNDRAPUR GRID SS end | -
520 | Polasponga | 11.09.25 | 22:58 | 22:58 | 0:00 | 132kV Polasponga-Turumunga Feeder | Polasponga end-DP relay: AG T,Zone-1,Ia-2194A,Ib-38A,Ic-266A,In-0,Ig-2464A,3I2-2083A,Dist-11.81km Turumunga end - DP relay,AR successful,Zone-1 ,AR OPTD,AR successful,R-phase pick up,R-phase OPTD,Dist-89.52km,Ia-1.049KA,Ib-31.62A,Ic-270.5A | - | - | - | - | - | AR operated successfully at both end | -
521 | Polasponga | 12.09.25 | 4:59 | 4:59 | 0:00 | 132kV Polasponga-Turumunga Feeder | Polasponga end-DP relay: AG T,Zone-1,Ia-2341A,Ib-69A,Ic-228A,In-0,Ig-2591A,3I2-2256A,Dist-11.90km Turumunga end - DP relay,AR successful,Zone-1 ,AR OPTD,AR successful,R-phase pick up,R-phase OPTD,Dist-88.76km,Ia-1.054KA,Ib-59.56A,Ic-239.1A | - | - | - | - | - | AR operated successfully at both end | -
522 | Lapanga | 12.09.25 | 13:10 | 14:58 | 1:48 | 132kV Lapanga- Burla PH CKT-II | Zone-1, L3-E,DIST-18.6KM,IL3=5.82KA, | - | - | - | - | - | - | -
523 | Kuchinda | 12.09.25 | 15:55 | 16:06 | 0:11 | 132kV Kuchinda-SMC Feeder | Local end :-1)Fault Loop - R-N,E/F, 2) Zone -01, 3) Dist : 20.70 KM, 4) IR=1.518 KA, Iy=84.78 A, IB=13.99 A, 5)Fault duration = 56.72 ms 6) Fault Resistance= 3.319 ohm | - | - | - | - | - | Lightning and rain fall. Tripped Kuchinda end only. | -
524 | Sambalpur | 12.09.25 | 13:31 | 15:39 | 2:08 | 132kV Burla PH-Sambalpur Feeder | At Sambalpur end: Tripped on R ph E/F,Z1,DP operated with Fault Dist:3.84 KM. Ia= 1710 A, Ib=443 A,Ic=431 A At Burla end: Z2,Fault Dist: 17KM,R-ph E/F,I=10.78 KA | - | - | - | - | - | Heavy rain & lightening observed | -
525 | Sambalpur | 12.09.25 | 13:31 | 15:43 | 2:12 | 132kV Sambalpur-Shyam DRI Feeder | At Sambalpur end: Tripped on R ph E/F,DP operated with Fault Dist: 5.47 KM. Ia=1868 A, Ib=634 A,Ic=351 A At Shyam DRIend: Ia=2.67 KA,Ib=0.01 A,Ic=0.01 A | - | - | - | - | - | Heavy rain & lightening observed | -
526 | Polasponga | 13.09.25 | 9:07 | 9:10 | 0:03 | 132kV Polasponga-Kendujhargarh RTSS Feeder | Back up relay,O/C, IA=298.3A, IB=210.4A, IC=102.4A, Inm=7.296A, Ind=7.828A | Kendujhargarh RTSS | 0:03 | - | - | 0.00041611 | OVER CURRENT | -
527 | Mendhasal | 13.09.25 | 10:58 | 11:21 | 0:23 | 220kV Mendhasal-Nayagarh Feeder | Mainn-1= Ir-0.07KA,Iy-0.26KA,Ib-2.31KA,D-57.2KM,Zone-2 Tripped Main-2= Ir-0.07KA,Iy-0.27KA,Ib-2.34KA,D-57.2KM,Zone-2 Tripped | - | - | - | - | - | AR succesful at Nayagarh end. | -
528 | Therubali | 13.09.25 | 12:16 | 15:37 | 3:21 | 220kV Therubali-Indravati CKT-III | At Therubali end: RY, Z-1, 30KM, Ir=4.1KA, Iy=4.18KA At Indravati end: RY, Z-1, 51.83KM, Ir=2.22KA, Iy=2.16KA | - | - | - | - | - | - | -
529 | Budhipadar | 13.09.25 | 12:24 | 13:04 | 0:40 | 132kV Budhipadar-Sundargar CKT-II | B/U relay(Siemens):-IL1-0.21KA, IL2-0.04KA, IL3-0.05KA, LED indication-Relay trip, R-ph, E/F | - | - | - | - | - | - | -
530 | Chainpal | 13.09.25 | 12:39 | 13:58 | 1:19 | 132kV Chainpal-Meramundali CKT-I | Fedder tripped on O/C B phase & E/F Ib:9.2 KA,IN:10.1 Kamp ,in Zone 1 with fault Dist 1.44 Km , | - | - | - | - | - | - | -
531 | Joda | 13.09.25 | 17:07 | 18:30 | 1:23 | 220kV Joda -Ramchandrapur Feeder | NO Indication at Joda end AtRamchandrapur end: 96 Operated | - | - | - | - | - | - | -
532 | Budhipadar | 13.09.25 | 17:39 | 17:39 | 0:00 | 132kV Budhipadar-Lakhanpur | D/P -(AREVA Micom P441) :-Zone 1, Fault loop- A-N, Fault Dist-13.35km,IL1-7.895KA, IL2-339.8A, IL3-372A, Fault duration-60ms. A/R-successful at both end. | - | - | - | - | - | - | -
533 | Balasore | 14.09.25 | 7:08 | 7:12 | 0:04 | 132kV Balasore-Balasore RTSS Feeder | Fault report: O/C,R-ph ,B-ph OPTD fault current:Ir=300A,Iy=298A. | Balasore RTSS | 0:04 | - | - | 0.00055864 | - | -
534 | Tarkera | 14.09.25 | 9:53 | 22:29 | 12:36 | 220kV Tarkera-Bamra Feeder | R-PH INSULATOR SNAPPED AT LOC. 177 | - | - | - | - | - | - | -
535 | Kesinga | 14.09.25 | 10:45 | 10:59 | 0:14 | 132kV Kesinga-Khariar Line | Dist protection relay operated,Zone-2,Dist-36.6 KM,R-154 A,Y-421 A,B-2.07KA | Khariar, Kantabanji, Kantabanji RTSS | 0:14 | - | - | 0.0092877 | - | -
536 | Kesinga | 14.09.25 | 12:10 | 12:24 | 0:14 | 132kV Kesinga-Khariar Line | Dist protection relay operated,Zone-2,Dist-39.34 KM,R-2.06 KA,Y-1.939 KA A,B-104 A | Khariar, Kantabanji, Kantabanji RTSS | 0:14 | - | - | 0.0092877 | - | -
537 | Therubali | 14.09.25 | 23:05 | 23:19 | 0:14 | 220kV Therubali-U.Kolab CKT | At Therubali end: AR Success, BG, Z-1, 90.30KM, Ib=1.72KA At Kolab end: BG, Z-1, 39.73KM, Ib=3.565KA | - | - | - | - | - | - | -
538 | Barbil | 15.09.25 | 7:55 | 7:56 | 0:01 | 132kV Barbil-Arya Feeder | 132kV ARYA Feeder Side Incoming Failure and avail from Nalda(Rourkela) end. | - | - | - | - | - | 132kV I/C supply Avails to ARYA(Joda) side. Due to132kV Bus Rectification Work For Red Hot Condition on 132kV Main Bus T-Clamp (R Phase ata Joda Grid s/s end) At Joda Grid end | -
539 | Barbil | 15.09.25 | 11:45 | 11:46 | 0:01 | 132kV Nalda Feeder | 132kV Nalda Feeder Side Incoming Failure and avail from Arya(Joda) end. | - | - | - | - | - | 132kV I/C supply Avails to ARYA(Joda) side. Due to132kV Bus Rectification Work For Red Hot Condition on 132kV Main Bus T-Clamp (R Phase ata Joda Grid s/s end) At Joda Grid end | -
540 | Basta | 15.09.25 | 12:00 | 14:37 | 2:37 | 132kV Basta-Jaleswar Feeder | At Basta end: Ib- 1.64kA At Jaleswar end: Dist-7.99km, Zone 1, Ib- 1.16kA | - | - | - | - | - | - | -
541 | Kantabanji | 15.09.25 | 12:18 | 12:20 | 0:02 | 132kV Kanatabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 300A | Kantabanji RTSS | 0:02 | - | - | 0.00011691 | - | -
542 | Khajuriakata | 15.09.25 | 12:19 | 12:38 | 0:19 | 132kV Khajuriakata- Dhenkanal- Nuapatana T Line | Z-1,Yph-Bph,O/C ,Iy-2.6kA,Ib-2.3kA,Dist-23.5km | - | - | - | - | - | - | -
543 | Khuntuni GIS | 15.09.25 | 12:19 | 12:38 | 0:19 | 132kV Dhenkanal-Khuntuni Feeder | At Khuntuni end- Zone-3, R-Ph & B-Ph Ir=1866.71A, Iy=356.33A, Ib=1559.97A At Khajuriakata end- Zone- 1.2&3, O/C, Y-Ph & B-Ph fault, fault Dist- 23.5KM, Iy=2.6KA, Ib=2.3KA. | Khuntuni GIS | 0:19 | - | - | 0.0042604 | - | -
544 | Khuntuni GIS | 15.09.25 | 13:08 | 13:18 | 0:10 | 132kV Dhenkanal-Khuntuni Feeder | At Khuntuni end- E/F Optd, 86A & 86B Optd, fault Current Ir=21.58A, Iy=1304.95A, Ib=22.82A. | - | - | - | - | - | - | -
545 | Kantabanji | 15.09.25 | 19:02 | 19:05 | 0:03 | 132kV Kanatabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 350A | Kantabanji RTSS | 0:03 | - | - | 0.00017536 | - | -
546 | Gondia | 15.09.25 | 21:54 | 22:21 | 0:27 | 132kV Gondia-JFAL Feeder | Tripped at Both end. | - | - | - | - | - | - | -
547 | Gondia | 16.09.25 | 4:57 | 5:27 | 0:30 | 132kV Gondia-OPCL Feeder | Tripped at Both end. | - | - | - | - | - | - | -
548 | Duburi-New | 16.09.25 | 9:41 | 9:50 | 0:09 | 220kV Duburi New-Dhamra Feeder | At Duburi New end: E/F (B-N), Dist- 24km, Zone 1, Ib- 4.71kA At Dhamra end: B-N, Dist- 87.1km, Zone 1, Ib- 1.242kA | - | - | - | - | - | - | -
549 | Khajuriakata | 16.09.25 | 11:34 | 11:49 | 0:15 | 132kV Khajuriakata-Dhenkanal-Nuapatna Feeder | Yph-E/F,Iy-1.4kA,B/U optd | - | - | - | - | - | - | -
[6 empty] | 132kV Dhenkanal-Khuntuni Feeder | At Khuntuni end- E/F Optd, 86A & 86B Optd, fault Current Ir=73.38A, Iy=74.89A, Ib=1004.05A At Khajuriakatal end- E/F Optd, Y-Ph Fault, Fault Current Iy=1.4KA.
550 | G. UDAYAGIRI | 16.09.25 | 14:55 | 17:20 | 2:25 | 132kV Bhanjanagar-G. UDAYAGIRI Feeder | Zone-1, D-40.67KM, Ia-3.182KA, Ib-3.285KA & Ic-3.445KA | G. UDAYAGIRI, Phulbani | 2:25 | - | - | 0.046844 | - | -
[6 empty] | 132kV G.Udayagiri - Phulbani SC Line | Incomer Power Supply Failure From Bhanjanagar GSS
551 | Duburi-New | 17.09.25 | 16:36 | 16:36 | 0:00 | 400kV Duburi New-Meramundali Feeder | At Duburi New end: B-N, Zone 1, Ib- 11.47kA At Meramundali end: B-N, Zone 1, Ib- 3.37kA, A/R successful | - | - | - | - | - | - | -
552 | Kantabanji | 18.09.25 | 5:24 | 5:31 | 0:07 | 132kV Kanatabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 600A | Kantabanji RTSS | 0:07 | - | - | 0.00040918 | - | -
553 | Balasore | 19.09.25 | 10:33 | 17:11 | 6:38 | 132kV Balasore-Basta Feeder | At Balasore end: B-N, Zone 1, Dist- 24.75km, Ib- 2.585kA At Basta end: B-N, Zone 1, Dist- 8.045km, Ib- 1.424kA | - | - | - | - | - | Touching of tree | -
554 | Kantabanji | 19.09.25 | 10:34 | 10:36 | 0:02 | 132kV Kanatabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 534A | Kantabanji RTSS | 0:02 | - | - | 0.00011691 | - | -
555 | Telkoi | 19.09.25 | 10:36 | 10:57 | 0:21 | 220kV Telkoi-TTPS Feeder | 220kV Telkoi-TTPS Tripped from both ends and AR sucessful from Telkoi end only. Relay details at Telkoi end. DP Main-1 (i) Started phase CN, Trip phase C (ii) Zone-1 , AR successful (iii) Dist =56.97 KM ,(iv) Ia= 69.14 A , Ib=96.32 A , Ic=889.4 A (v) Van=140.4 KV, Vbn=133.4 KV, Vcn=68.51 KV DP Main -2 (i) Fault type CG , (ii) Zone-1 ,(iii) Dist =53.6 KM ,(v) Ia= 25.131 A , Ib= 26.294 A , Ic=883.974 A, In= 902.84 A (vi) Van=137.227 KV, Vbn=127.666 KV, Vcn=41.828 KV at TTPS end DP Main-1 (i) Started phase CN, Trip phase ABC (ii) Zone-1 (iii) Dist =27.6 KM ,(iv) Ia= 79.19 A , Ib=112.6 A , Ic=4.923 KA (v) Van=131.1 KV, Vbn=123.5 KV, Vcn=117.3 KV | - | - | - | - | - | E/F | -
556 | Tarkera | 19.09.25 | 10:38 | 11:38 | 1:00 | 220kV Tarkera-PGCIL CKT-II | TRIPPED AT PGCIL end ONLY | - | - | - | - | - | Auto RECLOSE SUCCESSFUL AT Tarkera end | -
557 | Goda | 19.09.25 | 11:44 | 13:04 | 1:20 | 160MVA Auto TRF-II | Ir-919.6A,Iy-361.7A,Ib-423A | - | - | - | - | - | - | -
558 | Gondia | 19.09.25 | 12:10 | 12:26 | 0:16 | 132kV Gondia-OPCL Feeder | Tripped at Both end. | - | - | - | - | - | - | -
559 | Purushottampur | 19.09.25 | 12:47 | 18:13 | 5:26 | 132kV Aska (Old)-Purushottampur Feeder | A/R block, A/R Lockout, in R-Y ph, Zone-1, L1-L2 loop, IL1=2.99 ka, IL2=3.08 ka, IL3=0.17 ka, Dist-4.9 km | - | - | - | - | - | 132kV Power supply availed through Chatrapur-Purushottampur Feeder | -
560 | Joda | 19.09.25 | 13:54 | 20.09.25 01:40 | 11:46 | 220kV Joda-TTPS CKT-II | At Joda end: R-B-N, Zone 1, Dist- 58.38km, Ir- 2.931kA, Ib- 1.688kA At TTPS end: Zone-1, R-N, Dist- 96.49km, Ir-2.79kA | - | - | - | - | - | LOC NO -308 R -PH SUSPENSION INSULATOR STRING PUNCTURED | -
561 | Joda | 19.09.25 | 14:08 | 14:08 | 0:00 | 220kV Joda-Telkoi Feeder | At Joda end: B-N, Zone 1, Dist- 42.58km, Ib- 1.631kA At Telkoi end: B-N, Zone 1, Dist-31.58km, Ib- 1.712kA | - | - | - | - | - | - | -
562 | Jayanagar | 19.09.25 | 17:53 | 17:53 | 0:00 | 220kV Jayanagar-Laxmipur CKT-II | R-G,Z1,DIST-9.258Km,Ir-9.527KA | - | - | - | - | - | - | -
563 | Jayanagar | 19.09.25 | 18:01 | 18:32 | 0:31 | 132kV Jayanagar-Damanjodi Feeder | Dist : 6.7 KM, Y Ph : 7.0 KA, B Ph : 5.68 KA | - | - | - | - | - | - | -
564 | Jayanagar | 19.09.25 | 17:46 | 17:59 | 0:13 | 132kV Jayanagar-Jeypore RTSS Feeder | R-B-G,Z-1,72.82KM,Ir=1.943KA,Ib=1.848KA | Jeypore RTSS | 0:13 | - | - | 0.002415 | - | -
565 | Jayanagar | 19.09.25 | 18:01 | 18:32 | 0:31 | 132kV Jayanagar-Damanjodi Feeder | R-Y-G,Z-1,6.7KM,Ir-6.8KA,Iy-7.0KA | - | - | - | - | - | - | -
566 | Balasore | 20.09.25 | 10:34 | 10:34 | 0:00 | 132kV Balasore-Chandipur Feeder | At Balasore end: Y-N, Zone 1, Dist- 5.79km, Iy- 8.728kA At Chandipur end: Y-N, Zone 1, Iy- 0.998kA | - | - | - | - | - | A/R operated sucessfully | -
567 | Budhipadar | 20.09.25 | 10:39 | 11:38 | 0:59 | 220kV Budhipadar-IB CKT-III | D/P -( Micom P444) :-Zone 1, Fault loop- C-N, Fault Dist-1.776km,IL1-590A, IL2-183A, IL3-20.31KA, Fault duration-83.29ms. A/R-Un-successful | - | - | - | - | - | - | -
568 | Khuntuni GIS | 20.09.25 | 10:39 | 11:48 | 1:09 | 132kV Dhenkanal-Khuntuni Feeder | At Khuntuni end- E/F Optd, R-Ph Fault with 86A & 86B optd, Fault Current Ir=1018.14A, Iy=20.20A, Ib=20.04A At Khajuriakatal end- E/F Optd, B-Ph Fault, Zone-1, Fault Dist- 6.60 KM, Fault Current Ib=2.4KA. | - | - | - | - | - | 132kV Khuntuni-ICCL Feeder was in service. | -
569 | Goda | 20.09.25 | 11:44 | 13:52 | 2:08 | 220kV Meramundali B-Goda Feeder | At Meramundali B end: Tripped on DP in R-phase, Ir-6.26KA,Iy-176.8A,Ib-609.1A,Dist-795.8M,Zone-1,A/R Blocked. At Goda end: Tripped on DP in E/F, Ir-2.34KA,Dist-68.1kM,Zone-2. | Goda Kalarangi Kamakhyanagar, Kamakhyanagar RTSS Gondia, JFAL | 00:59 00:17 00:20 00:26 | - | - | 0.014112 | Weather condition : Heavey rain & lightning | -
|  |  |  | 12:43 | 0:59 | 220kV Duburi New- Goda Feeder | Tripped on DP relay.
|  |  | 12:27 | 12:44 | 0:17 | 132kV Kalarangi-Duburi Old Feeder | At Kalarangi end: Y-N, Zone 1, Dist- 27.7km, Iy- 0.636kA At Duburi Old end: Zone 1, Y-N, Dist- 12.47km, Iy- 3.943kA
|  |  |  | 12:44 | 0:17 | 132kV Goda-Kalarangi Feeder | Source faillure
|  |  |  | 12:58 | 0:31 | 132kV Gondia-OPCL Feeder
|  |  |  | 12:53 | 0:26 | 132kV Gondia-JFAL Feeder
|  |  |  | 12:47 | 0:20 | 132kV Kamakhyanagar-Goda Feeder
|  |  |  | 12:52 | 0:25 | 132kV Kamakhyanagar-OPCL Feeder
570 | Kalunga | 20.09.25 | 11:47 | 12:08 | 0:21 | 132kV Budhipadar-Kalunga Feeder | tripped from Budhipadar end only | Kalunga | 0:21 | - | - | 0.016561 | - | -
571 | Nuapatana | 20.09.25 | 12:03 | 12:22 | 0:19 | 132kV Nuapatna-Arati Feeder | At Nuapatna end: O/C (Y-B), Zone 1, Dist- 53.1km, Iy-1.28 kA Ib-1.41 kA At Arati end: O/C (R-Y), Dist-12 km, Ir-2.750 kA Iy-2.6 kA | - | - | - | - | - | - | -
572 | Bhadrak | 20.09.25 | 12:08 | 12:08 | 0:00 | 132kV Bhadrak-Soro Feeder | At Bhadrak Grid end: A/R Successful, Y-N, Zone-1, Dist.-1.943 km, Iy- 7.832 kA At Soro end: A/R Successful, Dist.-37.18 KM, Iy- 0.912 kA | - | - | - | - | - | - | -
573 | Puri | 20.09.25 | 13:00 | 15:39 | 2:39 | 132kV Puri-Nimapara Feeder | Tripped(Zone-2,Ia=1.99KA,Ib=19.01A,Ic=78:35A) | - | - | - | - | - | - | -
574 | Budhipadar | 20.09.25 | 14:27 | 21.09.25 13:46 | 23:19 | 132kV Budhipadar-Lakhanpur Feeder | R ph conductor snapped from gantry CVT T clamp to 1st tower at Budhipadar end. Zone 1, R-N, Dist-13.58km, Ir- 7.756kA | - | - | - | - | - | 132kV Brajrajnagar-Lakhanpur Feeder was in service during fault. | -
575 | Bhanjanagar | 20.09.25 | 14:39 | 17:49 | 3:10 | 220kV Bhanjanagar-Meramundali Feeder | BC, Zone-1, D= 23.58 Km, IB=4.57 KA,IC= 4.82 KA | - | - | - | - | - | - | -
576 | Podagada | 20.09.25 | 14:40 | 14:53 | 0:13 | 132kV Podagada-Rayagada Feeder | Tripped on Zone-1 trip, Y-Ph fault, IL1-0.14kA, IL2- 1.00kA, IL3- 0.01kA, Dist- 49.7KM | - | - | - | - | - | - | -
577 | Paradeep | 20.09.25 | 14:47 | 15:05 | 0:18 | 132kV Paradeep-Tirtol Feeder | Tripped on O/C on B-Ph, Zone-III, Dist-60.3 KM Ir=0 kA, Iy=0 kA Ib=3.5 kA | Tirtol | 0:18 | - | - | 0.0056423 | TRANSIENT FAULT | -
|  |  |  | 15:27 | 0:40 | 132kV Jagatsinghpur-Tirtol Feeder | 132kV P/S on 132kV Jspur-Titol line (which was in idle charged condition from Tirtol end) was failed due 132kV source failure at Tirtol end.
578 | Paradeep | 20.09.25 | 15:10 | 15:18 | 0:08 | 132kV Paradeep-Kendrapada Feeder | Tripped on O/C on B-Ph to G, Zone 1,Ir=0 kA, Iy=0 kA Ib=1.33 kA, | Kendrapada Pattamundai | 00:15 00:48 | - | - | 0.017412 | Heavy rain and thunderstorms | -
|  |  |  | 16:55 | 1:45 | 132kV Pattamundai-Olaver CKT-I | At Pattamundai end :-Zone 1, B-N, Ib- 3.68kA, Dist- 0.8km At Olaver end: O/C (B-N), Ib- 2.7kA
|  |  | 15:38 | 15:53 | 0:15 | 132kV Paradeep-Kendrapada Feeder | Tripped on O/C on B-N, Zone 1, Ir=1.8 kA
|  |  |  | 16:13 | 0:35 | 132kV Kendrapada-Pattamundai Feeder. | AT Kendrapada end: Ir=3.16kA, Iy=256A, Ib=150A AT Pattamundai end: Zone 1, Dist= 3.2Kms
579 | Bhadrak | 20.09.25 | 15:27 | 16:44 | 1:17 | 132kV Bhadrak-Dhamra Port RTSS Feeder | At Bhadrak Grid end: R-N, Zone 1, Dist- 17.87km, Ir- 4.189kA | Dhamra Port RTSS | 1:17 | - | - | 0.0040137 | - | -
580 | Kantabanji | 20.09.25 | 17:13 | 17:16 | 0:03 | 132kV Khariar-Kantabanji Feeder | TRIPPED AT GSS Kantabanji WITH CURRENT OF 310A | Kantabanji, Kantabanji RTSS | 0:03 | - | - | 0.00094002 | - | -
581 | Budhipadar | 20.09.25 | 17:16 | 17:16 | 0:00 | 132kV Budhipadar-Kalunga Feeder | At Budhipadar end: -Zone 1, Fault loop- A-N, Fault Dist-71.84km,IL1-1.281KAA/R-successful At Kalunga end: -R-N, Zone-1, Dist- 41.63 km, Ir-1.699 kA | - | - | - | - | - | - | -
582 | Rajgangpur | 20.09.25 | 17:16 | 17:16 | 0:00 | 132kV Rajgangpur-Bamra Feeder | A/R SUCCESSFUL,Zone-1,A-N, IA=2.676 KADist=21.44 KM | - | - | - | - | - | - | -
583 | Tarkera | 20.09.25 | 17:21 | 21.09.25 12:53 | 19:32 | 220kV Tarkera-Bamra Feeder | Y-PH INSULATOR SNAPPED AT LOC. 177 | - | - | - | - | - | - | -
584 | Gondia | 21.09.25 | 1:55 | 2:22 | 0:27 | 132kV Gondia-OPCL Feeder | Tripped at Both end. | - | - | - | - | - | - | -
585 | Keonjhar GIS | 21.09.25 | 3:20 | 12:12 | 8:52 | 220kV Keonjhar-Baripada PG Feeder | Tripped on Zone -1 Dist Protection | - | - | - | - | - | - | -
586 | Gondia | 21.09.25 | 3:44 | 10:45 | 7:01 | 132kV Gondia-OPCL Feeder | Tripped at Both end. | - | - | - | - | - | - | -
587 | Duburi | 21.09.25 | 11:04 | 11:13 | 0:09 | 132kV Duburi - Jakhapura RTSS Feeder | Tripped on Directional O/C MT(86) Operated. | Jakhapura RTSS | 0:09 | - | - | 0.0017524 | - | -
588 | Gondia | 21.09.25 | 12:26 | 12:57 | 0:31 | 132kV Gondia-OPCL Feeder | Tripped at Both end. | Gondia | 0:31 | - | - | 0.0037491 | - | -
589 | Mendhasal | 21.09.25 | 12:57 | 12:57 | 0:00 | 220kV Mendhasal-Bhanjanagar Feeder | At mendhasal end: Main 1Ir-2.5KA,Iy-0.05KA,D-30KM,Zone-1 Tripped Main-2= Ir-4.06KA,D-29.6KM,Zone-1 Tripped At Bhanjanagar end: Ib-1.3KA,Dist-115.6KM, Zone-1. | - | - | - | - | - | Fault tripping(AR unsuccessful at both end) | -
590 | Kantabanji | 21.09.25 | 13:55 | 13:58 | 0:03 | 132kV Kanatabanji-Kantabanji RTSS Feeder | L-L FAULT WITH FAULT CURRENT 400A | Kantabanji RTSS | 0:03 | - | - | 0.00017536 | - | -
591 | Bargarh New | 21.09.25 | 14:18 | 14:55 | 0:37 | 132kV Bargarh New-Bhatli CKT-I & II | Tripped at Bargarh New end (Zone-2, A-G, Loc;-36.4km) | Bhatli | 0:37 | - | - | 0.0088952 | - | -
592 | Duburi-New | 21.09.25 | 14:18 | 14:18 | 0:00 | 400kV Duburi New-Baripada Feeder | At Duburi New end: R-N, Zone 1, Dist- 23.7km, Ir- 7.98kA At Meramundali end: R-N, Dist- 14.5km, Zone 1, Ib- 2.43kA | - | - | - | - | - | - | -
593 | Atri | 21.09.25 | 14:30 | 14:30 | 0:00 | 220kV Atri- Narendrapur CKT-II | At Atri end: DP optd, B phase-N, Zone-1, IB= 4.75 kA, Dist= 23.64 km At Narendrapur end: DP optd, B phase-N, Zone-1, IB= 1.17 kA,Dist= 110.5 km | - | - | - | - | - | - | -
594 | Budhipadar | 21.09.25 | 14:38 | 14:38 | 0:00 | 132kV Budhipadar-Sundargarh CKT-II | D/P -(SEL 311C) :- Fault loop- A-N, Fault Dist-23.77km,IL1-3.153KA, IL2-68A, IL3-97A,IN-2.992KA, A/R-Successful | - | - | - | - | - | Weather-Lightening | -
595 | Telkoi | 21.09.25 | 14:43 | 14:54 | 0:11 | 220kV Telkoi-TTPS Feeder | No tripping from Telkoi end At TTPS end: Dist =123 KM ,Ia= 73.34 A, Ib=0 A , Ic=51.94 KA | - | - | - | - | - | - | -
|  |  |  | 14:43 | 0:00 | 220kV Telkoi-Joda Feeder | At Telkoi end: Y-N, Zone 1, Dist- 40.91km, Iy- 1.595kA, A/R successful At Joda end: Y-N, Zone 1, Dist- 51.61km, Iy- 2.45kA, A/R successful
596 | Budhipadar | 21.09.25 | 14:49 | 16:53 | 2:04 | 220kV Budhipadar-IB-I | D/P -I ( Siemens) :-Zone 1, Fault loop- Rph-Bph-N, Fault Dist-11.9km,IL1-8.21KA, IL2-0.26KA, IL3-8.98KA, Fault duration-92ms. D/P-II(ABBREL 670):-Zone-1, Rph-B-ph-E, IL1-7.389KA, IL2-308.62A, IL3-7.695KA, IN-4.457KA | - | - | - | - | - | Weather-Lightening | -
|  |  |  | 16:54 | 2:05 | 220kV Budhipadar-IB-II | D/P -I ( Micom-P444) :-Zone 1, Fault loop- Rph-Bph-N, Fault Dist-12.65km,IL1-7.969KA, IL2-319.9A, IL3-8.714KA, Fault duration-76.63ms. D/P-II(ABBREL 670):-Zone-1, Rph-B-ph-E, IL1-7.647KA, IL2-319A, IL3-8.451KA, IN-4.847KA
597 | Kuchinda | 21.09.25 | 15:06 | 15:39 | 0:33 | 132kV Kuchinda-SMC | Local end:- 1)Fault Loop - R-Y-N,O/C, E/F, 2) Zone -02, 3) Dist : 49.53 KM, 4) IR=894.4 A, Iy=937.0 A, IB=11.13 A, 5)Fault duration = 395.4 ms 6) Fault Resistance= 1.386 ohm Remote end:- 1)Fault Loop - R-Y-N,E/F, 2) Zone -01, 3)Fault Dist :3.349 KM 4) IR=8.085 KA, Iy=7.964 KA, IB=37.08 A, 5)Fault duration = 78.41 ms 6) Fault Resistance= 218.0 megaohm | - | - | - | - | - | Lightning and rain fall | -
598 | Rajgangpur | 21.09.25 | 15:06 | 15:13 | 0:07 | 132kV Rajgangpur-Bamra Feeder | POWER FAILURE | - | - | - | - | - | - | -
599 | Jharsuguda | 21.09.25 | 15:41 | 22.09.25 09:16 | 17:35 | 132kV Jharsuguda- Lapanga Feeder | At Jharsuguda end: Rph-Bph,Zone-2,Dist=8.954 km, Fault duration=418.1ms, Fault Current Ir= 6.319kA, Iy= 2.394A, Ib= 7.454kA At Lapanga end: Rph-Bph,Dist=6 km,Fault Current Ir= 6.57kA, Iy= 0.15kA, Ib= 4.88kA | - | - | - | - | - | - | -
600 | G. UDAYAGIRI | 21.09.25 | 16:31 | 17:06 | 0:35 | 132kV G. UDAYAGIRI-Phulbani line | Zone-1, D-10.1KM, IL1-0.20KA, IL2-1.63KA & IL3-0.11KA, A/R Block & Lockout. | G. UDAYAGIRI, Phulbani | 0:35 | - | - | 0.011307 | - | -
601 | Laxmipur | 21.09.25 | 18:12 | 20:05 | 1:53 | 220kV laxmipur-aditya CKT-II | y-phase,z-1,a/r optd successful,d-3.4km at laxmipur end | - | - | - | - | - | - | -
602 | Duburi | 21.09.25 | 18:21 | 18:28 | 0:07 | 132kV Duburi - Jakhapura RTSS Feeder | Tripped on Directional O/C MT(86) Operated. | Jakhapura RTSS | 0:07 | - | - | 0.001363 | - | -
603 | Tentulikhunti | 21.09.25 | 18:22 | 18:28 | 0:06 | 132kV Tentulikhunti- Dabugaon Line | DP Relay Operated,Zone-1, Dist=20.46km,E/F Ir=1.91kA,Iy=76.06A,Ib=53.8kA | - | - | - | - | - | - | -
604 | Rairakhol | 22.09.25 | 3:56 | 4:09 | 0:13 | 132kV Rairakhol-Boinda Feeder | At Rairakhol end-Dist -27.99KM, Current IL1-1.66KA, IL2-79.20A, IL3-288.6A, fault loop- A-N , Zone-1, R-Phase | Rairakhol, Boinda, Boinda RTSS | 0:13 | - | - | 0.0053382 | - | -
605 | Budhipadar | 22.09.25 | 13:28 | 19:08 | 5:40 | 220kV Budhipadar-Korba-II | D/P -I ( Micom-P444) :-Zone 1, Fault loop- Rph-N, Fault Dist-87.13km,IL1-1.878KA, IL2-154.4A, IL3-175.4A, Fault duration-66.60ms. A/R-Block,SOTF, D/P-II(ABBREL 670):-Zone-1, Rph-E,FD-86.78KM, IL1-1.878KA, IL2-153.87A, IL3-175.24A, IN-1.943KA | - | - | - | - | - | - | -
606 | Duburi-New | 22.09.25 | 14:48 | 15:11 | 0:23 | 220kV Duburi New-Paradeep Feeder | At Duburi New end: B-N, Dist- 5.51km, Zone 1, Ib- 14.83kA At Paradeep end: B-N, Dist- 88.24km, Zone 1, Ib- 1.529kA, A/R successful | - | - | - | - | - | - | -
607 | Padampur | 22.09.25 | 15:34 | 16:06 | 0:32 | 132kV Patnagarh-Padampur CKT-II | DP Operated, Zone1,Dist:25.89KM, Ia=597.8A, Ib=127.6A, Ic=258.6A(At GSS Padampur) | - | - | - | - | - | - | -
608 | Malkangiri | 22.09.25 | 16:02 | 16:35 | 0:33 | 220kV Malkangiri-Kalimela Feeder | R-Phase Pickup, Zone-1 Trip, A/R Close, Main-1 OPTD., Dist- 32.7km | - | - | - | - | - | - | -
609 | Cuttack | 22.09.25 | 16:27 | 16:27 | 0:00 | 220kV Cuttack-Pratapsasan CKT-II | AR Successfull DP Relay Main 1: Zone-1, A-N, Fault duration= 153.5ms, Relay trip time= 205.2ms, Dist=34.54km, Ir=1.636kA,Iy=164.6A,Ib=60.34A. (R-ph= Top conductor) , AR Successfull DP relay Main 2: Type AG, Loc: 36.1km, Resistance- 1.32 ohm, Reactance: 4.63 ohm, Reclose short 0 | - | - | - | - | - | - | -
610 | Rairangpur | 22.09.25 | 18:30 | 18:30 | 0:00 | 132kV Rairangpur-Karanjia Feeder | Zone-1, AR Close, B-Phase, Dist-6.707 KM, Ia=56.60 A, Ib=1.935KA, Ic=36.73A | - | - | - | - | - | - | -
611 | Purushottampur | 23.09.25 | 15:15 | 15:15 | 0:00 | 132kV Purushottampur-Chhatrapur Feeder | A/R operated, DP operated, in B ph, Zone-1, L3-E loop, IL1=0.00 KA, IL2=0.00 KA, IL3=2.20 KA, Dist-14.8 km | - | - | - | - | - | A/R operated successfilly.132kV Power supply availed through Aska(old)-Purushottampur Feeder | -
612 | Aska New | 23.09.25 | 15:25 | 15:25 | 0:00 | 132kV Aska New-Chatrapur Feeder | A/R optd, R-Ph E/F,Z=1,D=33.4Km,IR=2.15KA | - | - | - | - | - | - | -
613 | Hirakud | 23.09.25 | 15:35 | 16:16 | 0:41 | 132kV Lapanga-Hirakud-Burla P.H 'T' Feeder | Tripped on B-Ø, Zone - I, IA = 150.7 A, IB = 202.1 A, IC = 1.677 KA, IN = 1.469. Line was trial charged and stood ok. | - | - | - | - | - | - | -
614 | Budhipadar | 23.09.25 | 17:26 | 17:26 | 0:00 | 220kV Budhipadar-Korba-II | D/P -I ( Micom-P444) :-Zone 1, Fault loop- Bph-N, Fault Dist-37.76km,IL1-109.4A, IL2-82.09A, IL3-4.192KA, Fault duration-71.72ms. A/R-Successful, D/P-II(ABBREL 670):-Zone-1, Bph-E,FD-37.43KM, fault duration-0.5sec, IL1-108.1A, IL2-81.66A, IL3-4.139KA, | - | - | - | - | - | - | -
615 | Brajarajnagar | 23.09.25 | 17:46 | 17:46 | 0:00 | 132kV Brajrajnagar - Belpahar RTSS Feeder 2 | DP operated : Dist - 8.312 km, trip time - 66.72 ms, Ib - 5.914 kA,Y ph, Zone 1, L2 - E | - | - | - | - | - | a.Weather : Heavy Lightening & Rain b. Autoreclosure successful | -
616 | Budhipadar | 23.09.25 | 17:54 | 18:20 | 0:26 | 220kV Budhipadar-IB CKT-IV | D/P -I ( Micom-P444) :-Zone 1, Fault loop- Rph-N, Fault Dist-9.325km,IL1-11.60KA, IL2-419.5A, IL3-95.6A, Fault duration-54.42ms. A/R-Un-Successful, D/P-II(Siemens):-Zone-1, Rph-E,FD-8.9KM, fault duration-0sec, IL1-10.64KA, IL2-0.39KA, IL3-0.08KA, | - | - | - | - | - | - | -
617 | Brajarajnagar | 23.09.25 | 18:00 | 18:00 | 0:00 | 132kV Brajrajnagar - Jorabaga MCL Feeder | DP operated : Dist - 8.0 km, trip time - 55 ms, Ib - 5.91 kA,Y ph, Zone 1, L2 - E | - | - | - | - | - | a.Weather : Heavy Lightening & Rain b.Autoreclosure successful | -
618 | Budhipadar | 23.09.25 | 18:10 | 19:17 | 1:07 | 220kV Budhipadar-IB CKT-III | D/P -I ( Micom-P444) :-Zone 1, Fault loop- Rph-N, Fault Dist-11.37km,IL1-5.484KA, IL2-0A, IL3-0A, Fault duration-5ms. A/R-Un-Successful, | - | - | - | - | - | - | -
619 | Hirakud | 23.09.25 | 18:23 | 18:54 | 0:31 | 20 MVA TRF - I | Tripped on E/F, IA = 2.868 A, IB = 2.845 A, IC = 68.83 A, IN = 65.35 A. | Hirakud | 0:31 | - | - | 0.0025182 | E/F | -
620 | Budhipadar | 23.09.25 | 19:02 | 19:02 | 0:00 | 220kV Budhipadar-Korba-I | D/P -I ( Micom-P444) :-Zone 1, Fault loop- Rph-N, Fault Dist-54.07km,IL1-2.963KA, IL2-288.4A, IL3-96.13A, Fault duration-68.23ms. A/R-Successful, | - | - | - | - | - | - | -
621 | Lapanga | 24.09.25 | 0:41 | 17:30 | 16:49 | 400 KV Lapanga STERLITE CKT-II | At Lapanga end: DP RELAY-1(P444) Zone-1, L3-G,DIST-8.472KM, FD=101.6ms DP RELAY-2(d60),Zone-1, L3-G,DIST-10.9KM, | - | - | - | - | - | . AT LOC 13 B-PH insulator damaged. Replacement needed | -
622 | Nabarangpur | 24.09.25 | 03:36 | 04:09 | 0:33 | 132kV Nabarangpur-Borigumma Feeder | "AT Nabarangpur end: Dist PTRN R-ph Zone-1 AR Lockout Fault ditance-52.02KM Fault Current- Ia-831.2 A,Ib-53.15A, Ic-52.34A AT Borigumma end: Fault ditance-1.340 KM Fault Current-2.288KA " | - | - | - | - | - | - | -
623 | Karanjia | 24.09.25 | 14:51 | 23:28 | 8:37 | 132kV Karanjia-Turumunga Feeder | At Karanjia end:Gen Trip, Z1,Z2,Z3, B-Phase, A/R-Block, A/R Close, SOTF Operated DP relay: IL1-0.01KA, IL2-0.00KA, IL3-1.40KA, Dist=0.1km At Turumunga end: DP relay:B-Phase, Zone-2 Trip, IL1-236.6A, IL2-423.6KA,IL3-2.106A, Dist=33.93km | - | - | - | - | - | At the time of breakdown, Karanjia & Dhenkikote GSS avail power supply from Rairangpur GSS | -
624 | Rayagada | 24.09.25 | 23:58 | 25.09.25 00:11 | 0:13 | 132kV Rayagada-Podagada Feeder | Power supply failed at MKD generation end. | Rayagada, Rayagada RTSS, Podagada, Akhusingh | 0:13 | - | - | 0.0061624 | - | -
132kV Rayagada-Akhusingh Feeder
625 | Soro | 25.09.25 | 10:05 | 10:05 | 0:00 | 132kV Soro-Chandipur Feeder | Soro Grid end Relay Details: Dist protection relay: Zone -1, Dist -4.47km , Event-B G T, Ia-67A, Ib - 1.968A, Ic - 35A , IG-2.017 KA, Group- 1, SHOT-0. CHANDIPUR Grid end Realay Details: Y PHASE TO E , Zone - 1, Fault Duration - 31.05ms, Ia -70.99A , Ib - 1.13KA , Ic - 37.89A. | - | - | - | - | - | 132kV Soro-Chandipur line Auto reclouser operated Sucessfully. Soro grid power supply availed from Soro-Bhadrak Line . | -
626 | Junagarh | 25.09.25 | 10:12 | 10:33 | 0:21 | 132kV Bhawanipatna-Junagarh-Brundabahal T line | DP relay operated: Y ph E/F, Zone 1,Fault Dist=19.8km, Ia=65A, Ib=784A, Ic=57.5A | - | - | - | - | - | - | -
627 | Therubali | 25.09.25 | 10:24 | 11:25 | 1:01 | 160MVA Auto TRF-III | Tripped on Overflux | - | - | - | - | - | - | -
628 | Rourkela | 25.09.25 | 11:51 | 11:57 | 0:06 | 132kV Rourkela-Tarkera CKT-III |  | - | - | - | - | - | - | -
629 | Kalunga | 25.09.25 | 13:45 | 13:45 | 0:00 | 132kV Budhipadar-Kalunga Feeder | At Kalunga end: -Y-N, Zone-1, Fault duration- 53.31 ms, Relay trip time- 79.97 ms, Dist- 33.29 km, Ir-95.85A, Iy- 1.742 KA, Ib- 150.6 A At Budhipadar end: Y-N, Zone-1, Fault duration-111.6 ms,, Dist-66.95 km, Ir-21.21A,Iy-1.221 KA,Ib-26.51 A, | - | - | - | - | - | E/F | -
630 | Duburi | 25.09.25 | 20:33 | 20:40 | 0:07 | 132kV Duburi - Jakhapura RTSS Feeder | Tripped on Directional O/C MT(86) Operated. | Jakhapura RTSS | 0:14 | - | - | 0.002726 | - | -
|  |  | 20:47 | 20:54 | 0:07
631 | Bangiriposi | 25.09.25 | 23:07 | 23:07 | 0:00 | 132kV Baripada PG-Bangiriposi CKT-II | At Bangiriposi end: Y-N, Zone 1, Dist- 8.4km, Iy- 2.086kA At Barapada PG end: Y-N, Zone 1, Dist- 18.01km, Iy- 2.901kA | - | - | - | - | - | - | -
632 | Bhawanipatna | 26.09.25 | 10:12 | 10:34 | 0:22 | 132kV Bhawanipatna-Junagarh Feeder | DP REALY OPERATED | - | - | - | - | - | - | -
633 | Polasponga | 26.09.25 | 13:25 | 13:28 | 0:03 | 132kV Polasponga-Kendujhargarh RTSS Feeder | O/C, IA=299.9A, IB=263.3A, IC=43.72A | Kendujhargarh RTSS | 0:03 | - | - | 0.00041611 | OVER CURRENT | -
634 | Budhipadar | 26.09.25 | 13:45 | 14:03 | 0:18 | 132kV Budhipadar-Kalunga Feeder | Zone 1, Fault loop- Yph-N, Fault Dist-66.95km,IL1-21.21A, IL2-1.221KA, IL3-26.51A | - | - | - | - | - | - | -
635 | Nuapada | 26.09.25 | 15:21 | 15:32 | 0:11 | 132kV Nuapada-Padampur CKT-II | AN, Zone:1,Dist:45.30KM, Ia:595.8 A, Ib:26.38A, Ic:37.33 A | Nuapada | 0:11 | - | - | 0.002607 | - | -
636 | Hirakud | 26.09.25 | 15:40 | 16:30 | 0:50 | 132kV Hirakud-Burla PH Feeder | P/S Fail | - | - | - | - | - | - | -
637 | Kantabanji | 26.09.25 | 19:22 | 19:29 | 0:07 | 132kV Khariar-Kantabanji Feeder | TRIPPED AT GSS Kantabanji WITH CURRENT OF 500A | Kantabanji, Kantabanji RTSS | 0:07 | - | - | 0.0021934 | - | -
638 | Katapali | 26.09.25 | 19:50 | 20:04 | 0:14 | 220kV Katapali-Bargarh New Feeder | R-N, Zone-2 , Dist- 43.12km, Ir- 3.793kA | Bargarh New, Bhatli, Ghess Bargarh, ACC | 00:14 00:10 | - | - | 0.018077 | - | -
|  |  |  | 27.09.25 11:05 | 15:15 | 132kV Bargarh-Bargarh New Feeder | Source failed from Bargarh New end
|  |  |  | 20:04 | 0:14 | 132kV Bargarh New-Bhatli CKT-I & II | Supply Failure from Source Grid Bargarh New due to 220kV katapali Line tripped
639 | Bolangir New | 26.09.25 | 21:02 | 27.09.25 16:54 | 19:52 | 220kV Bolangir New-Bargarh New CKT | Tripped On operation of DP Relay. | - | - | - | - | - | - | -
640 | Gondia | 26.09.25 | 23:06 | 23:25 | 0:19 | 132kV Gondia-JFAL Feeder | Tripped at Both end. | - | - | - | - | - | - | -
641 | Sambalpur | 26.09.25 | 15:38 | 17:21 | 1:43 | 132kV Burla PH-Sambalpur Feeder | At Sambalpur end: Tripped on R Y B ph E/F, Z2 Z3, DP operated with Fault Dist: 23 KM. Ia= 4226 A, Ib=4354 A,Ic=3885 A, Ig=1298 A, Fault Duration: 533.7 ms, PSB operated At Burla PH end: Fault Dist: 0KM,Y-ph O/C,I=11.6 KA, PSB operated | - | - | - | - | - | Water level at Hirakud dam is high & released water through gate causing dense vapour below line which might be the cause of induction that leads to tripping. | -
642 | Narendrapur | 27.09.25 | 8:17 | 8:19 | 0:02 | 132kV Narendrapur-Narendrapur RTSS Feeder | R-ph & B-ph O/C. (Ir=1.05KA,Ib=1.06KA) | Narendrapur RTSS | 0:02 | - | - | 0.00018697 | - | -
643 | Bhawanipatna | 27.09.25 | 12:07 | 12:24 | 0:17 | 132kV Bhawanipatna-Kesinga Feeder | Source failure from Kesinga end | Bhawanipatna, Bhawanipatna RTSS, Lanjigarh RTSS, Brundabahal | 0:10 | - | - | 0.0045365 | - | -
|  |  |  | 12:17 | 0:10 | 132kV Bhawanipatna-Junagarh-Brundabahal T line | DP relay operated:R & Y ph E/F, Zone 2,Fault Dist=33.11 km, Ia=884.7A, Ib=877.1A, Ic=10.95A
644 | Rourkela | 27.09.25 | 13:40 | 14:37 | 0:57 | 132kV Rourkela-Tarkera CKT-III |  | - | - | - | - | - | - | -
645 | Ghess | 27.09.25 | 14:57 | 15:17 | 0:20 | 132kV Bargarh New-Ghess CKT-I | E/F on R phase, Ir- 1.283kA | - | - | - | - | - | - | -
646 | Tarkera | 28.09.25 | 9:01 | 15:08 | 6:07 | 132kV Rourkela-Tarkera CKT-III | AGT, LOC= 1.73, IA= 9.53KA, IB= 1.46KA, IC= 613A, IG= 7.55KA, GRP-1, Zone-1. | - | - | - | - | - | JUMPER SNAPPED AT LOC-93 | -
647 | Tarkera | 28.09.25 | 9:01 | 12:01 | 3:00 | 100MVA Auto TRF-IV | TRIPPED ON OSR | - | - | - | - | - | TRIPPED DURING FAULT IN 132kV Tarkera-Rourkela CKT-III | -
648 | Jaleswar | 28.09.25 | 11:16 | 11:20 | 0:04 | 132kV Jaleswar-Jaleswar RTSS Feeder | Tripped on over load. | Jaleswar RTSS | 0:04 | - | - | 0.00053329 | - | -
649 | Tarkera | 28.09.25 | 14:20 | 17:19 | 2:59 | 220kV Tarkera-PGCIL CKT-II | TRIPPED FROM Tarkera GRID end ONLY | - | - | - | - | - | - | -
650 | Nabarangpur | 28.09.25 | 23:33 | 23:48 | 0:15 | 132kV Nabarangpur-Borigumma Feeder | At Nabarangpur end: R-PH ,Zone-1, Ir- 0.826kA, Dist- 52.14km, At Borigumma end: Dist-1.3km, Ir- 2.24kA | - | - | - | - | - | - | -
651 | Duburi | 29.09.25 | 10:47 | 10:54 | 0:07 | 132kV Duburi - Jakhapura RTSS Feeder | Tripped on Directional O/C MT(86) Operated. | Jakhapura RTSS | 0:07 | - | - | 0.001363 | - | -
652 | Kalunga | 29.09.25 | 15:01 | 15:01 | 0:00 | 132kV Budhipadar-Kalunga Feeder | R-N, Zone 1, Dist- 79.4km, Ir- 1.047kA | - | - | - | - | - | E/F | -
653 | Boudh | 29.09.25 | 271:12 | 272:24 | 1:12 | 132kV Sonepur-Boudh Feeder | Dist Z1 | Boudh | 1:12 | - | - | 0.0095603 | - | -

## page-60
Format - C1.1
OVERALL PERFORMANCE
Frequency Profile for the quarter (JULY'25-SEPT'25)
Month | Total Hours | Total duration(in HRs) of frequency | Percentage | Total duration(in HRs) of frequency | Percentage
|  | ( > 50.05 Hz.) | of time | (<49.9 Hz.) | of time
|  |  | [=(3/2) * 100] |  | [=(5/2) * 100]
1 | 2 | 3 | 4 | 5 | 6
JULY | 744 | 139.5833 | 18.7612 | 52.1167 | 7.0049
AUGUST | 744 | 118.75 | 15.961 | 52.2333 | 7.0206
SEPTEMBER | 720 | 102.8833 | 14.2894 | 46.0333 | 6.3935
Total | 2208 | 361.2167 | 16.3595 | 150.3833 | 6.8108

## page-61
OVERALL PERFORMANCE | [6 empty] | Format - C1.2
Frequency Profile for the quarter (JULY'25-SEPT'25)
(Maximum continuous period of deviation)
Month |  | Frequency (>50.05 Hz.) |  |  |  | Frequency (<49.9 Hz.)
| Total duration | Percentage | Maximum continuous period of | Month | Total duration | Percentage | Maximum continuous period of
| (HRs) | of time | deviation with date, time and reason |  | (HRs) | of time | deviation with date, time and reason
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
August | 2.2833 | 0.10571 | 24.08.25 / 12:00 | September | 1.6667 | 0.07716 | 09.09.25 / 18:07
|  |  | . |  |  |  | .
|  |  | 24.08.25 / 14:17 |  |  |  | 09.09.25 / 19:46

## page-62
Format - C1.3
OVERALL PERFORMANCE
Frequency Profile for the quarter (JULY'25-SEPT'25)
Lowest / Highest frequency occurrence
Highest frequency occurrence |  |  | Lowest frequency occurrence |  |  | Details of the event if there is islanding
Frequency | Date of | Time of | Frequency | Date of | Time of
in Hz | occurrence | occurrence | in Hz | occurrence | occurrence
1 | 2 | 3 | 4 | 5 | 6 | 7
50.31 | 27.07.25 | 13:30 | 49.5 | 08.09.25 | 19:00 | -

## Page-63
| JULY | AUGUST | SEPT
<48.5Hz | 0 | 0 | 0
48.50 - 49.0Hz | 0 | 0 | 0
49.0 - 49.70Hz | 0.34946 | 0.21729 | 0.42593
49.70 - 49.90Hz | 6.6555 | 6.8033 | 5.9676
49.90 - 50.05Hz | 74.2339 | 77.0184 | 79.3171
>=50.05Hz | 18.7612 | 15.961 | 14.2894
>=51.0Hz | 0 | 0 | 0
| 100 | 100 | 100

## Page-64
132KV VOLTAGE AT DIFFERENT GRID SUBSTATIONS
CESU ZONE
SUBSTATIONS | 2025-07-01 | [5 empty] | 2025-08-01 | [5 empty] | 2025-09-01
| MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM
| KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME
Angul | 140.0033 | 2025-07-27 | 10:45 | 130.4773 | 2025-07-19 | 11:15 | 139.2528 | 2025-08-06 | 13:30 | 130.1887 | 2025-08-12 | 14:45 | 136.4816 | 2025-09-27 | 3:45 | 130.8237 | 2025-09-11 | 14:30 | 140.0033 | 2025-07-27 | 10:45 | 130.1887 | 2025-08-12 | 14:45
Argul | 136.8626 | 2025-07-05 | 4:00 | 125.8356 | 2025-07-18 | 22:30 | 137.1398 | 2025-08-28 | 3:00 | 125.0793 | 2025-08-12 | 22:45 | 137.7517 | 2025-09-21 | 14:00 | 125.2236 | 2025-09-11 | 14:45 | 137.7517 | 2025-09-21 | 14:00 | 125.0793 | 2025-08-12 | 22:45
Badagada | 140.5864 | 2025-07-05 | 4:00 | 127.989 | 2025-07-18 | 22:30 | 140.3844 | 2025-08-15 | 5:45 | 127.2558 | 2025-08-12 | 22:45 | 140.7019 | 2025-09-27 | 3:45 | 127.2962 | 2025-09-11 | 14:45 | 140.7019 | 2025-09-27 | 3:45 | 127.2558 | 2025-08-12 | 22:45
Balugaon | 136.7125 | 2025-07-23 | 16:30 | 118.5843 | 2025-07-23 | 12:30 | 136.4816 | 2025-08-09 | 3:15 | 122.2792 | 2025-08-12 | 22:45 | 137.2321 | 2025-09-21 | 15:45 | 124.1267 | 2025-09-11 | 14:45 | 137.2321 | 2025-09-21 | 15:45 | 118.5843 | 2025-07-23 | 12:30
Banki | 136.9781 | 2025-07-05 | 4:00 | 125.5873 | 2025-07-22 | 15:15 | 137.5728 | 2025-08-28 | 3:00 | 125.1716 | 2025-08-12 | 22:45 | 138.1212 | 2025-09-21 | 14:00 | 125.7201 | 2025-09-11 | 14:45 | 138.1212 | 2025-09-21 | 14:00 | 125.1716 | 2025-08-12 | 22:45
Bhubaneswar | 137.4457 | 2025-07-01 | 4:30 | 125.3506 | 2025-07-22 | 15:15 | 137.8672 | 2025-08-16 | 5:30 | 125.391 | 2025-08-12 | 22:45 | 138.0173 | 2025-09-27 | 3:45 | 125.2813 | 2025-09-11 | 14:45 | 138.0173 | 2025-09-27 | 3:45 | 125.2813 | 2025-09-11 | 14:45
Bidanasi | 138.8718 | 2025-07-01 | 4:30 | 126.3783 | 2025-07-22 | 15:15 | 137.6478 | 2025-08-01 | 5:45 | 127.862 | 2025-08-02 | 15:15 | 138.5889 | 2025-09-03 | 5:45 | 126.8113 | 2025-09-11 | 14:45 | 138.8718 | 2025-07-01 | 4:30 | 126.3783 | 2025-07-22 | 15:15
Boinda | 140.4075 | 2025-07-27 | 5:45 | 124.0112 | 2025-07-22 | 22:00 | 139.9456 | 2025-08-06 | 13:30 | 123.2029 | 2025-08-14 | 19:00 | 137.694 | 2025-09-27 | 4:00 | 121.5864 | 2025-09-08 | 16:00 | 140.4075 | 2025-07-27 | 5:45 | 121.5864 | 2025-09-08 | 16:00
Chainpal | 139.2355 | 2025-07-10 | 4:45 | 131.0431 | 2025-07-22 | 20:00 | 137.8961 | 2025-08-16 | 5:45 | 132.7001 | 2025-08-02 | 15:15 | 138.8256 | 2025-09-27 | 3:45 | 133.5834 | 2025-09-11 | 15:15 | 139.2355 | 2025-07-10 | 4:45 | 131.0431 | 2025-07-22 | 20:00
Chandaka | 136.2911 | 2025-07-01 | 4:30 | 124.7617 | 2025-07-22 | 15:15 | 136.7299 | 2025-08-16 | 5:30 | 124.7444 | 2025-08-12 | 22:45 | 136.6894 | 2025-09-27 | 3:45 | 124.6232 | 2025-09-11 | 14:45 | 136.7299 | 2025-08-16 | 5:30 | 124.6232 | 2025-09-11 | 14:45
Chandpur | 135.8465 | 2025-07-05 | 4:00 | 118.8729 | 2025-07-22 | 15:00 | 136.5393 | 2025-08-28 | 3:00 | 121.4652 | 2025-08-13 | 15:00 | 136.8107 | 2025-09-21 | 15:45 | 124.3461 | 2025-09-11 | 14:45 | 136.8107 | 2025-09-21 | 15:45 | 118.8729 | 2025-07-22 | 15:00
Choudwar | 139.3683 | 2025-07-01 | 4:30 | 125.4545 | 2025-07-22 | 15:15 | 138.9641 | 2025-08-28 | 3:45 | 126.6669 | 2025-08-12 | 14:45 | 139.9456 | 2025-09-15 | 13:00 | 120.8936 | 2025-09-19 | 12:00 | 139.9456 | 2025-09-15 | 13:00 | 120.8936 | 2025-09-19 | 12:00
Cuttack | 137.6363 | 2025-07-01 | 4:30 | 125.6277 | 2025-07-18 | 22:30 | 137.8614 | 2025-08-16 | 5:30 | 124.8368 | 2025-08-12 | 22:45 | 137.8672 | 2025-09-27 | 3:45 | 125.2698 | 2025-09-11 | 14:45 | 137.8672 | 2025-09-27 | 3:45 | 124.8368 | 2025-08-12 | 22:45
Dhenkanal | 138.9641 | 2025-07-12 | 18:00 | 133.6527 | 2025-07-01 | 19:45 | 137.5208 | 2025-08-16 | 5:15 | 129.4785 | 2025-08-11 | 15:00 | 138.2482 | 2025-09-21 | 13:30 | 130.3907 | 2025-09-11 | 15:45 | 138.9641 | 2025-07-12 | 18:00 | 129.4785 | 2025-08-11 | 15:00
Jagatsinghpur | 133.5949 | 2025-07-05 | 3:45 | 115.2357 | 2025-07-22 | 15:15 | 133.0753 | 2025-08-22 | 3:00 | 115.4667 | 2025-08-05 | 22:30 | 134.6919 | 2025-09-21 | 15:00 | 117.0832 | 2025-09-11 | 14:45 | 134.6919 | 2025-09-21 | 15:00 | 115.2357 | 2025-07-22 | 15:15
Kalarangi | 137.3476 | 2025-07-05 | 5:30 | 128.7453 | 2025-07-23 | 22:45 | 136.9435 | 2025-08-15 | 5:45 | 129.2649 | 2025-08-05 | 22:30 | 137.0589 | 2025-09-27 | 5:45 | 128.9185 | 2025-09-11 | 14:45 | 137.3476 | 2025-07-05 | 5:30 | 128.7453 | 2025-07-23 | 22:45
Kamakhyanagar | 136.9435 | 2025-07-05 | 5:30 | 126.7247 | 2025-07-23 | 22:45 | 135.9043 | 2025-08-06 | 15:45 | 127.4752 | 2025-08-05 | 22:30 | 136.8453 | 2025-09-27 | 5:45 | 128.6241 | 2025-09-11 | 14:45 | 136.9435 | 2025-07-05 | 5:30 | 126.7247 | 2025-07-23 | 22:45
Kendrapada | 140.6823 | 2025-07-13 | 14:45 | 120.8174 | 2025-07-23 | 22:45 | 138.3452 | 2025-08-23 | 6:00 | 117.9377 | 2025-08-12 | 22:45 | 138.2829 | 2025-09-20 | 16:15 | 121.6153 | 2025-09-10 | 22:30 | 140.6823 | 2025-07-13 | 14:45 | 117.9377 | 2025-08-12 | 22:45
Khajuriakata | 139.5992 | 2025-07-12 | 18:00 | 126.436 | 2025-07-22 | 22:30 | 137.4053 | 2025-08-16 | 5:30 | 131.2856 | 2025-08-11 | 15:00 | 138.6062 | 2025-09-23 | 13:30 | 130.4081 | 2025-09-19 | 12:00 | 139.5992 | 2025-07-12 | 18:00 | 126.436 | 2025-07-22 | 22:30
KhuntuniGIS | 139.553 | 2025-07-26 | 2:45 | 124.1036 | 2025-07-22 | 15:15 | 139.0911 | 2025-08-08 | 5:15 | 127.4059 | 2025-08-05 | 14:45 | 140.5691 | 2025-09-15 | 13:00 | 124.6347 | 2025-09-19 | 12:00 | 140.5691 | 2025-09-15 | 13:00 | 124.1036 | 2025-07-22 | 15:15
Khurda | 136.5971 | 2025-07-05 | 4:00 | 125.4488 | 2025-07-18 | 22:30 | 135.7946 | 2025-08-01 | 5:45 | 127.0711 | 2025-08-02 | 15:00 | 137.9192 | 2025-09-21 | 14:00 | 124.9927 | 2025-09-11 | 14:45 | 137.9192 | 2025-09-21 | 14:00 | 124.9927 | 2025-09-11 | 14:45
Konark | 137.1929 | 2025-07-26 | 3:00 | 124.226 | 2025-07-18 | 22:30 | 137.2737 | 2025-08-26 | 3:15 | 123.1267 | 2025-08-12 | 22:45 | 138.3233 | 2025-09-21 | 14:00 | 124.7329 | 2025-09-11 | 14:45 | 138.3233 | 2025-09-21 | 14:00 | 123.1267 | 2025-08-12 | 22:45
Mania | 139.478 | 2025-07-01 | 4:30 | 115.917 | 2025-07-19 | 22:45 | 138.6062 | 2025-08-28 | 3:45 | 124.2768 | 2025-08-11 | 15:00 | 140.0033 | 2025-09-15 | 13:00 | 116.858 | 2025-09-10 | 22:30 | 140.0033 | 2025-09-15 | 13:00 | 115.917 | 2025-07-19 | 22:45
Marshaghai | 137.8845 | 2025-07-13 | 14:45 | 120.9571 | 2025-07-23 | 23:00 | 136.0659 | 2025-08-23 | 6:00 | 118.9364 | 2025-08-12 | 22:45 | 137.7402 | 2025-09-20 | 16:15 | 122.2503 | 2025-09-10 | 22:45 | 137.8845 | 2025-07-13 | 14:45 | 118.9364 | 2025-08-12 | 22:45
Nimapara | 136.5797 | 2025-07-05 | 4:00 | 124.9811 | 2025-07-18 | 22:30 | 136.7068 | 2025-08-15 | 5:45 | 123.89 | 2025-08-12 | 22:45 | 137.9538 | 2025-09-21 | 14:00 | 124.8657 | 2025-09-11 | 14:45 | 137.9538 | 2025-09-21 | 14:00 | 123.89 | 2025-08-12 | 22:45
Nuapatana | 136.8857 | 2025-07-05 | 4:00 | 124.7617 | 2025-07-22 | 15:15 | 137.5785 | 2025-08-28 | 3:00 | 124.8772 | 2025-08-12 | 22:45 | 137.9827 | 2025-09-21 | 14:00 | 125.6277 | 2025-09-11 | 14:45 | 137.9827 | 2025-09-21 | 14:00 | 124.7617 | 2025-07-22 | 15:15
Olaver | 138.0635 | 2025-07-13 | 15:00 | 122.2388 | 2025-07-22 | 21:45 | 137.1686 | 2025-08-24 | 5:45 | 122.0136 | 2025-08-12 | 22:30 | 138.2194 | 2025-09-20 | 15:00 | 123.9881 | 2025-09-10 | 22:30 | 138.2194 | 2025-09-20 | 15:00 | 122.0136 | 2025-08-12 | 22:30
Paradeep | 135.096 | 2025-07-30 | 5:45 | 124.1844 | 2025-07-24 | 0:00 | 135.1537 | 2025-08-23 | 6:00 | 120.374 | 2025-08-12 | 22:45 | 137.7575 | 2025-09-20 | 16:15 | 124.5077 | 2025-09-10 | 23:00 | 137.7575 | 2025-09-20 | 16:15 | 120.374 | 2025-08-12 | 22:45
Pattamundai | 137.9653 | 2025-07-13 | 15:00 | 121.2689 | 2025-07-23 | 23:00 | 136.1525 | 2025-08-23 | 6:00 | 120.8474 | 2025-08-12 | 22:30 | 138.7505 | 2025-09-20 | 16:00 | 122.054 | 2025-09-10 | 22:30 | 138.7505 | 2025-09-20 | 16:00 | 120.8474 | 2025-08-12 | 22:30
Phulnakhara | 137.9538 | 2025-07-05 | 4:00 | 125.9049 | 2025-07-18 | 22:30 | 136.9261 | 2025-08-01 | 5:45 | 127.4752 | 2025-08-02 | 15:00 | 138.1443 | 2025-09-27 | 3:45 | 125.3333 | 2025-09-11 | 14:45 | 138.1443 | 2025-09-27 | 3:45 | 125.3333 | 2025-09-11 | 14:45
Puri | 137.4919 | 2025-07-05 | 4:00 | 126.1762 | 2025-07-22 | 15:00 | 137.6189 | 2025-08-15 | 5:45 | 125.6393 | 2025-08-12 | 22:45 | 138.1559 | 2025-09-21 | 14:00 | 125.9337 | 2025-09-11 | 14:45 | 138.1559 | 2025-09-21 | 14:00 | 125.6393 | 2025-08-12 | 22:45
Ranasinghpur | 136.5971 | 2025-07-01 | 4:30 | 123.5493 | 2025-07-22 | 15:15 | 136.8453 | 2025-08-16 | 5:30 | 123.584 | 2025-08-12 | 22:45 | 136.9088 | 2025-09-27 | 3:45 | 124.0516 | 2025-09-11 | 14:45 | 136.9088 | 2025-09-27 | 3:45 | 123.5493 | 2025-07-22 | 15:15
Salipur | 138.0577 | 2025-07-07 | 3:45 | 117.7356 | 2025-07-19 | 22:45 | 138.1212 | 2025-08-26 | 3:00 | 115.663 | 2025-08-12 | 22:45 | 138.3464 | 2025-09-20 | 16:15 | 118.4573 | 2025-09-10 | 22:30 | 138.3464 | 2025-09-20 | 16:15 | 115.663 | 2025-08-12 | 22:45
Samangara | 137.2379 | 2025-07-05 | 4:00 | 126.2743 | 2025-07-22 | 15:00 | 137.4919 | 2025-08-15 | 5:45 | 125.7143 | 2025-08-12 | 22:45 | 137.9596 | 2025-09-21 | 14:00 | 126.0261 | 2025-09-11 | 14:45 | 137.9596 | 2025-09-21 | 14:00 | 125.7143 | 2025-08-12 | 22:45
Shamuka | 134.8073 | 2025-07-09 | 4:00 | 128.0525 | 2025-07-02 | 23:00 | 136.2622 | 2025-08-15 | 5:45 | 122.0021 | 2025-08-12 | 22:45 | 136.5105 | 2025-09-27 | 5:30 | 122.5217 | 2025-09-11 | 14:45 | 136.5105 | 2025-09-27 | 5:30 | 122.0021 | 2025-08-12 | 22:45
Tirtol | 138.2944 | 2025-07-13 | 15:00 | 120.6742 | 2025-07-23 | 23:00 | 136.1756 | 2025-08-30 | 17:15 | 120.0565 | 2025-08-12 | 22:45 | 137.7517 | 2025-09-20 | 15:15 | 122.8912 | 2025-09-19 | 22:45 | 138.2944 | 2025-07-13 | 15:00 | 120.0565 | 2025-08-12 | 22:45
Unit-8GIS | 138.0924 | 2025-07-05 | 4:00 | 127.2616 | 2025-07-22 | 15:15 | 137.7113 | 2025-08-08 | 5:45 | 125.3968 | 2025-08-12 | 22:45 | 137.821 | 2025-09-21 | 14:00 | 126.4302 | 2025-09-11 | 14:45 | 138.0924 | 2025-07-05 | 4:00 | 125.3968 | 2025-08-12 | 22:45
| 140.6823 |  |  | 115.2357 |  |  | 140.3844 |  |  | 115.4667 |  |  | 140.7019 |  |  | 116.858

## Page-65
132KV VOLTAGE AT DIFFERENT GRID SUBSTATIONS
NESCO ZONE
SUBSTATIONS | 2025-07-01 | [5 empty] | 2025-08-01 | [5 empty] | 2025-09-01
| MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM
| KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME
Agarpada | 138.7447 | 2025-07-01 | 4:45 | 124.8657 | 2025-07-23 | 23:00 | 136.343 | 2025-08-18 | 6:15 | 122.2792 | 2025-08-12 | 22:30 | 135.7888 | 2025-09-09 | 20:45 | 123.8957 | 2025-09-11 | 14:45 | 138.7447 | 2025-07-01 | 4:45 | 122.2792 | 2025-08-12 | 22:30
Anandpur | 136.828 | 2025-07-05 | 5:30 | 126.3205 | 2025-07-23 | 22:45 | 136.5393 | 2025-08-15 | 5:45 | 127.2443 | 2025-08-11 | 22:30 | 136.5971 | 2025-09-27 | 5:45 | 127.4175 | 2025-09-11 | 14:45 | 136.828 | 2025-07-05 | 5:30 | 126.3205 | 2025-07-23 | 22:45
Balasore | 136.5971 | 2025-07-06 | 17:00 | 122.6025 | 2025-07-23 | 22:45 | 135.6733 | 2025-08-01 | 17:45 | 124.2421 | 2025-08-11 | 23:15 | 138.0404 | 2025-09-02 | 5:30 | 127.0133 | 2025-09-10 | 23:15 | 138.0404 | 2025-09-02 | 5:30 | 122.6025 | 2025-07-23 | 22:45
Bangiriposi | 139.426 | 2025-07-06 | 18:00 | 129.8423 | 2025-07-23 | 22:45 | 139.1373 | 2025-08-15 | 5:45 | 130.3041 | 2025-08-12 | 22:45 | 139.3105 | 2025-09-02 | 5:45 | 130.9392 | 2025-09-09 | 22:45 | 139.426 | 2025-07-06 | 18:00 | 129.8423 | 2025-07-23 | 22:45
Barbil | 139.1951 | 2025-07-26 | 5:45 | 130.3041 | 2025-07-19 | 11:45 | 138.6755 | 2025-08-10 | 6:00 | 127.7061 | 2025-08-19 | 12:15 | 137.7517 | 2025-09-04 | 6:00 | 131.4588 | 2025-09-01 | 19:45 | 139.1951 | 2025-07-26 | 5:45 | 127.7061 | 2025-08-19 | 12:15
Baripada | 138.9403 | 2025-07-06 | 18:00 | 114.5045 | 2025-07-23 | 13:45 | 137.8118 | 2025-08-24 | 6:00 | 123.3866 | 2025-08-25 | 14:30 | 138.1484 | 2025-09-02 | 4:15 | 129.2728 | 2025-09-09 | 22:00 | 138.9403 | 2025-07-06 | 18:00 | 114.5045 | 2025-07-23 | 13:45
Basta | 137.1167 | 2025-07-06 | 18:00 | 123.9535 | 2025-07-23 | 22:30 | 137.2321 | 2025-08-01 | 17:30 | 124.4153 | 2025-08-12 | 22:45 | 137.694 | 2025-09-20 | 15:15 | 125.9164 | 2025-09-10 | 23:30 | 137.694 | 2025-09-20 | 15:15 | 123.9535 | 2025-07-23 | 22:30
Betanati | 138.9179 | 2025-07-06 | 18:00 | 114.7219 | 2025-07-23 | 13:45 | 138.4792 | 2025-08-15 | 5:45 | 125.1716 | 2025-08-25 | 15:15 | 138.9122 | 2025-09-02 | 5:45 | 129.6575 | 2025-09-09 | 23:30 | 138.9179 | 2025-07-06 | 18:00 | 114.7219 | 2025-07-23 | 13:45
Bhadrak | 137.7517 | 2025-07-13 | 14:00 | 124.0112 | 2025-07-22 | 14:30 | 138.0404 | 2025-08-23 | 6:00 | 123.4339 | 2025-08-12 | 22:30 | 137.5785 | 2025-09-27 | 5:45 | 124.9349 | 2025-09-11 | 14:45 | 138.0404 | 2025-08-23 | 6:00 | 123.4339 | 2025-08-12 | 22:30
Bhograi | 137.5266 | 2025-07-06 | 18:00 | 123.3473 | 2025-07-12 | 15:15 | 138.1443 | 2025-08-17 | 10:30 | 125.4603 | 2025-08-12 | 22:45 | 137.9249 | 2025-09-20 | 15:15 | 126.9325 | 2025-09-09 | 22:45 | 138.1443 | 2025-08-17 | 10:30 | 123.3473 | 2025-07-12 | 15:15
Bolani | 139.3683 | 2025-07-26 | 5:45 | 130.1309 | 2025-07-19 | 11:45 | 138.6755 | 2025-08-10 | 6:00 | 127.7639 | 2025-08-19 | 12:15 | 137.8672 | 2025-09-04 | 6:00 | 131.2856 | 2025-09-10 | 11:15 | 139.3683 | 2025-07-26 | 5:45 | 127.7639 | 2025-08-19 | 12:15
ChandabaliGIS | 138.1097 | 2025-07-13 | 15:00 | 123.3242 | 2025-07-23 | 23:00 | 137.5035 | 2025-08-24 | 5:45 | 122.539 | 2025-08-12 | 22:30 | 139.2701 | 2025-09-20 | 16:00 | 124.8079 | 2025-09-10 | 22:30 | 139.2701 | 2025-09-20 | 16:00 | 122.539 | 2025-08-12 | 22:30
Chandikhol | 137.8095 | 2025-07-14 | 7:15 | 124.9927 | 2025-07-23 | 22:45 | 136.9435 | 2025-08-17 | 13:30 | 125.8587 | 2025-08-06 | 14:00 | 137.2899 | 2025-09-20 | 16:15 | 126.4937 | 2025-09-11 | 14:45 | 137.8095 | 2025-07-14 | 7:15 | 124.9927 | 2025-07-23 | 22:45
Dhenkikote | 136.5971 | 2025-07-09 | 4:00 | 125.9741 | 2025-07-19 | 22:45 | 136.1929 | 2025-08-30 | 17:15 | 127.302 | 2025-08-21 | 19:15 | 135.5001 | 2025-09-04 | 5:45 | 129.4959 | 2025-09-09 | 22:45 | 136.5971 | 2025-07-09 | 4:00 | 125.9741 | 2025-07-19 | 22:45
DuburiO | 137.1744 | 2025-07-05 | 5:45 | 127.8216 | 2025-07-23 | 22:45 | 136.4816 | 2025-08-15 | 5:45 | 128.4567 | 2025-08-12 | 22:30 | 136.7703 | 2025-09-27 | 5:45 | 127.9371 | 2025-09-11 | 14:45 | 137.1744 | 2025-07-05 | 5:45 | 127.8216 | 2025-07-23 | 22:45
JajpurRoad | 136.9435 | 2025-07-05 | 5:30 | 126.8401 | 2025-07-23 | 22:45 | 136.3661 | 2025-08-15 | 5:45 | 127.5907 | 2025-08-11 | 22:45 | 136.4816 | 2025-09-27 | 5:45 | 127.6484 | 2025-09-11 | 14:45 | 136.9435 | 2025-07-05 | 5:30 | 126.8401 | 2025-07-23 | 22:45
JajpurTown | 137.8095 | 2025-07-09 | 3:45 | 119.508 | 2025-07-23 | 22:45 | 136.2507 | 2025-08-19 | 9:45 | 118.6997 | 2025-08-12 | 22:30 | 137.5785 | 2025-09-20 | 15:15 | 121.3555 | 2025-09-11 | 15:00 | 137.8095 | 2025-07-09 | 3:45 | 118.6997 | 2025-08-12 | 22:30
Jaleswar | 136.828 | 2025-07-06 | 18:00 | 124.2421 | 2025-07-23 | 22:30 | 137.1744 | 2025-08-01 | 17:15 | 124.8772 | 2025-08-12 | 22:30 | 136.7703 | 2025-09-02 | 5:30 | 128.2835 | 2025-09-01 | 21:00 | 137.1744 | 2025-08-01 | 17:15 | 124.2421 | 2025-07-23 | 22:30
Joda | 138.3868 | 2025-07-26 | 5:45 | 130.4196 | 2025-07-19 | 11:45 | 137.5208 | 2025-08-10 | 6:00 | 126.8401 | 2025-08-19 | 10:45 | 137.2899 | 2025-09-10 | 13:15 | 131.2856 | 2025-09-19 | 20:30 | 138.3868 | 2025-07-26 | 5:45 | 126.8401 | 2025-08-19 | 10:45
Karanjia | 136.8857 | 2025-07-09 | 4:15 | 126.4937 | 2025-07-19 | 22:45 | 136.4816 | 2025-08-30 | 17:15 | 127.7061 | 2025-08-21 | 19:30 | 135.7888 | 2025-09-04 | 5:45 | 129.9577 | 2025-09-24 | 19:00 | 136.8857 | 2025-07-09 | 4:15 | 126.4937 | 2025-07-19 | 22:45
Polasponga | 137.3476 | 2025-07-10 | 3:45 | 120.7781 | 2025-07-16 | 9:00 | 136.3661 | 2025-08-19 | 11:00 | 118.5843 | 2025-08-20 | 11:15 | 136.0775 | 2025-09-04 | 6:00 | 120.5472 | 2025-09-15 | 8:15 | 137.3476 | 2025-07-10 | 3:45 | 118.5843 | 2025-08-20 | 11:15
Rairangpur | 138.9664 | 2025-07-09 | 4:15 | 128.7407 | 2025-07-19 | 22:45 | 138.5946 | 2025-08-22 | 11:15 | 128.713 | 2025-08-04 | 12:15 | 139.6454 | 2025-09-22 | 18:30 | 130.0178 | 2025-09-09 | 22:45 | 139.6454 | 2025-09-22 | 18:30 | 128.713 | 2025-08-04 | 12:15
Somnathpur | 137.2899 | 2025-07-01 | 5:45 | 124.6463 | 2025-07-12 | 12:45 | 137.5208 | 2025-08-23 | 6:00 | 124.8195 | 2025-08-12 | 22:45 | 137.5208 | 2025-09-02 | 5:45 | 126.3205 | 2025-09-10 | 23:30 | 137.5208 | 2025-08-23 | 6:00 | 124.6463 | 2025-07-12 | 12:45
Soro | 136.5971 | 2025-07-13 | 14:15 | 118.9307 | 2025-07-23 | 22:30 | 133.6527 | 2025-08-01 | 17:45 | 121.0091 | 2025-08-02 | 22:45 | 134.6919 | 2025-09-27 | 5:30 | 115.8131 | 2025-09-10 | 23:30 | 136.5971 | 2025-07-13 | 14:15 | 115.8131 | 2025-09-10 | 23:30
Udala | 138.4561 | 2025-07-06 | 18:00 | 119.3233 | 2025-07-23 | 13:45 | 138.0346 | 2025-08-24 | 5:45 | 123.6186 | 2025-08-12 | 22:45 | 137.8845 | 2025-09-02 | 5:45 | 125.2294 | 2025-09-10 | 23:30 | 138.4561 | 2025-07-06 | 18:00 | 119.3233 | 2025-07-23 | 13:45
SOUTHCO ZONE
SUBSTATIONS | 2025-07-01 | [5 empty] | 2025-08-01 | [5 empty] | 2025-09-01
| MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM
| KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME
Akhusingh | 139.0842 | 2025-07-07 | 23:00 | 115.0048 | 2025-07-31 | 15:15 | 141.4051 | 2025-08-16 | 16:15 | 116.8199 | 2025-08-01 | 11:00 | 139.3752 | 2025-09-12 | 14:15 | 118.0554 | 2025-09-15 | 14:45 | 141.4051 | 2025-08-16 | 16:15 | 115.0048 | 2025-07-31 | 15:15
Aska | 139.0219 | 2025-07-14 | 4:15 | 128.3412 | 2025-07-22 | 22:30 | 139.0219 | 2025-08-28 | 2:45 | 127.2443 | 2025-08-12 | 22:45 | 139.3105 | 2025-09-27 | 3:45 | 127.6484 | 2025-09-11 | 14:45 | 139.3105 | 2025-09-27 | 3:45 | 127.2443 | 2025-08-12 | 22:45
Berhampur | 138.0981 | 2025-07-05 | 4:00 | 126.1473 | 2025-07-22 | 23:00 | 138.1559 | 2025-08-28 | 3:00 | 125.2813 | 2025-08-12 | 22:45 | 138.3868 | 2025-09-27 | 3:45 | 125.8009 | 2025-09-11 | 14:45 | 138.3868 | 2025-09-27 | 3:45 | 125.2813 | 2025-08-12 | 22:45
Bhanjanagar | 139.6569 | 2025-07-14 | 4:15 | 129.034 | 2025-07-22 | 23:00 | 139.3105 | 2025-08-28 | 3:00 | 128.4567 | 2025-08-12 | 23:00 | 139.5415 | 2025-09-27 | 3:45 | 129.2649 | 2025-09-11 | 14:45 | 139.6569 | 2025-07-14 | 4:15 | 128.4567 | 2025-08-12 | 23:00
Boudh | 138.9757 | 2025-07-06 | 11:30 | 123.6417 | 2025-07-22 | 16:30 | 138.2829 | 2025-08-31 | 0:00 | 118.3302 | 2025-08-11 | 19:00 | 139.8763 | 2025-09-16 | 15:00 | 121.6326 | 2025-09-18 | 16:30 | 139.8763 | 2025-09-16 | 15:00 | 118.3302 | 2025-08-11 | 19:00
Chatrapur | 138.3868 | 2025-07-05 | 4:00 | 127.0133 | 2025-07-22 | 23:00 | 138.6177 | 2025-08-28 | 3:00 | 125.57 | 2025-08-12 | 22:45 | 138.8487 | 2025-09-27 | 3:45 | 126.2051 | 2025-09-11 | 14:45 | 138.8487 | 2025-09-27 | 3:45 | 125.57 | 2025-08-12 | 22:45
Chikiti | 138.2713 | 2025-07-14 | 4:15 | 126.8401 | 2025-07-22 | 23:00 | 138.2713 | 2025-08-28 | 3:00 | 125.6277 | 2025-08-12 | 22:45 | 138.6755 | 2025-09-23 | 15:00 | 126.2628 | 2025-09-11 | 15:00 | 138.6755 | 2025-09-23 | 15:00 | 125.6277 | 2025-08-12 | 22:45
Dabugaon | 137.985 | 2025-07-27 | 5:00 | 130.3365 | 2025-07-15 | 10:00 | 137.4839 | 2025-08-27 | 15:15 | 128.8954 | 2025-08-12 | 12:15 | 137.7171 | 2025-09-27 | 4:15 | 132.0338 | 2025-09-18 | 16:45 | 137.985 | 2025-07-27 | 5:00 | 128.8954 | 2025-08-12 | 12:15
Digapahandi | 140.3497 | 2025-07-05 | 4:00 | 128.9185 | 2025-07-22 | 23:00 | 140.4652 | 2025-08-28 | 3:00 | 127.7639 | 2025-08-12 | 22:45 | 140.8116 | 2025-09-27 | 3:45 | 128.3412 | 2025-09-11 | 14:45 | 140.8116 | 2025-09-27 | 3:45 | 127.7639 | 2025-08-12 | 22:45
Ganjam | 137.9769 | 2025-07-05 | 4:00 | 126.4071 | 2025-07-18 | 22:45 | 138.1443 | 2025-08-28 | 3:00 | 124.9349 | 2025-08-12 | 23:00 | 138.3117 | 2025-09-27 | 3:45 | 125.4834 | 2025-09-11 | 15:00 | 138.3117 | 2025-09-27 | 3:45 | 124.9349 | 2025-08-12 | 23:00
Jayanagar | 139.1373 | 2025-07-26 | 13:00 | 134.2877 | 2025-07-18 | 22:45 | 139.5992 | 2025-08-27 | 16:15 | 133.9991 | 2025-08-05 | 19:45 | 138.5023 | 2025-09-23 | 3:45 | 134.6341 | 2025-09-01 | 10:00 | 139.5992 | 2025-08-27 | 16:15 | 133.9991 | 2025-08-05 | 19:45
Mohana | 142.7861 | 2025-07-01 | 13:15 | 124.1498 | 2025-07-12 | 15:15 | 145.3494 | 2025-08-17 | 4:30 | 121.725 | 2025-08-09 | 9:00 | 143.8715 | 2025-09-02 | 3:45 | 125.9049 | 2025-09-17 | 10:00 | 145.3494 | 2025-08-17 | 4:30 | 121.725 | 2025-08-09 | 9:00
Narendrapur | 142.6591 | 2025-07-14 | 4:15 | 130.9392 | 2025-07-22 | 23:00 | 142.89 | 2025-08-28 | 3:00 | 129.5536 | 2025-08-12 | 22:45 | 143.0055 | 2025-09-27 | 3:45 | 130.0155 | 2025-09-11 | 14:45 | 143.0055 | 2025-09-27 | 3:45 | 129.5536 | 2025-08-12 | 22:45
Paralakhemendi | 135.5579 | 2025-07-17 | 6:00 | 113.2151 | 2025-07-12 | 22:15 | 135.7311 | 2025-08-28 | 3:00 | 115.4667 | 2025-08-01 | 11:00 | 135.5001 | 2025-09-03 | 15:00 | 117.1409 | 2025-09-16 | 15:30 | 135.7311 | 2025-08-28 | 3:00 | 113.2151 | 2025-07-12 | 22:15
Phulbani | 139.2667 | 2025-07-14 | 4:15 | 124.1082 | 2025-07-22 | 23:00 | 137.4377 | 2025-08-28 | 3:00 | 126.2767 | 2025-08-12 | 22:45 | 137.7818 | 2025-09-27 | 3:45 | 126.0411 | 2025-09-11 | 15:00 | 139.2667 | 2025-07-14 | 4:15 | 124.1082 | 2025-07-22 | 23:00
Podagada | 139.8532 | 2025-07-03 | 23:15 | 124.5193 | 2025-07-31 | 15:15 | 140.4767 | 2025-08-17 | 4:00 | 123.5724 | 2025-08-08 | 9:15 | 140.1073 | 2025-09-12 | 21:00 | 125.8818 | 2025-09-16 | 15:30 | 140.4767 | 2025-08-17 | 4:00 | 123.5724 | 2025-08-08 | 9:15
Potangi | 139.5761 | 2025-07-25 | 3:30 | 132.6481 | 2025-07-07 | 17:45 | 139.807 | 2025-08-27 | 15:30 | 129.0455 | 2025-08-26 | 6:45 | 139.5068 | 2025-09-11 | 4:30 | 127.8909 | 2025-09-06 | 14:45 | 139.807 | 2025-08-27 | 15:30 | 127.8909 | 2025-09-06 | 14:45
Purushottampur | 137.4746 | 2025-07-23 | 17:00 | 125.6739 | 2025-07-22 | 23:00 | 137.082 | 2025-08-28 | 3:00 | 124.1267 | 2025-08-12 | 22:45 | 137.7517 | 2025-09-23 | 15:00 | 118.6305 | 2025-09-06 | 13:00 | 137.7517 | 2025-09-23 | 15:00 | 118.6305 | 2025-09-06 | 13:00
Rayagada | 142.2549 | 2025-07-03 | 23:15 | 121.3786 | 2025-07-31 | 15:15 | 143.3634 | 2025-08-22 | 12:45 | 122.8334 | 2025-08-09 | 9:00 | 143.4558 | 2025-09-12 | 14:15 | 124.5885 | 2025-09-16 | 15:30 | 143.4558 | 2025-09-12 | 14:15 | 121.3786 | 2025-07-31 | 15:15
Sunabeda | 138.0981 | 2025-07-26 | 3:15 | 131.0316 | 2025-07-07 | 17:45 | 138.1905 | 2025-08-27 | 16:15 | 132.1401 | 2025-08-05 | 6:45 | 137.6825 | 2025-09-03 | 2:45 | 131.7475 | 2025-09-13 | 13:30 | 138.1905 | 2025-08-27 | 16:15 | 131.0316 | 2025-07-07 | 17:45
Tentulikhunti | 138.3868 | 2025-07-26 | 13:00 | 131.6897 | 2025-07-15 | 10:00 | 138.4445 | 2025-08-27 | 15:15 | 131.1701 | 2025-08-27 | 19:00 | 138.1559 | 2025-09-03 | 3:45 | 133.364 | 2025-09-12 | 11:15 | 138.4445 | 2025-08-27 | 15:15 | 131.1701 | 2025-08-27 | 19:00
Therubali | 140.8693 | 2025-07-14 | 4:00 | 132.8444 | 2025-07-23 | 22:45 | 140.5229 | 2025-08-31 | 0:00 | 132.7289 | 2025-08-12 | 23:00 | 140.292 | 2025-09-03 | 5:15 | 134.1723 | 2025-09-11 | 12:30 | 140.8693 | 2025-07-14 | 4:00 | 132.7289 | 2025-08-12 | 23:00
Umerkote | 135.5348 | 2025-07-18 | 3:00 | 125.0273 | 2025-07-15 | 10:00 | 134.7265 | 2025-08-27 | 15:15 | 124.9811 | 2025-08-12 | 12:15 | 135.9735 | 2025-09-03 | 2:30 | 128.6068 | 2025-09-20 | 10:30 | 135.9735 | 2025-09-03 | 2:30 | 124.9811 | 2025-08-12 | 12:15
| 142.7861 |  |  | 113.2151 |  |  | 145.3494 |  |  | 115.4667 |  |  | 143.8715 |  |  | 115.8131

## Page-66
132KV VOLTAGE AT DIFFERENT GRID SUBSTATIONS
WESCO ZONE
SUBSTATIONS | 2025-07-01 | [5 empty] | 2025-08-01 | [5 empty] | 2025-09-01
| MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM
| KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME
Barapalli | 136.3661 | 2025-07-09 | 4:15 | 120.4895 | 2025-07-22 | 16:30 | 137.2899 | 2025-08-31 | 0:00 | 116.3327 | 2025-08-11 | 19:00 | 138.0404 | 2025-09-16 | 15:30 | 116.9677 | 2025-09-11 | 16:45 | 138.0404 | 2025-09-16 | 15:30 | 116.3327 | 2025-08-11 | 19:00
Bargarh | 135.5001 | 2025-07-09 | 4:30 | 121.0668 | 2025-07-22 | 16:30 | 135.3847 | 2025-08-13 | 19:30 | 113.6769 | 2025-08-04 | 16:45 | 138.8487 | 2025-09-26 | 20:00 | 113.5615 | 2025-09-11 | 16:45 | 138.8487 | 2025-09-26 | 20:00 | 113.5615 | 2025-09-11 | 16:45
Bhawanipatna | 140.5702 | 2025-07-05 | 18:00 | 127.8079 | 2025-07-22 | 19:30 | 140.2534 | 2025-08-24 | 4:15 | 124.4226 | 2025-08-11 | 19:00 | 140.9529 | 2025-09-27 | 4:00 | 126.4023 | 2025-09-18 | 18:45 | 140.9529 | 2025-09-27 | 4:00 | 124.4226 | 2025-08-11 | 19:00
Bolangir | 137.6363 | 2025-07-10 | 3:30 | 126.4937 | 2025-07-22 | 16:30 | 137.5785 | 2025-08-31 | 0:00 | 122.2215 | 2025-08-11 | 19:00 | 138.56 | 2025-09-16 | 15:00 | 125.57 | 2025-09-18 | 16:30 | 138.56 | 2025-09-16 | 15:00 | 122.2215 | 2025-08-11 | 19:00
Brajarajnagar | 138.1674 | 2025-07-06 | 2:45 | 132.5788 | 2025-07-23 | 11:45 | 137.3822 | 2025-08-23 | 6:00 | 132.9714 | 2025-08-24 | 12:00 | 137.4515 | 2025-09-04 | 5:45 | 130.4311 | 2025-09-13 | 15:45 | 138.1674 | 2025-07-06 | 2:45 | 130.4311 | 2025-09-13 | 15:45
Budhipadar | 136.2507 | 2025-07-07 | 5:15 | 131.1124 | 2025-07-24 | 12:30 | 135.1537 | 2025-08-23 | 4:30 | 131.632 | 2025-08-05 | 19:30 | 135.2692 | 2025-09-04 | 5:45 | 131.1124 | 2025-09-08 | 15:30 | 136.2507 | 2025-07-07 | 5:15 | 131.1124 | 2025-07-24 | 12:30
Chend | 136.7125 | 2025-07-14 | 4:00 | 130.8237 | 2025-07-21 | 15:00 | 136.4239 | 2025-08-31 | 0:00 | 131.6897 | 2025-08-12 | 15:15 | 135.3269 | 2025-09-02 | 4:00 | 130.3041 | 2025-09-19 | 11:00 | 136.7125 | 2025-07-14 | 4:00 | 130.3041 | 2025-09-19 | 11:00
ChipilimaP.H. | 136.9897 | 2025-07-07 | 5:00 | 131.0316 | 2025-07-22 | 21:45 | 135.3731 | 2025-08-29 | 4:00 | 129.5536 | 2025-08-05 | 19:15 | 136.9897 | 2025-09-23 | 19:15 | 128.9763 | 2025-09-11 | 16:15 | 136.9897 | 2025-07-07 | 5:00 | 128.9763 | 2025-09-11 | 16:15
Ghens | 136.5393 | 2025-07-09 | 4:30 | 122.8565 | 2025-07-22 | 16:30 | 132.9599 | 2025-08-01 | 3:15 | 114.6584 | 2025-08-04 | 16:45 | 139.1951 | 2025-09-23 | 20:00 | 122.5101 | 2025-09-20 | 16:30 | 139.1951 | 2025-09-23 | 20:00 | 114.6584 | 2025-08-04 | 16:45
Jharsuguda | 136.3084 | 2025-07-07 | 5:15 | 131.0547 | 2025-07-24 | 12:30 | 135.2115 | 2025-08-23 | 3:45 | 131.5743 | 2025-08-05 | 16:45 | 135.3847 | 2025-09-04 | 5:45 | 129.6113 | 2025-09-12 | 8:45 | 136.3084 | 2025-07-07 | 5:15 | 129.6113 | 2025-09-12 | 8:45
Jayapatna | 139.3105 | 2025-07-17 | 6:00 | 131.4011 | 2025-07-22 | 14:45 | 137.7517 | 2025-08-27 | 16:15 | 131.8052 | 2025-08-12 | 23:00 | 138.2713 | 2025-09-10 | 18:00 | 127.8216 | 2025-09-02 | 13:00 | 139.3105 | 2025-07-17 | 6:00 | 127.8216 | 2025-09-02 | 13:00
Junagarah | 138.2136 | 2025-07-05 | 18:00 | 126.0319 | 2025-07-22 | 19:30 | 137.5785 | 2025-08-24 | 4:15 | 122.5101 | 2025-08-11 | 19:00 | 138.0404 | 2025-09-27 | 3:45 | 124.8195 | 2025-09-18 | 18:45 | 138.2136 | 2025-07-05 | 18:00 | 122.5101 | 2025-08-11 | 19:00
Kalunga | 137.1282 | 2025-07-14 | 4:00 | 116.8234 | 2025-07-24 | 10:30 | 136.4585 | 2025-08-31 | 0:00 | 120.5357 | 2025-08-29 | 15:00 | 135.5752 | 2025-09-11 | 17:15 | 118.8325 | 2025-09-20 | 11:45 | 137.1282 | 2025-07-14 | 4:00 | 116.8234 | 2025-07-24 | 10:30
Kantabanji | 141.1926 | 2025-07-29 | 13:15 | 122.972 | 2025-07-22 | 21:45 | 141.8393 | 2025-08-21 | 13:00 | 123.965 | 2025-08-11 | 19:00 | 142.8323 | 2025-09-22 | 19:30 | 122.718 | 2025-09-20 | 18:30 | 142.8323 | 2025-09-22 | 19:30 | 122.718 | 2025-09-20 | 18:30
Katapali | 137.6363 | 2025-07-07 | 5:00 | 132.7289 | 2025-07-22 | 21:45 | 136.3084 | 2025-08-23 | 4:30 | 131.2279 | 2025-08-05 | 16:30 | 137.1167 | 2025-09-23 | 18:45 | 131.1701 | 2025-09-11 | 16:15 | 137.6363 | 2025-07-07 | 5:00 | 131.1701 | 2025-09-11 | 16:15
Kesinga | 136.7125 | 2025-07-05 | 18:00 | 125.1081 | 2025-07-22 | 19:30 | 136.5393 | 2025-08-24 | 4:15 | 122.8565 | 2025-08-11 | 19:00 | 137.1167 | 2025-09-16 | 14:45 | 124.704 | 2025-09-18 | 18:45 | 137.1167 | 2025-09-16 | 14:45 | 122.8565 | 2025-08-11 | 19:00
Khariar | 141.4236 | 2025-07-05 | 18:00 | 126.436 | 2025-07-22 | 21:45 | 141.77 | 2025-08-24 | 2:45 | 122.7411 | 2025-08-04 | 16:45 | 145.4418 | 2025-09-11 | 19:30 | 127.0595 | 2025-09-18 | 18:45 | 145.4418 | 2025-09-11 | 19:30 | 122.7411 | 2025-08-04 | 16:45
Kuchinda | 141.1575 | 2025-07-05 | 22:15 | 130.7708 | 2025-07-30 | 21:15 | 135.6078 | 2025-08-08 | 4:45 | 126.8642 | 2025-08-27 | 16:15 | 138.7753 | 2025-09-24 | 13:15 | 122.7069 | 2025-09-19 | 11:15 | 141.1575 | 2025-07-05 | 22:15 | 122.7069 | 2025-09-19 | 11:15
Lapanga | 136.7703 | 2025-07-07 | 5:15 | 130.3619 | 2025-07-23 | 19:30 | 135.5579 | 2025-08-29 | 4:00 | 130.5928 | 2025-08-03 | 21:00 | 135.5579 | 2025-09-04 | 5:30 | 128.9763 | 2025-09-22 | 8:30 | 136.7703 | 2025-07-07 | 5:15 | 128.9763 | 2025-09-22 | 8:30
Maneswar | 138.6939 | 2025-07-07 | 5:00 | 129.4543 | 2025-07-22 | 21:45 | 134.8096 | 2025-08-25 | 3:15 | 127.0641 | 2025-08-16 | 15:30 | 135.4609 | 2025-09-23 | 18:45 | 127.8678 | 2025-09-09 | 10:00 | 138.6939 | 2025-07-07 | 5:00 | 127.0641 | 2025-08-16 | 15:30
Nuapada | 139.7147 | 2025-07-03 | 4:45 | 123.4108 | 2025-07-24 | 19:00 | 145.234 | 2025-08-12 | 13:15 | 118.7459 | 2025-08-31 | 18:30 | 139.0681 | 2025-09-26 | 13:15 | 119.8544 | 2025-09-10 | 16:45 | 145.234 | 2025-08-12 | 13:15 | 118.7459 | 2025-08-31 | 18:30
Padampur | 137.7113 | 2025-07-10 | 3:00 | 122.4293 | 2025-07-22 | 16:45 | 135.4713 | 2025-08-23 | 13:15 | 113.4575 | 2025-08-11 | 19:15 | 140.3209 | 2025-09-06 | 12:45 | 121.4017 | 2025-09-18 | 19:00 | 140.3209 | 2025-09-06 | 12:45 | 113.4575 | 2025-08-11 | 19:15
Patnagarh | 136.828 | 2025-07-10 | 3:00 | 123.5493 | 2025-07-22 | 19:30 | 135.4424 | 2025-08-23 | 13:00 | 117.0832 | 2025-08-11 | 19:00 | 137.4631 | 2025-09-06 | 12:45 | 122.6833 | 2025-09-18 | 16:45 | 137.4631 | 2025-09-06 | 12:45 | 117.0832 | 2025-08-11 | 19:00
Rairakhol | 138.0404 | 2025-07-01 | 4:45 | 125.8587 | 2025-07-22 | 21:45 | 135.7311 | 2025-08-25 | 3:15 | 125.1081 | 2025-08-16 | 15:30 | 134.1723 | 2025-09-02 | 13:15 | 123.6071 | 2025-09-08 | 16:00 | 138.0404 | 2025-07-01 | 4:45 | 123.6071 | 2025-09-08 | 16:00
Rajgangpur | 136.7125 | 2025-07-30 | 5:45 | 129.3804 | 2025-07-21 | 14:45 | 136.4816 | 2025-08-31 | 0:00 | 130.1887 | 2025-08-29 | 16:15 | 137.3476 | 2025-09-23 | 19:15 | 129.2649 | 2025-09-19 | 11:00 | 137.3476 | 2025-09-23 | 19:15 | 129.2649 | 2025-09-19 | 11:00
Rourkela | 136.7125 | 2025-07-14 | 4:00 | 130.8237 | 2025-07-21 | 15:15 | 136.4239 | 2025-08-31 | 0:00 | 131.8629 | 2025-08-12 | 15:15 | 135.3847 | 2025-09-02 | 0:15 | 130.3041 | 2025-09-19 | 11:00 | 136.7125 | 2025-07-14 | 4:00 | 130.3041 | 2025-09-19 | 11:00
Sadeipali | 139.8301 | 2025-07-10 | 3:30 | 129.2649 | 2025-07-22 | 16:30 | 140.1765 | 2025-08-31 | 0:00 | 124.7617 | 2025-08-11 | 19:00 | 141.1003 | 2025-09-16 | 15:00 | 127.8793 | 2025-09-18 | 16:45 | 141.1003 | 2025-09-16 | 15:00 | 124.7617 | 2025-08-11 | 19:00
Sambalpur | 137.5208 | 2025-07-07 | 5:00 | 130.9392 | 2025-07-22 | 21:45 | 135.3847 | 2025-08-25 | 3:15 | 129.0917 | 2025-08-12 | 12:30 | 136.3661 | 2025-09-23 | 19:15 | 129.1495 | 2025-09-09 | 10:00 | 137.5208 | 2025-07-07 | 5:00 | 129.0917 | 2025-08-12 | 12:30
Sonepur | 135.2692 | 2025-07-10 | 3:30 | 121.5864 | 2025-07-22 | 19:30 | 135.2115 | 2025-08-31 | 0:00 | 116.6791 | 2025-08-11 | 19:00 | 137.2321 | 2025-09-06 | 12:45 | 120.0853 | 2025-09-18 | 16:30 | 137.2321 | 2025-09-06 | 12:45 | 116.6791 | 2025-08-11 | 19:00
Sundargarah | 137.0012 | 2025-07-06 | 1:00 | 131.5165 | 2025-07-24 | 12:30 | 135.9043 | 2025-08-23 | 4:15 | 132.0361 | 2025-08-05 | 19:30 | 136.2507 | 2025-09-04 | 5:45 | 130.7083 | 2025-09-08 | 15:30 | 137.0012 | 2025-07-06 | 1:00 | 130.7083 | 2025-09-08 | 15:30
Tusura | 136.8742 | 2025-07-30 | 11:15 | 124.1959 | 2025-07-22 | 19:30 | 136.3199 | 2025-08-24 | 4:15 | 120.6627 | 2025-08-11 | 19:00 | 137.4284 | 2025-09-11 | 19:45 | 122.3716 | 2025-09-18 | 19:00 | 137.4284 | 2025-09-11 | 19:45 | 120.6627 | 2025-08-11 | 19:00
| 141.4236 |  |  | 116.8234 |  |  | 145.234 |  |  | 113.4575 |  |  | 145.4418 |  |  | 113.5615

## Page-67
400KV VOLTAGE AT DIFFERENT GRID SUBSTATIONS
SUBSTATIONS | 2025-07-01 | [5 empty] | 2025-08-01 | [5 empty] | 2025-09-01
| MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM
| KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME
Duburi Old | 415.6345 | 2025-07-12 | 282:00 | 396.5819 | 2025-07-19 | 454:45 | 414.8839 | 2025-08-15 | 341:45 | 398.314 | 2025-08-12 | 286:30 | 415.1148 | 2025-09-27 | 629:45 | 394.0416 | 2025-09-11 | 254:45
Lapanga | 418.9254 | 2025-07-07 | 149:45 | 401.2584 | 2025-07-22 | 524:15 | 412.4013 | 2025-08-13 | 288:45 | 404.8957 | 2025-08-01 | 6:30 | 411.7085 | 2025-09-23 | 541:30 | 404.7225 | 2025-09-08 | 175:00
Mendhasal | 414.8319 | 2025-07-23 | 534:00 | 392.8522 | 2025-07-18 | 430:30 | 417.7071 | 2025-08-15 | 341:45 | 393.8106 | 2025-08-12 | 286:45 | 415.6518 | 2025-09-27 | 629:45 | 391.0855 | 2025-09-11 | 254:45
Meramundali | 413.0364 | 2025-07-23 | 534:00 | 399.0068 | 2025-07-18 | 430:30 | 414.1333 | 2025-08-15 | 341:45 | 399.8151 | 2025-08-12 | 286:45 | 413.4405 | 2025-09-27 | 629:45 | 389.4805 | 2025-09-11 | 254:45
220KV VOLTAGE AT DIFFERENT GRID SUBSTATIONS
SUBSTATIONS | 2025-07-01 | [5 empty] | 2025-08-01 | [5 empty] | 2025-09-01
| MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM |  |  | MAXIMUM |  |  | MINIMUM
| KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | KV | DATE | TIME | MAXIMUM |  |  | MINIMUM
AskaN | 232.7923 | 2025-07-14 | 4:15 | 215.2761 | 2025-07-22 | 23:00 | 232.5499 | 2025-08-28 | 3:00 | 214.0637 | 2025-08-12 | 23:00 | 232.7981 | 2025-09-27 | 3:45 | 214.9816 | 2025-09-11 | 15:00 | 232.7981 | 2025-09-27 | 3:45 | 214.0637 | 2025-08-12 | 23:00
Atri | 229.3457 | 2025-07-05 | 4:00 | 213.0591 | 2025-07-18 | 22:30 | 230.1424 | 2025-08-15 | 5:45 | 212.2739 | 2025-08-12 | 22:45 | 229.975 | 2025-09-27 | 3:45 | 212.2277 | 2025-09-11 | 14:45 | 230.1424 | 2025-08-15 | 5:45 | 212.2277 | 2025-09-11 | 14:45
Balasore | 229.8941 | 2025-07-06 | 18:00 | 209.0524 | 2025-07-12 | 12:45 | 230.1828 | 2025-08-23 | 6:00 | 205.242 | 2025-08-11 | 15:45 | 229.6055 | 2025-09-02 | 5:45 | 213.3247 | 2025-09-10 | 23:30 | 230.1828 | 2025-08-23 | 6:00 | 205.242 | 2025-08-11 | 15:45
Balimela | 242.1336 | 2025-07-27 | 13:30 | 235.2056 | 2025-07-22 | 14:45 | 242.7109 | 2025-08-27 | 15:45 | 234.686 | 2025-08-05 | 14:45 | 240.1129 | 2025-09-01 | 4:00 | 235.1479 | 2025-09-08 | 12:15 | 242.7109 | 2025-08-27 | 15:45 | 234.686 | 2025-08-05 | 14:45
Barkote | 230.9333 | 2025-07-06 | 16:15 | 226.7765 | 2025-07-02 | 22:45 | 233.6468 | 2025-08-24 | 13:45 | 227.0652 | 2025-08-26 | 23:15 | 232.7231 | 2025-09-27 | 3:45 | 225.2177 | 2025-09-01 | 10:00 | 233.6468 | 2025-08-24 | 13:45 | 225.2177 | 2025-09-01 | 10:00
Bargarh | 226.6611 | 2025-07-08 | 4:15 | 208.5328 | 2025-07-21 | 16:30 | 226.3724 | 2025-08-12 | 19:30 | 197.448 | 2025-08-04 | 8:30 | 229.49 | 2025-09-23 | 20:15 | 201.9512 | 2025-09-10 | 17:00 | 229.49 | 2025-09-23 | 20:15 | 197.448 | 2025-08-04 | 8:30
Bhadrak | 227.2961 | 2025-07-05 | 6:00 | 205.7039 | 2025-07-22 | 14:30 | 227.8157 | 2025-08-23 | 6:00 | 206.4544 | 2025-08-12 | 22:30 | 226.892 | 2025-09-27 | 5:45 | 207.4359 | 2025-09-11 | 14:45 | 227.8157 | 2025-08-23 | 6:00 | 205.7039 | 2025-07-22 | 14:30
Bhanjanagar | 232.4344 | 2025-07-14 | 4:15 | 215.8649 | 2025-07-22 | 23:00 | 232.088 | 2025-08-28 | 3:00 | 214.8257 | 2025-08-12 | 22:45 | 232.4921 | 2025-09-27 | 3:45 | 216.0381 | 2025-09-11 | 14:45 | 232.4921 | 2025-09-27 | 3:45 | 214.8257 | 2025-08-12 | 22:45
Bidanasi | 231.6954 | 2025-07-05 | 4:00 | 213.6018 | 2025-07-18 | 22:30 | 232.0995 | 2025-08-16 | 5:30 | 212.857 | 2025-08-12 | 22:45 | 231.9841 | 2025-09-27 | 3:45 | 213.0014 | 2025-09-11 | 14:45 | 232.0995 | 2025-08-16 | 5:30 | 212.857 | 2025-08-12 | 22:45
BolangirN | 229.0281 | 2025-07-09 | 4:15 | 213.9597 | 2025-07-28 | 19:15 | 230.356 | 2025-08-31 | 4:45 | 208.9369 | 2025-08-11 | 19:00 | 231.9725 | 2025-09-16 | 15:00 | 212.8051 | 2025-09-18 | 16:45 | 231.9725 | 2025-09-16 | 15:00 | 208.9369 | 2025-08-11 | 19:00
Budhipadar | 229.7787 | 2025-07-07 | 5:15 | 224.1785 | 2025-07-23 | 11:45 | 228.1044 | 2025-08-23 | 4:15 | 198.5449 | 2025-08-13 | 23:15 | 227.8157 | 2025-09-11 | 16:15 | 223.6012 | 2025-09-10 | 11:30 | 229.7787 | 2025-07-07 | 5:15 | 198.5449 | 2025-08-13 | 23:15
Chandaka | 224.8482 | 2025-07-05 | 4:00 | 206.9163 | 2025-07-18 | 22:30 | 224.7847 | 2025-08-16 | 5:30 | 206.3967 | 2025-08-12 | 22:45 | 223.9245 | 2025-09-27 | 3:45 | 205.8597 | 2025-09-11 | 14:45 | 224.8482 | 2025-07-05 | 4:00 | 205.8597 | 2025-09-11 | 14:45
Cuttack | 227.1807 | 2025-07-01 | 4:30 | 209.2256 | 2025-07-18 | 22:30 | 227.5155 | 2025-08-16 | 4:00 | 208.325 | 2025-08-12 | 22:45 | 227.9254 | 2025-09-27 | 3:45 | 207.2511 | 2025-09-11 | 14:45 | 227.9254 | 2025-09-27 | 3:45 | 207.2511 | 2025-09-11 | 14:45
Duburi Old | 226.3724 | 2025-07-14 | 6:00 | 213.4401 | 2025-07-19 | 22:45 | 226.3147 | 2025-08-15 | 5:45 | 213.4401 | 2025-08-12 | 22:30 | 226.7765 | 2025-09-27 | 5:45 | 213.2092 | 2025-09-11 | 14:45 | 226.7765 | 2025-09-27 | 5:45 | 213.2092 | 2025-09-11 | 14:45
Duburi New | 229.3745 | 2025-07-05 | 6:00 | 214.8257 | 2025-07-19 | 22:45 | 228.2199 | 2025-08-15 | 5:45 | 214.8835 | 2025-08-12 | 22:30 | 228.3353 | 2025-09-27 | 5:45 | 214.8835 | 2025-09-11 | 14:45 | 229.3745 | 2025-07-05 | 6:00 | 214.8257 | 2025-07-19 | 22:45
Infocity-II GIS | 229.617 | 2025-07-05 | 4:00 | 213.4979 | 2025-07-18 | 22:30 | 230.483 | 2025-08-16 | 5:30 | 212.8282 | 2025-08-12 | 22:45 | 230.3214 | 2025-09-27 | 3:45 | 212.7877 | 2025-09-11 | 14:45 | 230.483 | 2025-08-16 | 5:30 | 212.7877 | 2025-09-11 | 14:45
Jayanagar | 238.5541 | 2025-07-26 | 13:15 | 230.6447 | 2025-07-21 | 22:00 | 239.5933 | 2025-08-27 | 15:15 | 229.49 | 2025-08-05 | 22:30 | 237.1108 | 2025-09-01 | 4:00 | 230.8179 | 2025-09-09 | 18:45 | 239.5933 | 2025-08-27 | 15:15 | 229.49 | 2025-08-05 | 22:30
Joda | 229.1436 | 2025-07-26 | 5:45 | 216.9619 | 2025-07-19 | 11:45 | 228.0467 | 2025-08-10 | 6:00 | 217.8856 | 2025-08-18 | 12:30 | 227.9889 | 2025-09-10 | 13:00 | 219.3289 | 2025-09-11 | 19:15 | 229.1436 | 2025-07-26 | 5:45 | 216.9619 | 2025-07-19 | 11:45
Katapalli | 229.9519 | 2025-07-07 | 5:15 | 218.7516 | 2025-07-22 | 20:00 | 226.4301 | 2025-08-23 | 4:30 | 214.9989 | 2025-08-05 | 16:45 | 227.5848 | 2025-09-23 | 20:15 | 216.4423 | 2025-09-11 | 16:45 | 229.9519 | 2025-07-07 | 5:15 | 214.9989 | 2025-08-05 | 16:45
KeonjharGIS | 225.1023 | 2025-07-01 | 5:15 | 223.0239 | 2025-07-01 | 9:30 | 223.8899 | 2025-08-15 | 5:45 | 212.8051 | 2025-08-21 | 19:15 | 223.7744 | 2025-09-02 | 4:00 | 215.9227 | 2025-09-01 | 10:00 | 225.1023 | 2025-07-01 | 5:15 | 212.8051 | 2025-08-21 | 19:15
Lapanga | 233.3004 | 2025-07-07 | 5:15 | 225.5641 | 2025-07-22 | 20:00 | 230.4715 | 2025-08-23 | 4:30 | 225.1023 | 2025-08-05 | 19:30 | 230.4137 | 2025-09-24 | 6:00 | 225.5641 | 2025-09-08 | 16:15 | 233.3004 | 2025-07-07 | 5:15 | 225.1023 | 2025-08-05 | 19:30
Laxmipur | 237.9191 | 2025-07-14 | 4:15 | 228.0467 | 2025-07-23 | 22:45 | 238.9005 | 2025-08-27 | 16:30 | 227.9889 | 2025-08-12 | 23:00 | 237.2263 | 2025-09-03 | 2:45 | 230.1828 | 2025-09-11 | 12:30 | 238.9005 | 2025-08-27 | 16:30 | 227.9889 | 2025-08-12 | 23:00
Malkangiri | 242.9015 | 2025-07-27 | 13:30 | 235.8291 | 2025-07-22 | 15:15 | 243.3864 | 2025-08-27 | 15:45 | 235.4308 | 2025-08-05 | 14:45 | 240.9154 | 2025-09-01 | 4:00 | 235.8233 | 2025-09-08 | 12:15 | 243.3864 | 2025-08-27 | 15:45 | 235.4308 | 2025-08-05 | 14:45
Mendhasal | 229.4842 | 2025-07-05 | 4:00 | 213.3882 | 2025-07-18 | 22:30 | 230.3098 | 2025-08-16 | 5:30 | 212.6954 | 2025-08-12 | 22:45 | 230.1655 | 2025-09-27 | 3:45 | 209.8145 | 2025-09-03 | 14:00 | 230.3098 | 2025-08-16 | 5:30 | 209.8145 | 2025-09-03 | 14:00
Meramundali | 228.1044 | 2025-07-27 | 6:15 | 220.5413 | 2025-07-18 | 23:00 | 227.5848 | 2025-08-15 | 6:00 | 219.2712 | 2025-08-12 | 11:30 | 227.0075 | 2025-09-28 | 13:30 | 218.2897 | 2025-09-11 | 14:45 | 228.1044 | 2025-07-27 | 6:15 | 218.2897 | 2025-09-11 | 14:45
Narsinghpur | 226.3147 | 2025-07-05 | 4:00 | 214.691 | 2025-07-18 | 23:00 | 225.6604 | 2025-08-16 | 5:30 | 215.2684 | 2025-08-20 | 19:00 | 226.0452 | 2025-09-16 | 3:15 | 214.9604 | 2025-09-08 | 14:30 | 226.3147 | 2025-07-05 | 4:00 | 214.691 | 2025-07-18 | 23:00
Narendrapur | 230.6447 | 2025-07-14 | 4:15 | 212.5741 | 2025-07-22 | 23:00 | 231.0488 | 2025-08-28 | 3:00 | 210.8421 | 2025-08-12 | 22:45 | 231.1065 | 2025-09-27 | 3:45 | 210.8999 | 2025-09-11 | 14:45 | 231.1065 | 2025-09-27 | 3:45 | 210.8421 | 2025-08-12 | 22:45
Nayagarh | 230.9718 | 2025-07-01 | 4:30 | 207.8015 | 2025-07-22 | 23:00 | 231.1989 | 2025-08-16 | 5:30 | 212.6665 | 2025-08-12 | 22:45 | 231.4703 | 2025-09-27 | 3:45 | 213.8789 | 2025-09-11 | 14:45 | 231.4703 | 2025-09-27 | 3:45 | 207.8015 | 2025-07-22 | 23:00
Paradeep | 226.5456 | 2025-07-05 | 6:00 | 204.8379 | 2025-07-23 | 22:45 | 224.3517 | 2025-08-08 | 9:00 | 202.8749 | 2025-08-12 | 22:45 | 225.5064 | 2025-09-20 | 16:15 | 206.6276 | 2025-09-10 | 23:00 | 226.5456 | 2025-07-05 | 6:00 | 202.8749 | 2025-08-12 | 22:45
Tarkera | 231.5107 | 2025-07-30 | 6:00 | 224.294 | 2025-07-21 | 15:15 | 230.4715 | 2025-08-31 | 5:00 | 225.3909 | 2025-08-11 | 20:45 | 229.8941 | 2025-09-02 | 4:00 | 222.7929 | 2025-09-19 | 11:00 | 231.5107 | 2025-07-30 | 6:00 | 222.7929 | 2025-09-19 | 11:00
Theruvali | 238.2655 | 2025-07-14 | 4:15 | 223.6012 | 2025-07-23 | 22:45 | 236.7067 | 2025-08-27 | 16:30 | 223.5435 | 2025-08-12 | 23:00 | 236.1293 | 2025-09-03 | 4:15 | 226.6033 | 2025-09-11 | 12:30 | 238.2655 | 2025-07-14 | 4:15 | 223.5435 | 2025-08-12 | 23:00
Rengali | 227.0652 | 2025-07-06 | 16:15 | 222.0424 | 2025-07-18 | 23:00 | 227.0075 | 2025-08-24 | 14:00 | 221.4073 | 2025-08-12 | 23:00 | 226.6033 | 2025-09-18 | 3:15 | 220.4259 | 2025-09-01 | 10:00 | 227.0652 | 2025-07-06 | 16:15 | 220.4259 | 2025-09-01 | 10:00
| 242.9015 |  |  | 204.8379 |  |  | 243.3864 |  |  | 197.448 |  |  | 240.9154 |  |  | 201.9512 |  |  | 243.3864 |  |  | 197.448
[12 empty] | OLD DATA | 255.8164 | 2025-03-05 | 11:30

## Page-68
Percentage of time voltage in the Quarter was beyond levels permitted under CEA (Grid Standards) Regulations, 2010.
Name of the Grid Sub-station | Hours in the Quarter | 400 kV |  |  |  | 220 kV |  |  |  | 132 kV |  |  |  | Maximum continuous period of deviation : with date and time* |  | Reasons for such deviation** | Tap position in concerned transformer during extreme condition.
|  | Hours in the Quarter voltage went beyond 420 kV | % | Hours in the Quarter voltage went below 380 kV | % | Hours in the Quarter voltage went beyond 245 kV | % | Hours in the Quarter voltage went below 198 kV | % | Hours in the Quarter voltage went beyond 145 kV | % | Hours in the Quarter voltage went below 122 kV | % | 220 kV | 132 kV |  | Auto Transformer | Power Transformer
1 | 2 | 3 | 4 | 5 | 6 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Balasore |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bhanjanagar |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bidanasi |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bolangir New |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Budhipadar |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chandaka |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cuttack |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Duburi New |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jayanagar |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Joda |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mendhasal |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meramundali |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Narendrapur |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tarkera |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Theruvali |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*Data relates to those Sub-stations where analog instrument facilities are available.
**Specific reasons, if any, may be mentioned.
Data for the above sub-stations could not be furnished for want of analog facilities.

## Page-69
GENERATION CAPACITY
SL.NO. | NAME OF POWER STATION | INSTALLED CAPACITY IN MW | FIRM POWER IN MW
1 | O.H.P.C.
HIRAKUD POWER STATION
| (a)BURLA | 2 x 49.5 = 99 | 134
2 x 32 = 64 287.8
1 x 37.5 = 37.5
2 x 43.65 = 87.3
| (b)CHIPLIMA | 3 x 24 = 72
| BALIMELA POWER HOUSE | 6 x 60+2 x75 = 510 | 135
| RENGALI POWER HOUSE | 5 x 50 = 250 | 60
| UPPER KOLAB POWER HOUSE | 4 x 80 = 320 | 95
| INDRAVATI POWER HOUSE | 4 x 150 = 600 | 224
| MACHHKUND POWER HOUSE | 3 x 17 = 51 60 | 60
| ( Orissa Share 30% purchase upto 20% extra) | 3 x 23 = 69
| TOTAL HYDRO , (A) | 2099.8
2 | O.P.G.C.
| IB TPS STAGE-I | 2 x 210 = 420 | 342.09
| IB TPS STAGE-II | 2 X 660 = 1320 | 680
| TOTAL THERMAL , (B) | 1740
IPP CAPACITY
SL.NO. | NAME OF POWER STATION | INSTALLED CAPACITY IN MW | SHARE OF INSTALLED CAPACITY OF GRIDCO |  | AUX. CONS. | % AGE AVAILABILITY(excluding UA)
|  |  | SHARE IN % | MW
1 | STERLITE | 1 X 600 = 600 | 100 | 600
2 | GMR | 3 X 350 = 1050 | 25 | 262.5
3 | NBVL IPP | 1 X 60 = 60 | 12 | 7.2
4 | JITPL | 2 X 600 = 1200 | 12 | 144
| TOTAL IPP , (C) |  |  | 1013.7
RENEWABLE CAPACITY
SL.NO. | NAME OF POWER STATION | INSTALLED CAPACITY IN MW
1 | SMALL HYDRO | 115.6
2 | BIOMASS | 59.2
3 | SOLAR | 409.2
| TOTAL IPP , (D) | 584
CENTRAL SECTOR GENERATION
SL.NO. | NAME OF POWER STATION | INSTALLED CAPACITY IN MW | SHARE OF INSTALLED CAPACITY OF GRIDCO |  | AUX. CONS. | % AGE AVAILABILITY(excluding UA)
|  |  | SHARE IN % | MW
1 | CHUKHA (BHUTAN) | 4 x 84 = 336 (270MW considered for calculating share) | 14.613 | 39.454 |  | 85
2 | TALA (BHUTAN) | 6 x 170 = 1020 | 4.25 | 43.35
3 | FARAKKA (WEST BENGAL) | 3 x 200 = 600 | 1.76 | 28.18
2 x 500 = 1000
|  | 1 x 500 = 500 | 18.65 | 93.25 | 7.5 | 85
4 | JITPL | 2 x 600 = 1200 | 12 | 144
5 | KAHALGAON (BIHAR) | 4 x 210 = 840 | 1.64 | 13.74 | 9
|  | 3 x 500 = 1500 | 3.38 | 50.73 | 9 | 62.11
6 | TSTPP, KANIHA (ORISSA) | 2 x 500 = 1000 | 33.43 | 334.27 | 7.5 | 85
|  | 4 x 500 = 2000 | 10 | 200 | 7.5
7 | TEETSA | 3 x 170 = 510 | 22.424 | 114.36 |  | 85
8 | MANGDECHU HEP (BHUTAN) | 4 X 180 = 720 | 10.797 | 77.736
9 | KBUNL (Mujafarpur) (BIHAR)# | 2 X 195 = 390 | 8.852 | 34.521
10 | DARLIPALI STPS | 2 X 800 = 1600 | 51.818 | 829.082
11 | BARH | 2 x 660 = 1320 | 12.2 | 161
|  | 2 x 660 = 1320 | 1.7 | 23
12 | RANGEET( SIKKIM) | 3 x 20 = 60 | 1.834 | 1.1
13 | NPGC (BIHAR) | 3 X 660 = 1980 | 0.789 | 15.618
14 | NORTH KARANPURA | 2 X 660 = 1320 | 21.834 | 288.028
15 | KURICHU | 1 X 60 = 60 | 1.018 | 0.611
|  | Total ISGS |  | 2492.03
OTHER THAN ISGS SHARE
SL.NO. | NAME OF POWER STATION | INSTALLED CAPACITY IN MW | SHARE OF INSTALLED CAPACITY OF GRIDCO |  | AUX. CONS. | % AGE AVAILABILITY(excluding UA)
|  |  | SHARE IN % | MW
1 | JSW Energy (Utkal) Ltd. (Earlier known as Ind. Bharat) | 1 x 350 = 336 | 12 | 38.2

## Page-70
FORMAT-D.2
MONTHLY NET GENERATION / EXCHANGE / DEMAND DATA IN MU
CONSTITUENTS | 2025-07-01 | 2025-08-01 | 2025-09-01 | Jul-Sep | April-Jun
BURLA | 153.921 | 158.34 | 174.055 | 486.316 | 99.934
CHIPLIMA | 26.618 | 31.68 | 28.233 | 86.531 | 55.426
BALIMELA | 151.817 | 136.233 | 134.874 | 422.924 | 307.357
RENGALI | 170.474 | 179.388 | 176.85 | 526.712 | 115.915
U.KOLAB | 77.327 | 71.301 | 100.561 | 249.189 | 138.44
INDRAVATI | 163.485 | 146.96 | 181.222 | 491.667 | 269.609
O.H.P.C | 743.642 | 723.902 | 795.795 | 2263.339 | 986.681 | 3250.02
MACHHAKUND(O/D) | 32.526 | 30.795 | 29.573 | 92.894 | 77.182
TOTAL STATE HYDRO | 776.168 | 754.697 | 825.368 | 2356.233 | 1063.863 | 3420.096
OPGC(UNIT 1& 2) | 240.457 | 235.423 | 224.303 | 700.183 | 680.165 | 1380.348
OPGC(UNIT 1& 2) SHP (Biribati & Kendupatana) | 0 | 0 | 0 | 0 | 0 | 0
OPGC(UNIT 3 & 4) | 861.034 | 714.91 | 215.616 | 1791.56 | 2324.118 | 4115.678
OPGC(UNIT 3 & 4) UI | 0 | 7.945 | 0 | 7.945 | 10.343 | 18.288
IPP-GMR | 178.946 | 148.661 | 169.342 | 496.949 | 495.772 | 992.721
GMR(UI) | -0.627 | -4.528 | 0 | -5.155 | -2.388 | -7.543
IPP-Vedanta Ltd | 0 | 139.489 | 165.031 | 304.52 | 677.648 | 982.168
NAVA LTD. | 4.35 | 2.038 | 1.756 | 8.144 | 11.034 | 19.178
JITPL (IPP) | 82.302 | 78.748 | 74.841 | 235.891 | 241.299 | 477.19
IBUIL LTD. | 41.89 | 30.193 | 21.699 | 93.782 | 117.098 | 210.88
MTPCL | 1.008 | 2.188 | 1.842 | 5.038 | 6.714 | 11.752
MTPCL (MED TERM) | 9.253 | 10.185 | 8.951 | 28.389 | 27.487 | 55.876
TOTAL THERMAL | 1418.613 | 1365.252 | 883.381 | 3667.246 | 4589.29 | 8256.536
IMFA | 0.859 | 0.794 | 0.771 | 2.424 | 2.247
NALCO | 1.582 | 1.482 | 1.186 | 4.25 | 3.396
OTHER CGPs | 30.387 | 43.268 | 39.918 | 113.573 | 117.07
TOTAL-CPPs | 32.828 | 45.544 | 41.875 | 120.247 | 122.713 | 242.96
Meenakshi | 29.483 | 27.38 | 26.97 | 83.833 | 31.226
Samal HEP | 3.806 | 8.683 | 8.802 | 21.291 | 21.832
M/S BPPPL | 21.357 | 21.889 | 19.856 | 63.102 | 11.19
Ms APPPL | 11.822 | 13.684 | 13.546 | 39.052 | 3.897
Kakatiya | 1.53 | 3.22 | 5.169 | 9.919 | 2.79
Shaheed Lakhan Nayak | 0 | 24.093 | 22.213
Total Small Hydro | 67.998 | 98.949 | 96.556 | 263.503 | 70.935 | 334.438
Solar Power under RPSSGP Scheme | 0.565 | 0.751 | 0.745 | 2.061 | 2.656
Alex Green Energy | 0.427 | 0.547 | 0.509 | 1.483 | 1.944
ACME Solar | 2.655 | 3.248 | 3.296 | 9.199 | 12.358
SECI (VGF Scheme Ph-II,Batch-I-GEDCOL) | 1.568 | 1.832 | 1.872 | 5.272 | 6.753
SECI (GEDCOL) MANAMUNDA | 0.182 | 0.206 | 0.222 | 0.61 | 0.769
SECI (GEDCOL) MAKHIGUDA | 0.064 | 0.083 | 0.099 | 0.246 | 0.344
SECI (GEDCOL) JAYANAGAR | 0.124 | 0.166 | 0.211 | 0.501 | 0.737
SECI (GEDCOL) BARIPADA | 0.089 | 0.092 | 0.103 | 0.284 | 0.361
SECI (GEDCOL) BOLANGIR | 0.179 | 0.214 | 0.223 | 0.616 | 0.791
SECI (VGF Scheme Ph-II,Batch-IV) | 26.382 | 33.318 | 34.035 | 93.735 | 119.813
Aditya Birla Pvt. Ltd.-1 | 3.229 | 3.576 | 3.691 | 10.496 | 13.815
Aditya Birla Pvt. Ltd.-2 | 2.866 | 3.571 | 3.42 | 9.857 | 12.546
Aditya Birla Pvt. Ltd.-3 | 2.938 | 3.743 | 3.637 | 10.318 | 13.131
NVVNL Bundle Power (Solar) Aftab | 0.595 | 0.587 | 0.675 | 1.857 | 2.366
Total State Solar | 41.863 | 51.934 | 52.738 | 146.535 | 188.384 | 334.919
Biomass-JPIPL | 0 | 0 | 0 | 0 | 0
Total Odisha | 2337.47 | 2316.376 | 1899.918 | 6553.764 | 6035.185 | 12588.949
SECI (VGF Scheme Ph-II,Batch-I-RaIasthan & GuIrat (including OA charges) | 5.603 | 5.534 | 5.139 | 16.276 | 21.753
Dadri Solar Bundle Power | 0.553 | 0.538 | 0.619 | 1.71 | 1.968
Faridabad Solar Bundle Power | 0.451 | 0.456 | 0.524 | 1.431 | 1.67
NVVNL Bundle Power(Solar) (Including OA Charges) | 1.265 | 1.693 | 1.84 | 4.798 | 5.098
SECI (AZURE POWER PVT. LTD.) 300 MW | 53.391 | 48.577 | 51.099 | 153.067 | 193.378
SECI (AZURE POWER PVT. LTD.) 200 MW | 35.764 | 37.685 | 39.942 | 113.391 | 129.808
XERGI | 48.417 | 51.697 | 49.903 | 150.017 | 25.487
Total Central Solar | 145.444 | 146.18 | 149.066 | 440.69 | 379.162 | 819.852
PTC-OSTRO | 13.042 | 11.373 | 10.689 | 35.104 | 46.566
SECI-GREEN INFRA | 26.952 | 23.606 | 21.864 | 72.422 | 94.043
VIVID SOLIRE | 48.163 | 34.26 | 33.683 | 116.106 | 59.23
RENEW WIND ENERGY | 12.263 | 9.251 | 8.184 | 29.698 | 31.721
ADANI WIND ENERGY | 12.817 | 11.506 | 10.299 | 34.622 | 47.453
GIWEL | 0.276 | 0.23 | 0.217 | 0.723 | 0.155
Total Central Wind | 113.513 | 90.226 | 84.936 | 288.675 | 279.168 | 567.843
TOTAL Central Thermal | 890.613 | 911.145 | 1031.304 | 2833.062 | 3516.728 | 6349.79
TOTAL Central Hydro | 116.7 | 121.395 | 111.821 | 349.916 | 144.937 | 494.853
Central Sector Over drawal | 29.332 | 24.578 | 24.127 | 78.037 | 114.379 | 192.416
EREB IMPORT | 1332.063 | 1412.262 | 1557.009 | 4301.334 | 5141.657 | 9442.991
EREB EXPORT | 44.792 | 55.413 | 57.223 | 157.428 | 155.91 | 313.338
NET EREB | 1287.271 | 1356.849 | 1499.786 | 4143.906 | 4985.747 | 9129.653
Banking Power(Import) | 30.301 | 8.376 | 0 | 38.677 | 369.755 | 408.432
TRADING(PXIL+IEX+Bilateral) (Import) | 6.159 | 110.362 | 155.755 | 272.276 | 337.53 | 609.806
OTHER SALE(Including Nalco+Imfa) | 51.587 | 40.694 | 48.056 | 140.337 | 122.906 | 263.243
TRADING(PXIL+IEX+Bilateral) (Export) (Incld. TPA sale) | 388.388 | 294.238 | 213.504 | 896.13 | 871.658 | 1767.788
Banking Power(Export) | 0 | 0.53 | 0.14 | 0.67 | 1.11 | 1.78
SYSTEM DEMAND | 3236.353 | 3378.457 | 3186.06 | 9800.87 | 10148.164
* Monthly Pool Account is yet to be finalised.
TPA SALE
TRADING(PXIL+IEX+Bilateral) (Export)

## Page-71
GRIDCO DRAWAL FROM DIFFERENT SOURCES FOR THE PERIOD (July'25-Sep'25)
Sl. | Source of | Drawal | Total Cost | Avg. Cost
No | Power | in MU | in Crore( Rs.) | in P/U
1 | TOTAL HYDRO | 2356.233 | 217.394 | 92.2634
2 | OPGC | 2499.688 | 842.445 | 337.0201
3 | ISGS | 4143.906 | 1593.819 | 384.6176
4 | CPPs | 120.247 |  | 0
5 | IPPs | 1167.558 | 318.953 | 273.1796
6 | Non-conventional(State) | 410.038 | 66.024 | 161.0192
| TOTAL | 10697.67 | 3038.635 | 284.0464
| TRADING+IEX+Banking Power+OA+TPA | 896.8
| Net Purchase | 9800.87
FIGURES ARE PROVISIONAL & SUBJECTED TO CHANGE.

## Page-72
FORMAT-D.4
CAPACITY ADDITION OF GRID SUB-STATIONS
Sl. | NAME OF THE | CAPACITY AS ON | PROGRESSIVE | CAPACITY | DATE | REMARKS
NO. | SUB-STATION | 31.09.25 IN MVA | IN MVA | ADDITION (MVA)
1 | Turumunga | - | 1 x 20 | 20 | 16.07.25 | 220/132/33kV 20MVA Power TRF No-II charged at 13:54 hrs.
2 | Bolani | 1 x 10 | 2 x 10 | 10 | 24.07.25 | 132/11kV 10MVA Power TRF No-II charged at 16:52 hrs.
3 | Rengali | 2 x 20 | 1 x 20 + 1 x 40 | 20 | 25.07.25 | 220/33kV 20MVA Power TRF No-II replaced with 40MVA and charged at 14:58 hrs.
4 | Shamuka | 1 x 40 + 1 x 31.5 | 1 x 40 + 1 x 31.5 + 1 x63 | 63 | 30.07.25 | 132/33kV 63MVA Power TRF No-III charged at 14:37 hrs.
5 | Rayagada | 3 x 12.5 | 1 x 20 + 2 x 12.5 | 7.5 | 22.08.25 | 132/33kV 12.5MVA Power TRF No-I replaced with 20MVA and charged at 19:00 hrs.
6 | Agalpur | - | 1 x 20 | 20 | 22.08.25 | 220/132/33kV 20MVA Power TRF No-I charged at 18:41 hrs.

## Page-73
Format-D.5
MAJOR FAILURES OF TRANSFORMERS & EQUIPMENTS IN GRID SUB-STATIONS
CIRCLE | DATE | GRID S/S | TRANSFORMER | BREAKER | CT & PT | LIGHTNING ARRESTER | Tower Collapse | MISC. (Isolator/ Wave Trap etc.) | REMARKS
Berhampur |  |  | - | - | - | - | - | - | -
Bhubaneswar | 05.08.25 | Mendhasal | - | - | - | 132kV B-Phase LA of 132kV Mendhasal-Khurda Feeder burst at Khurdha end. | - | - | -
| 06.08.25 | Mendhasal | - | - | - | 132kV B-Phase LA of 132kV Mendhasal-Khurda Feeder burst at Khurdha end. | - | - | -
Burla | 17.07.25 | Rajgangpur | - | - | 132kV Y-PH CT of 132kV Rajgangpur-Tarkera CKT-II burst at Rajgangpur GSS | - | - | - | -
| 05.07.25 | Budhipadar | - | - | - | LA falling from structure at Budhipadar end | - | - | -
Bolangir | - | - | - | - | - | - | - | - | -
Chainpal | - | - | - | - | - | - | - | - | -
Cuttack | 22.07.25 | Khuntuni GIS | - | - | - | Y-Ph LA of 132kV Khuntuni-ICCL Feeder was bursted at ICCL end. | - | - | -
| 11.09.25 | Pratapsasan | - | - | 220kV Main Bus Y-Ph Bus PT Burst | - | - | - | -
Jajpur Road | 21.08.25 | Rairangpur | - | - | - | B Ph LA of 132kV Karanjia-Rairangpur Line burst at Karanjia end. | - | - | -
| 06.07.25 | Baripada | - | - | - | R-ph LA of 132kV Balasore-Balasore RTSS Feeder at Railway end is brust. | -
| 11.08.25 | Balasore | - | - | Line cvt of 220kV Balasore-Bhadrak Feeder brust in Bhadrak GSS | - | -
Jeypore |  |  | - | - | - | - | - | - | -