## CBA
COST BENEFIT ANALYSIS
A. BENEFITS DUE TO ADDITIONAL SALE OF ENERGY ON ACCOUNT OF INSTALLATION OF 3X1500 MVA 765/400KV Sub-Station at Betakholi, Khuntuni
1 | Transformation Capacity considered for revenue calculation considering n-1 condition = 2x1500 MVA | 3000
2 | Power factor (PF) | 0.9
3 | Diversity factor (DF=1.3 ) | 1.3
4 | Load factor (LF=0.7 ) | 0.7
5 | Additional Avg. power available for sale on account of establishment of new 765/400KV Sub-Station at Khuntuni with 2X1500 MVA ( under n-1 Conrdition) transformers in MW (5 = 1 x 2 x 4 / 3) | 1453.8462 | 525600
6 | Additional energy available for sale in LU | 127356.9231
7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 123536.2154 | 7
8 | Anticipated revenue at a cost of Rs.0.24/ Unit in Lakhs | 29648.6917
B. BENEFITS OF THE SCHEME DUE TO REDUCTION IN LOSSES |  |  |  | 8760
1 | Total losses before implementation of the scheme in MW | 1216.0806
2 | Total losses after implementation of the scheme in MW | 1203.7454
3 | Total reduction in losses in MW | 12.3352
4 | Load factor | 0.7
5 | Loss load factor (0.8 LF2 + 0.2 LF) | 0.532
6 | The energy available for sale per year in LU | 574.8583
7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 557.6126
8 | Anticipated revenue due to reduction in losses in lakhs @ Rs. 0.24/Unit | 133.827
C. CALCULATION OF REVENUE RETURN
1 | Anticipated revenue due to reduction in losses [Rs. Lakhs] | 133.827
2 | Anticipated revenue due to sale of additional energy [Rs. Lakhs] | 29648.6917
3 | Total anticipated annual revenue [Rs. Cr.] | 297.8252
4 | Estimated Cost [Rs. Cr.] | 2678.9722
5 | Average Annual Rate of Return in % | 11.1171
6 | Internal Rate of Return | 11.15%

## IRR Khuntuni
Calculation of NPV and IRR : For 3X1500MVA, 765/400KV Sub-Station at Betakholi, Khuntuni
CoC (%) = | 70% | x | 8.03 | + | 30% | x | 15.5 | Average | 6.58 |  |  | RoI on Loan P.a |  |  | = | 7.75 |  | IRR = | 11.15% | [16 empty] | (Rs. in Crores)
Particulars | Constuction Period |  |  | Benefits Period | [34 empty] | Total
Financial Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
Cash Inflow (CI)
Equity | 121 | 482 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804
Loan(Principal) | 281 | 1125 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1875
Loan (Interest) | 22.56 | 112.9 | 150.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286.02
Revenue | 0 | 0 | 0 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 10423.8815
Salvage Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296.502 | 296.502
Total (CI) - (A) | 424.56 | 1719.9 | 820.56 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 297.8252 | 594.3272 | 13685.4035
Cash Outflow (CO)
CWIP | 402 | 1607 | 670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2679
IDC | 22.56 | 112.9 | 150.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286.02
Loan Repayment | 0 | 0 | 0 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2161.02
Interest on Loan | 0 | 0 | 0 | 166.3 | 151.84 | 137.38 | 122.92 | 108.46 | 94 | 79.53 | 65.07 | 50.61 | 36.15 | 21.69 | 7.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1041.18
R&M exp. @ 3 % PC | 0 | 0 | 0 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 3113.25
Total (CO) - (B) | 424.56 | 1719.9 | 820.56 | 435.335 | 420.875 | 406.415 | 391.955 | 377.495 | 363.035 | 348.565 | 334.105 | 319.645 | 305.185 | 290.725 | 276.265 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 88.95 | 9280.47 | IRR
Net Cash Inflow (A-B) | 0 | 0 | 0 | -137.5098 | -123.0498 | -108.5898 | -94.1298 | -79.6698 | -65.2098 | -50.7398 | -36.2798 | -21.8198 | -7.3598 | 7.1002 | 21.5602 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 208.8752 | 505.3772 | 4404.9335 | 11.15%
DF @ CoC | 1 | 0.938 | 0.88 | 0.826 | 0.775 | 0.727 | 0.682 | 0.64 | 0.601 | 0.564 | 0.529 | 0.496 | 0.465 | 0.437 | 0.41 | 0.384 | 0.361 | 0.338 | 0.318 | 0.298 | 0.28 | 0.262 | 0.246 | 0.231 | 0.217 | 0.203 | 0.191 | 0.179 | 0.168 | 0.158 | 0.148 | 0.139 | 0.13 | 0.122 | 0.115 | 0.107 | 0.101 | 0.095
Net Present value(NPV) | 0 | 0 | 0 | -113.58 | -95.36 | -78.94 | -64.2 | -50.99 | -39.19 | -28.62 | -19.19 | -10.82 | -3.42 | 3.1 | 8.84 | 80.21 | 75.4 | 70.6 | 66.42 | 62.24 | 58.49 | 54.73 | 51.38 | 48.25 | 45.33 | 42.4 | 39.9 | 37.39 | 35.09 | 33 | 30.91 | 29.03 | 27.15 | 25.48 | 24.02 | 22.35 | 21.1 | 48.01 | 536.51
NPV at IRR | 0 | 0 | 0 | -100.11 | -80.6 | -64.07 | -49.89 | -38 | -27.98 | -19.59 | -12.63 | -6.83 | -2.07 | 1.8 | 4.92 | 42.82 | 38.43 | 34.67 | 31.12 | 27.99 | 25.27 | 22.77 | 20.47 | 18.38 | 16.5 | 14.83 | 13.37 | 12.11 | 10.86 | 9.82 | 8.77 | 7.94 | 7.1 | 6.48 | 5.85 | 5.22 | 4.6 | 10.11 | 0.43
**
CoC - Cost of Capital
IDC- Interest During Construction
CWIP- Capital Work in Progress
DF- Discounting Factor
IRR- Internal Rate of Return
ARR- Average Annual Rate of Return
Opening Balance |  |  | 2161.02 | 1980.935 | 1800.85 | 1620.765 | 1440.68 | 1260.595 | 1080.51 | 900.425 | 720.34 | 540.255 | 360.17 | 180.085
Repayment |  |  | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085 | 180.085
Closing Balance |  |  | 1980.935 | 1800.85 | 1620.765 | 1440.68 | 1260.595 | 1080.51 | 900.425 | 720.34 | 540.255 | 360.17 | 180.085 | -3.979e-13
Agerage Loan |  |  | 2070.9775 | 1890.8925 | 1710.8075 | 1530.7225 | 1350.6375 | 1170.5525 | 990.4675 | 810.3825 | 630.2975 | 450.2125 | 270.1275 | 90.0425
Interest |  |  | 166.2995 | 151.8387 | 137.3778 | 122.917 | 108.4562 | 93.9954 | 79.5345 | 65.0737 | 50.6129 | 36.1521 | 21.6912 | 7.2304
|  |  | -0.00050675 | -0.0013323 | -0.0021578 | -0.0029833 | -0.0038088 | -0.0046343 | 0.0045402 | 0.0037147 | 0.0028892 | 0.0020637 | 0.0012382 | 0.00041275

## Data sheet
| Expenditure in Crores: | 2678.9722
| Year: | 2026-27 | 2027-28 | 2028-29
| % of Expenditure: | 15% | 60% | 25%
Year wise expenditure: |  | 401.8458 | 1607.3833 | 669.7431
Loan | 70% | 281 | 1125 | 469
Equity | 30% | 121 | 482 | 201
Total | 100% | 402 | 1607 | 670