## Summary
Estimate for Construction of 2x100 MVA, 220/33KV GIS at Pahala with SAS along with 220 KV D/C line (UG cabling length approx 8.805 Km & Over Head length approx 1.135 Km. Total Line Length=9.94 RKms approximately) from existing 220/132/33KV GIS at Balianta & 220 KV D/C line (Over Head length approx 13 Km & UG cabling length approx 1.135 Km. Total Line Length=14.135 RKms approximately) from existing 220/132/33KV GIS at Bidanasi along with 02 nos. of Bay extension at Balianta GIS & Bidanasi.
Sl. No. | Description | Amount (in INR)
A | Supply of Materials
1 | Cost of materials for Construction of 220/33kV GIS at Pahala | 672318711.812 | 672318711.812
2 | Cost of materials for Construction of 220kV TL( UG+OH) Pahala to Balianta | 1508060745.2134 |  | 1508060745.2134
3 | Cost of materials for Construction of 220kV TL( UG+OH) Pahala to Bidanasi | 319683049.9942 |  |  | 319683049.9942
4 | Cost of materials for Construction of 220/132/33kV Bay at Balianta (2 nos.) | 76272286.3477 |  |  |  | 76272286.3477
5 | Cost of materials for Construction of 220/132/33kV Bay at Bidanasi (2 nos.) | 40515677.9874 |  |  |  | 40515677.9874
6 | Total Cost of the Materials | 2616850471.3548 | 672318711.812 | 1508060745.2134 | 319683049.9942 | 116787964.3351
7 | Stock storage & Insurance @3% on Sl. 4 | 78505514.1406 | 20169561.3544 | 45241822.3564 | 9590491.4998 | 3503638.9301
8 | Sub-Total against supply of the materials (4+5) | 2695355985.4954 | 692488273.1664 | 1553302567.5698 | 329273541.494 | 120291603.2652
9 | Contigency @3% on Sl. No.6 | 80860679.5649 | 20774648.195 | 46599077.0271 | 9878206.2448 | 3608748.098
10 | T & P @ 2% on Sl. No.6 | 53907119.7099 | 13849765.4633 | 31066051.3514 | 6585470.8299 | 2405832.0653
11 | Transportation @ 5% on Sl. No. 6 | 134767799.2748 | 34624413.6583 | 77665128.3785 | 16463677.0747 | 6014580.1633
12 | Total Cost of Supply | 2964891584.045 | 761737100.483 | 1708632824.3268 | 362200895.6434 | 132320763.5917
B | Erection of Materials
13 | Erection of materials for Construction of 220/33kV GIS at Pahala | 248181605.5512 | 248181605.5512
14 | Erection of materials for Construction of 220kV TL( UG+OH) Pahala to Balianta | 236168100.203 |  | 236168100.203
15 | Erection of materials for Construction of 220kV TL( UG+OH) Pahala to Bidanasi | 114897084.5081 |  |  | 114897084.5081
16 | Erection of materials for Construction of 220/132/33kV Bay at Balianta (2 nos.) | 13640668.73 |  |  |  | 13640668.73
17 | Erection of materials for Construction of 220/132/33kV Bay at Bidanasi (2 nos.) | 24727244.4816 |  |  |  | 24727244.4816
18 | Total Cost of Erection | 637614703.4739 | 248181605.5512 | 236168100.203 | 114897084.5081 | 38367913.2116
Supply + Erection(A+B)
19 | Sub-Total (10 + 14) Supply + Erection | 3602506287.5189 | 1009918706.0342 | 1944800924.5299 | 477097980.1515 | 170688676.8033
20 | Total Other Charges as Statutory clearance | 5000000 | 1250000 | 1250000 | 1250000 | 1250000
21 | Grand Total (Sl. No. 15+16) | 3607506287.5189 | 1011168706.0342 | 1946050924.5299 | 478347980.1515 | 171938676.8033
| Rounded off to (in INR) | 3607506288 | 1011168706 | 1946050925 | 478347980 | 171938677
Rupees Three Hundred Sixty Crore Seventy Five Lakh Six Thousand Two Hundred Eighty Eight Only

## Pahala SUPPLY
|  |  |  | (SUPPLY SUB STATION) |  |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2x100 MVA, 220KV GIS and 33KV AIS Sub-Station at Pahala with SAS along with 220 KV D/C line from existing 220/132/33KV GIS at Balianta through UG cabling length approx 8.805 Km & Over Head length approx 1.135 Km.
220/33KV GIS Pahala: 220KV GIS feeder Bays-5 Nos +2 spare=7 Nos, Power Tfr-2 Nos, B/C-1 no 33KV AIS Bays- Feeder-5 Nos, Tfr-2 Nos, B/C-1 no
SAP CODE | SAP DESCRIPTION |  | price
|  | QUANTITY |  | Sl. No. | SUBSTATION EQUIPMENTS / MATERIALS | UNITS | QUANTITY | IN INR |  |  |  |  | Remarks
[5 empty] | DESCRIPTION OF ITEMS(SCHEDULE-VIIA-SS) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) |  |  | BASIC PRICE PER UNIT (Taxable Value) | CGST @ 9% PER UNIT | SGST @ 9% PER UNIT | TOTAL PRICE PER UNIT | TOTAL PRICE FOR THE QUANTITY
|  | 4 |  | 1 | 2 | 3 | 4 | 5 | 6=5*9% | 7=5*9% | 8=(5+6+7) | 9=4*8 | 10
|  |  |  | 1 | 245KV GIS EQUIPMENT as per latest IEC standard & type tested equipment as per technical specification, with open future proof & flexible system in line with IEC 61850 & IEC 62271-203. (Circuit breaker shall be C2 - M2 class as per IEC 62271-100).
1000000460 | 245 kV PTR bay module | 2 | 19782364.21 | 1.1 | Transformer feeder bay module: 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T) SF6 gas insulated Transformer feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar disconnectors with common grounding switch, Motorised disconnectors with safety grounding switch(es), high speed fault making motorised grounding switch, Stand alone Local control cubicle, SF6 gas monitoring system for complete bay, Cable Termination Arrangeement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete Transformer feeder bay module & its structures and earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per Technical Specification. | SET | 2 | 19782364.21 | 1780412.7789 | 1780412.7789 | 23343189.7678 | 46686379.5356 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
1000000457 | 245 kV Line bay module | 7 | 19782364.21 | 1.2 | Line feeder bay module: 245kV, 3150A,50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T), SF6 gas insulated Line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar disconnectors with common grounding switch, Motorised disconnectors with safety grounding switch(es), high speed fault making motorised grounding switch, Stand alone Local control cubicle, SF6 gas monitoring system for complete bay,Cable Termination Arrangeement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete Line feeder bay module & its structures and earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per Technical Specification. | SET | 6 | 19782364.21 | 1780412.7789 | 1780412.7789 | 23343189.7678 | 140059138.6068
1000000458 | 245 kV GIS bus bar | 2 | 10062203.83 | 1.3 | Bus Bar Module with Bus VT: 245kV , 3150A, 50 kA ( 3 sec for Bus bar ,1 sec for disconnector,grounding switch & bus P.T), 3- phase Isolated/3 ph common , SF6 gas insulated , metal enclosed bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. The gas compartments for bus bar shall be separate for each bays. Each bus bar set shall be complete with bus potential transformer (3 core), disconnectors , bus bar grounding switch, SF6 gas monitoring system PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete the bus & its earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | SET | 2 | 10062203.83 | 905598.3447 | 905598.3447 | 11873400.5194 | 23746801.0388
1000000459 | 245 kV bus coupler bay module | 1 | 15762077.29 | 1.4 | Bus Coupler Bay Module: 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector, Grounding switch,C.T) SF6 gas insulated Bus Coupler Bay Module comprising of SF6 gas insulated circuit breaker, current transformer, disconnectors switches, disconnector with safety grounding switch(es). Standalone Local control cubicle, SF6 gas monitoring system, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets, Nuts, Bolts & Washers Absorbent, Limit Switch ,SF6 Gas , etc to complete Bus Coupler bay module & its structure and earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification | SET | 1 | 15762077.29 | 1418586.9561 | 1418586.9561 | 18599251.2022 | 18599251.2022 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  | 0 | 1.5 | 245KV XLPE Cable and accessories: Type tested 220 kV XLPE insulated Copper Conductor Power Cable as per IS7098 & IEC62067 for interconnection of 220 kV AIS Feeder and Transformer Switchyard with 220 kV GIS. (The below mentioned cable quantity is only indicative, actual quantity shall be as per approved power cable schedule/site condition. Measurement shall be done accordingly.)
1000000850 | 245 kV, 1C X 1000 Sq. mm, Cu cable | 2280 | 18135.7 | 1.5.1 | 245KV XLPE cable, 1000 sqmm single core, Copper as per TS.(for interconnection from 245KV GIS to Line) | Km | 2.08 | 18135.7 | 1632.213 | 1632.213 | 21400.126 | 44512.2621 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000004265 | OD cable to Oil filled 220kV term kit | 27 | 1072166.14 | 1.5.2 | 245kV Cable Termination Kit including cable to Air bushing suitable for Outdoor for 220KV feeders suitable for 1C x 1000 sqmm Copper Cable. | Nos | 24 | 1072166.14 | 96494.9526 | 96494.9526 | 1265156.0452 | 30363745.0848
|  | 27 | 1072166.14 | 1.5.3 | 245kV Indoor Cable Termination Kit for 220KV feeders suitable for 1C x 1000 sqmm Copper Cable. (Termination at GIS) | Nos | 24 | 1072166.14 | 96494.9526 | 96494.9526 | 1265156.0452 | 30363745.0848 |  | NO CODE
3000004268 | 220kV 1 ph Link box without SVL | 27 | 21301.16 | 1.5.4 | Supply of 1 ph Link box without SVL with clamps and connectors with acessories | Nos | 24 | 21301.16 | 1917.1044 | 1917.1044 | 25135.3688 | 603248.8512 | As per TS 25/2025-26, dated. 19.12.2025 of SGM(P)- I, OPTCLfor RTSS Mancheswar
3000004267 | 220kV 1 ph Link box with SVL | 27 | 38675.29 | 1.5.5 | Supply of 1 ph Link box with SVL with clamps and connectors with acessories | Nos | 24 | 38675.29 | 3480.7761 | 3480.7761 | 45636.8422 | 1095284.2128
1000000934 | 400Sqmm XLPE bonding cable | 350 | 4217.43 | 1.5.6 | 400 Sq.MM Single core Bonding cable including connection/termination as required to make the system complete in all respect. (voltage Level to be determined by considering the fault level at seath) | Mtrs | 350 | 4217.43 | 379.5687 | 379.5687 | 4976.5674 | 1741798.59 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL | Rate adopted proportionately @33% of 3171.00
1000000462 | 220 kV online PD monitoring | 1 | 2233492.73 | 1.6 | Portable Partial Discharge(PD) monitoring system: 245 KV system shall have Portable Partial Discharge(PD) monitoring system & shall be capable for measuring PD in charged GIS environment, bandwidth in order of 100 MHz–2GHz & provision to select a wide range of intermediate bandwidths and the principle of operation shall be based on UHF principle of detection. The Detection and measurement of PD and bouncing particles having in built large coloured LCD for displaying and storing facility in the instrument for further analysis to locate actual source of PD such as free conducting particles, floating components, voids in spacers, particle on spacer surfaces etc. There shall be minimum six channels for measuring at a time. This includes all accessories as required for complete monitoring of the Partial Discharge of the GIS equipment and also as per Technical Specification. | SET | 1 | 2233492.73 | 201014.3457 | 201014.3457 | 2635521.4214 | 2635521.4214 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  | 0 | 2 | 220 KV and 33KV AIS Switchyard
1000000585 | 245 kV 3 core IVT | 21 | 231909.18 | 2.1 | 245KV, 3 Core, Single Phase Inductive Volatage Transformer (2 core 3P class & 1 core 0.2 class) (AIS) | NOS | 18 | 231909.18 | 20871.8262 | 20871.8262 | 273652.8324 | 4925750.9832 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  | 0 | 2.2 | 245KV, 2000A, 50KA, Isolator (AIS) including post insulators (8 KN) as per TS suitable for SCADA operation
1000000096 | 220KV SI WITH DB With ES OF 2000A | 7 | 378121.38 | 2.2.1 | 245KV Single Isolator with Earth switch (for feeder bay) (AIS) | SET | 6 | 378121.38 | 34030.9242 | 34030.9242 | 446183.2284 | 2677099.3704 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
1000000094 | 220KV SI WITH DB SI W/O ES 2000A | 2 | 329000.84 | 2.2.2 | 245KV Single Isolator without Earth switch (for Transformer bay) (AIS) | SET | 2 | 329000.84 | 29610.0756 | 29610.0756 | 388220.9912 | 776441.9824
3000000945 | 220KV Bus Post Insulator | 6 | 20931.02 | 2.3 | 245KV, 1 phase solid core Bus Post Insulator (8 kN) (AIS) as per Technical Specification. | NOS | 6 | 20931.02 | 1883.7918 | 1883.7918 | 24698.6036 | 148191.6216
1000000671 | 245 kV SM surge arrestor | 27 | 70578.02 | 2.4 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | NOS | 24 | 70578.02 | 6352.0218 | 6352.0218 | 83282.0636 | 1998769.5264
1000000672 | 36 kV, 800-400-200A, 3 core CT | 15 | 50825.97 | 2.5 | 36 KV,800-400-200, 31.5KA,3 CORE SINGLE PHASE CURRENT TRANSFORMER (2nos PX Class & 1 no 0.2s Class) - Feeder Bays | Nos | 15 | 50825.97 | 4574.3373 | 4574.3373 | 59974.6446 | 899619.669
1000000058 | 36KV OIL 1200-600-300/1-1-1A CT | 9 | 62012.84 | 2.6 | 36 KV, 2000-1000/1A, 31.5 kA,4 CORE SINGLE PHASE CURRENT TRANSFORMER(3 nos PX Class & 1 no 0.2s Class) - Transformer and Bus Coupler Bays | Nos | 9 | 62012.84 | 5581.1556 | 5581.1556 | 73175.1512 | 658576.3608 | CD SS-27
|  |  | 0 | 2.7 | 36 KV, 31.5KA for 1 sec, AIS ISOLATORS with post insulators as per TS.
1000000113 | 33KV SI W/O ES OF 1250A | 10 | 124595.84 | 2.7.1 | 36 KV, 1250A, 31.5KA for 1 sec, Single Isolator without Earth Switch (for Feeder ) | SET | 10 | 124595.84 | 11213.6256 | 11213.6256 | 147023.0912 | 1470230.912 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  | 124595.84 |  | 36 KV, 800A, 31.5KA for 1 sec, Single Isolator without Earth Switch (for Station Transformer ) | SET | 2 | 124595.84 | 11213.6256 | 11213.6256 | 147023.0912 | 294046.1824
1000000116 | 33KV SI WITH ES OF 1250A | 5 | 124595.84 | 2.7.2 | 36 KV, 1250A, 31.5KA for 1 sec, Single Isolator with Earth Switch (for Feeder ) | SET | 5 | 124595.84 | 11213.6256 | 11213.6256 | 147023.0912 | 735115.456
1000000463 | 36 kV SI 2000A with ES | 10 | 124595.84 |  | 36 KV, 2000A, 31.5KA for 1 sec,Single Isolator without Earth Switch (for Power Trf, B/C & Bus section) | SET | 10 | 124595.84 | 11213.6256 | 11213.6256 | 147023.0912 | 1470230.912
1000000556 | 33kV SL surge arrestor | 27 | 9296.39 | 2.8 | Metal oxide polymer housed surge arrrestor for 33 kV system. Station Class Low Duty (SL) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor - As per TS | Nos | 27 | 9296.39 | 836.6751 | 836.6751 | 10969.7402 | 296182.9854
1000000122 | 36KV 2C SP IVT/PT | 3 | 30800 | 2.9 | 36 KV, 2 Core Single Phase IVT (1 core 3P & 1 core 0.2) | Nos | 3 | 30800 | 2772 | 2772 | 36344 | 109032
|  |  | 219472.75 | 2.1 | 36 KV, 2500A, 31.5 kA Vacuum Circuit Breaker with supporting Structure as per TS. Facilities for integration with SAS as per the site requirement. | Nos | 8 | 219472.75 | 19752.5475 | 19752.5475 | 258977.845 | 2071822.76
3000000943 | 33 KV Bus Post Insulator | 80 | 1722.98 | 2.11 | 33 KV Solid Core Bus Post Insulator as per TS | Nos | 80 | 1722.98 | 155.0682 | 155.0682 | 2033.1164 | 162649.312
|  |  | 0 | 3 | ACSR CONDUCTORS/IPS Tube
1000000018 | ACSR MOOSE CONDUCTOR | 1 | 409923 | 3.1 | ACSR Moose Conductor (220KV outdoor CSE to outdoor CSE and 33KV Line bay jumpers) | KM | 1 | 409923 | 36893.07 | 36893.07 | 483709.14 | 483709.14 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
1000000616 | ACSR Panther Conductor | 0.1 | 17802.3 | 3.2 | ACSR Panther Conductor (Station Transformer connections) | M | 100 | 17802.3 | 1602.207 | 1602.207 | 21006.714 | 2100671.4
1000000472 | ACSR Bersimis conductor | 0.3 | 745706.3 | 3.3 | ACSR Bersimis Conductor (33KV Power Trf to 33KV isolator dropping and Bay jumpers) | KM | 0.3 | 745706.3 | 67113.567 | 67113.567 | 879933.434 | 263980.0302 | Rate derived from ACSR Moose conductor
3000004389 | 3" IPS Tube | 500 | 2400 | 3.4 | 3 inch IPS Aluminium Tube for 33 KV Main Bus & Reserve Bus | Mtrs | 500 | 2400 | 216 | 216 | 2832 | 1416000 | Ramakrushnapur
|  |  | 0 | 4 | HARDWARES & FITTINGS/ SPACERS/CLAMP & CONNECTORS FOR FOLLOWING ARRANGEMENT:
3000004005 | HW fittings for 220 kV system in substat | 1 | 500000 | 4.1 | All clamp and connector for complete substation as per requirement to complete the work in all respect. | LOT | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | MR
|  |  | 0 | 5 | SUBSTATION EARTHING SYSTEMS
3000004033 | Earthing Conductor for Earth Mat: 75 x 10 mm GI Flat. | 5 | 575000 | 5.1 | EARTHING CONDUCTOR FOR BURRIAL: 75X10 mm GI Flat for laying (spacing maximum 5m both way) | Mtrs | 5 | 575000 | 51750 | 51750 | 678500 | 3392500 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000004001 | Earthing Conductor for risers: 50 x 6 mm GI Flat | 4.5 | 231000 | 5.2 | EARTHING CONDUCTOR; 50X6 mm Gl Flat for Riser from the burial earth mat to equipment, structure, CR Panels, LT Panels, etc) | Mtrs | 4.5 | 231000 | 20790 | 20790 | 272580 | 1226610
3000000592 | 50 mm Heavy Duty GI Perforated Pipes, 3 mtrs long for treated earth pit | 350 | 3675.65 | 5.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty Gl PERFORATED PIPE 3 mtrs long for treated earth pit) | Nos | 350 | 3675.65 | 330.8085 | 330.8085 | 4337.267 | 1518043.45
|  |  | 100000 | 5.4 | Switchyard buildings lightning protection for GIS Hall and Control Room (all materials & accessories like Shielding Wire, PG clamp, Test link, D shackle, other required materials etc) as per IS/National Building code standard and as per approved drawing | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000
3000004072 | UPVC pipes for treated earth pits | 1 | 150000 | 5.5 | Supply of UPVC Pipes (2", 1.5", 1" & 1/2" etc), Joints, bends, Valves and all accessories for spreading the water network to each treated earth pit as per approved drawing. | Lot | 1 | 150000 | 13500 | 13500 | 177000 | 177000
|  |  | 0 | 6 | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained & High Quality ISI mark PVC-U selfit Pipe, PVC elbow bend,PVC Tee etc suitable for under ground burrial (HARD CONDUIT INCLUDING of adequate tensile strength minimum 7kg/sqmm or better) as per TS.
3000004065 | G.I Cable Trays(size: 450x75x2500mm) | 1500 | 638.1408 | 6.1 | G.I Cable Trays(size: 450x75x2500mm) | Mtrs | 1500 | 638.1408 | 57.4327 | 57.4327 | 753.0061 | 1129509.1828 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000004066 | G.I Cable Trays(size: 300x75x2500mm) | 500 | 478.6056 | 6.2 | G.I Cable Trays(size: 300x75x2500mm) | Mtrs | 500 | 478.6056 | 43.0745 | 43.0745 | 564.7546 | 282377.2957
3000004067 | G.I Cable Trays(size: 150x75x2500mm) | 500 | 319.0704 | 6.3 | G.I Cable Trays(size: 150x75x2500mm) | Mtrs | 500 | 319.0704 | 28.7163 | 28.7163 | 376.5031 | 188251.5305
3000003565 | Support G. I angle 50x50x6 mm for cable tray | 2.5 | 92260.97 | 6.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 2.5 | 92260.97 | 8303.4873 | 8303.4873 | 108867.9446 | 272169.8615
|  |  | 0 | 7 | SWITCH YARD STRUCTURES STEEL HDG - LATTICE TYPE FOR TOWER COLUMN, BEAMS & PIPE TYPE FOR ALL EQUIPMENT STRUCTURE ( INCLUDING FOUNDATION BOLTS - ITS NUTS, ITS WASHERS, ITS PLATE ETC ) FOR 220/33 KV CLASS (Weight in brackets are only indicative - Actual weight shall be as per approved BOM. Measurement shall be done accordingly.)
|  |  | 0 | 7.1 | DIFFERENT TYPE OF LATICE TYPE COLUMNS WITH DETAILS (including top earthing spike)
|  |  | 0 | 7.1.1 | P1S 220 KV Column Beam (Nominal Weight - 4.03 MT) - 4 Set. | MT | 16.12 | [6 empty] | Not Incorporated in Erection Portion
|  |  | 0 | 7.1.2 | T8S - 33KV (NOMINAL UNIT WT- 0.8 MT)) = 11Sets | MT | 9.13
|  |  | 0 | 7.2 | DIFFERENT TYPE OF BEAMS WITH DETAILS
|  |  | 0 | 7.2.1 | Q1-Beam 220 KV (NOMINAL UNIT WT- 1.598 MT) = 2 Sets | MT | 3.196
|  |  | 0 | 7.2.3 | G4 - 33KV(NOMINAL UNIT WT- 0.4 MT) =08 Sets | MT | 3.2
3000003445 | HDG MS SS equipment Structures | 31.646 | 92260.97 | 7.3 | TOTAL WEIGHT OF COLUMN & BEAM INCLUDING FOUNDATION BOLTS, - ITS NUTS, WASHERS PLATE ETC | MT | 31.646 | 92260.97 | 8303.4873 | 8303.4873 | 108867.9446 | 3445234.9748 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  | 0 | 7.4 | DIFFERENT TYPE OF TUBULAR SUPPORT STRUCTURES HDG TYPE FOR ALL 220KV & 33KV EQUIPMENT INCLUDING FOUNDATION BOLT - ITS NUTS, ITS WASHERS, ITS PLATE ETC )
|  |  | 0 | 7.4.1 | Structure for 220KV SA =27 Nos | MT | 8.4
|  |  | 0 | 7.4.2 | Structure for 220KV IVTs =21 Nos | MT | 7.35
|  |  | 0 | 7.4.3 | Structure for 220 KV Cable Termination (Nominal Wight - 0.219 MT) = 27 + 6 Nos. for line | MT | 5.256 | [6 empty] | Not Incorporated in Erection Portion
|  |  | 0 | 7.4.4 | 220 KV Single Isolator without Earth Switch =2 Nos | MT | 3
|  |  | 0 | 7.4.5 | 220 KV Single Isolator with Earth Switch = 7 Nos | MT | 9.9
|  |  | 0 | 7.4.6 | Structure for 220KV BPI =6 Nos | MT | 1.86
|  |  | 0 | 7.4.7 | Structure for 33KV CT =24 Nos | MT | 3.552
|  |  | 0 | 7.4.8 | Structure for 33KV IVTS =3 Nos | MT | 0.372
|  |  | 0 | 7.4.9 | Structure for 33KV LAs =27 Nos | MT | 3.996
|  |  | 0 | 7.4.10 | 33 KV Single Isolator without Earth Switch = 7 Nos | MT | 2.065
|  |  | 0 | 7.4.11 | 33 KV Single Isolator with Earth Switch = 5 Nos | MT | 1.625
|  |  | 0 | 7.4.12 | Structure for 33KV BPI =80 Nos | MT | 11.92
|  |  | 0 | 7.4.13 | Structure for 33KV HG Fuse =6 Nos | MT | 1.47
|  |  | 92260.97 | 7.5 | TOTAL WEIGHT OF TUBULAR SUPPORT STRUCTURE FOR ABOVE EQUIPMENT INCLUDING GI FOUNDATION BOLTS, ITS NUTS, WASHERS PLATE ETC | MT | 60.766 | 92260.97 | 8303.4873 | 8303.4873 | 108867.9446 | 6615469.5216 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000004093 | Different size HDG Nut bolt for Tower structure and substation structures | 4.7885 | 117049.77 | 7.6 | Gl bolts ,Nuts, washers - plain & spring etc for the above LATTICE/PIPE COLUMN, BEAM & EQUIPMENT structures | MT | 4.6206 | 117049.77 | 10534.4793 | 10534.4793 | 138118.7286 | 638191.3974 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
1000000859 | 40 mtrs high monopole LCLM | 2 | 1200000 | 8 | 40 Mtrs high Monopole (HDG) Lighting cum Lightning Mast suitable for wind zone-V, including LED lighting fixtures (controlled by Lux meter for variable lux output of the luminaire as per ambient light to attain the reqired lux level) with control gear panel etc and with all accessories like motor for hoisting / lowering the lighting platform and other switchgear & lighting control panel including copper cable, accessories etc. The number and rating of luminaire shall be as per the lighting calculation to attain the required lux level. | SET | 2 | 1200000 | 108000 | 108000 | 1416000 | 2832000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  | 0 | 9 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
|  |  | 0 | 9.1 | POWER CABLES, 1.1KV, XLPE & PVC, ARMOURED, FRLSH, ALUMINIUM CONDUCTOR (As per Specification) including Power cable termination, all accessories & other materials - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule, based on which material shall be supplied and measurement will be done.)
3000000207 | 3.5Cx300 Sqmm 4C AL POWER CABLE | 1 | 1017860 | 9.1.1 | 3.5 CX300 mm² XLPE | km | 1 | 1017860 | 91607.4 | 91607.4 | 1201074.8 | 1201074.8 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000004048 | 3.5CX185 Sq. mm. Al cable (XLPE) | 500 | 759.3 | 9.1.2 | 3.5 CX185 mm² XLPE | Mtrs | 500 | 759.3 | 68.337 | 68.337 | 895.974 | 447987
3000004049 | 3.5CX120 Sq. mm. Al cable (XLPE) | 200 | 453.26 | 9.1.3 | 3.5CX120 mm² XLPE | Mtrs | 200 | 453.26 | 40.7934 | 40.7934 | 534.8468 | 106969.36
3000004050 | 3.5CX70 Sq. mm. Al cable (XLPE) | 1000 | 262.3 | 9.1.4 | 3.5 CX70 mm² PVC | Mtrs | 1000 | 262.3 | 23.607 | 23.607 | 309.514 | 309514
3000004051 | 3.5CX35 Sq. mm. Al cable (XLPE) | 3000 | 145.625 | 9.1.5 | 3.5 CX35 mm² PVC | Mtrs | 3000 | 145.625 | 13.1062 | 13.1062 | 171.8375 | 515512.5
3000004052 | 4CX16 Sq. mm. Al cable (XLPE) | 1000 | 114.3 | 9.1.6 | 4 CX 16 mm² PVC | Mtrs | 1000 | 114.3 | 10.287 | 10.287 | 134.874 | 134874
3000004053 | 4CX6 Sq. mm. Al cable (XLPE) | 2000 | 112 | 9.1.7 | 4 CX 6 mm2 PVC | Mtrs | 2000 | 112 | 10.08 | 10.08 | 132.16 | 264320
3000004054 | 2CX6Sq. mm. Al cable (XLPE) | 2000 | 98 | 9.1.8 | 2CX 6 mm2 PVC | Mtrs | 2000 | 98 | 8.82 | 8.82 | 115.64 | 231280
|  |  | 0 | 9.2 | CONTROL CABLES,1.1 KV, PVC ARMOURED, FRLSH, Stranded Copper (As per specification) including control cable termination & other materials. - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule)
3000004098 | 2 CX 2.5 mm2 | 3000 | 77.41 | 9.2.1 | 2 CX 2.5 mm2 | Mtrs | 3000 | 77.41 | 6.9669 | 6.9669 | 91.3438 | 274031.4 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000004056 | 4 CX 2.5 mm2 | 3000 | 122.09 | 9.2.2 | 4 CX 2.5 mm2 | Mtrs | 8000 | 122.09 | 10.9881 | 10.9881 | 144.0662 | 1152529.6
3000000108 | 2.5SQMM 5C CONTROL CABLE | 3 | 122090 | 9.2.3 | 5CX 2.5 mm² | Mtrs | 3 | 122090 | 10988.1 | 10988.1 | 144066.2 | 432198.6
3000004058 | 7CX 2.5 mm2 | 3000 | 184.82 | 9.2.4 | 7CX 2.5 mm² | Mtrs | 3000 | 184.82 | 16.6338 | 16.6338 | 218.0876 | 654262.8
3000004059 | 10 CX 2.5 mm2 | 3000 | 251.17 | 9.2.5 | 10 CX 2.5 mm2 | Mtrs | 3000 | 251.17 | 22.6053 | 22.6053 | 296.3806 | 889141.8
3000000111 | 12C X 2.5 Sqmm control cable | 3 | 122090 | 9.2.6 | 12 CX 2.5 mm2 | Mtrs | 3 | 122090 | 10988.1 | 10988.1 | 144066.2 | 432198.6
3000004061 | 16 CX 2.5 mm2 | 500 | 382.1 | 9.2.7 | 16 CX 2.5 mm2 | Mtrs | 500 | 382.1 | 34.389 | 34.389 | 450.878 | 225439
3000000113 | 19C X 2.5 Sqmm control cable | 0.5 | 443110 | 9.2.8 | 19 CX 2.5 mm2 | km | 0.5 | 443110 | 39879.9 | 39879.9 | 522869.8 | 261434.9
|  |  | 0 | 9.3 | SINGLE CORE 1.1KV, PVC UN-ARMOURED COPPER CONDUCTOR: for connection from Battery Set to Battery Charger and from Battery Charger to DCDB on cable tray / HDPE pipe/PVC pipe etc
3000000218 | 1Cx120 SQMM POWER CABLE CU | 0.5 | 635000 | 9.3.1 | 1CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | Mtrs | 0.5 | 635000 | 57150 | 57150 | 749300 | 374650 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  | 0 | 9.4 | Supply of screened / Shielded Twisted pair copper cable for Analog Communication for showing winding temp, Oil temp,lighting, fire fighting, DG etc, LT current & LT voltage signals of sub-station auxiliary system in HMI
3000003918 | 8PX1.5 Sq. mm. screened copper cable | 2750 | 296 | 9.4.1 | 8PX1.5 mm2 screened copper cable | Mtrs | 2750 | 296 | 26.64 | 26.64 | 349.28 | 960520 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000003919 | 2PX1.5 Sq. mm. screened copper cable | 200 | 59.322 | 9.4.2 | 2PX1.5 mm2 screened copper cable | Mtrs | 200 | 59.322 | 5.339 | 5.339 | 70 | 14000
|  |  | 0 | 10 | Supply of Power Transformer with spares as per technical specification & conducting the type tests as per the TS. (Including NCT as per TS for High Impedance REF protection)
1000000515 | 220/33 kV, 100 MVA Power Transformer | 2 | 83211885 | 10.1 | 220/33 KV, 100 MVA Yn Yn Power Transformer with accessories and NCT's & spare as per TS | Nos | 2 | 83211885 | 7489069.65 | 7489069.65 | 98190024.3 | 196380048.6 | AS per PO 4100000080, date.18.03.2026 of CGM(CPC), OPTCL, HQRS( To Atlanta) | Not Incorporated in Erection Portion
3000004021 | Type test for 220/33 kV 100 MVA PTR | 1 | 15039999 | 10.2 | The following type tests shall be carried out in presence of Purchaser’s representative on one unit out of the lot at the discretion of the purchaser. - Temperature Rise Test - Top oil & hot spot temp. rise test-Winding temp rise test - Measurement of zero sequence reactance. IP 55 test | Lot | 1 | 15039999 | 1353599.91 | 1353599.91 | 17747198.82 | 17747198.82
|  |  | 0 | 10.3 | Other requirement of 100MVA 220/33KV Power Transformer as indicated below and as per technical specification.
4000000225 | Other requirement for 220/33 kV 100 MVA | 2 | 11711115 | 10.3.1 | 1. Nitrogen injection system for protection against fire & explosion as per T.S. 2. Online Insulating oil drying System in complete shape to complete the work as per T.S. 3. Digital RTCC Panel for Transformer in complete shape to complete the work as per T.S. and instruction of Engineer in Charge. | Lot | 1 | 11711115 | 1054000.35 | 1054000.35 | 13819115.7 | 13819115.7
|  |  | 0 | 11 | SUPPLY OF STATION TRANSFORMER & OTHER MATERIALS FOR MEETING THE AUXILIARY SUPPLY OF THE SUBSTATION AS PER TECHNICAL SPECIFICATION
1000000147 | 250KVA 33/0.4KV STATION Tfr or 200KVA | 2 | 614057.61 | 11.1 | STATION TRANSFORMER 33KV/0.43 KV,250 KVA (AS PER SPECIFICATION) | Nos | 2 | 614057.61 | 55265.1849 | 55265.1849 | 724587.9798 | 1449175.9596 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
2000000108 | HG Fuse set- 33kV side | 2 | 9569 | 11.2 | HG Fuse set- for 33kV side of the station transformer including the mounting insulators, channels complete in all respect (each set comprises three single HG fuse) | Sets | 2 | 9569 | 861.21 | 861.21 | 11291.42 | 22582.84
|  |  | 0 | 12 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS) (includes switchyard, colony street and other street area). The below mentioned quantity is only indicative. Actual quantity shall be as per the lighting calculation. Lux levels as per OPTCL TS/National Lighting Code/IS 6665 shall be maintained. (Supply of cables required are covered in the cable items indicated above)
3000004303 | Switchyard lighting | 20 | 15000 | 12.1 | SUB-STATION SWITCH YARD LIGHTING : IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED - 150 watt each) of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear, GI Conduit etc. (Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved). | Set | 20 | 15000 | 1350 | 1350 | 17700 | 354000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000000913 | STREET LIGHTING WITH GI T.POLE | 40 | 21750 | 12.2 | STREET LIGHTING: HDG Octagonal street lighting poles 7 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. The pole shall be manufactured in a single section with weight of galvanization 610 g/sqm or thickness of galvanization 86 micron. The pole shall be meant for installation in Wind Zone V. Poles should be suitable for installation on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes supply of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro), with switch gear, GI Conduit etc. & as per technical specification. The pole shall have separate or inbuilt GI junction box with suitable cover with (water/dust) ingress protection for housing electrical accessories. The JB shall have provision of fuses/MCB, buses, TBs as required for cable in and out. | Nos. | 40 | 21750 | 1957.5 | 1957.5 | 25665 | 1026600
3000004304 | Lighting provision | 1 | 50000 | 12.3 | Lighting provision for other Areas: Suitable for (a) Garden Lighting (8 nos of 70W LED) with necessary post top lantern with pole | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000
|  |  | 0 | 13 | AIR CONDITIONING: Supply of 2T capacity Split Air Conditioning Units (Dual Inverter, five star latest model - LG/Samsung/Hitachi/Carrier/Mitsubishi/Voltas/Daikin Make) with copper condensor having remote temperature & operation control facility with voltage stabilizer. This also includes AC Control Panel made of 2mm CR sheet, having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (As per specification) for CRB cum GIS (Control/SAS Room, AC DC Room, Communication room, office room & Conference room), Switchyard Kisok, Transit House. Supply of Logic controller for Auto Switch ON & OFF of AC units depending on requirement. Also includes supply of all other additional accessories such as copper tubes, copper cable, steel brackets for holding outdoor units and other accessories necessary for completion of the AC system. As per approved drawing and direction of engineer-in-charge.
1000000706 | Air conditioners inside substation | 16 | 65000 | 13.1 | AC for CRB and GIS(CRP Room): For Control/SAS Room, Relay panel room, ACDC Room Communication room, office room & Conference room. | Set | 16 | 65000 | 5850 | 5850 | 76700 | 1227200 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
1000000707 | AC for Switchyard Kiosk | 2 | 65000 | 13.2 | AC for Switchyard Kiosk as per T.S. (The ACs shall run in tandem i.e 1 of the ACs at a time for 4 hours each.) | Set | 2 | 65000 | 5850 | 5850 | 76700 | 153400
1000000706 | Air conditioners inside substation | 4 | 65000 | 13.3 | AC For Transit House | Set | 4 | 65000 | 5850 | 5850 | 76700 | 306800
|  |  | 0 | 14 | FIRE FIGHTING SYSTEM(PORTABLE /TROLLEY/ WHEEL MOUNTED FIRE EXTINGUSHERS SETS FOR CONTROL ROOM, EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC
4000000087 | Foam 09 Litres Fire Extinguishers | 4 | 2000 | 14.1 | FOAM TYPE-9 LTRS | Nos | 4 | 2000 | 180 | 180 | 2360 | 9440 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
4000000093 | DRY CHEMICAL POWDER - 22.5 KGS | 4 | 13000 | 14.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22 5 KGS | Nos | 4 | 13000 | 1170 | 1170 | 15340 | 61360
4000000090 | DCP TYPE 5KG FIRE EXTINGUISHER | 4 | 2500 | 14.3 | DRY POWDER TYPE - 5 KGS | Nos | 4 | 2500 | 225 | 225 | 2950 | 11800
4000000080 | CO2 TYPE 4.5 KG FIRE EXTINGUISHER | 10 | 5500 | 14.4 | Co₂- 4.5 KGS | Nos | 10 | 5500 | 495 | 495 | 6490 | 64900
4000000085 | CO2 TYPE 9 KG FIRE EXTINGUISHER | 15 | 12000 | 14.5 | CO₂ - 9 KGS | Nos | 15 | 12000 | 1080 | 1080 | 14160 | 212400
4000000084 | CO2 TYPE 22.5 KG FIRE EXTINGUISHER | 8 | 25000 | 14.6 | CO₂ (TROLLY MOUNTED)- 22.5 KGS | Nos | 8 | 25000 | 2250 | 2250 | 29500 | 236000
4000000094 | 9 litre water type | 4 | 2000 | 14.7 | 9 litre water type | Nos | 4 | 2000 | 180 | 180 | 2360 | 9440
4000000267 | DCP Type 4.5 kg fire extinguisher | 6 | 3000 | 14.8 | 4.5 kg DCP type | Nos | 6 | 3000 | 270 | 270 | 3540 | 21240
4000000207 | Foam FE 50 kg | 6 | 10000 | 14.9 | 50 Litres Mechanical Foam type | Set | 6 | 10000 | 900 | 900 | 11800 | 70800
4000000232 | Fire bucket with stand | 8 | 5000 | 14.1 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND & ITS CANOPY | Set | 8 | 5000 | 450 | 450 | 5900 | 47200
|  |  |  | 15 | SUBSTATION AUTOMATION SYSTEM FOR 220/33 KV SUBSTATION ON PRP MODE: Design , engineering , drawing, supervision, installation , testing & commissioning of Substation Automation system (IEC 61850) for (Complete 220 kV and 33 kV system) along with Supply of the following 220 and 33 kV level of protection panels consisting of Bay control Units & numerical protection relays and other auxiliary relays suitable for SAS as per technical specification. NOTE: All protective relays & BCU shall be numerical type.
1000000575 | Substation automation system | 1 | 9537255.79 | 15.1 | "SUBSTATION AUTOMATION SYSTEM (IEC 61850) Gateway Panel ( 2 layer type) : for Sub-Station Automation (in PRP on FO as per the specification) system (for All 132 & 33 KV side bays) and with other accessories, comprising: 1. Gateway (Non-Windows or Linus or Firmware based)- 2 nos. with 8 ethernet ports each 2. BCU for Substation Auxilliary System 3. Ethernet Switches (with 20% spares Port) for bay & station level 4. LIU 5. Multimode glass fibre Doublle jacket armoured optical cables 6. Red boxes etc. including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. | Set | 1 | 9537255.79 | 858353.0211 | 858353.0211 | 11253961.8322 | 11253961.8322 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project. | The price may be considered accordingly | Not Incorporated in Erection Portion
|  |  |  | 15.2 | RTCC Communication Panel (3 layer type) ; comprising of: 1. Substation Ethernet Switches- 2 nos 2. Firewall cum Router-2 set 3. Station Data Concentrator (SDC)- 2 nos 5. LIU 6. Multimode glass fibre Double jacket armoured optical cables 7. Red boxes etc. 8. Provision for mounting the VMS switch etc including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect for remote communication & as per technical specification. | [7 empty] | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project. | The price may be considered accordingly | Not Incorporated in Erection Portion
|  |  |  | 15.3 | Operator Workstations | [8 empty] | The price may be considered accordingly | Not Incorporated in Erection Portion
|  |  |  | 15.4 | Engineering workstation
|  |  |  | 15.5 | Workstation for RAS (Remote Access System)
|  |  |  | 15.6 | Black & whiter Laser jet Printer-1Nos
|  |  |  | 15.7 | Inverters - 3 KVA (Main & Stand by)
|  |  |  | 15.8 | Furniture (Operator desk 3 Nos (for SAS, RAS, VMS) & Chair-6Nos) etc.
|  |  |  | 15.9 | GPS System with IRIG-B/SNTP/PTP with VDU (Clock)
|  |  |  | 15.4 | 220 KV SIDE PROTECTION PANEL - Single Panel (1 Bay in One Panel) with IEC 61850-ED-2 PRP on FO
3000001290 | 220kv FP Relay panelDistance portection | 6 | 2850000 | 15.4.1 | 220KV FEEDER PROTECTION PANEL: Distance protection Relay (Main-I & Main-II of different make) with auto reclosure, Numerical Backup Protection Relay, Bay control unit (BCU) with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | NOS | 6 | 2850000 | 256500 | 256500 | 3363000 | 20178000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000001289 | 220KV Transformer Protection Panel | 2 | 3520000 | 15.4.2 | 220 KV TRANSFORMER PROTECTION PANEL: Numerical Differential protection Relay, Separate Numerical REF Relay (high impedance type), Numerical Back up protection relay & BCU for 220 KV side) CONSIDERING HV side of 220/33 KV, 100 MVA Two winding transformer with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | NOS | 2 | 3520000 | 316800 | 316800 | 4153600 | 8307200
1000000624 | 220 kV Buscoupler Protection Panel | 1 | 1200000 | 15.4.3 | 220 KV BUS COUPLER PROTECTION PANEL: With Bay control unit (BCU) & Numerical Back-up protection relay with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | SET | 1 | 1200000 | 108000 | 108000 | 1416000 | 1416000
1000000909 | 220KV BB PROTECTION PANEL (Centralized Architecture) | 1 | 3750000 | 15.4.4 | 220 KV BUS-BAR PROTECTION PANEL(s) (Centralized Architecture): Complete centralized type bus bar protection system for proposed bays and Provision for future bays (four nos) and with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | LOT | 1 | 3750000 | 337500 | 337500 | 4425000 | 4425000
|  | 0 | 0 | 15.5 | 33 KV SIDE PROTECTION PANELS
1000000577 | 33 kV twin feeder prt panel | 3 | 1015993.9167 | 15.5.1 | 33KV Feeder Protection Panel: with BCU, Numerical backup relay & with other Auxiliary relays as required as per the scheme compliant to IEC 61850 - ED-2 protocol with PRP on FO. Power Supply 220V DC. 33KV Buscoupler Protection Panel: with BCPU & with other Auxiliary relays as required as per the scheme compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Note: 5 Nos. of line feeder bays and 1 B/C bay to be considered in 3 panel. | NOS | 3 | 1015993.9167 | 91439.4525 | 91439.4525 | 1198872.8217 | 3596618.465 | cd ss-47 |  | 1015993.9167
1000000578 | 33 kV TFR feeder prt panel | 2 | 914394.515 |  | 33KV Transformer protection panel: with BCU, Numerical backup relay, separate numerical REF & with other Auxiliary relays as required as per the scheme, compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Note: 2 Nos. of transformer feeder bays to be considered in 1 panel. | Nos. | 2 | 914394.515 | 82295.5063 | 82295.5063 | 1078985.5277 | 2157971.0554 | cd ss-48 |  | 914394.515
|  |  | 0 | 16 | AC & DC SYSTEM
|  |  | 0 | 16.1 | AC SYSTEM
|  |  | 0 | 16.1.1 | Indoor Type as per TS: | [8 empty] | Not Incorporated in Erection Portion
3000000914 | MAIN AC DB (Indoor Type)800A | 1 | 371115.33 | 16.1.1.1 | MAIN AC DB (Indoor Type) as per T.S. | SET | 1 | 371115.33 | 33400.3797 | 33400.3797 | 437916.0894 | 437916.0894 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000000915 | ACDB (Indoor Type) 400A | 1 | 371115.33 | 16.1.1.2 | ACDB (Indoor Type) as per T.S. The ACDB shall be suitable for automatic switching OFF & ON , auto start of DG set etc during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 | 371115.33 | 33400.3797 | 33400.3797 | 437916.0894 | 437916.0894
3000000916 | MLDB (INDOOR) (INDOOR TYPE) | 1 | 191442.2344 | 16.1.1.3 | Main Lighting Distribution Board (Indoor Type) as per T.S. | SET | 1 | 191442.2344 | 17229.8011 | 17229.8011 | 225901.8366 | 225901.8366 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000000917 |  | 1 | 24249.3497 | 16.1.1.4 | Indoor Lighting Distribution Board (Indoor Type) as per T.S. | SET | 1 | 24249.3497 | 2182.4415 | 2182.4415 | 28614.2326 | 28614.2326
3000000918 | Emergency Lighting DB | 2 | 21058.6458 | 16.1.1.5 | Emergency Lighting Distribution Board (Outdoor type) as per T.S | SET | 2 | 21058.6458 | 1895.2781 | 1895.2781 | 24849.202 | 49698.404
3000000919 | Indoor Receptacle Board | 2 | 7657.6894 | 16.1.1.6 | INDOOR RECEPTACLE BOARD as per T.S. | SET | 2 | 7657.6894 | 689.192 | 689.192 | 9036.0735 | 18072.1469
3000000976 | ACDB for Yard Kiosk | 1 | 37115.33 | 16.1.1.7 | ACDB for Yard Kiosk (Indoor Type): LT supply to Protection panels, Kiosk lighting, AC etc as per T.S. | Nos | 1 | 37115.33 | 3340.3797 | 3340.3797 | 43796.0894 | 43796.0894
|  |  | 0 | 16.1.2 | Outdoor Type, Sub Station Swithyard Console Boxes, HDG type (86 micron), 3 mm thick CRCA, (BMK,AC CONSOLE & OTHER MB) as per TS.
3000001306 | BAY MARSHALLING KIOSK | 5 | 148445.88 | 16.1.2.1 | Bay Marshalling Kiosk: 2 BMK for 7 nos 220KV bays and 3 BMK for 5 nos 33KV bays & 2 nos of Tfr bays with 1 no of B/C bay | SET | 5 | 148445.88 | 13360.1292 | 13360.1292 | 175166.1384 | 875830.692 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000001310 | SWITCHYARD AC CONSOLE FOR LIGHTING | 2 | 54087.06 | 16.1.2.2 | Console box for switchyard lighting | SET | 2 | 54087.06 | 4867.8354 | 4867.8354 | 63822.7308 | 127645.4616
|  |  |  | 16.1.2.3 | Switchyard Receptacle Board for Transformer Oil Filteration | NOS | 1 | 54087.06 | 4867.8354 | 4867.8354 | 63822.7308 | 63822.7308
3000001309 | SWITCH YARD RECEPTACLE BOARD | 3 | 54087.06 | 16.1.2.4 | Switchyard Receptacle Board for welding and other emergency | NOS | 2 | 54087.06 | 4867.8354 | 4867.8354 | 63822.7308 | 127645.4616
3000000996 | CT CONSOLE BOX | 8 | 54087.06 | 16.1.2.5 | CT CONSOLE BOXES as per TS (33 KV CT) | NOS | 8 | 54087.06 | 4867.8354 | 4867.8354 | 63822.7308 | 510581.8464
3000000992 | CT/IVT/CVT CONSOLE BOX | 8 | 44533.64 | 16.1.2.6 | IVT CONSOLE BOXES as per TS (220 KV & 33 KV) | NOS | 8 | 44533.64 | 4008.0276 | 4008.0276 | 52549.6952 | 420397.5616
3000000975 | Console Box for StreetLight | 2 | 44533.64 | 16.1.2.7 | Console box for street lighting | NOS | 2 | 44533.64 | 4008.0276 | 4008.0276 | 52549.6952 | 105099.3904
1000000567 | Consoile for colony/TH supply | 1 | 148445.88 | 16.1.2.8 | Console box for Transit House/Colony Supply purpose | NOS | 1 | 148445.88 | 13360.1292 | 13360.1292 | 175166.1384 | 175166.1384
3000004085 | Outdoor kiosk for Station Transformer | 2 | 44533.64 | 16.1.2.9 | OUT DOOR KIOSK FOR STATION TRANSFORMER With Busbar & SFU of appropriate rating with required sizes of terminal studs for power cable termination & any other accessories as per T.S. and instruction of Engineer in Charge | SET | 2 | 44533.64 | 4008.0276 | 4008.0276 | 52549.6952 | 105099.3904
|  |  | 0 | 16.2 | DC SYSTEM
1000000609 | 220V DCDB (INDOOR TYPE) | 2 | 371115.33 | 16.2.1 | 220 V DC DISTRIBUTION BOARD (Indoor Type) as per T.S. | SET | 2 | 371115.33 | 33400.3797 | 33400.3797 | 437916.0894 | 875832.1788 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project. | Not Incorporated in Erection Portion
3000001304 | 220V DC Emergency Ligh DB | 6 | 93224 | 16.2.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD (Indoor Type) as per T.S. | Nos | 1 | 93224 | 8390.16 | 8390.16 | 110004.32 | 110004.32
3000004191 | 350 Ah, VRLA Battery set |  | 2025000 | 16.2.3 | BATTERY BANK (350 AH VRLA Type) for 220 V DC System as per TS | SET | 2 | 2025000 | 182250 | 182250 | 2389500 | 4779000
3000004192 | 350 Ah battery charger for VRLA battery |  | 400396.18 | 16.2.4 | Battery Charger For 350 AH VRLA Type Battery, Charger ON/OFF status, input/output voltage, output current, associated charger protection signals shall be provided for integration with SAS & its spare as per TS. | SET | 2 | 400396.18 | 36035.6562 | 36035.6562 | 472467.4924 | 944934.9848 | BADAKUSHASTHALI 29
3000001302 | DCDB for Yard Kiosk | 1 | 54087.06 | 16.2.5 | DCDB for Yard Kiosk (Indoor Type) as per T.S. | Nos | 1 | 54087.06 | 4867.8354 | 4867.8354 | 63822.7308 | 63822.7308
|  |  | 0 | 17 | GIS Hall Ventilation and Exhaust System:
4000000209 | 220kV GIS hall ventilation system | 1 | 382884.4688 | 17.1 | 220 KV GIS hall ventilation system through ducting with 04 air change cycle per hour (Pressurization type ventilation system) as per technical specification and recommendation of GIS manufacturer | LOT | 1 | 382884.4688 | 34459.6022 | 34459.6022 | 451803.6731 | 451803.6731 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
1000000863 | Exhaust system for 220 kV GIS hall | 1 | 100000 | 17.2 | GIS Hall exhaust system: Exhaust fans for installation at 1 feet above the GIS hall floor level for exhaust of SF6 gas. Sufficient numbers of exhaust fans of required capacity to be provided for 1 air change per hour, accordingly calculation to be submitted. The exhaust outlet shall be directed downwards at the outer side of the GIS hall and shall be fixed with aluminum mesh at outlet. The exhaust fans shall have louvers for automatic closing when not in use. Control of the system shall be from the SAS-HMI room. Includes supply of panels and other associated materials. | LOT | 1 | 100000 | 9000 | 9000 | 118000 | 118000
1000000812 | Smoke & Heat Detection - 220 kV GIS Hall | 1 | 811715.0737 | 18 | Supply of Smoke & Heat detection system: Addressable optical Smoke & Heat Multi detector (quantity as per approved design calculation) for GIS cum control room building including all accessories, the Main control panel (Microprocessor based 2 loop fire alarm control panel expandable upto 18 loops fully networkable with each loop capable of taking 99 devices, 8 line x 40 character alpha- numeric liquid crystal display .The panel shall be soft addressable type . The panel shall be able to give pin point location of all fire/fault conditions. Further, the panel must be able to automatically switch off respective control switches when ever any alarm is triggered. The panel shall have in built rectifier, Loop cards,provision for externel & internal printer(if required), L C D unit to indicate Fire/Fault Signal with address and analog output, built in printer to log all fire or fault events complete in all respects, integral SMF lead acid batteries with sealed cells of 24 V capable of running for a minimum of 8 hours with integral battery charger complete as required and as per specification. The fire alarm panel shall be suitable for software integration with BMS & PA system ,wall mounting loop powered addressable type hooter with all accessories , addressable manual call box made of polycarbonate with plastic break glass front and complete with monitor module MCB, addressable isolator module with required PVC box, fittings and fixtures, wiring with PVC FRLS wire to cover the required for fire & smoke detection etc. Should have facility for integration with SAS. | SET | 1 | 811715.0737 | 73054.3566 | 73054.3566 | 957823.787 | 957823.787
3000004413 | 100 kV automatic TFR BDV test set | 1 | 684775.3 | 19 | 100KV Automatic Transformer Oil Breakdown Voltage test set (Megger- OTS 100AF / Baur- DTA 100C) | NOS | 1 | 684775.3 | 61629.777 | 61629.777 | 808034.854 | 808034.854
4000000268 | 10 kV insulation tester | 1 | 505351.83 | 20 | 10KV Automatic Insulation Tester with 15m test lids (Megger- S1-568 / Sonel-MIC 10K1) | NOS | 1 | 505351.83 | 45481.6647 | 45481.6647 | 596315.1594 | 596315.1594
4000000219 | Maintenance Testing Equipment | 1 | 1500000 | 21 | Maintenance Testing Equipment (All equipment shall comply to the TS and as per list below) | Lot | 1 | 1500000 | 135000 | 135000 | 1770000 | 1770000
|  |  | 0 | 21.1 | Digital Earth Tester (Facility with soil resistivity measurement) (Megger-DET2/3 / Sonel MRU-120 / Fluke 1625) | NOS | 1
|  |  | 0 | 21.2 | Digital Multimeter (Megger / Fluke) | NOS | 2
|  |  | 0 | 21.3 | Digital Clamp meter (Megger/Fluke/Motwane) | NOS | 1
|  |  | 0 | 21.4 | Leakage current clamp meterAC & DC both (30mA / 300mA / 30A / 300A) (Megger/Fluke/Kyoritsu) | NOS | 1
|  |  | 0 | 21.5 | Oil sampling Bottle- Stainless Steel, Capacity- 1 Ltr (Make- Tosin/Scope) | NOS | 6
|  |  | 0 | 21.6 | Fibre Glass Discharge / Earth Rod: Grip up to 50mm, Min height-16ft, rubber grip, 35 sq.mm copper cable (1 set- 3 cables, 1 set of rod, carry bag) (Bemico) | SET | 6
|  |  | 0 | 21.7 | Electrical Rubber Hand Gloves | Pairs | 4
|  |  | 0 | 21.8 | Portable High Beam Light (rechargeable) | NOS | 2
|  |  | 0 | 21.9 | Desktop Computer: (HP/Lenovo/Dell) | SET | 2
|  |  | 0 |  | Desktop Computer: (HP/Lenovo/Dell) (i) Processor-Intel Core i5 10th Gen or better (ii) RAM- 8GB DDR4 or More (iii) ROM- 512GB SSD (iv) Monitor- 21.5" FHD (1920 x 1080) or higher (v) Graphics- Onboard/Integrated (vi) OS- Genuine Windows 10 or 11 Pro (vii) Webcam- 720P Logitech (viii) Speaker- 2 nos Stereo type (ix) UPS 600VA (APC/V Guard)
|  |  | 0 | 21.1 | Laser Printer, Black & White, Duplex printing (print, scan & copy) (HP/Canon/Epson) | NOS | 2
|  |  | 320000 | 22 | Other Tools And Plants (T&P'S) Requirement (As Per details below). The T & P materials shall be of Taparia/Bosch/Stanley make. | Lot | 1 | 320000 | 28800 | 28800 | 377600 | 377600 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  | 0 | 22.1 | D Spanner Set (6mm – 42mm) | SET | 1
|  |  | 0 | 22.2 | Ring Spanner Set (6mm – 42mm) | SET | 1
|  |  | 0 | 22.3 | Box spanner set | SET | 1
|  |  | 0 | 22.4 | Pipe Wrench 24 " | NOS | 1
|  |  | 0 | 22.5 | Pipe Wrench 18 " | NOS | 1
|  |  | 0 | 22.6 | Adjustable spanner -12”(slide wrench) | NOS | 1
|  |  | 0 | 22.7 | Adjustable spanner -18”(slide wrench) | NOS | 1
|  |  | 0 | 22.8 | Insulated cutting plier (standard size) | NOS | 1
|  |  | 0 | 22.9 | Nose Plier (standard size) | NOS | 1
|  |  | 0 | 22.1 | Screw Driver set
|  |  | 0 | 22.10.1 | 12” Plain head | NOS | 2
|  |  | 0 | 22.10.2 | 12” star head | NOS | 2
|  |  | 0 | 22.10.3 | 8” Plain head | NOS | 2
|  |  | 0 | 22.10.4 | 6” plain head | NOS | 2
|  |  | 0 | 22.10.5 | 6” star head | NOS | 2
|  |  | 0 | 22.10.6 | Set of screw driver cum line tester | SET | 1
|  |  | 0 | 22.11 | Allen Key set | SET | 2
|  |  | 0 | 22.12 | Files
|  |  | 0 | 22.12.1 | Flat File-12” | NOS | 1
|  |  | 0 | 22.12.2 | Flat file-6” | NOS | 1
|  |  | 0 | 22.12.3 | Round file- 12” | NOS | 1
|  |  | 0 | 22.12.4 | Round file- 6” | NOS | 1
|  |  | 0 | 22.13. | Hammer with Handle
|  |  | 0 | 22.13.1. | 1 lb | NOS | 2
|  |  | 0 | 22.13.2 | 2 lb | NOS | 1
|  |  | 0 | 22.13.3 | ½ lb | NOS | 2
|  |  | 0 | 22.14 | Steel Tape (Any reputed make)
|  |  | 0 | 22.14.1 | 5Mtr | NOS | 1
|  |  | 0 | 22.14.2 | 30Mtr | NOS | 1
|  |  | 0 | 22.15 | Crow bar (Any reputed make)
|  |  | 0 | 22.15.1 | 5ft | NOS | 2
|  |  | 0 | 22.15.2 | 3ft | NOS | 2
|  |  | 0 | 22.16 | Oil Cane (Any reputed make) | NOS | 2
|  |  | 0 | 22.17 | Hand Drill Machine (impact drill) with key (Make-Bosch/Black & Decker) | NOS | 1
|  |  | 0 | 22.18 | Vacuum Cleaner (at least 15L) (Make-Eureka Forbes / Black & Decker / Phillips / Karcher) | NOS | 1
|  |  | 0 | 22.19 | Stand Fan (450mm sweep,1400rpm, 240V AC) (Make-Crompton, Bajaj, Havells, Almonard, Usha) | NOS | 4
|  |  | 0 | 22.2 | Self supproted cum extendable Ladder-25ft (FRP) of Adequate Height to be used for Maintenance of Equipment Inside Switchyard. | NOS | 1
|  |  | 0 | 22.21 | Self supproted platform Ladder- 12feet (FRP) of Adequate Height to be used for Maintenance of Equipment Inside Switchyard. | NOS | 1
4000000007 | 20Ltr Storage Water Cooler | 1 | 50000 | 24 | 20 Ltr Storage Water Cooler (Voltas/Bluestar only) | NOS | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
4000000008 | Water Purifier-RO+UV+UF type | 1 | 20000 | 25 | Water Purifier (RO+UV+UF type) suitable for connecting to the above water storage cooler (Kent/Aquaguard/Livpure/Pureit/Bluestar/LG)only | NOS | 1 | 20000 | 1800 | 1800 | 23600 | 23600
4000000221 | Supply of Office Furniture | 1 | 500000 | 26 | Supply of Office Furniture: Godrej make (As per details below and TS). | Lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000
|  | 1 |  | 26.1 | For Control Room, conference room, office rooms, Library, testing room etc
|  |  |  | 26.1.1 | 5ftX3ft executive table with drawer on both sides | NOS | 4
|  | 4 |  | 26.1.2 | 4.5ft X 2.5ft Table with one side drawer | NOS | 7
|  | 7 |  | 26.1.3 | Computer table suitable keeping monitor, CPU, UPS and printer with two nos revolving arm chair suitable for computer use. | SET | 2
|  | 2 |  | 26.1.4 | Executive revolving, adjustable (height) chairs with arm | NOS | 4
|  | 4 |  | 26.1.5 | Cushion fixed “S” type steel chairs with arm | NOS | 16
|  | 16 |  | 26.1.6 | 6ftX3ft conference table | NOS | 1
|  | 1 |  | 26.1.7 | Cushion arm steel chairs for conference table purpose. | NOS | 6
|  | 6 |  | 26.1.8 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | NOS | 3
|  | 3 |  | 26.1.9 | 6ft height steel almirah with glass doors for library purpose | NOS | 2
|  | 2 |  | 26.1.10 | 6ft height (having minimum 6 lockers facility) steel cupboard with locking arrangement. | NOS | 2
|  | 2 |  | 26.1.11 | 4ft steel rack (minimum three selves) for keeping the files and other items. | NOS | 8
|  | 8 |  | 26.2 | For Communication Room
|  |  |  | 26.2.1 | 5ftX3ft executive table with drawer both sides | NOS | 1
|  |  |  | 26.2.2 | Executive revolving, adjustable (height) chairs with arm | NOS | 1
|  |  |  | 26.2.3 | Cushion fixed “S” type steel chairs with arm | NOS | 2
|  |  |  | 26.2.4 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | NOS | 1
|  |  | NOS | 27 | Essential Tools & Plants as per Technical Specification
4000000203 | SF6 gas anlyzer | 1 | 1152000 | 27.1 | SF6 gas analyzer: Portable type instruments (A). In-built calibration facility. (B). Sensitivity of the equipment shall not be affected by any atmospheric conditions like dust, humidity, heat, wind etc. (C). Equipment shall work on zero gas loss principle i.e. gas should be pumped back to the compartment after measurement without any exposure to the atmosphere.(D). Equipment shall be supplied with suitable regulator which can be used to connect SF6 cylinder if required. (E). Following acidic/impurities products should be detected as per IEC 60480 and IEC 60376 (i) SF6 purity – Range: 0-100 % & Accuracy: +/- 0.5 %, (ii) Dew point - Range : -60 to +20 deg C & Accuracy: +/- 0.5 deg C, (iii) SO2 - Range : 0-150 ppm & Accuracy : +/- 2 %,(iv) CF4 – Range : 0-60% vol & Accuracy : +/- 1 % , (v) HF - Range : 0-200ppm & Accuracy : +/- 5 %, (F). Instrument should work on AC source as well as on rechargeable battery, (G). Input pressure: upto 10 bar h. It should be housed in a robust IP67 case with wheels. | SET | 1 | 1152000 | 103680 | 103680 | 1359360 | 1359360 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
4000000204 | SF6 gas leak detector | 1 | 40000 | 27.2 | SF6 gas leak detector: The detector shall be portable, battery operated with built in battery charger, hand held type and having a minimum SF6 gas leakage sensitivity of 5gm/year. The sensor shall be connected through a flexible wand for easy accessibility to joints, seals and couplings in GIS equipment and provided with a protection filter. The equipment shall have on/off switch & suitable indicating lamps/LEDs, variable pitch audible signal for leakage indication, and a head phone jack. The equipment shall have automatic zeroing of background signals suitable for detecting SF6 gas leakage in charged switchyard AIS/GIS. The test kit shall be compatible for EMI/EMC environment as per IEC 1000. (DILO/KIKA make) | SET | 1 | 40000 | 3600 | 3600 | 47200 | 47200
4000000205 | SF6 filling/storage plant | 1 | 2050000 | 27.3 | SF6 Gas Filling, Evacuating, Filtering, Drying, Pumping & Storage Plant with spares for 5 years Operation. The plant necessary for filling and evacuating the SF6 gas in the switchgear shall be supplied to enable any maintenance work to be carried out. This shall include all the necessary gas cylinders for temporarily storing the evacuated SF6 gas. The capacity of the temporary storage facilities shall at least be sufficient for storing the maximum quantity of gas that could be removed from at least one phase of one complete bay. The minimum capacity of evacuation plant shall be: Vacuum Pump: 40 M3/Hour (Nominal suction pressure) Compressor : 15 M3/Hour(Delivery). The evacuation equipment shall be provided with all the necessary pipes, couplings, flexible tubes and valves for coupling up to the switchgear for filling or evacuating all the gases. The gases compartments shall be fitted with permanent non-return valves through which the gas is pumped into or evacuated form the compartments. The offered model should comply with the revovery and evacuation time as defined in TS which should be certified by TUV-SUD. Make: DILO, Model: B052INDIAR40 | SET | 1 | 2050000 | 184500 | 184500 | 2419000 | 2419000
1000000864 | 82.5 kVA Disel generator | 1 | 904291.31 | 28 | 82.5 KVA outdoor type silent Generator with control panel having adequate mechanical & electrical protection as per latest IS with Automatic Mains Failure feature and statrter CT for differential protection as per Technical spec.Metering CT for DG to be provided with installation of meter as per statutory requirements. Indoor AMF Panel with Switch Gear also included. | NOS | 1 | 904291.31 | 81386.2179 | 81386.2179 | 1067063.7458 | 1067063.7458
1000000484 | 5T EOT crane | 1 | 718400 | 29 | EOT Crane for GIS building for 220 kV GIS station as per T.S. | SET | 1 | 718400 | 64656 | 64656 | 847712 | 847712 |  | Not Incorporated in Erection Portion
2000000246 | BEST QUALITY INSULATING MAT | 60 | 1960 | 30 | Insulating Mat: Best Quality & approved make (Confirming to IS:15652:2006) to be kept infront of all panels, boards etc.(2000X1000X3mm Size) | NOS | 60 | 1960 | 176.4 | 176.4 | 2312.8 | 138768
|  | 1 | 0 | 31 | ACCESSORIES FOR OPGW SYSTEM With OPGW cable
1000000338 | 48F UNDER GROUND FIBRE OPTIC CABLE | 1 | 83537.09 | 31.1 | 48 Fibre Optic Approach cable along with HDPE Pipes | Km | 1 | 83537.09 | 7518.3381 | 7518.3381 | 98573.7662 | 98573.7662 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000003453 | OLTE - STM4 type SDH | 1 | 1200000 | 31.2 | Optical line Terminal Equipment(OLTE) -STM4 type SDH equipment with integrated MUX & tributary cards for speech & data ports for interfacing of Speech & data which should be of same make that has been commssioned at other end susbstation of OPTCL for seamless data integration including all accessories for successful commissioning. | NOS | 1 | 1200000 | 108000 | 108000 | 1416000 | 1416000
3000004092 | Digital Teleprotection Eqpt with SDHMUX | 1 | 309578.34 | 31.3 | Digital Teleprotection Equipment and accessories to be suitable for interfacing with SDHMUX | NOS | 1 | 309578.34 | 27862.0506 | 27862.0506 | 365302.4412 | 365302.4412
1000000295 | 48V,300Ah VRLA Battery | 1 | 117656.93 | 31.4 | 48 V, 300 AH, maintenance free VRLA Battery set. | Set | 1 | 117656.93 | 10589.1237 | 10589.1237 | 138835.1774 | 138835.1774
3000000005 | 48V BATTERY CHARGER | 1 | 109324.96 | 31.5 | SMPS based battery charger of 75A suitable for 48V VRLA battery. | NOS | 1 | 109324.96 | 9839.2464 | 9839.2464 | 129003.4528 | 129003.4528
1000000866 | 48V DCDB | 1 | 42373 | 31.6 | 48V DCDB | NOS | 1 | 42373 | 3813.57 | 3813.57 | 50000.14 | 50000.14
4000000242 | ACDB, DCDB, with accessories | 1 | 15000 | 31.7 | Earth flat, cable tray, telephone cable, ACDB, DCDB, foundation rail, Junction Box, Cat 5 cable & Misc items | Set | 1 | 15000 | 1350 | 1350 | 17700 | 17700
4000000029 | IP Based CCTV Surveillance System | 1 | 819624.16 | 32 | VMS System for survelliance as per T.S. (Supply, Installtion and Commissioning) | Lot | 1 | 819624.16 | 73766.1744 | 73766.1744 | 967156.5088 | 967156.5088 |  | Not Incorporated in Erection Portion
|  | 0 | 0 |  | TOTAL OF SUBSTATION-2A (SUPPLY) | [6 empty] | 660169945.8224 |  |  | 453598139.61 | -206571806.2124
0
|  |  | 0 | B | Part-B_Supply_Mandatory spares
|  |  | BASIC PRICE PER UNIT (Taxable Value) (INR) | SL NO | DESCRIPTION OF ITEMS(SCHEDULE-VIIA-LINE) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | Unit | QUANTITY | BASIC PRICE PER UNIT (Taxable Value) (INR) | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | AMOUNT | REMARK
|  |  | 0 | 1 | SPARES FOR 245KV GIS
3000004265 | OD cable to Oil filled 220kV term kit | 3 | 1072166.14 | 1.1 | 245kV Cable Termination Kit including cable to Air bushing suitable for Outdoor for 220KV feeders and Transformers suitable for 1C x 1000 sqmm Copper Cable. | Nos | 3 | 1072166.14 | 96494.9526 | 96494.9526 | 1265156.0452 | 3795468.1356 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  | 3 | 1072166.14 | 1.2 | 245kV Cable Termination Kit suitable for Indoor for 220KV feeders and Transformers suitable for 1C x 1000 sqmm Copper Cable. (Termination at GIS) | Nos | 3 | 1072166.14 | 96494.9526 | 96494.9526 | 1265156.0452 | 3795468.1356
3000000666 | Set of spares for LCC-220KV GIS | 1 | 310704.068 | 1.3 | Set of spares for local control cabinet (LCC) including M.C.B.(1 nos for each rating used), fuses (3 nos each rating), time relays ( 1 nos for each rating), all type of auxiliary relay (1 nos for each type) & contactors (1 nos for each type), lamps (3 nos for each type), semaphore (3 nos for each type), terminals ( 50 nos), push buttons ( 3 nos for each type) etc for 245KV GIS | SET | 1 | 310704.068 | 27963.3661 | 27963.3661 | 366630.8002 | 366630.8002
3000003980 | SF6 Pressure gauges cum switch or Densi | 1 | 108530.85 | 1.4 | SF6 Pressure gauges cum switch or Density Monitors and pressure switches for 245KV GIS : 2 nos. of each type | SET | 1 | 108530.85 | 9767.7765 | 9767.7765 | 128066.403 | 128066.403
3000004436 | Tripping coil assembly for 220 kV GIS | 4 | 5565.29 | 1.5 | Trip coil assembly with resistor for 245KV GIS Circuit breaker | SET | 4 | 5565.29 | 500.8761 | 500.8761 | 6567.0422 | 26268.1688
3000003982 | Closing coil assembly with resistor for | 4 | 5565.29 | 1.6 | Closing coil assembly with resistor for 245KV GIS Circuit breaker | SET | 4 | 5565.29 | 500.8761 | 500.8761 | 6567.0422 | 26268.1688
3000003984 | Auxiliary contacts for 245 kV GIS circui | 2 | 20871.63 | 1.7 | Auxiliary contacts for 245KV GIS circuit breaker | SET | 2 | 20871.63 | 1878.4467 | 1878.4467 | 24628.5234 | 49257.0468
3000003985 | L.S. & A.C. for 245 kV GIS DS & ES | 2 | 41741.24 | 1.8 | Limit switch & Auxiliary contacts for 245KV GIS DS and ES | SET | 2 | 41741.24 | 3756.7116 | 3756.7116 | 49254.6632 | 98509.3264
3000003986 | SF6 gas in steel bottle 50 Kg / bottle | 2 | 116547.47 | 1.9 | SF6 gas in steel bottle 50 Kg / bottle | SET | 2 | 116547.47 | 10489.2723 | 10489.2723 | 137526.0146 | 275052.0292
3000003987 | Spring charge motor for 245 kV GIS CB | 1 | 20871.63 | 1.1 | Spring charge motor for 245KV GIS circuit breakers | SET | 1 | 20871.63 | 1878.4467 | 1878.4467 | 24628.5234 | 24628.5234
3000004499 | Complete drive for 245 kV GIS CB | 1 | 20871.21 | 1.11 | Complete Drive for 245KV GIS circuit breaker: | SET | 1 | 20871.21 | 1878.4089 | 1878.4089 | 24628.0278 | 24628.0278
3000003989 | Drive mechanism for 245 kV GIS | 1 | 208712.21 | 1.12 | Complete drive mechanism for disconnect switches and grounding switches for 245KV GIS | SET | 1 | 208712.21 | 18784.0989 | 18784.0989 | 246280.4078 | 246280.4078
3000003990 | Motor for discon switch for 245 kV GIS | 1 | 27828.5 | 1.13 | Motor for disconnect switches and grounding switches for 245KV GIS | SET | 1 | 27828.5 | 2504.565 | 2504.565 | 32837.63 | 32837.63
3000003991 | Drive mechanism for 245 kV GIS | 1 | 132184.61 | 1.14 | Complete drive mechanism for fast acting grounding switches for 245KV GIS | SET | 1 | 132184.61 | 11896.6149 | 11896.6149 | 155977.8398 | 155977.8398
3000003992 | Motor for 245 kV GIS | 1 | 27828.5 | 1.15 | Motor for fast acting grounding switches for 245KV GIS | SET | 1 | 27828.5 | 2504.565 | 2504.565 | 32837.63 | 32837.63
3000003983 | Locking device to keep the Disconnectors | 1 | 50000 | 1.16 | Locking device to keep the Disconnectors and Earthing switches in close or Open position in case of removal of driving mechanism for 245KV GIS. | SET | 1 | 50000 | 4500 | 4500 | 59000 | 59000
|  | 0 | 0 | 2 | 245 KV, 2000A, 50KA ISOLATORS
3000002393 | Male&Female contacts of 220KV Isolator | 1 | 50000 | 2.1 | Fixed & Moving Contact Assembly set for One complete Isolator | SET | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
1000000671 | 245 kV SM surge arrestor | 3 | 59726.14 | 3 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 3 | 59726.14 | 5375.3526 | 5375.3526 | 70476.8452 | 211430.5356
1000000555 | 36 kV CT 2000-1000-500 | 3 | 57070.26 | 4 | 36 KV,2000-1000/1A, 31.5 KA, 4CORE SINGLE PHASE CURRENT TRANSFORMER(3 nos PX Class & 1 no 0.2s Class) | Nos | 3 | 57070.26 | 5136.3234 | 5136.3234 | 67342.9068 | 202028.7204
1000000064 | 36KV CT 800-400-200/1-1-1A 0.2s | 3 | 57070.26 | 5 | 36 KV,800-400-200, 31.5KA, 3CORE SINGLE PHASE CURRENT TRANSFORMER (2nos PX Class & 1 no 0.2s Class) | Nos | 3 | 57070.26 | 5136.3234 | 5136.3234 | 67342.9068 | 202028.7204
|  |  | NOS | 6 | 36 KV,1250A & 2000A, ISOLATORS
3000002449 | MALE&FEMALE CONTACT-36KV ISOLATOR | 1 |  | 6.1 | Fixed & Moving Contact Assembly set for One complete Isolator for 1250 A | SET | 1 | 38136 | 3432.24 | 3432.24 | 45000.48 | 45000.48 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  | 0 | 6.2 | Fixed & Moving Contact Assembly set for One complete Isolator for 2000 A | SET | 1
1000000556 | 33kV SL surge arrestor | 3 | 8150 | 7 | Metal oxide polymer housed surge arrrestor for 33 kV system. Station Class Low Duty (SL) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 3 | 8150 | 733.5 | 733.5 | 9617 | 28851
1000000122 | 36KV 2C SP IVT/PT | 1 | 22800 | 8 | 36 KV, 2 Core Single Phase IVT (1 core 3P & 1 core 0.2) | Nos | 1 | 22800 | 2052 | 2052 | 26904 | 26904
|  | 0 | 0 | 9 | 36KV, 1600A 2500 A, VACUUM CIRCUIT BREAKER
3000004503 | One pole assembly for 33kV VCB | 1 | 59322 | 9.1 | One complete Pole Assembly of Circuit Breaker in dust proof and safe packing. | SET | 1 | 59322 | 5338.98 | 5338.98 | 69999.96 | 69999.96 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000001956 | Tripping coil for 36KV VCB SEIL | 4 | 1865 | 9.2 | TRIPPING CIOLS | Nos | 4 | 1865 | 167.85 | 167.85 | 2200.7 | 8802.8
3000001957 | Closing coil for 36KV VCB SEIL | 4 | 1865 | 9.3 | CLOSING COIL | Nos | 4 | 1865 | 167.85 | 167.85 | 2200.7 | 8802.8
3000000943 | 33 KV Bus Post Insulator | 3 | 3503 | 10 | 33 KV Bus Post Insulators | Nos | 3 | 3503 | 315.27 | 315.27 | 4133.54 | 12400.62
|  | 0 | 0 | 11 | BUS BAR & CIRCUIT MATERIALS
3000004504 | Clamps & connectors spare for 220/ 33kV | 1 | 21187 | 12 | Clamps & Connectors for 220 KV & 33 KV (Each type Three Nos - as supplied for the work) . The exact qty of each item under this shall be mentioned by the agency and shall be incorporated in the P.O | Lot | 1 | 21187 | 1906.83 | 1906.83 | 25000.66 | 25000.66 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000001477 | E.cards for 300AH, 48V VRLA Bat charger | 1 | 25424 | 13 | One complete set of Electronic cards for One no. of Battery Charger for 48V VRLA Battery Set. The exact qty of each item under this shall be mentioned by the agency and shall be incorporated in the P.O. | Nos. | 1 | 25424 | 2288.16 | 2288.16 | 30000.32 | 30000.32
3000001478 | E.cards-350AH,220V Plante Bat charger | 1 | 29661 | 14 | One complete set of Electronic cards for One no. of Battery Charger for 220V VRLA Set. The exact qty of each item under this shall be mentioned by the agency and shall be incorporated in the P.O. | SET | 1 | 29661 | 2669.49 | 2669.49 | 34999.98 | 34999.98
|  | 0 | 0 | 15 | Spares for Protection system
|  | 0 | 0 | 15.1 | 220 KV side
3000001350 | DP RELAY M-I | 2 | 211865 | 15.1.1 | Distance Protection Relay (Main-I) | Nos | 1 | 211865 | 19067.85 | 19067.85 | 250000.7 | 250000.7 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  |  | 15.1.2 | Distance Protection Relay (Main-II) | Nos | 1 | 211865 | 19067.85 | 19067.85 | 250000.7 | 250000.7
3000003959 | Diff prot relay set for 220 kV panel | 1 | 220339 | 15.1.3 | Differential Protection Relay (Main-I) | Nos | 1 | 220339 | 19830.51 | 19830.51 | 260000.02 | 260000.02
3000003960 | OC/EF relay set for 220 kV panel | 1 | 220339 | 15.1.4 | Backup O/C & E/F Relay | Nos | 1 | 220339 | 19830.51 | 19830.51 | 260000.02 | 260000.02
3000003957 | BCU for 220 kV panel | 1 | 516011 | 15.1.5 | BCU | Nos | 1 | 516011 | 46440.99 | 46440.99 | 608892.98 | 608892.98
3000001454 | High Impedance REF Relay | 1 | 11695 | 15.1.6 | HV REF Relay | Nos | 1 | 11695 | 1052.55 | 1052.55 | 13800.1 | 13800.1
3000001454 | High Impedance REF Relay | 1 | 11695 | 15.1.7 | LV REF Relay | Nos | 1 | 11695 | 1052.55 | 1052.55 | 13800.1 | 13800.1
3000001427 | Bus VT Selection Relay | 1 | 21187 | 15.1.8 | Bus VT Selection Relay | Nos | 1 | 21187 | 1906.83 | 1906.83 | 25000.66 | 25000.66
3000003961 | Master trip relay for 220 kV panel | 1 | 21187 | 15.1.9 | Master Trip Relay | Nos | 1 | 21187 | 1906.83 | 1906.83 | 25000.66 | 25000.66
3000001336 | Busbar Trip Relay | 1 | 21187 | 15.1.10 | Busbar Trip Relay | Nos | 1 | 21187 | 1906.83 | 1906.83 | 25000.66 | 25000.66
3000001420 | DC Supervision Relay | 1 | 6780 | 15.1.11 | DC Supervision Relay | Nos | 1 | 6780 | 610.2 | 610.2 | 8000.4 | 8000.4
3000003962 | TC supervision relay for 220 kV panel | 1 | 6780 | 15.1.12 | TC Supervision Relay | Nos | 1 | 6780 | 610.2 | 610.2 | 8000.4 | 8000.4
|  | 0 | 0 | 15.2 | 33 KV side
3000003965 | BCPU for 33 kV panel | 1 | 198837 | 15.2.1 | BCPU | Nos | 1 | 198837 | 17895.33 | 17895.33 | 234627.66 | 234627.66
3000001386 | Master Trip Relay | 1 | 21187 | 15.2.2 | Master Trip Relay | Nos | 1 | 21187 | 1906.83 | 1906.83 | 25000.66 | 25000.66
3000001336 | Busbar Trip Relay | 1 | 21187 | 15.2.3 | LBB Trip Relay | Nos | 1 | 21187 | 1906.83 | 1906.83 | 25000.66 | 25000.66
3000001420 | DC Supervision Relay | 1 | 5263 | 15.2.4 | DC Supervision Relay | Nos | 1 | 5263 | 473.67 | 473.67 | 6210.34 | 6210.34
3000001421 | TC Supervision Relay | 1 | 6780 | 15.2.5 | TC Supervision Relay | Nos | 1 | 6780 | 610.2 | 610.2 | 8000.4 | 8000.4
|  |  |  | B | TOTAL SUPPLY OF MANDATORY SPARES FOR SUB-STATION | [6 empty] | 12148765.9896 |  |  | 9742690.05 | -2406075.9396
[5 empty] | Total Supply(PART A+B) | [6 empty] | 672318711.812
Note on A53: PRASANTA: 3000004065
Note on A54: PRASANTA: 3000004066
Note on A55: PRASANTA:
Note on C165: DILLIP: 1+2

## Pahala ERECTION
(ERECTION SUB-STATION) |  |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2x100 MVA, 220KV GIS and 33KV AIS Sub-Station at Pahala with SAS along with 220 KV D/C line from existing 220/132/33KV GIS at Balianta through UG cabling length approx 8.805 Km & Over Head length approx 1.135 Km.
220/33KV GIS Pahala: 220KV GIS feeder Bays-5 Nos +2 spare=7 Nos, Power Tfr-2 Nos, B/C-1 no 33KV AIS Bays- Feeder-5 Nos, Tfr-2 Nos, B/C-1 no
Sl. No. | SUBSTATION EQUIPMENTS / MATERIALS | UNIT | QUANTITY | IN INR |  |  |  |  | Remark
| DESCRIPTION OF ITEMS(SS) ERECTION, INSTALLATION, TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS (As per Technical Specification) |  |  | BASIC PRICE PER UNIT (Taxable Value) | CGST @ 9% PER UNIT | SGST @ 9% PER UNIT | TOTAL PRICE PER UNIT | TOTAL PRICE FOR THE QUANTITY
1 | 2 | 3 | 4 | 5 | 6=5*9% | 7=5*9% | 8=(5+6+7) | 9=4*8 | 10
A | ELECTRICAL WORKS
SUB-STATION
1 | Installation, Testing and Commissioning of 245KV GIS EQUIPMENT as per latest IEC standard & type tested equipment as per technical specification, with open future proof & flexible system in line with IEC 61850 & IEC 62271-203. (Circuit breaker shall be C2 - M2 class as per IEC 62271-100).
1.1 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T,PT), SF6 gas insulated Transformer feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Stand alone Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct (inside the GIS room) & its termination arrangement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete Transformer feeder bay module & its structure and earthing arrangement in complete with earthing strips of adequate size and SF6 gas Insulated Bus Duct inside GIS Hall alongwith associated Support structure arrangement as per the technical specification. | SET | 2 | 325000 | 29250 | 29250 | 383500 | 767000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
1.2 | 245kV, 3150A,50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T & P.T), SF6 gas insulated line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Stand alone Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct (inside the GIS room) & its termination arrangement,PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete line feeder bay module & its structures & earthing arrangement with earthing strips of adequate size and SF6 gas Insulated Bus Duct inside GIS Hall alongwith associated Support structure arrangement as per the technical specification. | SET | 6 | 325000 | 29250 | 29250 | 383500 | 2301000
1.3 | 245kV , 3150A, 50 kA ( 3 sec for Bus bar ,1 sec for disconnector,grounding switch & bus P.T), 3- phase Isolated , SF6 gas insulated , metal enclosed bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with bus potential transformer (3 core), dis connectors , bus bar grounding switch, SF6 gas monitoring system PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete the bus & its earthing arrangement with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | SET | 2 | 325000 | 29250 | 29250 | 383500 | 767000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
1.4 | Bus Coupler Bay Module: 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector, Grounding switch,C.T) SF6 gas insulated Bus Coupler Bay Module comprising of SF6 gas insulated circuit breaker, current transformer, disconnectors switches, disconnector with safety grounding switch(es). Standalone Local control cubicle, SF6 gas monitoring system, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets, Nuts, Bolts & Washers Absorbent, Limit Switch ,SF6 Gas , etc to complete Bus Coupler bay module & its structure and earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification | SET | 1 | 325000 | 29250 | 29250 | 383500 | 383500
1.5 | Laying & Termination of EHV XLPE Power Copper Conductor Cable for the GIS system 245 Kv class including suitable indoor and outdoor cable termination kit and associated cable accessories, clamps etc as per technical specification & direction of Engineer -In-Charge. It also includes all civil works required for laying and termination of EHV cables, earthing cable as per OPTCL TS, including (but not limited to) supply of labour, all materials, T&P, such as excavation, backfilling, disposal of excess earth, RCC concrete slab, filling sand, thermal bakfill etc to complete the work in full shape.
1.5.1 | Laying & Termination including civil works 245KV XLPE cable, 1000 sqmm single core, Copper as per TS.(for interconnection from 245KV GIS to Line) | Mtrs | 2.08 | 4000 | 360 | 360 | 4720 | 9817.6
1.5.2 | 245kV Cable Termination Kit including cable to Air bushing suitable for Outdoor for 220KV feeders suitable for 1C x 1000 sqmm Copper Cable. | Nos | 24 | 100000 | 9000 | 9000 | 118000 | 2832000
1.5.3 | 245kV Indoor Cable Termination Kit for 220KV feeders suitable for 1C x 1000 sqmm Copper Cable. (Termination at GIS) | Nos | 24 | 100000 | 9000 | 9000 | 118000 | 2832000
1.6 | Demonstration of Portable Partial Discharge(PD) monitoring system: 245 KV system shall have Portable Partial Discharge(PD) monitoring system & shall be capable for measuring PD in charged GIS environment , bandwidth in order of 100 MHz–2GHz & provision to select a wide range of intermediate bandwidths and the principle of operation shall be based on UHF principle of detection. The Detection and measurement of PD and bouncing particles having in built large coloured LCD for displaying and storing facility in the instrument for further analysis to locate actual source of PD such as free conducting particles, floating components, voids in spacers, particle on spacer surfaces etc. There shall be minimum six channels for measuring at a time. This includes all accessories. | SET | 1 | 10000 | 900 | 900 | 11800 | 11800 | Market Rate
2 | 220 KV and 33KV AIS Switchyard
2.1 | 245KV, 3 Core, Single Phase Inductive Volatage Transformer (2 core 3P class & 1 core 0.2 class) (AIS) | NOS | 18 | 12207.78 | 1098.7002 | 1098.7002 | 14405.1804 | 259293.2472 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
2.2 | 245KV, 2000A, 50KA, Isolator (AIS) including post insulators (8 KN) as per TS suitable for SCADA operation
2.2.1 | 245KV Single Isolator with Earth switch (for feeder bay) (AIS) | SET | 6 | 25786.48 | 2320.7832 | 2320.7832 | 30428.0464 | 182568.2784 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
2.2.2 | 245KV Single Isolator without Earth switch (for Transformer bay) (AIS) | SET | 2 | 23240.47 | 2091.6423 | 2091.6423 | 27423.7546 | 54847.5092
2.3 | 245KV, 1 phase solid core Bus Post Insulator (8 kN) (AIS) as per Technical Specification. | NOS | 6 | 2219.6 | 199.764 | 199.764 | 2619.128 | 15714.768
2.4 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | NOS | 24 | 4047.57 | 364.2813 | 364.2813 | 4776.1326 | 114627.1824
2.5 | 36 KV,800-400-200, 31.5KA,3CORE SINGLE PHASE CURRENT TRANSFORMER (2nos PX Class & 1 no 0.2s Class) - Feeder Bays | Nos | 15 | 1827.9 | 164.511 | 164.511 | 2156.922 | 32353.83
2.6 | 36 KV,800-400-200, 31.5 KA,4CORE SINGLE PHASE CURRENT TRANSFORMER(3 nos PX Class & 1 no 0.2s Class) - Transformer and Bus Coupler Bays | Nos | 9 | 1827.9 | 164.511 | 164.511 | 2156.922 | 19412.298
2.7 | 36 KV, 31.5KA for 1 sec, AIS ISOLATORS with post insulators as per TS.
2.7.1 | 36 KV, 1250A, 31.5KA for 1 sec, Single Isolator without Earth Switch (for Feeder ) | Nos | 10 | 5222.58 | 470.0322 | 470.0322 | 6162.6444 | 61626.444 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
| 36 KV, 800A, 31.5KA for 1 sec, Single Isolator without Earth Switch (for Station Transformer ) | SET | 2 | 5222.58 | 470.0322 | 470.0322 | 6162.6444 | 12325.2888
2.7.2 | Single Isolator with Earth Switch (Only for Feeder) | Nos | 5 | 5222.58 | 470.0322 | 470.0322 | 6162.6444 | 30813.222
| 36 KV, 2000A, 31.5KA for 1 sec,Single Isolator without Earth Switch (for Power Trf, B/C & Bus section) | SET | 10 | 5222.58 | 470.0322 | 470.0322 | 6162.6444 | 61626.444
2.8 | Metal oxide polymer housed surge arrrestor for 33 kV system. Station Class Low Duty (SL) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor - As per TS | Nos | 27 | 1011.87 | 91.0683 | 91.0683 | 1194.0066 | 32238.1782
2.9 | 36 KV, 2 Core Single Phase IVT (1 core 3P & 1 core 0.2) | Nos | 3 | 1827.9 | 164.511 | 164.511 | 2156.922 | 6470.766
2.1 | 36 KV, 1600A 2500A, 31.5 kA Vacuum Circuit Breaker with supporting Structure as per TS. Facilities for integration with SAS as per the site requirement. | SET | 8 | 18801.28 | 1692.1152 | 1692.1152 | 22185.5104 | 177484.0832
2.11 | 33 KV Solid Core Bus Post Insulator as per TS | Nos | 80 | 509.2 | 45.828 | 45.828 | 600.856 | 48068.48
3 | BUS BAR STRINGING/HOISTING OF INSULATORS/ERECTION OF HW FITTINGS CLAMPS & CONNECTORS: Supply of labour,T&P and other necessary arrangements for stringing of bus bar conductors, hoisting of single or double insulator strings, erection of Single or Double; Suspension/Tension Hard-wares Fittings, Erection of Clamp & connectors, as per requirements, Jumpers, connections to Equipments, testing, commissioning etc. as per the instruction of Engineer-in charge.
3.1 | Single conductor/Phase/Mtr. (ACSR Moose) | MTR | 1000 | 143.62 | 12.9258 | 12.9258 | 169.4716 | 169471.6 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
3.2 | Twin Conductor /Phase/Mtr. (ACSR Bersimis) | MTR | 150 | 196.04 | 17.6436 | 17.6436 | 231.3272 | 34699.08
3.3 | Single conductor/Phase/Mtr. (ACSR Panther) | MTR | 100 | 500 | 45 | 45 | 590 | 59000
3.4 | 3 inch IPS Aluminium Tube for 33 KV Main Bus & Reserve Bus | MTR | 500 | 294.06 | 26.4654 | 26.4654 | 346.9908 | 173495.4
4 | SUBSTATION EARTHING SYSTEMS: Substation earth mat Design, engineering, erection inclusive of corrosion protection measures, laying of earth mat conductors , excavation, welding/jointing of ground conductors along with riser, painting etc as per relenant national and international standards. Substation earth-mat: (a) The Soil resistivity for the substation area is to be measured and approved by OPTCL. (b) The Earth Mat design and layout is to prepared based on the soil resistivity and approved by OPTCL. (c) Laying of earth-mat conductors of Hot dip galvanized flats of size 75X10mm, excavation of earth for laying of earth flat as per approved design & drawing, welding/jointing, application of two coats of bituminous Paint, wrapping of HT Tape etc of ground conductors & etc with back filling and good compaction. The spacing between the earth conductor not more than 5 Mtrs (both way) and to be buried at depth of 700mm from the finished ground level. (d) 50 mm,3 mtr long Heavy duty perforated GI pipes: for treated earth pits (with details of treatment as per IS). (e) Provision of water taps inside the switch yard areas and peripheral for treated earth pit for watering the treated earth pits. Note: The no. of treated and un treated earth pits are to be done as per the practice and as indicated in the drawing for different equipment. (f) The erection of risers of size 50 x 6 mm / 75 x 10 mm GI flats including welding/jointing, application of two coats of bituminous Paint, wrapping of HT Tape etc as per requirement. This is as per approved drawing and specification.
4.1 | EARTHING CONDUCTOR FOR BURRIAL : 75X10 mm GI Flat for laying (spacing maximum 5m both way) The flat is also to be laid from the earth mat up to the foundation level. | MTRS | 5 | 85.77 | 7.7193 | 7.7193 | 101.2086 | 506.043 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
4.2 | EARTHING CONDUCTOR: 50X6 mm GI Flat for Raiser from the foundation level to equipment, structure, columns and up to the bottom of spikes etc.). Each equipment strructure & Columns shall be connected to earth at two separate points. | MTRS | 4.5 | 67.39 | 6.0651 | 6.0651 | 79.5202 | 357.8409
4.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty Gl PERFORATED PIPE 3 mtrs long for treated earth pit) | Nos | 350 | 2327.91 | 209.5119 | 209.5119 | 2746.9338 | 961426.83
4.4 | Switchyard buildings lightning protection (all materials & accessories like Shielding Wire, PG clamp, Test link, D shackle, other required materials etc) as per IS/National Building code standard and as per approved drawing | LOT | 1 | 50000 | 4500 | 4500 | 59000 | 59000
4.5 | Installation of water pipe network from the overhead tank to each treated earth pit as per approved drawing using the UPVC Pipes (2", 1.5", 1" & 1/2" etc), Joints, bends, Valves and all accessories, including the excavation, labour, T & P complete as per instruction of the Site engineer. | LOT | 1 | 100000 | 9000 | 9000 | 118000 | 118000
5 | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained & High Quality ISI mark PVC-U selfit Pipe, PVC elbow bend,PVC Tee etc suitable for under ground burrial (HARD CONDUIT INCLUDING of adequate tensile strength minimum 7kg/sqmm or better) as per TS.
5.1 | G.I Cable Trays(size: 450x75x2500mm) | Mtrs | 1500 | 35 | 3.15 | 3.15 | 41.3 | 61950 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
5.2 | G.I Cable Trays(size: 300x75x2500mm) | Mtrs | 500 | 35 | 3.15 | 3.15 | 41.3 | 20650
5.3 | G.I Cable Trays(size: 150x75x2500mm) | Mtrs | 500 | 35 | 3.15 | 3.15 | 41.3 | 20650
5.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 2.5 | 10000 | 900 | 900 | 11800 | 29500
6 | SWITCH YARD STRUCTURES STEEL HDG - LATTICE TYPE FOR TOWER COLUMN, BEAMS & PIPE TYPE FOR ALL EQUIPMENT STRUCTURE ( INCLUDING FOUNDATION BOLTS - ITS NUTS, ITS WASHERS, ITS PLATE ETC ) FOR 220/33 KV CLASS (Weight in brackets are only indicative - Actual weight shall be as per approved BOM. Measurement shall be done accordingly.)
6.1 | DIFFERENT TYPE OF LATICE TYPE COLUMNS WITH DETAILS (including top earthing spike)
6.1.1 | P1S 220 KV Column Beam (Nominal Weight - 4.03 MT) - 4 Set. | MT | 16.12
6.1.2 | T8S - 33KV (NOMINAL UNIT WT- 0.8 MT)) = 11Sets | MT | 9.13
6.2 | DIFFERENT TYPE OF BEAMS WITH DETAILS
6.2.1 | Q1-Beam 220 KV (NOMINAL UNIT WT- 1.598 MT) = 2 Sets | MT | 3.196
6.2.4 | G4 - 33KV(NOMINAL UNIT WT- 0.4 MT) =08 Sets | MT | 3.2
6.3 | TOTAL WEIGHT OF COLUMN & BEAM INCLUDING FOUNDATION BOLTS, - ITS NUTS, WASHERS PLATE ETC | MT | 31.646 | 4533.3 | 407.997 | 407.997 | 5349.294 | 169283.7579 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
7 | DIFFERENT TYPE OF TUBULAR SUPPORT STRUCTURES HDG TYPE FOR ALL 220KV & 33KV EQUIPMENT INCLUDING FOUNDATION BOLT - ITS NUTS, ITS WASHERS, ITS PLATE ETC )
7.1 | Structure for 220KV SA =27 Nos | MT | 8.4
7.2 | Structure for 220KV IVTs =21 Nos | MT | 7.35
7.3 | Structure for 220 KV Cable Termination (Nominal Wight - 0.219 MT) = 27 + 6 Nos. for line | MT | 5.256
7.4 | 220 KV Single Isolator without Earth Switch =2 Nos | MT | 3
7.5 | 220 KV Single Isolator with Earth Switch = 7 Nos | MT | 9.9
7.6 | Structure for 220KV BPI =6 Nos | MT | 1.86
7.7 | Structure for 33KV CT =24 Nos | MT | 3.552
7.8 | Structure for 33KV IVTS =3 Nos | MT | 0.372
7.9 | Structure for 33KV LAs =27 Nos | MT | 3.996
7.1 | 33 KV Single Isolator without Earth Switch = 7 Nos | MT | 2.065
7.11 | 33 KV Single Isolator with Earth Switch = 5 Nos | MT | 1.625
7.12 | Structure for 33KV BPI =80 Nos | MT | 11.92
7.13 | Structure for 33KV HG Fuse =6 Nos | MT | 1.47
7.14 | TOTAL WEIGHT OF TUBULAR SUPPORT STRUCTURE FOR ABOVE EQUIPMENT INCLUDING GI FOUNDATION BOLTS, ITS NUTS, WASHERS PLATE ETC | MT | 60.766 | 4533.3 | 407.997 | 407.997 | 5349.294 | 325055.1992 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
7.15 | Gl bolts ,Nuts, washers - plain & spring etc for the above LATTICE/PIPE COLUMN, BEAM & EQUIPMENT structures | MT | 4.6206 | 4533.3 | 407.997 | 407.997 | 5349.294 | 24716.9479
8 | 40 Mtrs high Monopole (HDG) Lighting cum Lightning Mast suitable for wind zone-V, including LED lighting fixtures (controlled by Lux meter for variable lux output of the luminaire as per ambient light to attain the reqired lux level) with control gear panel etc and with all accessories like motor for hoisting / lowering the lighting platform and other switchgear & lighting control panel including copper cable, accessories etc. The number and rating of luminaire shall be as per the lighting calculation to attain the required lux level. | SET | 2 | 100000 | 9000 | 9000 | 118000 | 236000
9 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
9.1 | POWER CABLES, 1.1KV, XLPE & PVC, ARMOURED, FRLSH, ALUMINIUM CONDUCTOR (As per Specification) including Power cable termination, all accessories & other materials - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule, based on which material shall be supplied and measurement will be done.)
9.1.1 | 3.5 CX300 mm² XLPE | Mtrs | 1 | 1776.57 | 159.8913 | 159.8913 | 2096.3526 | 2096.3526 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
9.1.2 | 3.5 CX185 mm² XLPE | Mtrs | 500 | 1347.74 | 121.2966 | 121.2966 | 1590.3332 | 795166.6
9.1.3 | 3.5CX120 mm² XLPE | Mtrs | 200 | 796.4 | 71.676 | 71.676 | 939.752 | 187950.4
9.1.4 | 3.5 CX70 mm² PVC | Mtrs | 1000 | 532.97 | 47.9673 | 47.9673 | 628.9046 | 628904.6
9.1.5 | 3.5 CX35 mm² PVC | Mtrs | 3000 | 404.32 | 36.3888 | 36.3888 | 477.0976 | 1431292.8
9.1.6 | 4 CX 16 mm² PVC | Mtrs | 1000 | 214.41 | 19.2969 | 19.2969 | 253.0038 | 253003.8
9.1.7 | 4 CX 6 mm2 PVC | Mtrs | 2000 | 122.52 | 11.0268 | 11.0268 | 144.5736 | 289147.2
9.1.8 | 2CX 6 mm2 PVC | Mtrs | 2000 | 98.02 | 8.8218 | 8.8218 | 115.6636 | 231327.2
9.2 | CONTROL CABLES,1.1 KV, PVC ARMOURED, FRLSH, Stranded Copper (As per specification) including control cable termination & other materials. - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule)
9.2.1 | 2 CX 2.5 mm2 | Mtrs | 3000 | 42.88 | 3.8592 | 3.8592 | 50.5984 | 151795.2 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
9.2.2 | 4 CX 2.5 mm2 | Mtrs | 8000 | 42.88 | 3.8592 | 3.8592 | 50.5984 | 404787.2
9.2.3 | 5CX 2.5 mm² | Mtrs | 3 | 42.88 | 3.8592 | 3.8592 | 50.5984 | 151.7952
9.2.4 | 7CX 2.5 mm² | Mtrs | 3000 | 42.88 | 3.8592 | 3.8592 | 50.5984 | 151795.2
9.2.5 | 10 CX 2.5 mm2 | Mtrs | 3000 | 49 | 4.41 | 4.41 | 57.82 | 173460
9.2.6 | 12 CX 2.5 mm2 | Mtrs | 3 | 49 | 4.41 | 4.41 | 57.82 | 173.46
9.2.7 | 16 CX 2.5 mm2 | Mtrs | 500 | 49 | 4.41 | 4.41 | 57.82 | 28910
9.2.8 | 19 CX 2.5 mm2 | Mtrs | 0.5 | 61.27 | 5.5143 | 5.5143 | 72.2986 | 36.1493
9.3 | SINGLE CORE 1.1KV, PVC UN-ARMOURED COPPER CONDUCTOR: for connection from Battery Set to Battery Charger and from Battery Charger to DCDB on cable tray / HDPE pipe/PVC pipe etc
9.3.1 | 1CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | Mtrs | 0.5 | 230 | 20.7 | 20.7 | 271.4 | 135.7 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
9.4 | Supply of screened / Shielded Twisted pair copper cable for Analog Communication for showing winding temp, Oil temp,lighting, fire fighting, DG etc, LT current & LT voltage signals of sub-station auxiliary system in HMI
9.4.1 | 8PX1.5 mm2 screened copper cable | Mtrs | 2750 | 42.88 | 3.8592 | 3.8592 | 50.5984 | 139145.6 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
9.4.2 | 2PX1.5 mm2 screened copper cable | Mtrs | 200 | 42.88 | 3.8592 | 3.8592 | 50.5984 | 10119.68
10 | Installation, Testing and Commissioning of Transformers/Reactors: Receiving the Transformers and its accessories from nearest OPTCL stores, dragging and installing on the plinth and placing in position, Erection of accessories of the Transformers, erection of NCTs on the Transformers, Earthing as per Standard (Including Supply of Materials), Vacuum Treatment of the tank and winding, Oil Filtration (Including Supply of Vacuum cum Oil Filter Machine), Supply & Laying of all types of Control & Power Cables Pertaining to Transformers, Testing and Commissioning including all tests of the Oil as per stipulation in the Standard Approved Testing Laboratory and as per the instruction of the Engineer in Charge. This include all related works for Erection, Testing and Commissioning of the Power Transformers/Auto Transformers. (Contractor to arrange Power Supply for Filtration And Vacuum Treatment works). It also includes supply of all materials required for erection Including T & P's.
10.1 | 100 MVA, 220/33 KV Power Transformer with accessories (including the NIFPES, Online insulating drying out system, oil storage tank etc) in complete shape as per Technical spec: | Nos | 2 | 318865.155 | 28697.8639 | 28697.8639 | 376260.8829 | 752521.77 | Technical Sanction Order no. - 82 , dated. 12.08.2025 of SGM(P) II, OPTCL
10.2 | Testing & commisioning of the Digital RTCC relays for each trasnformer. The DM & the Marshalling box of the transformer shall be wired with the RTCC relay and tested for its performance locally(HMI of relay) and through SAS. | Nos | 2 | 20000 | 1800 | 1800 | 23600 | 47200 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
11 | Erection, Testing and commissioning of Station Transformer complete with all accessories & Other materials for meeting the auxiliary supply of the subsation as per technical Specification.
11.1 | STATION TRANSFORMER 33KV/0.43 KV,250 KVA (AS PER SPECIFICATION) | NOS | 2 | 23501.6 | 2115.144 | 2115.144 | 27731.888 | 55463.776 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
11.2 | HG Fuse set- for 33kV side of the station transformer including the mounting insulators, channels complete in all respect (each set comprises three single HG fuse) | SET | 2 | 5000 | 450 | 450 | 5900 | 11800
12 | ERECTION TESTING AND COMISIONING OF SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS) (includes switchyard, colony street and other street area). The below mentioned quantity is only indicative. Actual quantity shall be as per the lighting calculation. Lux levels as per OPTCL TS/National Lighting Code/IS 6665 shall be maintained. (Supply of cables required are covered in the cable items indicated above)
12.1 | SUB-STATION SWITCH YARD LIGHTING : IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED - 150 watt each) of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear, GI Conduit etc. (Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved). | NOS | 20 | 2219.6 | 199.764 | 199.764 | 2619.128 | 52382.56 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
12.2 | STREET LIGHTING: HDG Octagonal street lighting poles 7 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. The pole shall be manufactured in a single section with weight of galvanization 610 g/sqm or thickness of galvanization 86 micron. The pole shall be meant for installation in Wind Zone V. Poles should be suitable for installation on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes supply of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro), with switch gear, GI Conduit etc. & as per technical specification. The pole shall have separate or inbuilt GI junction box with suitable cover with (water/dust) ingress protection for housing electrical accessories. The JB shall have provision of fuses/MCB, buses, TBs as required for cable in and out. | SET | 40 | 2219.6 | 199.764 | 199.764 | 2619.128 | 104765.12
12.3 | Lighting provision for other Areas: Suitable for (a) Garden Lighting (8 nos of 70W LED) with necessary post top lantern with decorative pole | Lot | 1 | 10000 | 900 | 900 | 11800 | 11800
13 | Installation,Testing and Commissioining of Air Conditioner with AC Control Panels, Stabilizers, Logic Controller and other required accessories as described in Supply Schedule etc. to complete the AC System as per approved drawing and direction of engineer-in-charge
13.1 | Installation of AC and accessories in CRB cum GIS Building | Set | 16 | 5000 | 450 | 450 | 5900 | 94400 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
13.2 | Installation of AC and accessories in switchyard AC Kisok for 33kV Switchyard | Set | 2 | 5000 | 450 | 450 | 5900 | 11800
13.3 | Installation of AC and accessories in Transit House | Set | 4 | 5000 | 450 | 450 | 5900 | 23600
14 | FIRE FIGHTING SYSTEM(PORTABLE /TROLLEY/ WHEEL MOUNTED FIRE EXTINGUSHERS SETS FOR CONTROL ROOM, EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC
14.1 | FOAM TYPE-9 LTRS | NOS | 4 | 146 | 13.14 | 13.14 | 172.28 | 689.12 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
14.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22 5 KGS | NOS | 4 | 336 | 30.24 | 30.24 | 396.48 | 1585.92
14.3 | DRY POWDER TYPE - 5 KGS | NOS | 4 | 135 | 12.15 | 12.15 | 159.3 | 637.2
14.4 | Co₂- 4.5 KGS | NOS | 10 | 146 | 13.14 | 13.14 | 172.28 | 1722.8
14.5 | CO₂ - 9 KGS | NOS | 15 | 146 | 13.14 | 13.14 | 172.28 | 2584.2
14.6 | CO₂ (TROLLY MOUNTED)- 22.5 KGS | NOS | 8 | 146 | 13.14 | 13.14 | 172.28 | 1378.24
14.7 | 9 litre water type | NOS | 4 | 336 | 30.24 | 30.24 | 396.48 | 1585.92
14.8 | 4.5 kg DCP type | NOS | 6 | 224 | 20.16 | 20.16 | 264.32 | 1585.92
14.9 | 50 Litres Mechanical Foam type | NOS | 6 | 224 | 20.16 | 20.16 | 264.32 | 1585.92
14.1 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND & ITS CANOPY | SET | 8 | 224 | 20.16 | 20.16 | 264.32 | 2114.56
15 | Installation of Substation Automation System(IEC 61850): Installation, Testing and commissioning of the Digital Substation equipment including imparting training (on Job/site) to atleast 6 Engineers of OPTCL regarding the softwares used, configuration of the devices & switches, testing, probable faults & tracing procedures. Erection of the items under this section sahll be considered complete only when the firm shall submit a successful training completion certificate from the nominated engineers. The firm shall intimate the training schedule to OPTCL sufficiently before commencing the training for nomination of engineers. | [8 empty] | To be incorporated inline with supply
15.1 | "SUBSTATION AUTOMATION SYSTEM (IEC 61850) Gateway Panel ( 2 layer type) : for Sub-Station Automation (in PRP on FO as per the specification) system (for All 132 & 33 KV side bays) and with other accessories, comprising: 1. Gateway (Non-Windows or Linus or Firmware based)- 2 nos. with 8 ethernet ports each 2. BCU for Substation Auxilliary System 3. Ethernet Switches (with 20% spares Port) for bay & station level 4. LIU 5. Multimode glass fibre Doublle jacket armoured optical cables 6. Red boxes etc. including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. | Set | 1 | 620000 | 55800 | 55800 | 731600 | 731600 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
15.2 | RTCC Communication Panel (3 layer type) ; comprising of: 1. Substation Ethernet Switches- 2 nos 2. Firewall cum Router-2 set 3. Station Data Concentrator (SDC)- 2 nos 5. LIU 6. Multimode glass fibre Double jacket armoured optical cables 7. Red boxes etc. 8. Provision for mounting the VMS switch etc including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect for remote communication & as per technical specification.
15.3 | Operator Workstations
15.4 | Engineering workstation
15.5 | Workstation for RAS (Remote Access System)
15.6 | Black & whiter Laser jet Printer-1Nos
15.7 | Inverters - 3 KVA (Main & Stand by)
15.8 | Furniture (Operator desk 3 Nos (for SAS, RAS, VMS) & Chair-6Nos) etc.
15.9 | GPS System with IRIG-B/SNTP/PTP with VDU (Clock)
15.4 | 220 KV SIDE PROTECTION PANEL - Single Panel (1 Bay in One Panel) with IEC 61850-ED-2 PRP on FO
15.4.1 | 220KV FEEDER PROTECTION PANEL: Distance protection Relay (Main-I & Main-II of different make) with auto reclosure, Numerical Backup Protection Relay, Bay control unit (BCU) with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | NOS | 6 | 24807.25 | 2232.6525 | 2232.6525 | 29272.555 | 175635.33 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
15.4.2 | 220 KV TRANSFORMER PROTECTION PANEL: Numerical Differential protection Relay, Separate Numerical REF Relay (high impedance type), Numerical Back up protection relay & BCU for 220 KV side) CONSIDERING HV side of 220/33 KV, 100 MVA Two winding transformer with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | NOS | 2 | 24807.25 | 2232.6525 | 2232.6525 | 29272.555 | 58545.11
15.4.3 | 220 KV BUS COUPLER PROTECTION PANEL: With Bay control unit (BCU) & Numerical Back-up protection relay with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | NOS | 1 | 24807.25 | 2232.6525 | 2232.6525 | 29272.555 | 29272.555
15.4.4 | 220 KV BUS-BAR PROTECTION PANEL(s) (Centralized Architecture): Complete centralized type bus bar protection system for proposed bays and Provision for future bays (four nos) and with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | LOT | 1 | 24807.25 | 2232.6525 | 2232.6525 | 29272.555 | 29272.555
15.5 | 33 KV SIDE PROTECTION PANELS (Erection)
15.5.1 | 33KV Feeder Protection Panel: with BCU, Numerical backup relay & with other Auxiliary relays as required as per the scheme compliant to IEC 61850 - ED-2 protocol with PRP on FO. Power Supply 220V DC. 33KV Buscoupler Protection Panel: with BCPU & with other Auxiliary relays as required as per the scheme compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Note: 5 Nos. of line feeder bays and 1 B/C bay to be considered in 3 panel. | NOS | 3 | 14362.09 | 1292.5881 | 1292.5881 | 16947.2662 | 50841.7986 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project | To be incorporated inline with supply
16 | AC & DC SYSTEM
16.1 | AC SYSTEM
16.1.1 | Indoor Type with 2 mm CRCA sheet and 3 mm CRCA gland plate & as per TS:
16.1.1.1 | MAIN AC DB (Indoor Type) as per T.S. | SET | 1 | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 9613.7196 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
16.1.1.2 | ACDB (Indoor Type) as per T.S. The ACDB shall be suitable for automatic switching OFF & ON , auto start of DG set etc during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 9613.7196
16.1.1.3 | Main Lighting Distribution Board (Indoor Type) as per T.S. | SET | 1 | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 9613.7196
16.1.1.4 | Indoor Lighting Distribution Board (Indoor Type) as per T.S. | SET | 1 | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 9613.7196
16.1.1.5 | Emergency Lighting Distribution Board (Outdoor type) as per T.S | SET | 2 | 7703.3 | 693.297 | 693.297 | 9089.894 | 18179.788
16.1.1.6 | INDOOR RECEPTACLE BOARD as per T.S. | SET | 2 | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 19227.4392
16.1.1.7 | ACDB for Yard Kiosk (Indoor Type): LT supply to Protection panels, Kiosk lighting, AC etc as per T.S. | SET | 1 | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 9613.7196
16.1.2 | Outdoor Type, Sub Station Swithyard Console Boxes, HDG type (86 micron), 3 mm thick CRCA, (BMK,AC CONSOLE & OTHER MB) as per TS.
16.1.2.1 | Bay Marshalling Kiosk: 2 BMK for 7 nos 220KV bays and 3 BMK for 5 nos 33KV bays & 2 nos of Tfr bays with 1 no of B/C bay | SET | 5 | 6601 | 594.09 | 594.09 | 7789.18 | 38945.9 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
16.1.2.2 | Console box for switchyard lighting | SET | 2 | 5900 | 531 | 531 | 6962 | 13924
16.1.2.3 | Switchyard Receptacle Board for Transformer Oil Filteration | SET | 1 | 2037 | 183.33 | 183.33 | 2403.66 | 2403.66
16.1.2.4 | Switchyard Receptacle Board for welding and other emergency | SET | 2 | 2037 | 183.33 | 183.33 | 2403.66 | 4807.32
16.1.2.5 | CT CONSOLE BOXES as per TS (33 KV CT) | SET | 8 | 2037 | 183.33 | 183.33 | 2403.66 | 19229.28
16.1.2.6 | IVT CONSOLE BOXES as per TS (220 KV & 33 KV) | SET | 8 | 2037 | 183.33 | 183.33 | 2403.66 | 19229.28
16.1.2.7 | Console box for street lighting | SET | 2 | 5900 | 531 | 531 | 6962 | 13924
16.1.2.8 | Console box for Transit House/Colony Supply purpose | SET | 1 | 8260 | 743.4 | 743.4 | 9746.8 | 9746.8
16.1.2.9 | OUT DOOR KIOSK FOR STATION TRANSFORMER With Busbar & SFU of appropriate rating with required sizes of terminal studs for power cable termination & any other accessories as per T.S. and instruction of Engineer in Charge | SET | 2 | 8260 | 743.4 | 743.4 | 9746.8 | 19493.6
16.2 | DC SYSTEM
16.2.1 | 220 V DC DISTRIBUTION BOARD (Indoor Type) as per T.S. | SET | 2 | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 19227.4392 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
16.2.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD (Indoor Type) as per T.S. | SET | 1 | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 9613.7196
16.2.3 | BATTERY BANK (350 AH VRLA Type) for 220 V DC System as per TS | SET | 2 | 15276.04 | 1374.8436 | 1374.8436 | 18025.7272 | 36051.4544
16.2.4 | Battery Charger For 350 AH VRLA Type Battery, Charger ON/OFF status, input/output voltage, output current, associated charger protection signals shall be provided for integration with SAS & its spare as per TS. | SET | 2 | 4582.81 | 412.4529 | 412.4529 | 5407.7158 | 10815.4316
16.2.5 | DCDB for Yard Kiosk (Indoor Type) as per T.S. | SET | 1 | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 9613.7196
17 | Installation, testing and commissioning of GIS Hall Ventilation and Exhaust System:
17.1 | Installation, Commissioning, Testing of GIS Hall Ventilation System as described in supply part, & TS | LOT | 1 | 200000 | 18000 | 18000 | 236000 | 236000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
17.2 | Installation, Commissioning, Testing of GIS Hall exhaust System as described in supply part | LOT | 1 | 100000 | 9000 | 9000 | 118000 | 118000
18 | Installation of Smoke & Heat detection system: Addressable optical Smoke & Heat Multi detector (quantity as per approved design calculation) for GIS cum control room building including all accessories, the Main control panel (Microprocessor based 2 loop fire alarm control panel expandable upto 18 loops fully networkable with each loop capable of taking 99 devices, 8 line x 40 character alpha- numeric liquid crystal display .The panel shall be soft addressable type . The panel shall be able to give pin point location of all fire/fault conditions. Further, the panel must be able to automatically switch off respective control switches when ever any alarm is triggered. The panel shall have in built rectifier, Loop cards,provision for externel & internal printer(if required), L C D unit to indicate Fire/Fault Signal with address and analog output, built in printer to log all fire or fault events complete in all respects, integral SMF lead acid batteries with sealed cells of 24 V capable of running for a minimum of 8 hours with integral battery charger complete as required and as per specification. The fire alarm panel shall be suitable for software integration with BMS & PA system ,wall mounting loop powered addressable type hooter with all accessories , addressable manual call box made of polycarbonate with plastic break glass front and complete with monitor module MCB, addressable isolator module with required PVC box, fittings and fixtures, wiring with PVC FRLS wire to cover the required for fire & smoke detection etc. Should have facility for integration with SAS. | SET | 1 | 50000 | 4500 | 4500 | 59000 | 59000
19 | Installation & demo of the 20 Ltr Storage Water Cooler (Voltas/Bluestar only) for performance | Nos | 1 | 5000 | 450 | 450 | 5900 | 5900
20 | Installation & demo of the Water Purifier (RO+UV+UF type) suitable for connecting to the above water storage cooler (Kent/Aquaguard/Livpure/Pureit/Bluestar/LG)only for performance | Nos | 1 | 5000 | 450 | 450 | 5900 | 5900
21 | Installation/Demonstration of Maintenance Testing Equipment (All equipment shall comply to the TS and as per list of Supply) | SET | 1 | 200000 | 18000 | 18000 | 236000 | 236000
21.1 | Digital Earth Tester (Facility with soil resistivity measurement) (Megger-DET2/3 / Sonel MRU-120 / Fluke 1625) | NOS | 1
21.2 | Digital Multimeter (Megger / Fluke) | NOS | 2
21.3 | Digital Clamp meter (Megger/Fluke/Motwane) | NOS | 1
21.4 | Leakage current clamp meterAC & DC both (30mA / 300mA / 30A / 300A) (Megger/Fluke/Kyoritsu) | NOS | 1
21.5 | Oil sampling Bottle- Stainless Steel, Capacity- 1 Ltr (Make- Tosin) | NOS | 6
21.6 | Fibre Glass Discharge / Earth Rod: Grip up to 50mm, Min height-16ft, rubber grip, 35 sq.mm copper cable (1 set- 3 cables, 1 set of rod, carry bag) (Bemico) | SET | 6
21.7 | Electrical Rubber Hand Gloves | Pairs | 4
21.8 | Portable High Beam Light (rechargeable) | NOS | 2
21.9 | Installation of the Desktop Computer: (HP/Lenovo/Dell) (i) Processor-Intel Core i5 10th Gen or better (ii) RAM- 8GB DDR4 or More (iii) ROM- 512GB SSD (iv) Monitor- 21.5" FHD (1920 x 1080) or higher (v) Graphics- Onboard/Integrated (vi) OS- Genuine Windows 10 or 11 Pro (vii) Webcam- 720P Logitech (viii) Speaker- 2 nos Stereo type (ix) UPS 600VA (APC/V Guard) | Set | 2
21.1 | Installation of the Laser Printer, Black & White, Duplex printing (print, scan & copy) (HP/Canon/Epson) | Nos | 2
22 | Office Furniture: Godrej make (As per details below). Placing In Control Room, Communication Room, Conference Room, Office Rooms, Library, Testing Lab etc. | Lot | 1 | 10000 | 900 | 900 | 11800 | 11800 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
22.1 | For Control Room, conference room, office rooms, Library, testing room etc
22.1.1 | 5ftX3ft executive table with drawer on both sides | Nos | 4
22.1.2 | 4.5ft X 2.5ft Table with one side drawer | Nos | 7
22.1.3 | Computer table suitable keeping monitor, CPU, UPS and printer with two nos revolving arm chair suitable for computer use. | Set | 2
22.1.4 | Executive revolving, adjustable (height) chairs with arm | Nos | 4
22.1.5 | Cushion fixed “S” type steel chairs with arm | Nos | 16
22.1.6 | 6ftX3ft conference table | Nos | 1
22.1.7 | Cushion arm steel chairs for conference table purpose. | Nos | 6
22.1.8 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 3
22.1.9 | 6ft height steel almirah with glass doors for library purpose | Nos | 2
22.1.10 | 6ft height (having minimum 6 lockers facility) steel cupboard with locking arrangement. | Nos | 2
22.1.11 | 4ft steel rack (minimum three selves) for keeping the files and other items. | Nos | 8
22.2 | For Communication Room
22.2.1 | 5ftX3ft executive table with drawer both sides | Nos | 1
22.2.2 | Executive revolving, adjustable (height) chairs with arm | Nos | 1
22.2.3 | Cushion fixed “S” type steel chairs with arm | Nos | 2
22.2.4 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 1
23 | Lifting, installation, testing, commissioning of Diesel Generator and other accessories required for complete installation in compliance with the Standard applicable, specifications and the manufacturer’s instructions, with all statuatory approvals for Stand Fan (450mm sweep,1400rpm, 240V AC) (Make-Crompton, Bajaj, Havells, Almonard, Usha). | Nos | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
24 | Installation of De-Mineralised Plant of 50 L/Hr for Making Distilled Water for Battery Banks. (Cation and anion resin bed type) | Set | 1 | 10000 | 900 | 900 | 11800 | 11800
25 | Insulating Mat: Best Quality & approved make (Confirming to IS:15652:2006) to be kept infront of all panels, boards etc.(2000X1000X3mm Size) | NOS | 60 | 20 | 1.8 | 1.8 | 23.6 | 1416
26 | Installation, Commissioning, Testing for IP Based CCTV Surveillance System as described in supply part | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000
27 | EOT Crane for GIS building for 220 kV GIS station (as per T.S. with safe working load & minimum height of crane have shall be 8.0 meters or as per actual requirement whichever is higher. The crane shall have minimum speeds under full load of: Speed (a) Hoisting 2 meters/minute (b) Cross Travel 10 meters/minute (c) Long Travel 20 meters/minute (d) Creep speed shall be of 25% of operating speed.The crane shall be possible to be operated through the cable, through the pendant control and which shall be easily accessible from the floor of GIS building and through remote control device. ) including all accessories with control panel. | NOS | 1 | 500000 | 45000 | 45000 | 590000 | 590000
28 | ACCESSORIES FOR OPGW SYSTEM With OPGW cable
28.1 | 48 Fibre Optic Approach cable along with HDPE Pipes | Km | 1 | 70800 | 6372 | 6372 | 83544 | 83544 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
28.2 | Optical line Terminal Equipment(OLTE) -STM4 type SDH equipment with integrated MUX & tributary cards for speech & data ports for interfacing of Speech & data which should be of same make that has been commssioned at other end susbstation of OPTCL for seamless data integration including all accessories for successful commissioning. | Nos | 1 | 295000 | 26550 | 26550 | 348100 | 348100
28.3 | Digital Teleprotection Equipment and accessories to be suitable for interfacing with SDHMUX | Nos | 1 | 3540 | 318.6 | 318.6 | 4177.2 | 4177.2
28.4 | 48 V, 300 AH, maintenance free VRLA Battery set. | Set | 1 | 10000 | 900 | 900 | 11800 | 11800
28.5 | SMPS based battery charger of 75A suitable for 48V VRLA battery. | Nos | 1 | 29500 | 2655 | 2655 | 34810 | 34810
28.6 | 48V DCDB | Nos | 1 | 7800 | 702 | 702 | 9204 | 9204
28.7 | Earth flat, cable tray, telephone cable, ACDB, DCDB, foundation rail, Junction Box, Cat 5 cable & Misc items | Set | 1 | 7800 | 702 | 702 | 9204 | 9204
PART-A | ERECTION COMPONENT OF THE WORKS CONTRACT FOR SUBSTATION | [6 empty] | 22820276.2596 |  |  | 22503165 | -317111.2596
#REF!
Note on B104: OPTCL: CPC order

## Pahala CIVIL WORKS
(CIVIL WORKS SUB-STATION) |  |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2x100 MVA, 220KV GIS and 33KV AIS Sub-Station at Pahala with SAS along with 220 KV D/C line from existing 220/132/33KV GIS at Balianta through UG cabling length approx 8.805 Km & Over Head length approx 1.135 Km.
220/33KV GIS Pahala: 220KV GIS feeder Bays-5 Nos +2 spare=7 Nos, Power Tfr-2 Nos, B/C-1 no 33KV AIS Bays- Feeder-5 Nos, Tfr-2 Nos, B/C-1 no
CIVIL WORKS _SUBSTATION
Sl. No. | DESCRIPTION OF ITEMS(SCHEDULE-VIIC-SS) CIVIL WORK COMPONENT OF THE WORKS CONTRACT OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT OF MEASUREMENT | QUANTITY: | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY | Remark
1 | 2 | 3 | 4 | 5 | 6= {5*9%} | 7= {5*9%} | 8= {5+6+7} | 9= {8*4} | 10
CIVIL WORKS
1 | CONTOUR SURVEY,AND LEVELING, BACK FILLING
1.1 | Contour survey and furnishing contour map including supply of all materials, Labour and T&P | SQ.MTRS. | 50000 | 4.57 | 0.4113 | 0.4113 | 5.3926 | 269630 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
1.2 | Soil investigation : Supply of labour,T&P and other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge. (15.00mtrs) | PER POINT | 5 | 30029.82 | 2702.6838 | 2702.6838 | 35435.1876 | 177175.94
2 | Excavation for following type of soil and rocks (including shoring/shuttering where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge
2.1 | Normal Soil(SOFT/LOOSE) | Cum | 2000 | 156.68 | 14.1012 | 14.1012 | 184.8824 | 369764.8
2.2 | Hard Soil | Cum | 1000 | 248.08 | 22.3272 | 22.3272 | 292.7344 | 292734.4
2.3 | Soft Rock | Cum | 1000 | 554.9 | 49.941 | 49.941 | 654.782 | 654782
2.4 | Hard Rock(Requiring Blasting/Using breaker machinery) | Cum | 500 | 913.95 | 82.2555 | 82.2555 | 1078.461 | 539230.5
3 | OPEN CAST/SHALLOW FOUNDATION CONCRETE WORKS Foundations: Design, engineering, supply of all labour, material and construction(open cast foundation) of PCC, RCC footings of any depth, pedestal, concreting, cement, reinforcement steel, fine and coarse aggregated, shoring & shuttering, grouting, underpinning and back filling of foundations etc complete for the switchyard gantry/ portal /column structures and equipment support as per the technical specification and approved drawings & disposal of excess earth as per direction of Engineer In charge. (a) For Switch yard gantry/portal structure foundations (b) For 400KV, 220KV, 33 KV Equipment foundations. (c) For other equipment foundations.
3.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement in tower foundation as blind layer inclusive of labour charges for concrete mixing, dewatering, shoring, shuttering & curing. This includes supply of all labourers, T&P, head loading of all type of Civil materials (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification and instruction of Engineer In charge | Cum | 100 | 5237.8 | 471.402 | 471.402 | 6180.604 | 618060.4 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1.5:3) of grade M20 for open cast foundation with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement for tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, dewatering, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P, head loading of all type of Civil materials (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification and instruction of Engineer In charge | Cum | 1000 | 7565.71 | 680.9139 | 680.9139 | 8927.5378 | 8927537.8
3.3 | Supply of steel different sizes(TATA/RINL/SAIL/JINDAL make only). No other make of steel shall be allowed. As per the design with cutting, bending, binding and placing in position of steel rods for foundation concreting including cost of binding wire. | MT | 80 | 68623.36 | 6176.1024 | 6176.1024 | 80975.5648 | 6478045.18
4 | Cutting, Filling and Leveling of Sub-station area including supply of labour and T&P Providing, neatly dressing up and levelling of substation area including switchyard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification.
4.1 | CUTTING of substation area and utilising the usable soil for filling and compaction and disposing the unsuable soil from site
4.1.1 | Soft/loose soil | Cum | 15000 | 156.68 | 14.1012 | 14.1012 | 184.8824 | 2773236 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
4.1.2 | Dense/ Compact soil | Cum | 10000 | 248.07 | 22.3263 | 22.3263 | 292.7226 | 2927226
4.1.3 | Soft/Disintegrated rock[not requiring blasting] | Cum | 3000 | 509.2 | 45.828 | 45.828 | 600.856 | 1802568
4.1.4 | Hard rock[requiring blasting or by using concrete breaker machinery] | Cum | 400 | 966.17 | 86.9553 | 86.9553 | 1140.0806 | 456032.24
4.2 | FILLING of substation area with borrowed earth with supply of all labour,T & P.
4.2.1 | Up to 30 mtr lead | Cum | 5000 | 355.31 | 31.9779 | 31.9779 | 419.2658 | 2096329
4.2.2 | Beyond 30 mtr & up to 100mtr lead | Cum | 15000 | 551.35 | 49.6215 | 49.6215 | 650.593 | 9758895
4.2.3 | Beyond 100mtr lead | Cum | 10000 | 980.17 | 88.2153 | 88.2153 | 1156.6006 | 11566006
5 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling and disposal of excess earth as per the direction of Engineer In charge.
(2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in cable trench as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge.
(3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing), including supply of Labour all materials like MS Rod, Cement, coarse and fine aggregates, shuttering, cutting, bending, binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Fly ash Brickwork with fly ash Brick, plastering (1:6 Ratio) & curing, wherever required including the supply of labour, material, cement, etc.
(5) The outdoor cable trench wall top surface shall be "L" shaped and the cover slabs shall be placed with in the"L shaped" surface of both the walls. The top surface of the trench shall be smooth finished. (6)Supply,fabrication & Fixing of GI Angle for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the GI insert plate fixed on the trench wall for better rigidity. The Insert plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting.
(7) Precast of RCC covers (1:1.5:3) with MS sheet(2mm) frame and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (8) All the RCC cover slabs shall have the lifting hooks. The slabs without the MS sheet frame and Lifting hooks shall not be accepted.
(9) Cable Trenches Inside The Control Room Shall Be Covered With M.S Chequered Plate(Duly Painted As Per Instruction Of Engg In Charge) Including Standard Support Stand {Hd Galvanised (M.S Joist , Channel, Angle). Stoppers shall be fixed at the underneath so that the chequered shall not be falling into the cable trench in any case.
5.1 | Section 2-2 | Mtrs | 800 | 17788.46 | 1600.9614 | 1600.9614 | 20990.3828 | 16792306.24 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
5.2 | Section 3-3 | Mtrs | 600 | 12019.23 | 1081.7307 | 1081.7307 | 14182.6914 | 8509614.84
5.3 | Section 4-4 (inside dimensions- width- 400mm, height- 400mm), wall- 75mm, bottom concrete-75mm, two 150mm trays shall be laid side by side in one layer. | Mtrs | 500 | 7211.54 | 649.0386 | 649.0386 | 8509.6172 | 4254808.6
6 | Cable trench crossing:Design,engineering,construction including supply of labour,materials,cement,reinforcement steel,formwork etc,and all associated works for construction of trench crossing as per technical specification and approved drawing.(Road crossing )
6.1 | Section 2-2 | LOT | 1 | 250000 | 22500 | 22500 | 295000 | 295000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
6.2 | Section 3-3 | LOT | 1 | 250000 | 22500 | 22500 | 295000 | 295000
7 | Roads: Design, construction of roads and walkways/ shoulders within sub-station(Switch yard area,colony area,approach road,control room building area, main gate to the switch yard gate etc) as per specification, layout and approved drawings complete. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. Provision of drains on both the side of the roads for easy discharge of rain water.
7.1 | 7 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section(from the switch yard main gate to power transformer & infront of GIS cum control room building. | Mtrs | 800 | 10000 | 900 | 900 | 11800 | 9440000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
7.2 | Approach Road: 7 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section(from the switch yard main gate to the govt road. | Mtrs | 100 | 10000 | 900 | 900 | 11800 | 1180000
7.3 | 3.75 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section( Periphery roads outside switch yard fencing and colony roads) | Mtrs | 500 | 5000 | 450 | 450 | 5900 | 2950000
8 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme (RCC type), road-culverts,Shall have drain on both side of the road and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. All the switch yard bays , roads water drainage shall be connected to the main surface drain. As per approved drawing and specification. All the drainage system shall be RCC type with M20 grade concrete.
8.1 | Storm water drain (RCC type) as per design above and subsequent approval | Mtrs. | 800 | 6000 | 540 | 540 | 7080 | 5664000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
8.2 | Road side drains(RCC type)-on each side of the 3.75 mtr and 7 mtr concrete roads as per design above & subsequent apporval | Mtrs | 2000 | 3000 | 270 | 270 | 3540 | 7080000
8.3 | Road-culverts, drain crossings (RCC type) | Lots | 1 | 600000 | 54000 | 54000 | 708000 | 708000
9 | Rain water harvesting system as per Technical specification and approval of drawing and as per the direction of the Engineer in charge. | Nos | 2 | 200000 | 18000 | 18000 | 236000 | 472000
10 | Foundations for transformers: Design, engineering, supply of labour, material, equipments and construction of Auto-transformer/Transformer foundation including piling if any, all associated works, rail tracks, jacking pads,anchor block RCC and PCC, miscellaneous structural steel including oil collection pits (for 30% of the tfr oil capacity) below the transformer, MS grating(if required), gravel filling, and other items etc. not mentioned herein, but specifically required for the completion of the work as per technical specification and approved drawing. (Rate shall be inclusive of cement, reinforcement steel, angles,flats and form work etc.)(all cement concrete shall have RCC ratio 1:1.5:3). Transformer RCC foundation and Rail Track should be extended upto the approaching road (However,the height of RCC foundation beyond transformer main plinth area should be same as height of concrete road ). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth.
10.1 | 100 MVA 220/33 KV Power Transformer Total weight with oil and tank: 250 MT Approximately | Nos | 2 | 3427797.73 | 308501.7957 | 308501.7957 | 4044801.3214 | 8089602.64 | Technical Sanction Order no. - 82 , dated. 12.08.2025 of SGM(P) II, OPTCL
10.2 | All civil works related to NIFPES of 100 MVA 220/33 KV Power Transformer as per approved drawing including excavation in all type of soil, PCC, RCC, Steel , backfilling, compaction etc complete in all respect as per instruction of site in-charge. | Lot | 1 | 200000 | 18000 | 18000 | 236000 | 236000
10.3 | OIL SUMP PIT (150% of tfr oil capacity of one transformer): Design, engineering, supply of labour, material, equipments and construction of oil sump pit (RCC with ratio 1:1.5:3) including piling if any, all associated works & suitable connectivity oil collector pit provisioned near the transformer to the main oil sump pit and with provision of pump (suitable for handling transformer oil having capacity of 5 HP, with auto level control , including cabling, fixing of control gear & provision of a pump shed (of sufficient size to allow person to install, dismantle, make cable connection & maintain etc) over the oil sump pit). This oil sump pit shall be as per CIGRE standard for the oil collection pit inorder to separate oil from the water. Other piping with necessary valves arrangement shall also be provided to remove water from the oil sump pit. As per spec and approved drawing.
10.3.1 | Oil capacity of each Transformer 220/33 KV: 50000 ltrs. (approx) | Nos. | 2 | 252000 | 22680 | 22680 | 297360 | 594720 | Technical Sanction Order no. - 82 , dated. 12.08.2025 of SGM(P) II, OPTCL
11 | FIRE FIGHTING (Nitrogen Injection Type Fire Prevention & Extinguishing System) All civil works related to NIFPES as per approved drawing including excavation in all type of soil, PCC, RCC, Steel , backfilling, compaction etc complete in all respect as per instruction of site in-charge.
11.1 | For 100 MVA, 220/33KV Power Transformer | Lot | 2 | 100000 | 9000 | 9000 | 118000 | 236000
12 | Fire wall: Design, engineering, procurement of labour, material including all associated works for construction of fire-walls as per technical specification and approved drawings(column shall be RCC ratio 1:1.5:3 and the walls are of fire resistant bricks).This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Enginer In charge. As per approved drawing and specification. The MS Rod FE-550 as per BIS-1786 to be used .Painting of the walls as per direction of the Engineer in charge. | NO. | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
13 | STATION TRANSFORMER:Design, engineering, procurement of labour, material including all associated works for construction of foundation(RCC) for the station transformers 2X33/0.415 KV, 250 KVA (plinth mounted) including piling if any as per approved drawing and specification. It includes other accessories & materials as required need to be supplied for complete installation of transformer as per the instruction of Engineer In charge and as per the specification and approved drawing. | Nos | 2 | 300000 | 27000 | 27000 | 354000 | 708000
14 | Out door bay kiosks : Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The indicative drawing provided in the TS may be referred to. As per approved drawings and specification. The internal dimensions of the Bay Kiosks are as mentioned against the switchyards below. Doors shall be heat insulated and hinge type.
14.1 | For 33KV Switchyard (1 lot) of internal size-5m x 5m x 3.3m
14.1.1 | Excavation in all type of Soil including Hard Rock,PCC & RCC volume including MS rods (FE-550-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. ( including for Pile foundation if required with cost of boring, Column ,Beams and roofs etc. ) | Lot | 1 | 504348.05 | 45391.3245 | 45391.3245 | 595130.699 | 595130.7 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
14.1.2 | Fly Ash Brick masonry work in cement sand mortar 1: 5 with bricks of class designation 75kg/mm2 as per technical spec & approved drawings. | Lot | 1 | 162608.83 | 14634.7947 | 14634.7947 | 191878.4194 | 191878.42
14.1.3 | Flooring shall be with vitrified digital double charged tiles (Kajaria/Johnson/Somany/Varmora/Cera) with dado as per technical spec & approved drawings. | Lot | 1 | 80869.61 | 7278.2649 | 7278.2649 | 95426.1398 | 95426.14
14.1.4 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings and External,Internal & Ceiling Plastering as per technical Specification and as per instruction of Engineer In Charge. | Lot | 1 | 260434.81 | 23439.1329 | 23439.1329 | 307313.0758 | 307313.08
14.1.5 | Doors shall be of hinge operated openable and window shall be sliding type with adequate locking facility. The door window frame shall be of UPVC (Fenesta make) heavy sections with double layer toughened glaze of 6mm (min.) & windows shall have anodised aluminium grills. As per technical spec & approved drawing. | Lot | 1 | 50869.61 | 4578.2649 | 4578.2649 | 60026.1398 | 60026.14
14.1.6 | Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make) ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 91739.22 | 8256.5298 | 8256.5298 | 108252.2796 | 108252.28
14.1.7 | Provision of smoke and fire detection & Alarm system of the kiosks - to be integrated with the system in the main CRB. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 | 47390.65 | 4265.1585 | 4265.1585 | 55920.967 | 55920.97
15 | Anti-Weed Treatment :Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treat of the switch-yard areas,controlroom etc. as per the instruction of Engineer-in-Charge.The chemical to be sprayed as per the standard practice adopted for antiweed treatment of sub-station area & as per the technical specification. | Sq Mtrs | 10000 | 17.84 | 1.6056 | 1.6056 | 21.0512 | 210512
16 | Providing and Laying of non-woven Geo-synthetic fabric of minimum 200gsm as separation layer between switchyard soil and metal spreading as per direction of Engineer in charge. This also includes anchoring the fabric to existing soil, with all necessary fixtures, labour, T&P etc. complete in all respect There shall be an overlap of 250mm of the geo synthetic fabric at the end to end. | sqm | 25000 | 55 | 4.95 | 4.95 | 64.9 | 1622500 | 765 KV Estimate
17 | METAL SPREADING IN THE SWITCH-YARD: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:4:8). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 2000 | 2867 | 258.03 | 258.03 | 3383.06 | 6766120
18 | Switch yard fencing: Providing and fixing of G.I Goat mesh fencing (the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings and as required under the safety regulation of local, State and Central Government bodies and as per instruction of the Engineer-in-Charge. This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing shall be as per specification. The fencing shall be continuous i.e. a GI flat of 50 x 6mm shall run continuous at top & at bottom all along the fence. The fencing shall be connected to the earth mat every 3 mtrs. | Mtr | 1500 | 2240 | 201.6 | 201.6 | 2643.2 | 3964800
19 | SWITCHYARD GATE: Design, engineering, procurement of labour, material including all associated works for construction and fixing of switch yard gates and switchyard wicket gates as per specification and approved drawing. Switchyard gates shall have RCC pillars on both sides having open or pile founfdation and the gate shall be of stainless steel square pipes of 304 grade. The main entrance gate to switchyard shall have a wicket gate made of the same material. This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth, PCC/RCC concreting, supply of cement aggregates, rebar rod etc as per the direction of Engineer In charge. It includes supply of all materials and all other associated works required to complete works as per specification and approved drawings and instruction of engineer in charge.
19.1 | Switchyard gate (On both sides of 7 m. road of switchyard) | NOS | 2 | 550908.54 | 49581.7686 | 49581.7686 | 650072.0772 | 1300144.1544 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
19.2 | Wicket gate | NOS | 1 | 50908.54 | 4581.7686 | 4581.7686 | 60072.0772 | 60072.0772
20 | STONE PITCHING & TOE WALL:Stone pitching including making of toe walls both at top and bottom, including surface drain both at top and bottom and partition wall in every 10 mtrs by using boulders and RR masonry walls respectively. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth and supply of materials and labour as per the direction of Engineer In charge and as per approved drawing and specification.
20.1 | Excavation of Soil | Cum | 400 | 248.08 | 22.3272 | 22.3272 | 292.7344 | 117093.76
20.2 | P.C.C (1:3:6): Lean Concrete Grade M-10 | Cum | 30 | 5237.8 | 471.402 | 471.402 | 6180.604 | 185418.12
20.3 | RR Masonry (1:5) | Cum | 500 | 2511.7 | 226.053 | 226.053 | 2963.806 | 1481903
20.4 | P.C.C (1:2:4): Lean Concrete Grade M-15 | Cum | 5 | 6371.13 | 573.4017 | 573.4017 | 7517.9334 | 37589.67
20.5 | Brick masonary in ratio 1:5 with supply of first class K.B bricks,good quality river sand, cement, labour & T&P etc. as required. | Cum | 300 | 4533.3 | 407.997 | 407.997 | 5349.294 | 1604788.2
21 | RETAINING WALL: Construction of RCC retaining wall below the FGL and from NSL as per the site condition to sustain the earth pressure. The depth and length of RCC wall shall be designed as per site requirement. This includes excavation in all type of soil, RCC (1:1.5:3) with supply of steel(Fe-550), cement ,sand etc. including cutting, bending, binding, backfilling in layers after concreting for soil compaction and also supply of other required materials and labour . The work shall be executed as per the approved design , drawing as per direction of Engineer In charge | [7 empty] | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
21.1 | Exacavation all type of soil | Cum | 300 | 5237.8 | 471.402 | 471.402 | 6180.604 | 1854181.2
21.2 | PCC (1:3:6) | Cum | 40 | 5237.8 | 471.402 | 471.402 | 6180.604 | 247224.16
21.3 | RCC volume (M20) | Cum | 200 | 7565.71 | 680.9139 | 680.9139 | 8927.5378 | 1785507.56
22 | STORE SHED+OPEN STOCKYARD:Design, engineering, procurement of labour, material including all associated works for construction of store shed & open stockyard as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the specification,approved drawing and direction of Engineer In charge. One no store shed of floor size 10X10 mtr having Fly ash Brick walls and plastering with RCC roof. The flooring shall be of 75 mm thickness PCC (mix ratio1:2:4) over RR masonry works (as per standard practice of flooring). Provision of adequate nos of MS racks (proper paintings also to be done as per the direction of site in charge) for keeping the spare materials. The height of the shed shall be 4mtrs above the plinth. Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc),fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators( including supply) and provision of incoming AC supply from the main ACDB/outdoor kiosks installed for street light or colony quarters. Foundation shall be as per actual soil condition as per soil test, including piling where required. | Lot | 1 | 1100000 | 99000 | 99000 | 1298000 | 1298000
Also includes painting of the building (in side and out side) as per recommended for colony building in the specification.Store shed door shall have access control system which is sensor operated with key card for entry. Log of all the persons accessing the store shed with date and time stamp shall be kept in the system. There shall be provision for manual override of the system for exigencies as per direction of engineer in charge. Installation of smoke and fire detection & Alarm system of the building. Provision of conventional fire fighting equipment (including supply of FFE) at strategic location suitable for wall hanging as per direction of engineer in charge. The MS Rod ( FE-550 as per BIS-1786 ) to be used in the building. (* REMARKS : FOR SUPPLY OF ALL THE CABLES AS INDICATED ARE COVERED IN THE supply)}
23 | VEHICLE PARKING SHED: Design, engineering, construction of parking area shall be with the cost of all required material, procurement of labour, all T&P etc. This includes supply of all materials and all associated works for construction of vehicle parking shed, complete in all respect as per technical specification and enclosed drawing. This also includes, excavation in all type soil and rocks, backfilling and disposal of excavated soil, (cement, reinforcement steel, form work for) PCC, RCC (1:1.5:3), M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal), Fly ash Brick work with mortar 1:5, Plastering, Flooring, External and Internal Painting, all electrical works (Including but not limited to wires, conduits, GI boxes, switches, luminaires (Phillips/Crompton/Bajaj/Havells/Wipro), electrical fixtures and all other switchgear etc.)etc. and any other works required for completion of the work in all respect. Foundation shall be as per actual soil condition as per soil test, including piling where required. | Lot | 1 | 700000 | 63000 | 63000 | 826000 | 826000
24 | PROVISION OF SAND BED:Design, engineering, procurement of labour, material including all associated works for construction of sand bed as per specification and approved drawing. This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth as per the direction of Engineer In charge. The sand bed size shall be of 10m x 10m constructed with bricks, plastered & painted and the filled with river sand for storing of Transformer Bushings and other Insulators. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000
25 | RCC Foundations for Octagonal Lighting Poles: Design, engineering, procurement of labour, material including piling if any, all associated works for construction of foundations for octagonal lighting poles as per approved drawings (RCC ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawing and specification. Pcc padding ratio (1:4:8). The MS Rod (FE-550-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 to be used. | Nos | 40 | 10000 | 900 | 900 | 11800 | 472000
26 | COLOUR CODING, BAY MARKING Etc: Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (Red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof sticker (fluorescent type) may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. Stainless Steel sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000
27 | Switch yard buildings as per the indicative drawing attached: Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel ( FE-550 as per BIS-1786) (TATA/ RINL/ Sail/JINDAL), form work and excavation as per the approved drawing and technical specification (The RCC structure frame should be in the ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawings and specification. 220/33 KV GIS CUM CONTROL ROOM BUILDING WITH RAMP: (one building having the following rooms, Cable cellar, Store room, Battery room, AC/DC Room, Toilets, corridor & stair case, 220 KV GIS Equipment with 5T EOT Crane as per T.S. , GIS equipment loading unloading bay, Control room cum Relay panel room, communication room, conference room, Office rooms, SAS room, Maintenance Room, toilets, rest room, pantry etc). A) Size of the Building (Except Portico Area): 750 Square Meters (Each in Ground and First floor i.e 750+750) B) Plinth shall be at +500mm FGL C) Cable basement room & Other portions of Ground Floor at +500 mm Level upto +4200 mm Level D) 220 KV GIS Floor/Hall at +4200mm Level upto +14500 mm Level (or higher if required as per GIS manufacturer's recomendations) ,having EOT crane arrangement. E) Control Room & other room plan at First Floor at +4200 mm Level upto +8200mm Level. (F) Stair case & Toilet (for Gents & Ladies) and ramp on one side of the building G) Portico at both side of the building where Stair case provided, and a ramp at the backside for easy transportation of panels to the control room to be located . The indicative plan drawing of the building is provided and details of the building shall be as per the drawing (indicative) & Tech spec. The GIS cum Control room biulding shall be complete in all respect so as to accomodate all the GIS equipments, EOT crane, loading/unloading bay, all cotrol relay panels, Battery (2 sets), ACDC distribution panels, cable trench etc. The contractor shall finalize the dimensions of the hall & rooms according to the equipment offered by them providing enough space & access for erection, operation and maintenance & future expansion. This work including anti-termite treatment, plinth protection, DPC, water supply, plumbing, sanitation, fire-fighting, electrification etc
27.1 | Excavation in all type of soil including hard rock,PCC,RCC volume including MS rods (FE-550D-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. ( including for Pile foundation if required with cost of boring, Column ,Beams and roofs etc. ) | Lot | 1 | 25000000 | 2250000 | 2250000 | 29500000 | 29500000
27.2 | Fly Ash Brick masonry work in cement sand mortar 1: 5 with bricks of class designation 75kg/mm2 as per technical spec & approved drawings. | Lot | 1 | 5500000 | 495000 | 495000 | 6490000 | 6490000
27.3 | Flooring of GIS room shall be epoxy paint of adequate thickness & Flooring adjacent panel rooms shall be with vitrified digital double charged tiles (Kajaria/Johnson/Somany/Varmora/Cera) with dado as per technical spec & approved drawings. Bath and toilets shall be provided with anti skid ceramic digital tiles (wall of the same also to be provided with ceramic digital tiles upto 8 ft), Acid proof industrial tiles to be provided on the floor and full wall of the battery room as per technical spec & approved drawings. Stair case & its landing platforms are to be provided with Granite flooring. | Lot | 1 | 3000000 | 270000 | 270000 | 3540000 | 3540000
27.4 | External and internal wall (External 18mm thick ) and internal (12 mm thick) wall and ceiling plastering as per technical spec mentioned in the civil section) & building internal & external & ceiling paintings as per technical spec mentioned in the civil section. The ceiling of battery room shall be acid proof paints as per specification & approved drawings. Refer the specification. | Lot | 1 | 3000000 | 270000 | 270000 | 3540000 | 3540000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
27.5 | Provision of ceiling in the control room area as per specification mentioned in the civil section & approved drawings including, relay panel room, office room, SAS room, conference room, transit room etc as per direction of the engineer in charge. | Lot | 1 | 1500000 | 135000 | 135000 | 1770000 | 1770000
27.6 | Doors and Rolling shutters - Motorized type with outside control (steel with weather proof paint) as per requirement and design and as per technical spec & approved drawing. Doors and windows shall be of clear openable (door) and sliding (window) type with adequate locking facility. The door window frame shall be of UPVC (Fenesta make) heavy sections with double layer toughened glaze of 6mm (min.) & windows shall have anodised aluminium grills. Windows shall be provided with vertical window blinder to protect from the sun ray. As per technical spec & approved drawing. All bath room & toilet doors shall opaque. Provision of sliding louvers in toilet/bath. | Lot | 1 | 1000000 | 90000 | 90000 | 1180000 | 1180000
27.7 | Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make), fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 700000 | 63000 | 63000 | 826000 | 826000
27.8 | Supply ,fitting & fixing of stainless steel of 304 grade in hand railing using 50mm dia of 2mm thick circular pipe with balustrade of size 32mm*32mm*32mm @0.90mtr C/C and stainless suqare pipe bracing of size 32mm*32mm*32mm in three rows in staircase as per approved design and specification, buffing, polishing etc with cost, conveyance, taxes of all materials, labour, T7P etc required for the comlete in all respect. | Lot | 1 | 750000 | 67500 | 67500 | 885000 | 885000
27.9 | Provision of rails & other arrangement including all type of Civil works for EOT crane in GIS Hall. This is as per the standard practice adopted in GIS sub-station and as directed by the Engineer in Charge. | Lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000
27.1 | Provision of PHD and other fittings of reputed make (JAQUAR) for the control room building (in Toilets, wash room, overhead water tank of adequate capacity etc) of reputed make, provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing. There shall be septic tank and soak pit of required capacity including complete sewage system as per approved drawing & technical specification & as per instruction of Engg- in-Charge. It includes supply of all types of materials of reputed make for HDPE, UPVC pipe,fittings etc, labour etc to complete the work. Toilets (Provision of commode & granite platform base standalone type wash basin) for Gents & Ladies to be provided including all good quality fittings of Jaquar make as per specification. Provision of two nos of overhead water tank of 2000 ltrs capacity etc as per requirement and approved drawing. | Lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000
28 | MAIN GATE, WICKET GATE & SECURITY SHED (GATE COMPLEX): The Main gate, wicket gate and the Secirity shed shall be constructed as per the drawing provided and technical specification, complete in all respect and as per instruction of Engineer in charge. The foundation shall be designed as per actual site soil condition and shall be constructed as per approved drawing.
28.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil & rock as per drawing and technical specification complete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the surplus earth/unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. This includes cost, conveyance of all materials, all labour, T&P articles required for the work, stacking the useful materials separately, including shoring, shuttering, propping and dewatering if required etc. | Lot | 1 | 35532.43 | 3197.92 | 3197.92 | 41928.27 | 41928.27 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
28.2 | Providing and lying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 30322.32 | 2729.01 | 2729.01 | 35780.34 | 35780.34
28.3 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundation & base of column work, all column, all beam, all pedestal, all lintel, all chajja, all slab, all projection etc.), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 443372.68 | 39903.54 | 39903.54 | 523179.76 | 523179.76
28.4 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, including cost of binding wires, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 565359.94 | 50882.39 | 50882.39 | 667124.72 | 667124.72
28.5 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 90680.42 | 8161.24 | 8161.24 | 107002.9 | 107002.9
28.6 | Providing 12 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 14705.25 | 1323.47 | 1323.47 | 17352.19 | 17352.19
28.7 | Providing 16mm thick cement plaster ( 1:6) finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 16080.99 | 1447.29 | 1447.29 | 18975.57 | 18975.57
28.8 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 8988.68 | 808.98 | 808.98 | 10606.64 | 10606.64 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
28.9 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 8613.92 | 775.25 | 775.25 | 10164.42 | 10164.42
28.1 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 2071.9 | 186.47 | 186.47 | 2444.84 | 2444.84
28.11 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 2782.87 | 250.46 | 250.46 | 3283.79 | 3283.79
28.12 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 6003.88 | 540.35 | 540.35 | 7084.58 | 7084.58
28.13 | Providing and fixing of 35mm thick WPC Door Shutter(Solid) with teak edge leaping to the periphery of the shutter with pilishing as per detailed drawing with including, all hardwares & fixtures, SS tower bolt(150mm), Door stopper, SS aldrop(250mm), SS handle(200mm length), ss handle (150mm length) & SS Butt hinges -125mm x 65mm x2.12mm .including cost, conveyance, loading, T&P required for the work etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 12476.16 | 1122.85 | 1122.85 | 14721.86 | 14721.86
28.14 | Supplying, fitting and fixing of M.S grills for windows, Main Gate, wicket gate etc. (as per I.S. specification and as per approved drawings ) in proper position in all floors and at all height including making holes to brick walls/ R.C.C structure/wood work etc. and making good to the damaged walls/ structures with cement concrete (1:2:4) with black hard crusher broken granite stone chips of 12mm to 20mm size ( 20mm size not to exceeds 25% ) including watering and curing etc. complete in all respect as directed by the Engineer in charge. (W.I. / M.S. windows grills, grill gates, collapsible gates with top and bottom rails, steel windows, steel doors, steel frames for doors and windows, staircase and parapet railings square bar along with required nos. of nails and screws and other required materials of approved quality and approved size shall be supplied by the contractor at his own cost.) | Lot | 1 | 136012.19 | 12241.1 | 12241.1 | 160494.39 | 160494.39 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
28.15 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge.
28.15.1 | Inside walls and Ceiling: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 36222.67 | 3260.04 | 3260.04 | 42742.75 | 42742.75
28.15.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 14163.64 | 1274.73 | 1274.73 | 16713.1 | 16713.1
28.15.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 5032.84 | 452.96 | 452.96 | 5938.76 | 5938.76
28.16 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 14502.83 | 1305.25 | 1305.25 | 17113.33 | 17113.33
28.17 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 6770.36 | 609.33 | 609.33 | 7989.02 | 7989.02
28.18 | Providing and fixing of UPVC sliding windows in the Transit house as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 26280 | 2365.2 | 2365.2 | 31010.4 | 31010.4
28.19 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 24914.7 | 2242.32 | 2242.32 | 29399.34 | 29399.34
28.2 | GFRC Letter: Manufacturing, providing and installation of GFRC mouldings (Glass Fiber Reinforced Concrete) of approved make of thickness 230mm±5mm with pattern, design and colour of approved make to be fixed on/beteween RCC/ block work column or structural work with dry fixing method with all required T & P , manpower and all other material as required for completion of work in all respect.
i | Per Letter (450mm(h) x 40mm (d) x 50mm (w)) | Nos | 40 | 800 | 72 | 72 | 944 | 37760
ii | OPTCL Logo | Nos | 1 | 1000 | 90 | 90 | 1180 | 1180
28.21 | Electrical works of Main Gate, Wicket gate and Security Shed: As per the provided drawing and as per specification in TS. This also includes supply of all electrical materials (of specified manufacturer as indicated in the TS) for main gate, wicket gate & security shed to complete the work as as per description provided in the relevant section of TS. | Lot | 1 | 244423.62 | 21998.13 | 21998.13 | 288419.88 | 288419.88
28.22 | Supply of the following materials: a) First Aid Box - 1 set b) Shock Treatment Chart (Odia, Hindi & English) - 1 set c) Insulating mat - 6 sq. m. d) Danger Board - 1 set | Lot | 1 | 6015 | 541.35 | 541.35 | 7097.7 | 7097.7
29 | BOUNDARY WALL (RCC structure, Brickwall type & Precast type)
29.1 | BOUNDARY WALL: The boundary wall shall be constructed to a height of 2 mtrs above finished ground level of the substation area with 10” wide brick masonry work with RCC(1:1.5:3) ground tie beam to be rested on the RCC pillars (pillar to pillar distance @ 3mtrs) as per specification. | RM | 500 | 11800 | 1062 | 1062 | 13924 | 6962000
29.1.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil and rock as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plinth with sand, compaction, carriage & disposal of the unsuable earth material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1
29.1.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1
29.1.3 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations & bases of column, Beams, pedestal & column, rcc band etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour, Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1
29.1.4 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1
29.1.5 | Providing Brick work with Fly ash bricks 25cm x 12cm x 8cm size having crushing strength not less than 75 kg/cm2 with dimensional tolerance +/ - 2 percent in cement mortar (1:6) ( 1 cement: 6 sand), with all necessary projection, splay cutting, circular moulding, corbelling, etc., including cost of all materials, labour, conveyance, loading ,and unloadining, royalties, scaffolding, watering, curing, sundries, tools and plants, etc., as per the direction of the Engineer-in-charge. | Lot | 1
29.1.6 | Providing 16 mm. thick cement plaster in all floors at all height with cement mortar of mix (1:6) with portland slag cement (PSC) finished smooth to inside rough surface of brick masonry walls after racking out joints including watering and curing rounding of corners etc. complete with cost, coveyance, loading and unloading, royalties and ,es of all materials and cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. (Inside) | Lot | 1
29.1.7 | Painting of wall surface with weather coat two coats over a coat of primer of approved shade and quality of approved design after cleaning by watering & removing the dirts etc. to the surface to be painted including watering, curing, cost, conveyance of all materials, cost of all labour, brushes, T&P etc. and necessary scaffolding work complete as directed by the Engineer-in-charge. | Lot | 1
29.1.8 | Providing and fixing of GI 'Y' angles over the boundary wall at every 1m rigdly & sufficently (at least 200mm) grouted inside the wall for the support of the concertina wire. | Lot | 1
29.1.9 | Providing and fixing concertina coil fencing with punched tape concertina coil 600mm dia 10metr openable length (total length90m), having 50nos rounds per 6m length, upto 3m height of wall with existing angle iron 'Y' shaped placed 2.4m or 3m apart and with 9 horizontal R.B.T. reinforced barbed wire, stud tied with G.I. staples and G.I. clips to retain horizontal, including necessary bolts or G.I. barbed wire tied to angle iron, all complete as per direction of Engineer-in-charge, with reinforced barbed tape(R.B.T.) / Spring core (2.5mm thick) wire of high tensile strength of 165kg/sq.mm with tape (0.52mm thick) and weight 43.478 gm/meter. | Lot | 1
29.2 | Precast Boundary Wall: Supplying and fixing precast RCC/ SFRC boundary wall precast RCC/ SFRC fencing compound wall pole having finished dimension of 200mmx200mmx3000mm (long) made of M 30 grade concrete with 10 nos of 4mm dia HTPC (High Tension Pre Coated) wire, fixed in cast-in-situ PCC M-20 concrete in Foundation footing of size 600 mm dia 300mm depth from top and P.C.C. of proportion in CC(1:4:8) of size 600 mm dia 300mm depth at bottom Inside the RCC collar pipe of 600mm internal dia placed over a base of plain cement concrete of proportion with C.C. (1:4:8) of size 680 mm dia 100mm depth including excavating foundation pit for each pole in hard stony earth of size 680 mm dia 700mm depth including providing cast-in-situ PCC of proportion in CC.(1:4:8) of size 1520 mm length, 150 mm width & 100mm depth below slab panel including watering & curing for required days, along with supplying, fixing befitting precast RCC/SFRC slab having dimension of 2100mm (long) x 300mm (wide) x 50mm (thick) made with M-30 grade concrete having 4mm dia GI wire 3 nos covering the top of the compound wall poles with a precast RCC/SFRC cover of size (300x300x150) mm in order to prevent the slab panels from removing. All complete as a set to be measured in term of running meter including such precast RCC/SFRC top cover, slab, pole, including painting two coats of approved cement paint over a coat of cement wash including curing, cost and conveyance of all materials, royalties, taxes, all labour, labour cess, T & P required for the work etc. complete including dewatering if required as per the direction of the Engineer-in-charge excluding cost of GST. | Mtr | 100 | 6411.02 | 576.99 | 576.99 | 7565 | 756500 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
30 | TRANSIT HOUSE: Design, engineering and construction of switch yard buildings including excavation, construction of foundations (open cast or pile as per soil conditions), construction of RCC super structure, brick the cost of material, supply of labour, cement, reinforcement- steel and form work as per the enclosed drawing and technical specification ( The RCC structure frame and the foundations should be in the ratio 1:1.5:3). The indicative drawings of the building is provided and the foundation of the building shall be designed based on the actual soil condition. Foundation shall be as per actual soil condition as per soil test, including piling where required.
30.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 | 301211.02 | 27108.99 | 27108.99 | 355429 | 355429 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
30.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 260559.34 | 23450.34 | 23450.34 | 307460.02 | 307460.02
30.3 | Providing & laying Plain cement concrete (1:2:4) (in sunken slab areas) using 12mm size black hard crusher broken granite chips of approved quality from approved quarry including hoisting, lowering and laying concrete in layers, watering, curing etc. complete including cost, conveyance, royalties and taxes of all materials with labour, cess and T&P etc. required for the work complete. | Lot | 1 | 9942.65 | 894.84 | 894.84 | 11732.33 | 11732.33
30.4 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations, columns, Beams, lintels, chhajas, roof slabs, stair case etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 6576113.36 | 591850.2 | 591850.2 | 7759813.76 | 7759813.76 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
30.5 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 2500000 | 225000 | 225000 | 2950000 | 2950000
30.6 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) for foundation and plinth and in cement mortar of mix (1:4) for other area in ground floor, first floor & head room with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 585242.08 | 52671.79 | 52671.79 | 690585.66 | 690585.66
30.7 | Providing 16 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 277975.53 | 25017.8 | 25017.8 | 328011.13 | 328011.13
30.8 | Providing 18mm C.P. in two coats underlayer 12mm C.P. 1:5 and top layer 6mm thick C.P. 1:6 finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 204882.42 | 18439.42 | 18439.42 | 241761.26 | 241761.26
30.9 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 52842.74 | 4755.85 | 4755.85 | 62354.44 | 62354.44
30.1 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 539188.36 | 48526.95 | 48526.95 | 636242.26 | 636242.26
30.11 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 51802.87 | 4662.26 | 4662.26 | 61127.39 | 61127.39 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
30.12 | Providing, fitting & fixing anti-skid ceramic floor tiles in flooring in toilets using special plain/ printed series anti-skid ceramic floor tile of premium grade (having minimum thickness 7 mm to 8 mm & size 300 mm x 300 mm confirming to IS 13755 of approved quality and shade of Somany/ Kajaria / Johnson on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened & washed sharp river sand for mortar ceramic floor tiles with neat white cement slurry, mixed with required (tiles are to be immersed in the water for required time before use) quantities of pigments of approved marks to match the shades of the anti-skid ceramic floor tiles if required including cost, conveyance, loading, unloading, stacking, royalties of all material, cost of all labour, sundries, T&P required for the work, watering, complete in all respect as per specification excluding GST as per specification as directed by Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 12140.52 | 1092.65 | 1092.65 | 14325.82 | 14325.82
30.13 | Providing & Fixing tiles of size 30cm x 45 cm glazed ceramic wall tiles (All Toilet walls) of premium grade of approved quality and shade having thickness 8mm to 10mm confirming to IS 13755 in dados skirting and risers of steps on 12mm thick cement plaster (1:3) to proper slope, line and level including cutting to required size and shape, fixing at corners and splays etc including filling the joints with neat white cement slurry mixed with pigments to match the shade of the tiles including cost, Conveyance, loading, unloading, stacking, royalities of all materials, cost of all labour,T&P, sundries, watering and curing for the required period for the work complete in all respect excluding GST as directed by the Engineer-in-charge.(Note- Sample of tiles shall be approved before procurement and use.) | Lot | 1 | 65578.7 | 5902.08 | 5902.08 | 77382.86 | 77382.86
30.14 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 123268.36 | 11094.15 | 11094.15 | 145456.66 | 145456.66
30.15 | Providing Granite stone prepolished 10mm thick in dado of approved quality, colour and size in dado, riser of steps and dado of landings in all floors at all height on 12mm thick bed of cement mortar of mix (1:3) with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 19217.93 | 1729.61 | 1729.61 | 22677.15 | 22677.15
30.16 | Providing,Fixing 16m thick Kota stone in floors treads or steps and landing on 20mm thick cement mortar (1:4) (1cement : 4 course and) and filling joints with of approved quality including cost, conveyance, taxes, cost of all labour etc. complete. Providing,Fixing 16m thick Kota stone in dado ,riser on 12mm thick cement mortar (1:3) (1cement : 3 course and) and filling joints with of approved quality including cost, conveyance, taxes, cost of all labour etc. complete. | Lot | 1 | 44895.68 | 4040.61 | 4040.61 | 52976.9 | 52976.9 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
30.17 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 125157.9 | 11264.21 | 11264.21 | 147686.32 | 147686.32
30.18 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board and pasting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. | Lot | 1 | 448363.08 | 40352.68 | 40352.68 | 529068.44 | 529068.44
30.19 | Supplying, fitting and fixing of M.S grills, Grill window ( as per I.S. specification and as per approved drawings ) in proper position in all floorsas per TS, approved drawing, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 126161.42 | 11354.53 | 11354.53 | 148870.48 | 148870.48
30.2 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge.
30.20.1 | Inside walls: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 280619.13 | 25255.72 | 25255.72 | 331130.57 | 331130.57 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
30.20.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 65795.51 | 5921.6 | 5921.6 | 77638.71 | 77638.71
30.20.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 607.66 | 54.69 | 54.69 | 717.04 | 717.04
30.21 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 71130.56 | 6401.75 | 6401.75 | 83934.06 | 83934.06
30.22 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 44317.83 | 3988.6 | 3988.6 | 52295.03 | 52295.03
30.23 | Providing and fixing of UPVC sliding windows in the Transit house as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 424584 | 38212.56 | 38212.56 | 501009.12 | 501009.12
30.24 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 122196.6 | 10997.69 | 10997.69 | 144191.98 | 144191.98
30.25 | Water proofing to the sunken slab including providing and filling it with 40mm size brick bat as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 3348 | 301.32 | 301.32 | 3950.64 | 3950.64
30.26 | Providing and laying tactile tile (for vision impaired persons as per standards) of size 300x300x9.8 mm having with water absorption less than 0.5% and conforming to IS:15622 of approved make in all colours and shades in for outdor floors such as footpath, courtyard, multi modals location etc., laid on 20mm thick base of cement mortar 1:4 (1 cement : 4 coarse sand) in all shapes & patterns including grouting the joints with white cement mixed with matching pigments etc. complete as per direction of Engineer-in-Charge | Lot | 1 | 21505.13 | 1935.46 | 1935.46 | 25376.05 | 25376.05
30.27 | Supplying, fitting and fixing in position 16mm thick chequred tile of approved make and quality, colour and size in all floors at all height on 25mm thick bed of cement mortar of mix (1:1) laid in proper slope and gradient with screened and washed sharp sand for mortar and with Portland Slag Cement (PSC) grouted with neat white cement slurry with required quantities of pigments of approved marks watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 15829.76 | 1424.68 | 1424.68 | 18679.12 | 18679.12 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
30.28 | Plinth Potection for Transit house as per the provided drawing and as per sepcification in TS. | Lot | 1 | 71707.51 | 6453.68 | 6453.68 | 84614.87 | 84614.87
30.29 | Construction of covered drain for Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 257416.05 | 23167.44 | 23167.44 | 303750.93 | 303750.93
30.3 | Provision of PH work for the Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 570758.62 | 51368.28 | 51368.28 | 673495.18 | 673495.18
30.31 | Construction of septic tank and soak pit for Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 255823.4 | 23024.11 | 23024.11 | 301871.62 | 301871.62
30.32 | Provision of Electrical works the Transit house as per the provided drawing and as per specification in TS. This also includes supply of all electrical materials (of specified manufacturer as indicated in the TS) to complete the work as as per description provided in the relevant section of TS. | Lot | 1 | 467669.25 | 42090.23 | 42090.23 | 551849.71 | 551849.71
30.33 | Furnishings for Transit House: Supply and installation of the following items- 1. 55 inch Full HD LED TV set of Sony/LG/Samsung make with supply of Set up Box for the television unit with 1 year recharge from the date of commissioning (1set) 2. Durian make Sofa set (3+1+1) with center table for lobby (1 set) 3. Durian make King size cot with mattress & all other amenities like study table with 2 chair (Godrej) in all the bed rooms, bed sheets, pillow etc (Bombay Dyeing/Raymond Home) make. 2 Person wardrobe (Godrej Interio), hangers for hanging cloths in each room for storage of Baggages and Cloths etc. Bathing requirements like Bath Towels, Hand Towels etc. (02 sets for all the bed rooms). Decoratives Such as wall ceinic Hangers, Doors and Windows Curtains (02 Sets for all doors and Windows) - Total 4 sets for 4 guest rooms 4. Geyser-3 Ltr capacity of Bajaj/V-Guard/Phillips/Crompton make (4 set) 5. Dining table with 6 chairs of Durian/Godrej make (1 set) 6. Modular kitchen with exhaust chimney system, gas stove, and required utensils (1. 02 Cook Ware and Dinner Sets for 08 persons 2. Induction cooking heaters for cooking capacity of 10 persons at a stretch) 7. RO & UV Water purifier with cooling water system of Aquaguard/Bluestar/Kent make (1 set) 8. 3 star inverter compressor frost free Refrigerator of 230 Ltr or above capacity, double door type (LG/Samsung/Whirlpool/Godrej/Panasonic Make) (1 set) | LOT | 1 | 2000000 | 180000 | 180000 | 2360000 | 2360000
31 | Construction of borewell for Transit house as per the specification in TS (as in control room building). The starter is to be installed in the transit house as per the instruction of the site Engineer. The deliveries of borewell of transit house and the cotrol room building shall also be connected with each other through gate valves to use any one borewell for the entire substation premises in case of exigencies, including supply of all materials such as UPVC Pipes, joints, valves etc for completion of the work as per instruction of site Engineer. | Lot | 1 | 250000 | 22500 | 22500 | 295000 | 295000
32 | DG SHED: Design, engineering, procurement of labour, material including all associated works for construction of 82.5KVA DG shed as per the approved drawing and instruction of Engineer in charge. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth. The size of the DG shed shall be 9 mtrsX4mtrs and adequate height of RCC roof with RCC Column & Beam, plastering, painting and wiring. DG shed shall be open type, so side wall not required. | LOT | 1 | 2000000 | 180000 | 180000 | 2360000 | 2360000
33 | Land scaping & provision for platform for hoisting of National Flags and Provision of Garden: As per site condition of the substation and approval of the gardening layout. The qty may vary as per the approved layout and instrcution of engineer in charge.
33.1 | Provision of gardens/ lawn area with garden grass in front of the control room building & other areas that can be developed as a garden as per the site Engineer's instruction. This include the all required work including the soil treatment for laying of the lawn grass. | sqm | 400 | 500 | 45 | 45 | 590 | 236000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
33.2 | Motorised fountain at a suitable location as per instrcution of Engineer in charge. | Nos | 1 | 50000 | 4500 | 4500 | 59000 | 59000
33.3 | Sprinkler arrangement in the lawn to cover all the lawn area and water tap arrangement at different location to all areas of plantation. | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000
33.4 | Flowering plants (Rose, jasmine, hibiscus or as per instruction of Engineer in Charge at least 50 each | Nos | 200 | 100 | 9 | 9 | 118 | 23600
33.5 | Fruit bering Non Fruit bearing Plants (Mango, guava, Neem, Acacia) as per instruction of Engineer in Charge. 25 nos of each type of trees to be plantedin the free areas immediately after the substation layout paln is finalised. It must be ensured that the plants survive till hand over. Therefore, proper care shall be taken by the contractor. | Nos | 100 | 200 | 18 | 18 | 236 | 23600
33.6 | Decorative Plants for Lawn/garden (varieties of Hedge, thuja) as per instruction of Engineer in Charge | Nos | 150 | 200 | 18 | 18 | 236 | 35400
33.7 | Decorative plants (foxtail palm of at least 5 ft height) for both side of the 7m road from the main gate as per instruction of the Engineer in charge. | Nos | 100 | 1119.89 | 100.7901 | 100.7901 | 1321.4702 | 132147.02
33.8 | Construction of platform & suitable GI pipe & other attachment for hoisting of National Flags as per the direction of Engineer incharge. | Nos | 1 | 50000 | 4500 | 4500 | 59000 | 59000
| TOTAL CIVIL_SUBSTATION | [6 empty] | 225361329.2916 |  | 143217057.88 | -82144271.4116
CIVIL WORKS _TRANSMISSION LINE
Sl. No. | DESCRIPTION OF ITEMS(SCHEDULE-VIIC-LINE) CIVIL WORK COMPONENT OF THE WORKS CONTRACT OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT | QUANTITY: | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY
1 | 2 | 3 | 4 | 5 | 6= {5*9%} | 7= {5*9%} | 8= {5+6+7} | 9= {8*4}
PART B | CIVIL WORKS
1 | SURVEY OF LINE & PREPARATION OF LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting
1.1 | Preliminary Survey:- Making walk over survey, ascertaining feasible route and marking on Topo sheet, preparation of Route Alignment map. | Kms. | 6 | 4953.75 | 445.8375 | 445.8375 | 5845.425 | 35072.55 | 1.1
1.2 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | Kms. | 6 | 6604.99 | 594.4491 | 594.4491 | 7793.8882 | 46763.3292 | 1.4
1.3 | Detailed Survey:- Including taking of levels, profile plotting, tower spotting, showing P & T, Power lines, Railway lines, River crossing, Roads and submission of profile & Suvey report. The P & T lines and Railway lines for a minimum distance of 8kms on either side of alignment shall be clearly indicated. With plot no, khsts no, mouza on revenue maps indicating alignment therein duly authenticated by Revenue Inspector and Tahasildar, enumeration of trees with help of Forest Officers and other prominent features required for alignment of line. | Kms. | 6 | 14035.61 | 1263.2049 | 1263.2049 | 16562.0198 | 99372.1188 | 1.2
1.4 | Preparation of land schedule with HAL & SAVIK classification on revenue maps indicating alignment therein duly authenticated by Revenue Inspector & Tahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 220 KV line. Final route to be plotted on 1:50000 topo sheet for approval. | KM. | 6 | 10733.12 | 965.9808 | 965.9808 | 12665.0816 | 75990.4896 | 1.3
1.5 | Soil Investigation for preparation/design of Foundation
1.5.1 | Soil Testing in complete shape along with submission of report etc. up to the depth of 7.0 Mtrs. | Per Loc. | 7 | 28071.23 | 2526.4107 | 2526.4107 | 33124.0514 | 231868.3598 | 1.5(a)
1.5.2 | Soil Testing in complete shape along with submission of report etc. up to the depth of 15 Mtrs. (Only if required after obtaining approval from OPTCL) | Per Loc. | 1 | 37978.72 | 3418.0848 | 3418.0848 | 44814.8896 | 44814.8896 | 1.5(b)
1.5.3 | Soil Testing in complete shape along with submission of report etc. upto the depth of 45 mtrs for River bed pile. (Only if required after obtaining approval from OPTCL). | Per Loc. | 0 | 74306.19 | 6687.5571 | 6687.5571 | 87681.3042 | 0
2 | EXCAVATION WORKS FOR OPEN CAST/SHALLOW TYPE FOUNDATIONS
2.1 | Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge.
2.1.1 | Soft/Loose soil | CUM | 1776 | 228.78 | 20.5902 | 20.5902 | 269.9604 | 479449.6704 | 2(i)
2.1.2 | Dense/Compact soil/Wet soil | CUM | 888 | 358.41 | 32.2569 | 32.2569 | 422.9238 | 375556.3344 | 2(ii)
2.1.4 | Partial Submerged soil | CUM | 444 | 411.79 | 37.0611 | 37.0611 | 485.9122 | 215745.0168 | 2(vi)
2.1.5 | Fully submerged soil | CUM | 444 | 411.79 | 37.0611 | 37.0611 | 485.9122 | 215745.0168 | 2(v)
2.1.6 | Soft/Disintegrated rock(Not requiring Blasting) | CUM | 444 | 686.31 | 61.7679 | 61.7679 | 809.8458 | 359571.5352 | 2(iii)
2.1.7 | Hard Rock(Requiring Blasting/Using breaker machinery) | CUM | 444 | 1372.61 | 123.5349 | 123.5349 | 1619.6798 | 719137.8312 | 2(iv)
3 | FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge
3.1 | OPEN CAST FOUNDATION
3.1.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower foundation as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification and instruction of Engineer In charge. | CUM | 67 | 6218.65 | 559.6785 | 559.6785 | 7338.007 | 491646.469 | 6.2(iii)
3.1.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1.5:3) of grade M20 for open cast foundation with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement for tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, dewatering, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P, head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification and instruction of Engineer In charge. | CUM | 723 | 8877.05 | 798.9345 | 798.9345 | 10474.919 | 7573366.437 | 6.4(i)
3.1.3 | Cutting bending hooking, fixing and binding in poisition of MS bars for rainforcement of foundation concrete of towers including supply of wire for binding With supply of steel rod(TATA/RINL/SAIL/JINDAL Make) and head loading. No other make of steel shall be allowed. | MT | 78 | 65511.29 | 5896.0161 | 5896.0161 | 77303.3222 | 6029659.1316 | 6.5(i)
4 | PILE FOUNDATION (UNDER-REAM PILE) BORING &CONCRETE WORKS
4.1 | Boring for under ream cast-in-Situ piling, with Manual Auger method or by using Motor driven Machinery ,including supply of Bentonite required for as per required procedure depending on the length of the bore stabilization bore of required diameter bore holes as per required design length of the bore.
4.1.1 | 500MM DIA | Mtrs. | 0 | 1658.31 | 149.2479 | 149.2479 | 1956.8058 | 0
4.2 | Supply of all materials like cement, coarse aggregates (Nominal size 12mm to 20mm), fine aggregates and making Under-reamed pile foundations (after pile boring as per required depth, basing on design) as per requirement, including supply of all equipment with labours, head loading of all type of Civil materials , proper curing of the foundations and T&P as per specification in the concrete ratio 1:1.5:3 (Grade M-20) and disposal of excess earth as per the direction of Engineer In Charge. | CUM | 0 | 8877.05 | 798.9345 | 798.9345 | 10474.919 | 0
4.3 | Supply of Steel of different size (as per design) with cutting, bending, welding and binding in position of M.S.Rod for reinfocement of foundation concrete of Piles(Under reem Pile) including supply of binding wire With supply of steel rod ( TATA/RINL/SAIL/JINDAL make) and head loading. | MT. | 0 | 65511.29 | 5896.0161 | 5896.0161 | 77303.3222 | 0
4.4 | PILE RISER,CAPPING,PEDESTAL & TIE-BEAM CONCRETE WORKS
4.4.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower foundation as blind layer inclusive of labour charges for concrete mixing, shoring,shuttering & curing. This includes supply of all labourers, T&P head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) wherever required as per Technical specification and instruction of Engineer In charge. | CUM | 0 | 6218.65 | 559.6785 | 559.6785 | 7338.007 | 0
4.4.2 | Pile riser (if required),capping, tie beams etc, required for foundation of columns, equipment etc. with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates including supply of cement, different gradient for concrete ratio 1:1.5:3 (Grade M-20.) including head loading, concrete mixing,shoring,shuttering soils and back filling etc and disposal of excess earth as per the direction of Engineer In charge. | CUM | 0 | 8877.05 | 798.9345 | 798.9345 | 10474.919 | 0
4.4.3 | Supply of Steel of different size (as per design ) with cutting, bending, welding,binding in position of M.S.Rod for reinfocement of foundation concrete of Pile Risers including supply of binding wire With supply of steel rod ( TATA/RINL/SAIL/JINDAL make only) and head loading. No other make steel shall be accepted. | MT. | 0 | 65511.29 | 5896.0161 | 5896.0161 | 77303.3222 | 0
4.4.4 | Excavation in any type of soil or rocks and back filling and disposal of excess quantity of excavated soil at suitable place after back filling, & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required. | CUM | 0 | 358.41 | 32.2569 | 32.2569 | 422.9238 | 0
4.4.5 | Supply and putting of MS liner including all asociated works | MT | 0 | 65511.29 | 5896.0161 | 5896.0161 | 77303.3222 | 0
5 | Welding of Tower Nuts & Bolts
5.1 | Supply of all materials for continuous welding of bolts & nuts (around the bolt threads to the nuts) up to top of tower without cross arm, including welding rods, welding generator machine (diesel engine operator), application of required zinc rich paints around the welding portion after welding (two coats), fuel, lubricants,T&P and labours and other arrangements etc. | Nos. | 16868 | 10.01 | 0.9009 | 0.9009 | 11.8118 | 199241.4424 | 8.2(i)
6 | REVERTMENT: (including Benching) supply of all materials like cement,Laterite stone( stone masonary) all type of aggregate,labours & T&P for construction of revertment wall as per requirement to protect the tower where felt unsafe and as per approved drawing and the direction of Engineer Incharge. Including head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.).
6.1 | Excavation in all type of soil including rock & back filling including supply of sand with back filling. | CUM | 50 | 358.41 | 32.2569 | 32.2569 | 422.9238 | 21146.19
6.2 | Lean concrete in the ratio 1:3:6(grade-M10) including supply of sand & chips etc. | CUM | 5 | 6218.65 | 559.6785 | 559.6785 | 7338.007 | 36690.035 | 6.2.(iii)
6.3 | PCC in the ratio 1:2:4(grade-M15) as above | CUM | 5 | 7531.48 | 677.8332 | 677.8332 | 8887.1464 | 44435.732 | 6.3(i)
6.4 | RR masonary work in the ratio 1:5 | CUM | 200 | 3721.06 | 334.8954 | 334.8954 | 4390.8508 | 878170.16 | 15.1(i)
7 | Approval for PTCC , railway crossing, NHAI, Water and other Statutory/Govt. bodies clearances (except payment of statutory fees) has to be obtained by submitting the required documents to the concerned department through OPTCL. The documents for above clearances including required drawings etc has to be submitted by the contractor within 3 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000
8 | Forest clearances ( Stage-I & II) (Excluding payment of statutory fees) has to be obtained by submitting the required docuemnts to the concerned departments through OPTCL. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 06 months of award of contract. The contractor have to pay the DGPS authnetication & base point fees and all other payments to ORSAC. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | Hectare | 2 | 400000 | 36000 | 36000 | 472000 | 944000
9 | ROW (Right Of Way):- The agency shall pay the compensation @100% of the bench mark value of the land for construction of tower foundation and erection and 15% of bench mark value for acquisition of ROW in the land required for transmission line corridor as per the required width as per the letter no-RDM-LRGEA-POLICY-0003/43341/R&DM Dated 21.12.2022 of Additional Chief Secretary to Govt, R&DM Department, Govt. of Odisha or subsequent amendment. The agency shall also pay the crops compensation if any during the construction of transmission line in the own cost. The agency is sole responsible for obtaining ROW clearance. The agency shall pay all the cost for obtaining the ROW clearance for construction of Tower foundation, Erection and stringing of said line.
9.1 | Compensation for construction of Tower foudation & erection of transmission line including crops compensation & etc. (100% Bench mark cost plus other compensation) | Per location | 24 | 125000 | 11250 | 11250 | 147500 | 3540000
9.2 | Compensation for or acquisition of ROW in the land required & trees & crops compensation to owners for transmission line corridor as per the required width (15% Bench mark cost plus other compensation if any) | RKM | 6 | 250000 | 22500 | 22500 | 295000 | 1770000
| TOTAL OF (Civil Work) (PART-B)_TRANSMISSION LINE | [6 empty] | 24545442.7388 |  | 23195732 | -1349710.7388
| TOTAL OF CIVIL WORKS COMPONET OF WORKS CONTRACT PRICE_ SS & TRANSMISSION LINE (A+B) | [6 empty] | 249906772.0304
943320593.6228
Note on C219: Aditya Mishra:Description does not match with Raigarh estimate

## Supply-LINE n UG
ODISHA POWER TRANSMISSION CORPORATION LIMITED
|  |  |  | Name of the Work: Construction of 220 KV D/C line (UG cabling length approx 8.805 Km & Over Head length approx 1.135 Km. Total Line Length=9.94 RKms approximately) from existing 220/132/33KV GIS at Balianta | [12 empty] | 1328351724
SCHEDULE-2A-SUPPLY (FOR TRANSMISSION LINE)
|  |  |  | Sl. No. | DESCRIPTION OF ITEMS(SCHEDULE-2A-LINE) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNITS | QUANTITY | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTER-STATE) | OGST @ 9% PER UNIT(INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY | Remarks
SAP CODE | SAP DESCRIPTION |  | price
4.26
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | 52.83
1000000012 | 245 kV, 1C X 1000 Sq. mm, Cu cable | 54 | 20846700 | 1 | 220 KV GRADE Single CORE, 1000 SQ.MM.XLPE INSULATED COPPER CABLE AS PER TECHNICAL SPECIFICATION | km | 54 | 20846700 | 1876203 | 1876203 | 24599106 | 1328351724 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project |  |  | 108 | 6.1329
3000004263 | HS IL type cable jt kit for 220 kV cable | 66 | 386906 | 2 | SUPPLY OF 220 KV XLPE CABLE STRAIGHT THROUGH JOINT KIT IN COMPLETE shape SUITABLE FOR 220 KV 1000 SQMM WITH LINK BOXES with and without SLV as per site requirements and technical specification. | Nos. | 66 | 386906 | 34821.54 | 34821.54 | 456549.08 | 30132239.28 |  |  |  |  | 36
3000004264 | HS SB type cable jt kit for 220 kV cable | 36 | 386906 | 3 | Supply of Shield break type Straight through jointing kits Heat Shrink /cold shrink /premoulded type suitable for 220 kV, 1 Core, 1000 mm², copper UG Cable and Link box connection with Single Core Bonding cables as per approved bonding calculation.(Cross Bonded Joint:-30 Nos +Joints with Mid Points Bonding-6Nos.) | Nos. | 36 | 386906 | 34821.54 | 34821.54 | 456549.08 | 16435766.88
3000004265 | OD cable to Oil filled 220kV term kit | 12 | 1086005.79 | 4 | 220KV Cable Termination kit outdoor type for 220KV volatege level suitable for 1C X 1000 Sq. mm copper cable including accessorries and all consumables. | Nos. | 12 | 1086005.79 | 97740.5211 | 97740.5211 | 1281486.8322 | 15377841.9864
1000000671 | 245 kV SM surge arrestor | 6 | 71489.05 | 5 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos. | 6 | 71489.05 | 6434.0145 | 6434.0145 | 84357.079 | 506142.474
1000000932 | 200 mm dia HDPE pipe PE 80-PN8 | 52 | 1470000 | 6 | Supply of High Density Polyethylene(HDPE) pipe 200mm dia PE 80- PN8 for laying of 220kV UG cable | kM | 52 | 1470000 | 132300 | 132300 | 1734600 | 90199200 | As per Technical sanction 406, dated. 01.02.2025 of ED, CZ, BBSR(Diversion of 220kV Paradeep- Essar Line)
3000004268 | 220kV 1 ph Link box without SVL | 6 | 21301.16 | 7 | Supply of 1 ph Link box without SVL with clamps and connectors with accessories for Terminal Connection | Nos. | 6 | 21301.16 | 1917.1044 | 1917.1044 | 25135.3688 | 150812.2128 | cost data 24-25
3000004267 | 220kV 1 ph Link box with SVL | 6 | 38675.29 | 8 | Supply of 1 ph Link box with SVL with clamps and connectors with acessories for terminal connector | Nos. | 6 | 38675.29 | 3480.7761 | 3480.7761 | 45636.8422 | 273821.0532 | cost data 24-25
1000000933 | 220kV 3ph Link box without SVL | 6 | 39181 | 9 | Supply of 3 ph Link box without SVL with clamps and connectors with acessories for mid point bonding | Nos. | 6 | 39181 | 3526.29 | 3526.29 | 46233.58 | 277401.48 | Rate considered from CPC W.O- 250(14), 14.03.2024 (Samagara-Puri UG Cable)
3000004269 | 220kV 3ph Link box with SVL | 10 | 47140 | 10 | Supply of 3 ph Link box with SVL with clamps and connectors with acessories for Cross Bonding | Nos. | 10 | 47140 | 4242.6 | 4242.6 | 55625.2 | 556252
1000000934 | 400Sqmm XLPE bonding cable | 1650 | 4217.43 | 11 | 400 Sq.MM Single core Bonding cable including connection/termination as required to make the system complete in all respect. (voltage Level to be determined by considering the fault level at seath) | MTR | 1650 | 4217.43 | 379.5687 | 379.5687 | 4976.5674 | 8211336.21 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL | Rate adopted proportionately @33% of 3171.00
3000000595 | 50 MM GI PORFORATED EARTHING PIPE | 40 | 14050 | 12 | Supply of Earthing materials 3 Mtr ,50mm ID Heavy gauge type pipe (with provision of with GI clamp fixtures welded allaround the pipe and connecting separately to main equipment for grounding (Single Electrode with accessories) with GI Flat 75x10mm siz | Nos. | 40 | 14050 | 1264.5 | 1264.5 | 16579 | 663160 | Rate considered from CPC W.O- 250(14), 14.03.2024 (Samagara-Puri UG Cable)
1000000331 | 48 F OPGW CABLE | 9 | 127089.72 | 13 | 48 Fibre Optic Approach Cable(DWSM) | KM | 9 | 127089.72 | 11438.0748 | 11438.0748 | 149965.8696 | 1349692.8264 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3000004096 | Hardware for 48 Fibre (DWSM) | 9 | 93762.74 | 13.1 | Installation hardware set((HDPE Duct,HDPE couplingetc) for 48 Fibre FOAC. | KM | 9 | 93762.74 | 8438.6466 | 8438.6466 | 110640.0332 | 995760.2988
3000003657 | 48 F OPGW SPLICING ENCLOSER | 2 | 6491 | 13.2 | Joint Box (Splice enclosure),48 Fibre | Nos | 2 | 6491 | 584.19 | 584.19 | 7659.38 | 15318.76
3000004081 | ST, PC & accessories for OFC connection | 8 | 5142 | 13.3 | Supply of straight through Connectors (Plastic Coupler) and acessories for OFC connection | Set | 8 | 5142 | 462.78 | 462.78 | 6067.56 | 48540.48 | Rate considered from CPC W.O- 250(14), 14.03.2024 (Samagara-Puri UG Cable)
3000004270 | OFC end connectors at GSS end | 2 | 7958 | 13.4 | Supply of end Connectors and acessories for OFC connection at GRID subststions | Set | 2 | 7958 | 716.22 | 716.22 | 9390.44 | 18780.88
|  | 2 | 153053 | 14 | GI Support for Cantiliver arrangement at Drain, Bridge etc. | Mt | 2 | 153053 | 13774.77 | 13774.77 | 180602.54 | 361205.08 |  | 1493924995.9016 | 202990894.4464
|  | 0 | 0 | 1: 15; 2: SUPPLY of Following type tested Lattice type Galvanized steel tangent / Angle tower with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification.
|  | 1 | 0 | 2: OA TYPE TOWERS (Nominal unit weight 4.33 MT); 3: Nos.; 4: 1; 10: Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
|  | 0 | 0 | 2: +3 EXTENSION to OA type Towers (Nominal unit weight- 0.759 MT); 3: Nos.; 4: 0
|  | 0 | 0 | 2: +6 EXTENSION to OA type Towers (Nominal unit weight- 1.495 MT); 3: Nos.; 4: 0
|  | 3 | 0 | 2: OB TYPE TOWERS (Nominal unit weight 6.54 MT); 3: Nos.; 4: 3
|  | 0 | 0 | 2: +3 EXTENSION to OB type Towers (Nominal unit weight 1.334 MT); 3: Nos.; 4: 0
|  | 2 | 0 | 2: +6 EXTENSION to OB type Towers (Nominal unit weight- 2.308 MT); 3: Nos.; 4: 2
|  | 2 | 0 | 2: OC TYPE TOWERS (Nominal unit weight- 9.191 MT); 3: Nos.; 4: 2
|  | 0 | 0 | 2: +3 EXTENSION to OC type Towers (Nominal unit weight- 1.477 MT); 3: Nos.; 4: 0
|  | 0 | 0 | 2: +6 EXTENSION to OC type Towers (Nominal unit weight- 2.715 MT); 3: Nos.; 4: 0
|  | 1 | 0 | 2: +15 mtr Extension to OC type Tower (nominal Weight- 8.66 MT); 3: Nos.; 4: 1
|  | 0 | 0 | 2: +24 mtr Extension to OC type Tower (nominal Weight- 8.66 MT); 3: Nos.; 4: 0
|  | 1 | 0 | 2: Composite tower portion to OC ( nominal Weight-6.347; 3: Nos.; 4: 1
1000000140 | TOWER STRUCTURE (MS) | 66.121 | 90371.05 |  | TOTAL WEIGHT OF THE STRUCTURES INCLUDING TOWER STUB | MT | 66.121 | 90371.05 | 8133.3945 | 8133.3945 | 106637.839 | 7051000.5525
|  | 0 | 0 | 2: STUBS; 10: Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
|  | 1 | 0 | 2: OA type (Nominal unit weight 0.233MT); 3: Nos.; 4: 1
|  | 3 | 0 | 2: OB type (Nominal unit weight 0.438MT); 3: Nos.; 4: 3
|  | 2 | 0 | 2: OC type (Nominal unit weight 0.776MT); 3: Nos.; 4: 2
|  | 1 | 0 | 2: OC +15 Extension to OC type (Nominal unit weight 1.067MT); 3: Nos.; 4: 1
Stub w t added to structure |  | 4.166 | 0 | 2: TOTAL WEIGHT OF THE TOWER STUB; 3: MT; 4: 4.166
|  | 0 | 0 | 2: MS Enamel Painted TEMPLATES
|  | 1 | 0 | 2: OA (Nominal unit weight- 0.579 MT); 3: Nos.; 4: 1
|  | 1 | 0 | 2: OB (Nominal unit weight- 0.794 MT); 3: Nos.; 4: 1
|  | 1 | 0 | 2: OC (Nominal unit weight- 1.006 MT); 3: Nos.; 4: 1
|  | 1 | 0 | 2: OC+15/24(Nominal unit weight- 2.073 MT); 3: Nos.; 4: 1
3000003442 | MS enamel painted Templates | 4.452 | 69832.18 | 15.8 | TOTAL WEIGHT OF THE TEMPLATES | MT | 4.452 | 69832.18 | 6284.8962 | 6284.8962 | 82401.9724 | 366853.5811
3000004093 | G.I. nuts & bolts | 3.5286 | 118560.66 | 15.9 | Weight of different type G.I Nuts and Bolts | MT | 3.5286 | 118560.66 | 10670.4594 | 10670.4594 | 139901.5788 | 493663.706
|  | 0 | 0 | 1: 16; 2: Supply of the following tower accessories as per technical specification and as directed by the engineer in charge.
3000000574 | EARTHING DEVICE | 8 | 2280.98 | 16.1 | EARTHING DEVICE | Nos | 8 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 21532.4512 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3000003561 | DANGER BOARD | 14 | 236.77 | 16.2 | DANGER BOARD | Nos | 14 | 236.77 | 21.3093 | 21.3093 | 279.3886 | 3911.4404
3000003578 | TOWER NUMBER PLATE | 14 | 129.38 | 16.3 | NUMBER PLATE | Nos | 14 | 129.38 | 11.6442 | 11.6442 | 152.6684 | 2137.3576
3000003579 | TOWER PHASE PLATE | 84 | 100.92 | 16.4 | PHASE PLATE | Nos | 84 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 10003.1904
3000003555 | ANTICLIMBING DEVICE | 14 | 4400.23 | 16.5 | ANTICLIMBING DEVICE | Nos | 14 | 4400.23 | 396.0207 | 396.0207 | 5192.2714 | 72691.7996
3000003558 | TOWER CIRCUIT PLATE | 28 | 100.92 | 16.6 | CIRCUIT PLATE | Nos | 28 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 3334.3968
|  | 0 | 0 | 1: 17; 2: Supply of following POWER CONDUCTORS in the proposed 220kV lines as per the technical specification and as per the instruction of the engineer in charge.
1000000017 | ACSR ZEBRA CONDUCTOR | 6.9121 | 363162.06 | 17.1 | ACSR ZEBRA CONDUCTOR | KM | 6.9121 | 363162.06 | 32684.5854 | 32684.5854 | 428531.2308 | 2962072.147 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
|  | 0 | 0 | 1: 18; 2: POWER CONDUCTOR ACESSORIES
|  | 0 | 0 | 1: 18.1; 2: For ACSR Zebra
3000000456 | VD OF ACSR ZEBRA CONDUCTOR | 48 | 756.44 | 18.1.1 | VIBRATION DAMPER | Nos | 48 | 756.44 | 68.0796 | 68.0796 | 892.5992 | 42844.7616
3000000438 | MS JOINT FOR ACSR ZEBRA CONDUCTOR | 25 | 797.33 | 18.1.2 | MID SPAN JOINT | Set | 25 | 797.33 | 71.7597 | 71.7597 | 940.8494 | 23521.235
3000000466 | REPAIR SLEEVE FOR ACSR ZEBRA CONDUCTOR | 5 | 324.04 | 18.1.3 | REPAIR SLEEVE | Set | 5 | 324.04 | 29.1636 | 29.1636 | 382.3672 | 1911.836
|  | 0 | 0 | 1: 19; 2: Supply of the following insulators as per the technical specification and as per the instruction of the Engineer in charge.
3000000950 | 160KN 220 KV PORCELAIN LONG ROD INSULATO | 107.1 | 14593.68 | 19.1 | 160KN Porcelain Longrod Insulators String for 220KV | SET | 107.1 | 14593.68 | 1313.4312 | 1313.4312 | 17220.5424 | 1844320.091 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3000004306 | 220 kV LR 120 kN porcelain insulator | 25.2 | 14593.68 | 19.2 | 120KN Porcelain Longrod Insulators String for 220KV | SET | 25.2 | 14593.68 | 1313.4312 | 1313.4312 | 17220.5424 | 433957.6685
3000000953 | 90KN 220KV PORCELAIN LONG ROD | 3 | 11187.5 | 19.3 | 90KN Porcelain Longrod Insulators String for 220KV (For Pilot) | SET | 3 | 11187.5 | 1006.875 | 1006.875 | 13201.25 | 39603.75 | CD TL- 59
|  | 0 | 0 | 1: 20; 2: Supply of the following hard ware fittings suitable for ACSR Zebra conductors as per the technical specification.
|  | 0 | 0 | 1: 20.1; 2: For ACSR Zebra
3000000877 | ST Hard wares fittings 120KN insulator | 0 | 2698.67 | 20.1.1 | Single suspension Hard wares fittings suitable for 120 KN insulator. | Nos | 0 | 2698.67 | 242.8803 | 242.8803 | 3184.4306 | 0 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3000004183 | DS HWF FOR ACSR ZEBRA 120KN | 12 | 4566.27 | 20.1.2 | Double suspension Hard wares fittings suitable for 120 KN insulator. | Nos | 12 | 4566.27 | 410.9643 | 410.9643 | 5388.1986 | 64658.3832
3000004327 | ST HW fitting for 160 kN insulator | 30 | 2076.13 | 20.1.3 | Single tension Hard wares fittings suitable for 160 KN insulator. | Nos | 30 | 2076.13 | 186.8517 | 186.8517 | 2449.8334 | 73495.002
3000004328 | DT HW fitting for 160 kN insulator | 36 | 4735.96 | 20.1.4 | Double tension Hard wares fittings suitable for 160 KN insulator. | Nos | 36 | 4735.96 | 426.2364 | 426.2364 | 5588.4328 | 201183.5808
3000004184 | SS HWF FOR ACSR ZEBRA 90KN | 3 | 2698.67 | 20.1.5 | Single suspension Hard wares fittings suitable for 90KN insulator(Pilot) |  | 3 | 2698.67 | 242.8803 | 242.8803 | 3184.4306 | 9553.2918 | CD TL- 15
4000000050 | D SHACKLE | 10 | 350 | 20.1.6 | “D” Shackle | Nos | 10 | 350 | 31.5 | 31.5 | 413 | 4130 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3000003802 | U BOLT | 10 | 99.63 | 20.1.7 | U'-Bolt. | Nos | 10 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 1175.634
|  | 0 | 0 | 1: 21; 2: Supply of OPGW Fibre Optic Cable & Hard ware for Speech , data & protection
1000000331 | 48 F OPGW CABLE | 1.225 | 215500 | 21.1 | 48 fibre (DWSM) OPGW fibre optic cable. | Km | 1.225 | 215500 | 19395 | 19395 | 254290 | 311505.25 | CD- TEL- 25
3000000820 | OPGW hardware set | 1.225 | 22597.72 | 21.2 | OPGW hardware set like suspension Assembly,Tensin Assembly(Dead end assembly, Pass through assembly) ,Vibration Damper,Down Lead Clamp Assemblies for 24/48 Fibre(DWSM) OPGW,Joint Box | KM | 1.225 | 22597.72 | 2033.7948 | 2033.7948 | 26665.3096 | 32665.0043 | CD- TEL- 26
3000003450 | Supply of FODP-48F | 1 | 54256.95 | 21.3 | Supply of FODP (fiber Optic Distribution Panel) 48F, Indoor type mounted with FCPC coupling and pigtails (DWSm fibre) | Nos. | 1 | 54256.95 | 4883.1255 | 4883.1255 | 64023.201 | 64023.201 | CD- TEL- 29
|  |  |  | 2: TOTAL OF LINE -2A (SUPPLY); 9: 1508060745.2134 | 14135749.3118
1744228845.4165
Note on H54: DILLIP: 1 earthing extra fro composite tower

## Erection- Line n UG
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of the Work: Construction of 220 KV D/C line (UG cabling length approx 8.805 Km & Over Head length approx 1.135 Km. Total Line Length=9.94 RKms approximately) from existing 220/132/33KV GIS at Balianta
SCHEDULE-2C-ERECTION & CIVILWORKS (FOR TRANSMISSION LINE)
Sl. No. | DESCRIPTION OF ITEMS(SCHEDULE-2C-LINE) ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENT/MATERIALS ALONG WITH CIVIL WORKS (As per Technical Specification) | UNIT | QUANTITY | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTER-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
PART-A | ELECTRICAL WORKS
1 | Laying , Comissioning & Testing of 220 kV, 1 Core,1-Run, 1000 mm² Copper, XLPE insulation UG Cable by HDD method with 200 mm dia PE 80- PN8, HDPE pipe for laying of individual run of UG cable at Main Road /Drain crossing / Railway Crossing/unaccessible place as per instruction of Engg in Charge. | Km. | 48.42 | 1820000 | 163800 | 163800 | 2147600 | 103986792 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project |  |  |  | 54
2 | Laying , Comissioning & Testing of 220 kV, 1 Core,3-Runs, 1000 mm² Copper, XLPE insulation UG Cable by open treanch method ( S/C, 3 Runs) in Direct buried or as per instruction of Engg in Charge | Km. | 4 | 127190 | 11447.1 | 11447.1 | 150084.2 | 600336.8 | Autonagar
3 | Laying, Testing & Comissioning of 220 kV, 1 Core,3-Runs, 1000 mm² Copper, XLPE insulation UG Cable for Sneking,Bending, looping and raising at both the termination end | Km. | 1.08 | 572355 | 51511.95 | 51511.95 | 675378.9 | 729409.212 | Autonagar
4 | Laying, Testing & Comissioning of of 220 kV, 1 Core,3-Runs, 1000 mm² Copper, XLPE insulation UG Cable along with HDPE pipe of 160 mm dia with Cantiliver support at drain crossing/Bridge Crossing [3nos cable to be laid per RKM]. | Km. | 0.5 | 254642.37 | 22917.8133 | 22917.8133 | 300477.9966 | 150238.9983 | Autonagar
5 | Erection OF 220 KV 1Cx1000 Sq Mm XLPE CABLE STRAIGHT THROUGH JOINT KIT COMPLETE SUITABLE FOR 220 KV 1000 SQMM WITH LINK BOXES. This also includes construction of temporary water proof tent shed for Cable Jointing Bay, including arrangement of all the necessary tools and plants, including Air Conditioner, temporary power supply etc. at the jointing bay site not limiting to the above and any other requirements for completion of the work as per specification. | Nos | 66 | 150000 | 13500 | 13500 | 177000 | 11682000 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
6 | Erection of Shield break type Straight through jointing kits Heat Shrink /cold shrink /premoulded type suitable for 220 kV, 1 Core, 1000 mm², copper UG Cable and Link box connection with Single Core Bonding cables as per approved bonding calculation.(Cross Bonded Joint:-30 Nos +Joints with Mid Points Bonding-6Nos.) | Nos | 36 | 40064.85 | 3605.8365 | 3605.8365 | 47276.523 | 1701954.828 | Autonagar
7 | Erection of 220 KV 1Cx1000 Sq Mm XLPE Cable end termination(s) kits on Cable Termination Tower Structure as per technical specification.This also includes construction of temporary water proof tent shed for Cable Jointing Bay, including arrangement of all the necessary tools and plants, including Air Conditioner, temporary power supply etc. at the termination bay site not limiting to the above and any other requirements for completion of the work as per specification. | Nos | 6 | 250000 | 22500 | 22500 | 295000 | 1770000 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
8 | Erection of 220KV Cable Termination kit outdoor type for 220KV voltage level suitable for 1C X 1000 Sq. mm copper cable including accessories and all consumables at Pahala GSS | Nos | 6 | 100000 | 9000 | 9000 | 118000 | 708000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
9 | Erection of 220 kV Surge arrestor with clamp & connectors on Cable Termination Tower Structure | Nos | 6 | 5203.87 | 468.3483 | 468.3483 | 6140.5666 | 36843.3996 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
10 | Erection of 1 ph Link box without SVL with clamps and connectors with acessories | Nos. | 6 | 2712 | 244.08 | 244.08 | 3200.16 | 19200.96 | RTSS Mancheswar
11 | Erection of 1 ph Link box with SVL with clamps and connectors with acessories | Nos. | 6 | 2712 | 244.08 | 244.08 | 3200.16 | 19200.96
12 | Erection of 3 ph Link box without SVL with clamps and connectors with acessories | Nos. | 6 | 2712 | 244.08 | 244.08 | 3200.16 | 19200.96
13 | Erection of 3 ph Link box with SVL with clamps and connectors with acessories | Nos. | 10 | 2712 | 244.08 | 244.08 | 3200.16 | 32001.6
14 | 400 Sq.MM Single core Bonding cable including connection/termination as required to make the system complete in all respect. (voltage Level to be determined by considering the fault level at seath) | MTR | 1650 | 80 | 7.2 | 7.2 | 94.4 | 155760 | Same as 300 Sq.mm
14 | Erection of Earthing materials 3 Mtr ,100mm ID Heavy gauge type pipe (with provision of GI clamp fixtures welded allaround the pipe and connecting separately to main equipment for grounding (Single Electrode with accessories) with GI Flat 75x10mm siz | Nos. | 40 | 8881 | 799.29 | 799.29 | 10479.58 | 419183.2 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
15 | Laying of 48 core fibre optic cables single mode, duct type, fibre armoured with duct pipe, laid along 220kV UG cable laying by open treanch method & HDD method .
15.1 | Laying of 48 core single mode fibre optic cables with HDPE PLB duct of size 32/26mm and connectors , laid along 220kV UG cable through open trench method. | Km. | 9 | 40370 | 3633.3 | 3633.3 | 47636.6 | 428729.4 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
15.2 | Laying of 48 Core single mode Fibre Optic Cables with Duct pipe of size 32/26mm and connectors through HDD method laid along 220kV UG Cable in main road crossing and Railway crossing. | Km. | 9 | 161480 | 14533.2 | 14533.2 | 190546.4 | 1714917.6
15.3 | Erection of straight through Connectors (Plastic Coupler) and acessories for OFC connection | Nos. | 8 | 4709 | 423.81 | 423.81 | 5556.62 | 44452.96
15.4 | Erection of end Connectors and acessories for OFC connection at GRID subststions | Nos. | 2 | 4709 | 423.81 | 423.81 | 5556.62 | 11113.24
16 | Scalffolding at Composite tower for termination of UG Cable including man, materials, machinaries etc. | LOT | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | Market Rate |  | 124819336.1179
17 | ERECTION,TESTING & COMMISSIONING of Following tested Lattice type Galvanized steel tangent / Angle tower without stubs and cleats including different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete with tightening, punching of bolts including step bolts. All other left out portion of the bolts above bottom cross arm shall be riveted by using suitable hammer. Painting of black bituminous paints three coats shall be provided up to a height of 500mm above(for all the legs of the towers) the cooping legs & bracing members including head loading of tower materials T & P etc. All Erection should confirm to the Technical Specification laid there in the Tender Specification.
17.1 | OA TYPE TOWERS (Nominal unit weight 4.33 MT) | Nos. | 1
17.1.1 | +3 EXTENSION to OA type Towers (Nominal unit weight- 0.759 MT) | Nos. | 0
17.1.2 | +6 EXTENSION to OA type Towers (Nominal unit weight- 1.495 MT) | Nos. | 0
17.2 | OB TYPE TOWERS (Nominal unit weight 6.54 MT) | Nos. | 3
17.2.1 | +3 EXTENSION to OB type Towers (Nominal unit weight 1.334 MT) | Nos. | 0
17.2.2 | +6 EXTENSION to OB type Towers (Nominal unit weight- 2.308 MT) | Nos. | 2
17.3 | OC TYPE TOWERS (Nominal unit weight- 9.191 MT) | Nos. | 2
17.3.1 | +3 EXTENSION to OC type Towers (Nominal unit weight- 1.477 MT) | Nos. | 0
17.3.2 | +6 EXTENSION to OC type Towers (Nominal unit weight- 2.715 MT) | Nos. | 0
17.3.3 | +15 mtr Extension to OC type Tower (nominal Weight- 8.66 MT) | Nos. | 1
17.3.4 | +24 mtr Extension to OC type Tower (nominal Weight- 8.66 MT) | Nos. | 0
17.3.5 | Composite tower portion to OC ( nominal Weight-6.347 | Nos. | 1
17.4 | WEIGHT OF THE GI TOWER STRUCTURES Complete with tightening ,checking and punching of bolts including step bolts(Including Transportation from nearest OPTCL Store) | MT | 66.121 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 576287.1763 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
17.5 | Weight of different type G.I Nuts & Bolts and including different size of plain washer / spring washer for tower structure | MT | 3.5286 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 30754.4614
17.6 | STUB SETTING
17.6.1 | OA type (Nominal unit weight 0.233MT) | Nos. | 1
17.6.2 | OB type (Nominal unit weight 0.438MT) | Nos. | 3
17.6.3 | OC type (Nominal unit weight 0.776MT) | Nos. | 2
17.6.4 | OC +15 Extension to OC type (Nominal unit weight 1.067MT) | Nos. | 1
17.6.5 | OC +24 Extension to OC type (Nominal unit weight 1.067 MT) | Nos. | 0
17.7 | TOTAL WEIGHT OF THE TOWER STUB | MT | 4.166 | 5738.91 | 516.5019 | 516.5019 | 6771.9138 | 28211.7929 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
17.8 | TEMPLATES FITTING
17.8.1 | OA (Nominal unit weight- 0.579 MT) | Nos. | 1
17.8.2 | OB (Nominal unit weight- 0.794 MT) | Nos. | 3
17.8.3 | OC (Nominal unit weight- 1.006 MT) | Nos. | 2
17.8.4 | OC+15/24(Nominal unit weight- 2.073 MT) | Nos. | 1
17.9 | Fixing of of Stub Setting Templates and setting of Stub | MT | 4.45 | 5738.91 | 516.5019 | 516.5019 | 6771.9138 | 30135.0164 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
17.1 | Erection of the following tower accessories as per technical specification and as directed by the engineer in charge.
17.10.1 | EARTHING DEVICE | Nos. | 8 | 3071.77 | 276.4593 | 276.4593 | 3624.6886 | 28997.5088 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
17.10.2 | DANGER BOARD | Nos. | 7 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 1317.2222
17.10.3 | NUMBER PLATE | Nos. | 7 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 1317.2222
17.10.4 | PHASE PLATE | Nos. | 42 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 7903.3332
17.10.5 | ANTICLIMBING DEVICE | Nos. | 7 | 3441.28 | 309.7152 | 309.7152 | 4060.7104 | 28424.9728
17.10.6 | CIRCUIT PLATE | Nos. | 14 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 2634.4444
18 | Hoisting and fixing of insulators with required accessories etc , paying out of conductor ,jointing, stringing, sagging & Jumpering etc. of power conductor in the proposed lines and without earth wire with all required accessories including scaffolding for 33 KV,11 KV, LT , P&T lines, roads (SH & NH) and using own required T&P and compression jointing machines etc. with 1.5% provision for Sag & Wastage including head loading of stringing materials T & P etc. and as per the direction of Engineer in charge.
18.1 | Double Circuit (ACSR Zebra, Three Power Conductor with OPGW/Earthwire ) | RKM | 1.135 | 70504.02 | 6345.3618 | 6345.3618 | 83194.7436 | 94426.034 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
18.2 | Erection of OPGW wire with Hardware fittings and accessories like suspension Assembly,Tensin Assembly(Dead end assembly, Pass through assembly) ,Vibration Damper,Down Lead Clamp Assemblies for 24/48 Fibre(DWSM) OPGW,Joint Box | RKM | 1.135 | 45000 | 4050 | 4050 | 53100 | 60268.5 | Estimate Ramakrushnapur
| TOTAL of ELECTRICAL WORKS Part-I (A) | [6 empty] | 125710013.8025
PART B | CIVIL WORKS
Over Head Line
1 | Preliminary survey, Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | RKM | 1.135 | 14268.67 | 1284.1803 | 1284.1803 | 16837.0306 | 19110.0297 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
2 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | RKM | 1.135 | 6714.67 | 604.3203 | 604.3203 | 7923.3106 | 8992.9575 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3 | Preparation of land schedule-with HAL & SAVIKclassification on revenue maps plot No, khata No, Mouza on revenue mapsindicating alignment therein duly authenticated by Revenue Inspector andTahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 220 KV line. Final route to be plotted on 1:50000 topo sheet for approval. | RKM | 1.135 | 10911.34 | 982.0206 | 982.0206 | 12875.3812 | 14613.5577 | RC TL 1.3
4 | Soil investigation per location (c)river bed pile foundation( boring to 30.0m depth) | Nos. | 6 | 75540.02 | 6798.6018 | 6798.6018 | 89137.2236 | 534823.3416 | RC TL- Annex- I- 1.5-C
5 | Excavation in all depths for following type of soil and rocks and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required.
5.1 | Soft/Loose soil | CUM | 120 | 233.97 | 21.0573 | 21.0573 | 276.0846 | 33130.152 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
5.2 | Dense/Compact soil | CUM | 80 | 366.54 | 32.9886 | 32.9886 | 432.5172 | 34601.376
5.3 | Partial Submerged soil | CUM | 80 | 421.13 | 37.9017 | 37.9017 | 496.9334 | 39754.672
5.4 | Fully submerged soil | CUM | 120 | 421.13 | 37.9017 | 37.9017 | 496.9334 | 59632.008
6 | FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge
6.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM | 80 | 6377.44 | 573.9696 | 573.9696 | 7525.3792 | 602030.336 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
6.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1:2) of grade M25 for open cast foundation and UG cable Trench as per specification and approved drawings with supply of approved quality coarse aggregates(Nominal size 12mm to 20mm), fine aggregates, cement and steel of different size(as per design) with cutting, bending, binding of M.S.Rod (FE-500) including supply of binding wire in tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM | 5 | 10266.65 | 923.9985 | 923.9985 | 12114.647 | 60573.235
6.3 | Cutting bending hooking ,fixing and binding in poisition of MS bars for rainforcement of foundation concrete of towers including supply of wire for binding (With supply of steel rod(TATA/RINL/SAIL Make). | MT | 0.3 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 22650.4847 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
7 | RIVER BED PILING: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making river bed pile by DMC method (Motor Driven) boring of piles foundations for river crossing locations with vertical boring of piles (pile bore as per required depth, basing on design) , preparation of cage, lowering and positioning (cutting,bending,binding/welding of M.S.Rod including supply of binding wire/way of welding) of the required above mentioned Tower foundation as indicated above and as per requirement, including supply of all materials,labours, de-watering, proper curing of the foundations and T&P as per specification and instruction of Engineer in charge in the RCC : 1:1:2 (Grade M-25.) including stabilization of bore :- Pile diameter (1000 MM).
7.1 | Pile foundation without under reemed boring 1000mm dia | Mtrs. | 700 | 4464.21 | 401.7789 | 401.7789 | 5267.7678 | 3687437.46 | RC TL- Annex- I- 7.2-vii | 62.5 | 7 | 437.5
7.2 | RCC M-25 (1:1:2) (Excluding Steel) With cement and without rod | CUM | 600 | 10266.65 | 923.9985 | 923.9985 | 12114.647 | 7268788.2 | RC TL- Annex- I- 6.7-i
7.3 | Supply of Steel of different size (as per design) with cutting, bending, welding and binding in position of M.S.Rod for reinfocement of foundation concrete of Piles(Under reem Pile) including supply of binding wire With supply of steel rod ( TATA/RINL/SAIL/JINDAL make) and head loading. | MT. | 25 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 1887540.39 | RC TL- Annex- I- 6.5-i
7.4 | 1000 MM dia MS liners of required numbers each of 1mtr height made of 6mm thick MS plate(MS plate of SAIL / TISCO make only) including,supply,cutting,bending,rolling,welding,face cutting,driving,transportation,loading,unloading etc for different location in river bed piling work. | MT. | 50 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 3775080.78 | RC TL- Annex- I- 7.6-i
8 | PILE RISER,CAPPING,PEDESTAL & TIE-BEAM CONCRETE WORKS
8.1 | Pile riser,cap,tie-beam with RCC: 1:1.5:3 (Grade M-20) for above river bed piling ,including supply of all materials like MS Rod(cutting,bending,binding of M.S.Rod including supply of binding wire),Cement, coarse and fine aggregates, shuttering and centering and temporary road on the river and supply of labours, de-watering, proper curing of the foundations /concrete and T&P in line with the Specification and as per direction of Engineer in Charge.
8.2 | Excavation in all type soil and rocks and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/murrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required. (i) Soft/Loose Soil. | CUM | 350 | 366.54 | 32.9886 | 32.9886 | 432.5172 | 151381.02 | RC TL- Annex- I-2-ii
8.3 | Providing and laying ordinary plain/reinforced concrete work of grade M- 20 (1:1.5:3) with approved quality stone chips of normal size up to 20 mm in tower foundation and couping inclusive of cost of cement mixing by curring etc. and cost of all materials(Form Boxes and other consumables to be supplied by the contractor) conforming to relevant IS.With cement and without rod | CUM | 550 | 9103.72 | 819.3348 | 819.3348 | 10742.3896 | 5908314.28 | RC TL- Annex- I- 6.4-i
8.4 | Providing mud-matting before concreting of stubs with lean concrete including cost of agree gates,mixing, layig, curring etc(Form Boxes and other consumables to be supplied by the contractor) 1:3:6 mix with cement . | CUM | 18 | 6377.44 | 573.9696 | 573.9696 | 7525.3792 | 135456.8256 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
8.5 | Supply of Steel of different size (as per design ) with cutting, bending, welding,binding in position of M.S.Rod for reinfocement of foundation concrete of Pile Risers including supply of binding wire With supply of steel rod ( TATA/RINL/SAIL/JINDAL make only) and head loading. No other make steel shall be accepted. | MT. | 85 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 6417637.326 | RC TL- Annex- I- 6.5-i
8.6 | SHORING & SHUTTERING- required in wet or special locations with supply of all materials,T&P and Labour. | Sq. Mtr. | 150 | 452.32 | 40.7088 | 40.7088 | 533.7376 | 80060.64 | RC TL- Annex- I- 4
8.7 | DE-WATERING (i) With Supply of all T&P on Man Hr basis. | HP Hr | 60 | 272.95 | 24.5655 | 24.5655 | 322.081 | 19324.86 | RC TL- Annex- I- 4
8.8 | Pipe type earthing including cost of bentonate compound and good borrowed earth where necessary in accordance with IS:3043-1966 and with supply of all T&P and Laobur.Without cost of earthing pipe and G.I.Flat | No. | 7 | 3071.77 | 276.4593 | 276.4593 | 3624.6886 | 25372.8202
8.9 | Supply & painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping(both leg & bracing members) | Sq. Mtr. | 150 | 146.36 | 13.1724 | 13.1724 | 172.7048 | 25905.72 | RC TL- Annex- I- 17
8.10 | Welding (including supply of electrods and zinc rich paints with application after welding) Bolt and nut | No. | 8000 | 10.24 | 0.9216 | 0.9216 | 12.0832 | 96665.6 | RC TL- Annex- I- 16.2-I
9 | RIGHT OF WAY COMPENSATION
9.1 | Per location for foundation and erection of tower including approach to the Location as per prevailing Guidelines and as decided by the District Adminstartion. The ROW Clearance/NOC documents duly signed by the Claimant shall be submitted to OPTCL. | Per Loc | 3 | 200000 | 18000 | 18000 | 236000 | 708000 | Price taken from Lumsum amount on assumption bais.
9.2 | Per Kilometer for stringing including approach to the Locations as per prevailing Guidelines and as decided by the District Adminstartion.The ROW Clearance/NOC documents duly signed by the Claimant shall be submitted to OPTCL. | Per Km. | 1.135 | 500000 | 45000 | 45000 | 590000 | 669650 | Price taken from Lumsum amount on assumption bais. |  | 32286528.072
10 | Under Ground Cable
10.1 | CIVIL Works with supply of all materials like Cement, MS tor rod, Brick, Coarse & Fine Agregrates & Labour,T&P etc For RCC Slabs & Others (PART-B)
10.1.1 | Open trench (direct burried) for laying of 220 kV cables Width : 1000mm Depth : 1850mm
10.1.1.1 | Earth work excavation of soil- Trench Dimension : (1mtr w x 1.85mtr d) | Cum | 20000 | 296 | 26.64 | 26.64 | 349.28 | 6985600 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
10.1.1.2 | Shifing of excavated soil to a lead distance of 10 Km | Cum | 4000 | 370 | 33.3 | 33.3 | 436.6 | 1746400
10.1.1.3 | Filling with fine river sand after laying of Cable inside the trench | Cum | 4000 | 1345 | 121.05 | 121.05 | 1587.1 | 6348400
10.1.1.4 | Back filling with excavated soils | Cum | 16000 | 134 | 12.06 | 12.06 | 158.12 | 2529920
10.1.1.5 | Casting and erection of RCC partition slab with supply of cement, aggregates etc including supply of all labour, T & P etc but without cost of steel. The slab size shall be 950x450x50mm and the conctrete shall be of M20 grade. | Cum | 230 | 9103.72 | 819.3348 | 819.3348 | 10742.3896 | 2470749.608
10.1.1.6 | Supply of rod, bending ,cutting and binding for prefabricated RCC slabs | MT | 2.5 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 188754.039
10.1.1.7 | Damage of Asphalt/Tar road & other utilities (1mtr width) Asphalt : 25 - 50 mm,Binder course : 50 - 100 mm, Base course : 100 - 300 mm Subgrade : 100 - 300 mm,Compacted Subgrade : 150 - 300 mm | kM | 10 | 336418 | 30277.62 | 30277.62 | 396973.24 | 3969732.4
10.1.1.8 | Reconstructing of Asphalt/Tar road & other utilities to bring its origional shape after laying of cable in open trench (1mtr width) Asphalt : 25 - 50 mm,Binder course : 50 - 100 mm,Base course : 100 - 300 mm Subgrade : 100 - 300 mm,Compacted Subgrade : 150 - 300 mm | kM | 10 | 4037023 | 363332.07 | 363332.07 | 4763687.14 | 47636871.4
10.1.1.9 | Damage of Concrete road / Concrete Footpath & other utilities (1mtr width) | kM | 0.5 | 336418 | 30277.62 | 30277.62 | 396973.24 | 198486.62
10.1.1.10 | Reconstructing of Concrete road / Concrete Footpath & other utilities to bring its origional shape after laying of cable in open trench (1mtr width) | kM | 0.5 | 2691349 | 242221.41 | 242221.41 | 3175791.82 | 1587895.91
B | Other Civil Works
11 | Supply of all materials and Erection of 220KV Jointing Bays (2mtrx8Mtr) along trench for straght through joints with RCC protection slab of 150mm thick. With Civil materials like bricks ,cements,sand,Materials for temporary shed,Airconditioners etc | Nos | 17 | 161480 | 14533.2 | 14533.2 | 190546.4 | 3239288.8
12 | Supply and erection of Route Marker along the Cable Routes at an interval of 30 Mtrs as per the drawing with civil works | Nos. | 300 | 1345 | 121.05 | 121.05 | 1587.1 | 476130
13 | Construction of RCC Foundation for 220kV Link Box including supply of all materials (cement, steel, aggregates, labolr, T & P etc.) | Nos. | 16 | 26913 | 2422.17 | 2422.17 | 31757.34 | 508117.44
14 | Making of earth chamber including excavation, soil treatment with Bentonite powder, supply of charcoal, etc with brick masonary (1:5), PCC (1:4:8) and with cast iron cover size of the pit 450mmX450mm X600 mm depth as per direction of Engineer in Charge. | Nos. | 40 | 740 | 66.6 | 66.6 | 873.2 | 34928
15 | Detailed survey- For ascertaining feasible route,identifying the under ground utilities by making ground penetration method survey,identifying the utilities over the ground, preparation of the detailed marking on topo sheet , preparation of route alignment map, submission of profile and survey report and interaction with the utilities & Govt. bodies for obtaining necessary clearances for laying of cables. | kM | 8.894 | 23848.12 | 2146.3308 | 2146.3308 | 28140.7816 | 250284.1116 | Autonagar
| Total Part B | [6 empty] | 110458086.4006 |  |  |  | 78171558.3286
| TOTAL OF LINE -2A (Erection A+B) | [6 empty] | 236168100.203 |  |  |  | 202990894.4465

## Supply Bidanasi
ODISHA POWER TRANSMISSION CORPORATION LIMITED
|  |  |  | Name of the Work: Construction of 220 KV D/C line (Over Head length approx 13 Km & UG cabling length approx 1.135 Km. Total Line Length=14.135 RKms approximately) from existing 220/132/33KV GIS at Bidanasi. | [12 empty] | 1328351724
SCHEDULE-2A-SUPPLY (FOR TRANSMISSION LINE)
|  |  |  | Sl. No. | DESCRIPTION OF ITEMS(SCHEDULE-2A-LINE) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNITS | QUANTITY | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTER-STATE) | OGST @ 9% PER UNIT(INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY | Remarks
SAP CODE | SAP DESCRIPTION |  | price
4.26
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | 52.83
1000000012 | 245 kV, 1C X 1000 Sq. mm, Cu cable | 8.1 | 20846700 | 1 | 220 KV GRADE Single CORE, 1000 SQ.MM.XLPE INSULATED COPPER CABLE AS PER TECHNICAL SPECIFICATION | km | 8.1 | 20846700 | 1876203 | 1876203 | 24599106 | 199252758.6 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project |  |  | 108 | 6.1329
3000004263 | HS IL type cable jt kit for 220 kV cable | 2 | 386906 | 2 | SUPPLY OF 220 KV XLPE CABLE STRAIGHT THROUGH JOINT KIT IN COMPLETE shape SUITABLE FOR 220 KV 1000 SQMM WITH LINK BOXES with and without SLV as per site requirements and technical specification. | Nos. | 2 | 386906 | 34821.54 | 34821.54 | 456549.08 | 913098.16 |  |  |  |  | 36
3000004264 | HS SB type cable jt kit for 220 kV cable | 1 | 386906 | 3 | Supply of Shield break type Straight through jointing kits Heat Shrink /cold shrink /premoulded type suitable for 220 kV, 1 Core, 1000 mm², copper UG Cable and Link box connection with Single Core Bonding cables as per approved bonding calculation.(Cross Bonded Joint:-30 Nos +Joints with Mid Points Bonding-6Nos.) | Nos. | 1 | 386906 | 34821.54 | 34821.54 | 456549.08 | 456549.08
3000004265 | OD cable to Oil filled 220kV term kit | 12 | 1086005.79 | 4 | 220KV Cable Termination kit outdoor type for 220KV volatege level suitable for 1C X 1000 Sq. mm copper cable including accessorries and all consumables. | Nos. | 12 | 1086005.79 | 97740.5211 | 97740.5211 | 1281486.8322 | 15377841.9864
1000000671 | 245 kV SM surge arrestor | 6 | 71489.05 | 5 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos. | 6 | 71489.05 | 6434.0145 | 6434.0145 | 84357.079 | 506142.474
1000000932 | 200 mm dia HDPE pipe PE 80-PN8 | 8.1 | 1470000 | 6 | Supply of High Density Polyethylene(HDPE) pipe 200mm dia PE 80- PN8 for laying of 220kV UG cable | kM | 8.1 | 1470000 | 132300 | 132300 | 1734600 | 14050260 | As per Technical sanction 406, dated. 01.02.2025 of ED, CZ, BBSR(Diversion of 220kV Paradeep- Essar Line)
3000004268 | 220kV 1 ph Link box without SVL | 6 | 21301.16 | 7 | Supply of 1 ph Link box without SVL with clamps and connectors with accessories for Terminal Connection | Nos. | 6 | 21301.16 | 1917.1044 | 1917.1044 | 25135.3688 | 150812.2128 | cost data 24-25
3000004267 | 220kV 1 ph Link box with SVL | 6 | 38675.29 | 8 | Supply of 1 ph Link box with SVL with clamps and connectors with acessories for terminal connector | Nos. | 6 | 38675.29 | 3480.7761 | 3480.7761 | 45636.8422 | 273821.0532 | cost data 24-25
1000000933 | 220kV 3ph Link box without SVL | 0 | 39181 | 9 | Supply of 3 ph Link box without SVL with clamps and connectors with acessories for mid point bonding | Nos. | 0 | 39181 | 3526.29 | 3526.29 | 46233.58 | 0 | Rate considered from CPC W.O- 250(14), 14.03.2024 (Samagara-Puri UG Cable)
3000004269 | 220kV 3ph Link box with SVL | 1 | 47140 | 10 | Supply of 3 ph Link box with SVL with clamps and connectors with acessories for Cross Bonding | Nos. | 1 | 47140 | 4242.6 | 4242.6 | 55625.2 | 55625.2
1000000934 | 400Sqmm XLPE bonding cable | 264 | 4217.43 | 11 | 400 Sq.MM Single core Bonding cable including connection/termination as required to make the system complete in all respect. (voltage Level to be determined by considering the fault level at seath) | MTR | 264 | 4217.43 | 379.5687 | 379.5687 | 4976.5674 | 1313813.7936 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL | Rate adopted proportionately @33% of 3171.00
3000000595 | 50 MM GI PORFORATED EARTHING PIPE | 1 | 14050 | 12 | Supply of Earthing materials 3 Mtr ,50mm ID Heavy gauge type pipe (with provision of with GI clamp fixtures welded allaround the pipe and connecting separately to main equipment for grounding (Single Electrode with accessories) with GI Flat 75x10mm siz | Nos. | 1 | 14050 | 1264.5 | 1264.5 | 16579 | 16579 | Rate considered from CPC W.O- 250(14), 14.03.2024 (Samagara-Puri UG Cable)
1000000331 | 48 F OPGW CABLE | 1.35 | 127089.72 | 13 | 48 Fibre Optic Approach Cable(DWSM) | KM | 1.35 | 127089.72 | 11438.0748 | 11438.0748 | 149965.8696 | 202453.924 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3000004096 | Hardware for 48 Fibre (DWSM) | 1.35 | 93762.74 | 13.1 | Installation hardware set((HDPE Duct,HDPE couplingetc) for 48 Fibre FOAC. | KM | 1.35 | 93762.74 | 8438.6466 | 8438.6466 | 110640.0332 | 149364.0448
3000003657 | 48 F OPGW SPLICING ENCLOSER | 2 | 6491 | 13.2 | Joint Box (Splice enclosure),48 Fibre | Nos | 2 | 6491 | 584.19 | 584.19 | 7659.38 | 15318.76
3000004081 | ST, PC & accessories for OFC connection | 6 | 5142 | 13.3 | Supply of straight through Connectors (Plastic Coupler) and acessories for OFC connection | Set | 6 | 5142 | 462.78 | 462.78 | 6067.56 | 36405.36 | Rate considered from CPC W.O- 250(14), 14.03.2024 (Samagara-Puri UG Cable)
3000004270 | OFC end connectors at GSS end | 2 | 7958 | 13.4 | Supply of end Connectors and acessories for OFC connection at GRID subststions | Set | 2 | 7958 | 716.22 | 716.22 | 9390.44 | 18780.88
|  | 0.5 | 153053 | 14 | GI Support for Cantiliver arrangement at Drain, Bridge etc. | Mt | 0.5 | 153053 | 13774.77 | 13774.77 | 180602.54 | 90301.27 |  | 232879925.7988 | 202990894.4464
|  | 0 | 0 | 1: 15; 2: SUPPLY of Following type tested Lattice type Galvanized steel tangent / Angle tower with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification.
|  | 23 | 0 | 2: OA TYPE TOWERS (Nominal unit weight 4.33 MT); 3: Nos.; 4: 23; 10: Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
|  | 11 | 0 | 2: +3 EXTENSION to OA type Towers (Nominal unit weight- 0.759 MT); 3: Nos.; 4: 11
|  | 6 | 0 | 2: +6 EXTENSION to OA type Towers (Nominal unit weight- 1.495 MT); 3: Nos.; 4: 6
|  | 3 | 0 | 2: OB TYPE TOWERS (Nominal unit weight 6.54 MT); 3: Nos.; 4: 3
|  | 3 | 0 | 2: +3 EXTENSION to OB type Towers (Nominal unit weight 1.334 MT); 3: Nos.; 4: 3
|  | 0 | 0 | 2: +6 EXTENSION to OB type Towers (Nominal unit weight- 2.308 MT); 3: Nos.; 4: 0
|  | 11 | 0 | 2: OC TYPE TOWERS (Nominal unit weight- 9.191 MT); 3: Nos.; 4: 11
|  | 1 | 0 | 2: +3 EXTENSION to OC type Towers (Nominal unit weight- 1.477 MT); 3: Nos.; 4: 1
|  | 7 | 0 | 2: +6 EXTENSION to OC type Towers (Nominal unit weight- 2.715 MT); 3: Nos.; 4: 7
|  | 2 | 0 | 2: +15 mtr Extension to OC type Tower (nominal Weight- 8.66 MT); 3: Nos.; 4: 2
|  | 0 | 0 | 2: +24 mtr Extension to OC type Tower (nominal Weight- 8.66 MT); 3: Nos.; 4: 0
|  | 1 | 0 | 2: Composite tower portion to OC ( nominal Weight-6.347; 3: Nos.; 4: 1
1000000140 | TOWER STRUCTURE (MS) | 300.328 | 90371.05 |  | TOTAL WEIGHT OF THE STRUCTURES INCLUDING TOWER STUB | MT | 300.328 | 90371.05 | 8133.3945 | 8133.3945 | 106637.839 | 32026328.9112
|  | 0 | 0 | 2: STUBS; 10: Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
|  | 11 | 0 | 2: OA type (Nominal unit weight 0.233MT); 3: Nos.; 4: 11
|  | 3 | 0 | 2: OB type (Nominal unit weight 0.438MT); 3: Nos.; 4: 3
|  | 11 | 0 | 2: OC type (Nominal unit weight 0.776MT); 3: Nos.; 4: 11
|  | 2 | 0 | 2: OC +15 Extension to OC type (Nominal unit weight 1.067MT); 3: Nos.; 4: 2
Stub w t added to structure |  | 14.547 | 0 | 2: TOTAL WEIGHT OF THE TOWER STUB; 3: MT; 4: 14.547
|  | 0 | 0 | 2: MS Enamel Painted TEMPLATES
|  | 1 | 0 | 2: OA (Nominal unit weight- 0.579 MT); 3: Nos.; 4: 1
|  | 1 | 0 | 2: OB (Nominal unit weight- 0.794 MT); 3: Nos.; 4: 1
|  | 1 | 0 | 2: OC (Nominal unit weight- 1.006 MT); 3: Nos.; 4: 1
|  | 1 | 0 | 2: OC+15/24(Nominal unit weight- 2.073 MT); 3: Nos.; 4: 1
3000003442 | MS enamel painted Templates | 4.452 | 69832.18 | 15.8 | TOTAL WEIGHT OF THE TEMPLATES | MT | 4.452 | 69832.18 | 6284.8962 | 6284.8962 | 82401.9724 | 366853.5811
3000004093 | G.I. nuts & bolts | 15.239 | 118560.66 | 15.9 | Weight of different type G.I Nuts and Bolts | MT | 15.239 | 118560.66 | 10670.4594 | 10670.4594 | 139901.5788 | 2131960.1593
|  | 0 | 0 | 1: 16; 2: Supply of the following tower accessories as per technical specification and as directed by the engineer in charge.
3000000574 | EARTHING DEVICE | 49 | 2280.98 | 16.1 | EARTHING DEVICE | Nos | 49 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 131886.2636 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3000003561 | DANGER BOARD | 47 | 236.77 | 16.2 | DANGER BOARD | Nos | 47 | 236.77 | 21.3093 | 21.3093 | 279.3886 | 13131.2642
3000003578 | TOWER NUMBER PLATE | 47 | 129.38 | 16.3 | NUMBER PLATE | Nos | 47 | 129.38 | 11.6442 | 11.6442 | 152.6684 | 7175.4148
3000003579 | TOWER PHASE PLATE | 282 | 100.92 | 16.4 | PHASE PLATE | Nos | 282 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 33582.1392
3000003555 | ANTICLIMBING DEVICE | 47 | 4400.23 | 16.5 | ANTICLIMBING DEVICE | Nos | 47 | 4400.23 | 396.0207 | 396.0207 | 5192.2714 | 244036.7558
3000003558 | TOWER CIRCUIT PLATE | 94 | 100.92 | 16.6 | CIRCUIT PLATE | Nos | 94 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 11194.0464
|  | 0 | 0 | 1: 17; 2: Supply of following POWER CONDUCTORS in the proposed 220kV lines as per the technical specification and as per the instruction of the engineer in charge.
1000000017 | ACSR ZEBRA CONDUCTOR | 85.26 | 363162.06 | 17.1 | ACSR ZEBRA CONDUCTOR | KM | 85.26 | 363162.06 | 32684.5854 | 32684.5854 | 428531.2308 | 36536572.738 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
|  | 0 | 0 | 1: 18; 2: POWER CONDUCTOR ACESSORIES
|  | 0 | 0 | 1: 18.1; 2: For ACSR Zebra
3000000456 | VD OF ACSR ZEBRA CONDUCTOR | 147 | 756.44 | 18.1.1 | VIBRATION DAMPER | Nos | 147 | 756.44 | 68.0796 | 68.0796 | 892.5992 | 131212.0824
3000000438 | MS JOINT FOR ACSR ZEBRA CONDUCTOR | 25 | 797.33 | 18.1.2 | MID SPAN JOINT | Set | 25 | 797.33 | 71.7597 | 71.7597 | 940.8494 | 23521.235
3000000466 | REPAIR SLEEVE FOR ACSR ZEBRA CONDUCTOR | 5 | 324.04 | 18.1.3 | REPAIR SLEEVE | Set | 5 | 324.04 | 29.1636 | 29.1636 | 382.3672 | 1911.836
|  | 0 | 0 | 1: 19; 2: Supply of the following insulators as per the technical specification and as per the instruction of the Engineer in charge.
3000000950 | 160KN 220 KV PORCELAIN LONG ROD INSULATO | 277.2 | 14593.68 | 19.1 | 160KN Porcelain Longrod Insulators String for 220KV | SET | 277.2 | 14593.68 | 1313.4312 | 1313.4312 | 17220.5424 | 4773534.3533 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3000004306 | 220 kV LR 120 kN porcelain insulator | 289.8 | 14593.68 | 19.2 | 120KN Porcelain Longrod Insulators String for 220KV | SET | 289.8 | 14593.68 | 1313.4312 | 1313.4312 | 17220.5424 | 4990513.1875
3000000953 | 90KN 220KV PORCELAIN LONG ROD | 15 | 11187.5 | 19.3 | 90KN Porcelain Longrod Insulators String for 220KV (For Pilot) | SET | 15 | 11187.5 | 1006.875 | 1006.875 | 13201.25 | 198018.75 | CD TL- 59
|  | 0 | 0 | 1: 20; 2: Supply of the following hard ware fittings suitable for ACSR Zebra conductors as per the technical specification.
|  | 0 | 0 | 1: 20.1; 2: For ACSR Zebra
3000000877 | ST Hard wares fittings 120KN insulator | 84 | 2698.67 | 20.1.1 | Single suspension Hard wares fittings suitable for 120 KN insulator. | Nos | 84 | 2698.67 | 242.8803 | 242.8803 | 3184.4306 | 267492.1704 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3000004183 | DS HWF FOR ACSR ZEBRA 120KN | 96 | 4566.27 | 20.1.2 | Double suspension Hard wares fittings suitable for 120 KN insulator. | Nos | 96 | 4566.27 | 410.9643 | 410.9643 | 5388.1986 | 517267.0656
3000004327 | ST HW fitting for 160 kN insulator | 60 | 2076.13 | 20.1.3 | Single tension Hard wares fittings suitable for 160 KN insulator. | Nos | 60 | 2076.13 | 186.8517 | 186.8517 | 2449.8334 | 146990.004
3000004328 | DT HW fitting for 160 kN insulator | 102 | 4735.96 | 20.1.4 | Double tension Hard wares fittings suitable for 160 KN insulator. | Nos | 102 | 4735.96 | 426.2364 | 426.2364 | 5588.4328 | 570020.1456
3000004184 | SS HWF FOR ACSR ZEBRA 90KN | 15 | 2698.67 | 20.1.5 | Single suspension Hard wares fittings suitable for 90KN insulator(Pilot) |  | 15 | 2698.67 | 242.8803 | 242.8803 | 3184.4306 | 47766.459 | CD TL- 15
4000000050 | D SHACKLE | 0 | 350 | 20.1.6 | “D” Shackle | Nos |  | 350 | 31.5 | 31.5 | 413 | 0 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3000003802 | U BOLT | 0 | 99.63 | 20.1.7 | U'-Bolt. | Nos |  | 99.63 | 8.9667 | 8.9667 | 117.5634 | 0
|  | 0 | 0 | 1: 21; 2: Supply of OPGW Fibre Optic Cable & Hard ware for Speech , data & protection
1000000331 | 48 F OPGW CABLE | 12.7 | 215500 | 21.1 | 48 fibre (DWSM) OPGW fibre optic cable. | Km | 12.7 | 215500 | 19395 | 19395 | 254290 | 3229483 | CD- TEL- 25
3000000820 | OPGW hardware set | 12.7 | 22597.72 | 21.2 | OPGW hardware set like suspension Assembly,Tensin Assembly(Dead end assembly, Pass through assembly) ,Vibration Damper,Down Lead Clamp Assemblies for 24/48 Fibre(DWSM) OPGW,Joint Box | KM | 12.7 | 22597.72 | 2033.7948 | 2033.7948 | 26665.3096 | 338649.4319 | CD- TEL- 26
3000003450 | Supply of FODP-48F | 1 | 54256.95 | 21.3 | Supply of FODP (fiber Optic Distribution Panel) 48F, Indoor type mounted with FCPC coupling and pigtails (DWSm fibre) | Nos. | 1 | 54256.95 | 4883.1255 | 4883.1255 | 64023.201 | 64023.201 | CD- TEL- 29 | 86803124.1954
[5 empty] | TOTAL OF LINE -2A (SUPPLY) | [6 empty] | 319683049.9942
555851150.1972
Note on H54: DILLIP: 1 earthing extra fro composite tower

## Erection- Bidanasi
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of the Work: Construction of 220 KV D/C line (Over Head length approx 13 Km & UG cabling length approx 1.135 Km. Total Line Length=14.135 RKms approximately) from existing 220/132/33KV GIS at Bidanasi.
SCHEDULE-2C-ERECTION & CIVILWORKS (FOR TRANSMISSION LINE)
Sl. No. | DESCRIPTION OF ITEMS(SCHEDULE-2C-LINE) ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENT/MATERIALS ALONG WITH CIVIL WORKS (As per Technical Specification) | UNIT | QUANTITY | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTER-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
PART-A | ELECTRICAL WORKS
1 | Laying , Comissioning & Testing of 220 kV, 1 Core,1-Run, 1000 mm² Copper, XLPE insulation UG Cable by HDD method with 200 mm dia PE 80- PN8, HDPE pipe for laying of individual run of UG cable at Main Road /Drain crossing / Railway Crossing/unaccessible place as per instruction of Engg in Charge. | Km. | 7.438 | 1820000 | 163800 | 163800 | 2147600 | 15973848.8 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project |  |  |  | 49.082
2 | Laying , Comissioning & Testing of 220 kV, 1 Core,3-Runs, 1000 mm² Copper, XLPE insulation UG Cable by open treanch method ( S/C, 3 Runs) in Direct buried or as per instruction of Engg in Charge | Km. | 0 | 127190 | 11447.1 | 11447.1 | 150084.2 | 0 | Autonagar
3 | Laying, Testing & Comissioning of 220 kV, 1 Core,3-Runs, 1000 mm² Copper, XLPE insulation UG Cable for Sneking,Bending, looping and raising at both the termination end | Km. | 0.162 | 572355 | 51511.95 | 51511.95 | 675378.9 | 109411.3818 | Autonagar
4 | Laying, Testing & Comissioning of of 220 kV, 1 Core,3-Runs, 1000 mm² Copper, XLPE insulation UG Cable along with HDPE pipe of 160 mm dia with Cantiliver support at drain crossing/Bridge Crossing [3nos cable to be laid per RKM]. | Km. | 0.5 | 254642.37 | 22917.8133 | 22917.8133 | 300477.9966 | 150238.9983 | Autonagar
5 | Erection OF 220 KV 1Cx1000 Sq Mm XLPE CABLE STRAIGHT THROUGH JOINT KIT COMPLETE SUITABLE FOR 220 KV 1000 SQMM WITH LINK BOXES. This also includes construction of temporary water proof tent shed for Cable Jointing Bay, including arrangement of all the necessary tools and plants, including Air Conditioner, temporary power supply etc. at the jointing bay site not limiting to the above and any other requirements for completion of the work as per specification. | Nos | 2 | 150000 | 13500 | 13500 | 177000 | 354000 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
6 | Erection of Shield break type Straight through jointing kits Heat Shrink /cold shrink /premoulded type suitable for 220 kV, 1 Core, 1000 mm², copper UG Cable and Link box connection with Single Core Bonding cables as per approved bonding calculation.(Cross Bonded Joint:-30 Nos +Joints with Mid Points Bonding-6Nos.) | Nos | 1 | 40064.85 | 3605.8365 | 3605.8365 | 47276.523 | 47276.523 | Autonagar
7 | Erection of 220 KV 1Cx1000 Sq Mm XLPE Cable end termination(s) kits on Cable Termination Tower Structure as per technical specification.This also includes construction of temporary water proof tent shed for Cable Jointing Bay, including arrangement of all the necessary tools and plants, including Air Conditioner, temporary power supply etc. at the termination bay site not limiting to the above and any other requirements for completion of the work as per specification. | Nos | 6 | 250000 | 22500 | 22500 | 295000 | 1770000 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
8 | Erection of 220KV Cable Termination kit outdoor type for 220KV voltage level suitable for 1C X 1000 Sq. mm copper cable including accessories and all consumables at Pahala GSS | Nos | 6 | 100000 | 9000 | 9000 | 118000 | 708000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
9 | Erection of 220 kV Surge arrestor with clamp & connectors on Cable Termination Tower Structure | Nos | 6 | 5203.87 | 468.3483 | 468.3483 | 6140.5666 | 36843.3996 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
10 | Erection of 1 ph Link box without SVL with clamps and connectors with acessories | Nos. | 6 | 2712 | 244.08 | 244.08 | 3200.16 | 19200.96 | RTSS Mancheswar
11 | Erection of 1 ph Link box with SVL with clamps and connectors with acessories | Nos. | 6 | 2712 | 244.08 | 244.08 | 3200.16 | 19200.96
12 | Erection of 3 ph Link box without SVL with clamps and connectors with acessories | Nos. | 0 | 2712 | 244.08 | 244.08 | 3200.16 | 0
13 | Erection of 3 ph Link box with SVL with clamps and connectors with acessories | Nos. | 1 | 2712 | 244.08 | 244.08 | 3200.16 | 3200.16
14 | 400 Sq.MM Single core Bonding cable including connection/termination as required to make the system complete in all respect. (voltage Level to be determined by considering the fault level at seath) | MTR | 264 | 80 | 7.2 | 7.2 | 94.4 | 24921.6 | Same as 300 Sq.mm
14 | Erection of Earthing materials 3 Mtr ,100mm ID Heavy gauge type pipe (with provision of GI clamp fixtures welded allaround the pipe and connecting separately to main equipment for grounding (Single Electrode with accessories) with GI Flat 75x10mm siz | Nos. | 40 | 8881 | 799.29 | 799.29 | 10479.58 | 419183.2 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
15 | Laying of 48 core fibre optic cables single mode, duct type, fibre armoured with duct pipe, laid along 220kV UG cable laying by open treanch method & HDD method .
15.1 | Laying of 48 core single mode fibre optic cables with HDPE PLB duct of size 32/26mm and connectors , laid along 220kV UG cable through open trench method. | Km. | 1.35 | 40370 | 3633.3 | 3633.3 | 47636.6 | 64309.41 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
15.2 | Laying of 48 Core single mode Fibre Optic Cables with Duct pipe of size 32/26mm and connectors through HDD method laid along 220kV UG Cable in main road crossing and Railway crossing. | Km. | 1.35 | 161480 | 14533.2 | 14533.2 | 190546.4 | 257237.64
15.3 | Erection of straight through Connectors (Plastic Coupler) and acessories for OFC connection | Nos. | 6 | 4709 | 423.81 | 423.81 | 5556.62 | 33339.72
15.4 | Erection of end Connectors and acessories for OFC connection at GRID subststions | Nos. | 2 | 4709 | 423.81 | 423.81 | 5556.62 | 11113.24
16 | Scalffolding at Composite tower for termination of UG Cable including man, materials, machinaries etc. | LOT | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | Market Rate |  | 20591325.9927
17 | ERECTION,TESTING & COMMISSIONING of Following tested Lattice type Galvanized steel tangent / Angle tower without stubs and cleats including different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete with tightening, punching of bolts including step bolts. All other left out portion of the bolts above bottom cross arm shall be riveted by using suitable hammer. Painting of black bituminous paints three coats shall be provided up to a height of 500mm above(for all the legs of the towers) the cooping legs & bracing members including head loading of tower materials T & P etc. All Erection should confirm to the Technical Specification laid there in the Tender Specification.
17.1 | OA TYPE TOWERS (Nominal unit weight 4.33 MT) | Nos. | 1
17.1.1 | +3 EXTENSION to OA type Towers (Nominal unit weight- 0.759 MT) | Nos. | 0
17.1.2 | +6 EXTENSION to OA type Towers (Nominal unit weight- 1.495 MT) | Nos. | 0
17.2 | OB TYPE TOWERS (Nominal unit weight 6.54 MT) | Nos. | 3
17.2.1 | +3 EXTENSION to OB type Towers (Nominal unit weight 1.334 MT) | Nos. | 0
17.2.2 | +6 EXTENSION to OB type Towers (Nominal unit weight- 2.308 MT) | Nos. | 2
17.3 | OC TYPE TOWERS (Nominal unit weight- 9.191 MT) | Nos. | 2
17.3.1 | +3 EXTENSION to OC type Towers (Nominal unit weight- 1.477 MT) | Nos. | 0
17.3.2 | +6 EXTENSION to OC type Towers (Nominal unit weight- 2.715 MT) | Nos. | 0
17.3.3 | +15 mtr Extension to OC type Tower (nominal Weight- 8.66 MT) | Nos. | 1
17.3.4 | +24 mtr Extension to OC type Tower (nominal Weight- 8.66 MT) | Nos. | 0
17.3.5 | Composite tower portion to OC ( nominal Weight-6.347 | Nos. | 1
17.4 | WEIGHT OF THE GI TOWER STRUCTURES Complete with tightening ,checking and punching of bolts including step bolts(Including Transportation from nearest OPTCL Store) | MT | 66.121 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 576287.1763 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
17.5 | Weight of different type G.I Nuts & Bolts and including different size of plain washer / spring washer for tower structure | MT | 3.5286 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 30754.4614
17.6 | STUB SETTING
17.6.1 | OA type (Nominal unit weight 0.233MT) | Nos. | 1
17.6.2 | OB type (Nominal unit weight 0.438MT) | Nos. | 3
17.6.3 | OC type (Nominal unit weight 0.776MT) | Nos. | 2
17.6.4 | OC +15 Extension to OC type (Nominal unit weight 1.067MT) | Nos. | 1
17.6.5 | OC +24 Extension to OC type (Nominal unit weight 1.067 MT) | Nos. | 0
17.7 | TOTAL WEIGHT OF THE TOWER STUB | MT | 4.166 | 5738.91 | 516.5019 | 516.5019 | 6771.9138 | 28211.7929 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
17.8 | TEMPLATES FITTING
17.8.1 | OA (Nominal unit weight- 0.579 MT) | Nos. | 1
17.8.2 | OB (Nominal unit weight- 0.794 MT) | Nos. | 3
17.8.3 | OC (Nominal unit weight- 1.006 MT) | Nos. | 2
17.8.4 | OC+15/24(Nominal unit weight- 2.073 MT) | Nos. | 1
17.9 | Fixing of of Stub Setting Templates and setting of Stub | MT | 4.45 | 5738.91 | 516.5019 | 516.5019 | 6771.9138 | 30135.0164 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
17.1 | Erection of the following tower accessories as per technical specification and as directed by the engineer in charge.
17.10.1 | EARTHING DEVICE | Nos. | 8 | 3071.77 | 276.4593 | 276.4593 | 3624.6886 | 28997.5088 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
17.10.2 | DANGER BOARD | Nos. | 7 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 1317.2222
17.10.3 | NUMBER PLATE | Nos. | 7 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 1317.2222
17.10.4 | PHASE PLATE | Nos. | 42 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 7903.3332
17.10.5 | ANTICLIMBING DEVICE | Nos. | 7 | 3441.28 | 309.7152 | 309.7152 | 4060.7104 | 28424.9728
17.10.6 | CIRCUIT PLATE | Nos. | 14 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 2634.4444
18 | Hoisting and fixing of insulators with required accessories etc , paying out of conductor ,jointing, stringing, sagging & Jumpering etc. of power conductor in the proposed lines and without earth wire with all required accessories including scaffolding for 33 KV,11 KV, LT , P&T lines, roads (SH & NH) and using own required T&P and compression jointing machines etc. with 1.5% provision for Sag & Wastage including head loading of stringing materials T & P etc. and as per the direction of Engineer in charge.
18.1 | Double Circuit (ACSR Zebra, Three Power Conductor with OPGW/Earthwire ) | RKM | 1.135 | 70504.02 | 6345.3618 | 6345.3618 | 83194.7436 | 94426.034 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
18.2 | Erection of OPGW wire with Hardware fittings and accessories like suspension Assembly,Tensin Assembly(Dead end assembly, Pass through assembly) ,Vibration Damper,Down Lead Clamp Assemblies for 24/48 Fibre(DWSM) OPGW,Joint Box | RKM | 1.135 | 45000 | 4050 | 4050 | 53100 | 60268.5 | Estimate Ramakrushnapur
| TOTAL of ELECTRICAL WORKS Part-I (A) | [6 empty] | 21482003.6773
PART B | CIVIL WORKS
Over Head Line
1 | Preliminary survey, Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | RKM | 12.7 | 14268.67 | 1284.1803 | 1284.1803 | 16837.0306 | 213830.2886 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
2 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | RKM | 12.7 | 6714.67 | 604.3203 | 604.3203 | 7923.3106 | 100626.0446 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
3 | Preparation of land schedule-with HAL & SAVIKclassification on revenue maps plot No, khata No, Mouza on revenue mapsindicating alignment therein duly authenticated by Revenue Inspector andTahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 220 KV line. Final route to be plotted on 1:50000 topo sheet for approval. | RKM | 12.7 | 10911.34 | 982.0206 | 982.0206 | 12875.3812 | 163517.3412 | RC TL 1.3
4 | Soil investigation per location (c)river bed pile foundation( boring to 30.0m depth) | Nos. | 18 | 75540.02 | 6798.6018 | 6798.6018 | 89137.2236 | 1604470.0248 | RC TL- Annex- I- 1.5-C
| Soil Testing in complete shape along with submission of report etc. up to the depth of 15.0 Mtrs. | Nos. | 11 | 38609.34 | 3474.8406 | 3474.8406 | 45559.0212 | 501149.2332 | TFL
5 | Excavation in all depths for following type of soil and rocks and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required.
5.1 | Soft/Loose soil | CUM | 1740 | 233.97 | 21.0573 | 21.0573 | 276.0846 | 480387.204 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
5.2 | Dense/Compact soil | CUM | 1160 | 366.54 | 32.9886 | 32.9886 | 432.5172 | 501719.952
5.3 | Partial Submerged soil | CUM | 1160 | 421.13 | 37.9017 | 37.9017 | 496.9334 | 576442.744
5.4 | Fully submerged soil | CUM | 1740 | 421.13 | 37.9017 | 37.9017 | 496.9334 | 864664.116
6 | FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge
6.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM | 150 | 6377.44 | 573.9696 | 573.9696 | 7525.3792 | 1128806.88 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project | 188.1
6.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1:2) of grade M25 for open cast foundation and UG cable Trench as per specification and approved drawings with supply of approved quality coarse aggregates(Nominal size 12mm to 20mm), fine aggregates, cement and steel of different size(as per design) with cutting, bending, binding of M.S.Rod (FE-500) including supply of binding wire in tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM | 627 | 10266.65 | 923.9985 | 923.9985 | 12114.647 | 7595883.669
6.3 | Cutting bending hooking ,fixing and binding in poisition of MS bars for rainforcement of foundation concrete of towers including supply of wire for binding (With supply of steel rod(TATA/RINL/SAIL Make). | MT | 8 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 604012.9248 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project | 31.35
7 | RIVER BED PILING: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making river bed pile by DMC method (Motor Driven) boring of piles foundations for river crossing locations with vertical boring of piles (pile bore as per required depth, basing on design) , preparation of cage, lowering and positioning (cutting,bending,binding/welding of M.S.Rod including supply of binding wire/way of welding) of the required above mentioned Tower foundation as indicated above and as per requirement, including supply of all materials,labours, de-watering, proper curing of the foundations and T&P as per specification and instruction of Engineer in charge in the RCC : 1:1:2 (Grade M-25.) including stabilization of bore :- Pile diameter (1000 MM).
7.1 | Pile foundation without under reemed boring 1000mm dia | Mtrs. | 1224 | 4464.21 | 401.7789 | 401.7789 | 5267.7678 | 6447747.7872 | RC TL- Annex- I- 7.2-vii | 62.5 | 7 | 437.5
7.2 | RCC M-25 (1:1:2) (Excluding Steel) With cement and without rod | CUM | 1026 | 10266.65 | 923.9985 | 923.9985 | 12114.647 | 12429627.822 | RC TL- Annex- I- 6.7-i
7.3 | Supply of Steel of different size (as per design) with cutting, bending, welding and binding in position of M.S.Rod for reinfocement of foundation concrete of Piles(Under reem Pile) including supply of binding wire With supply of steel rod ( TATA/RINL/SAIL/JINDAL make) and head loading. | MT. | 81 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 6115630.8636 | RC TL- Annex- I- 6.5-i
7.4 | 1000 MM dia MS liners of required numbers each of 1mtr height made of 6mm thick MS plate(MS plate of SAIL / TISCO make only) including,supply,cutting,bending,rolling,welding,face cutting,driving,transportation,loading,unloading etc for different location in river bed piling work. | MT. | 126 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 9513203.5656 | RC TL- Annex- I- 7.6-i
8 | PILE RISER,CAPPING,PEDESTAL & TIE-BEAM CONCRETE WORKS
8.1 | Pile riser,cap,tie-beam with RCC: 1:1.5:3 (Grade M-20) for above river bed piling ,including supply of all materials like MS Rod(cutting,bending,binding of M.S.Rod including supply of binding wire),Cement, coarse and fine aggregates, shuttering and centering and temporary road on the river and supply of labours, de-watering, proper curing of the foundations /concrete and T&P in line with the Specification and as per direction of Engineer in Charge.
8.2 | Excavation in all type soil and rocks and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/murrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required. (i) Soft/Loose Soil. | CUM | 846 | 366.54 | 32.9886 | 32.9886 | 432.5172 | 365909.5512 | RC TL- Annex- I-2-ii
8.3 | Providing and laying ordinary plain/reinforced concrete work of grade M- 20 (1:1.5:3) with approved quality stone chips of normal size up to 20 mm in tower foundation and couping inclusive of cost of cement mixing by curring etc. and cost of all materials(Form Boxes and other consumables to be supplied by the contractor) conforming to relevant IS.With cement and without rod | CUM | 1692 | 9103.72 | 819.3348 | 819.3348 | 10742.3896 | 18176123.2032 | RC TL- Annex- I- 6.4-i
8.4 | Providing mud-matting before concreting of stubs with lean concrete including cost of agree gates,mixing, layig, curring etc(Form Boxes and other consumables to be supplied by the contractor) 1:3:6 mix with cement . | CUM | 45 | 6377.44 | 573.9696 | 573.9696 | 7525.3792 | 338642.064 | Rate as per Technical Sanction No.- 03/2026-27 , dated. 23.04.2026 of CGM(P)- I, OPTCL - For TFL Project
8.5 | Supply of Steel of different size (as per design ) with cutting, bending, welding,binding in position of M.S.Rod for reinfocement of foundation concrete of Pile Risers including supply of binding wire With supply of steel rod ( TATA/RINL/SAIL/JINDAL make only) and head loading. No other make steel shall be accepted. | MT. | 126 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 9513203.5656 | RC TL- Annex- I- 6.5-i
8.6 | SHORING & SHUTTERING- required in wet or special locations with supply of all materials,T&P and Labour. | Sq. Mtr. | 396 | 452.32 | 40.7088 | 40.7088 | 533.7376 | 211360.0896 | RC TL- Annex- I- 4
8.7 | DE-WATERING (i) With Supply of all T&P on Man Hr basis. | HP Hr | 180 | 272.95 | 24.5655 | 24.5655 | 322.081 | 57974.58 | RC TL- Annex- I- 4
8.8 | Pipe type earthing including cost of bentonate compound and good borrowed earth where necessary in accordance with IS:3043-1966 and with supply of all T&P and Laobur.Without cost of earthing pipe and G.I.Flat | No. | 47 | 3071.77 | 276.4593 | 276.4593 | 3624.6886 | 170360.3642
8.9 | Supply & painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping(both leg & bracing members) | Sq. Mtr. | 600 | 146.36 | 13.1724 | 13.1724 | 172.7048 | 103622.88 | RC TL- Annex- I- 17
8.10 | Welding (including supply of electrods and zinc rich paints with application after welding) Bolt and nut | No. | 16356 | 10.24 | 0.9216 | 0.9216 | 12.0832 | 197632.8192 | RC TL- Annex- I- 16.2-I
9 | RIGHT OF WAY COMPENSATION
9.1 | Per location for foundation and erection of tower including approach to the Location as per prevailing Guidelines and as decided by the District Adminstartion. The ROW Clearance/NOC documents duly signed by the Claimant shall be submitted to OPTCL. | Per Loc | 29 | 200000 | 18000 | 18000 | 236000 | 6844000 | Price taken from Lumsum amount on assumption bais.
9.2 | Per Kilometer for stringing including approach to the Locations as per prevailing Guidelines and as decided by the District Adminstartion.The ROW Clearance/NOC documents duly signed by the Claimant shall be submitted to OPTCL. | Per Km. | 12.7 | 200000 | 18000 | 18000 | 236000 | 2997200 | Price taken from Lumsum amount on assumption bais. |  | 87817749.5777
10 | Under Ground Cable
10.1 | CIVIL Works with supply of all materials like Cement, MS tor rod, Brick, Coarse & Fine Agregrates & Labour,T&P etc For RCC Slabs & Others (PART-B)
10.1.1 | Open trench (direct burried) for laying of 220 kV cables Width : 1000mm Depth : 1850mm
10.1.1.1 | Earth work excavation of soil- Trench Dimension : (1mtr w x 1.85mtr d) | Cum | 0 | 296 | 26.64 | 26.64 | 349.28 | 0 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
10.1.1.2 | Shifing of excavated soil to a lead distance of 10 Km | Cum | 0 | 370 | 33.3 | 33.3 | 436.6 | 0
10.1.1.3 | Filling with fine river sand after laying of Cable inside the trench | Cum | 0 | 1345 | 121.05 | 121.05 | 1587.1 | 0
10.1.1.4 | Back filling with excavated soils | Cum | 0 | 134 | 12.06 | 12.06 | 158.12 | 0
10.1.1.5 | Casting and erection of RCC partition slab with supply of cement, aggregates etc including supply of all labour, T & P etc but without cost of steel. The slab size shall be 950x450x50mm and the conctrete shall be of M20 grade. | Cum | 0 | 9103.72 | 819.3348 | 819.3348 | 10742.3896 | 0
10.1.1.6 | Supply of rod, bending ,cutting and binding for prefabricated RCC slabs | MT | 0 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 0
10.1.1.7 | Damage of Asphalt/Tar road & other utilities (1mtr width) Asphalt : 25 - 50 mm,Binder course : 50 - 100 mm, Base course : 100 - 300 mm Subgrade : 100 - 300 mm,Compacted Subgrade : 150 - 300 mm | kM | 0.6 | 336418 | 30277.62 | 30277.62 | 396973.24 | 238183.944
10.1.1.8 | Reconstructing of Asphalt/Tar road & other utilities to bring its origional shape after laying of cable in open trench (1mtr width) Asphalt : 25 - 50 mm,Binder course : 50 - 100 mm,Base course : 100 - 300 mm Subgrade : 100 - 300 mm,Compacted Subgrade : 150 - 300 mm | kM | 0.6 | 4037023 | 363332.07 | 363332.07 | 4763687.14 | 2858212.284
10.1.1.9 | Damage of Concrete road / Concrete Footpath & other utilities (1mtr width) | kM | 0.5 | 336418 | 30277.62 | 30277.62 | 396973.24 | 198486.62
10.1.1.10 | Reconstructing of Concrete road / Concrete Footpath & other utilities to bring its origional shape after laying of cable in open trench (1mtr width) | kM | 0.5 | 2691349 | 242221.41 | 242221.41 | 3175791.82 | 1587895.91
B | Other Civil Works
11 | Supply of all materials and Erection of 220KV Jointing Bays (2mtrx8Mtr) along trench for straght through joints with RCC protection slab of 150mm thick. With Civil materials like bricks ,cements,sand,Materials for temporary shed,Airconditioners etc | Nos | 3 | 161480 | 14533.2 | 14533.2 | 190546.4 | 571639.2
12 | Supply and erection of Route Marker along the Cable Routes at an interval of 30 Mtrs as per the drawing with civil works | Nos. | 45 | 1345 | 121.05 | 121.05 | 1587.1 | 71419.5
13 | Construction of RCC Foundation for 220kV Link Box including supply of all materials (cement, steel, aggregates, labolr, T & P etc.) | Nos. | 1 | 26913 | 2422.17 | 2422.17 | 31757.34 | 31757.34
14 | Making of earth chamber including excavation, soil treatment with Bentonite powder, supply of charcoal, etc with brick masonary (1:5), PCC (1:4:8) and with cast iron cover size of the pit 450mmX450mm X600 mm depth as per direction of Engineer in Charge. | Nos. | 2 | 740 | 66.6 | 66.6 | 873.2 | 1746.4
15 | Detailed survey- For ascertaining feasible route,identifying the under ground utilities by making ground penetration method survey,identifying the utilities over the ground, preparation of the detailed marking on topo sheet , preparation of route alignment map, submission of profile and survey report and interaction with the utilities & Govt. bodies for obtaining necessary clearances for laying of cables. | kM | 1.35 | 23848.12 | 2146.3308 | 2146.3308 | 28140.7816 | 37990.0552 | Autonagar
| Total Part B | [6 empty] | 93415080.8308 |  |  |  | 5597331.2532
| TOTAL OF LINE -2A (Erection A+B) | [6 empty] | 114897084.5081 |  |  |  | 26188657.2459

## BAY SUPPLY Balianta
|  |  |  | (SUPPLY BAY EXTENSION) |  |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
Constrcution of 02 nos. of 220kV GIS bay Extension work at existing 220/132/33kV GIS Balianta.
SAP CODE | SAP DESCRIPTION |  | UNIT | PART -I | DESCRIPTION OF ITEMS (SCHEDULE-VIIA-SS) | UNITS | Quantity | IN INR |  |  |  |  | Remarks
|  |  |  | SL. No. | SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) |  |  | BASIC PRICE PER UNIT (Taxable Value) IN INR | CGST @ 9% PER UNIT IN INR | OGST @ 9% PER UNIT IN INR | TOTAL PRICE PER UNIT IN INR | TOTAL PRICE for for the Quantity
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6= (5x9%) | 7= (5x9%) | 8= (5+6+7) | 9 | 10
|  |  |  | 1 | 245KV GIS EQUIPMENT as per latest IEC standard & type tested equipment as per technical specification, with open future proof & flexible system in line with IEC 61850 & IEC 62271-203. (Circuit breaker shall be C2 - M2 class as per IEC 62271-100). (Compatible with existing GIS)
1000000457 | 245 kV Line bay module | 2 | SET | 1.1 | 245kV, 3150A,50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T & P.T), SF6 gas insulated line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer,Line Potential Transformer (3 core), bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Stand alone Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct (inside the GIS room) & its termination arrangement,PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete line feeder bay module & its earthing arrangement with earthing strips of adequate size and SF6 gas Insulated Bus Duct inside GIS Hall alongwith associated Support structure arrangement as per the technical specification. | SET | 2 | 19782364.21 | 1780412.7789 | 1780412.7789 | 23343189.7678 | 46686379.5356 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000004010 | 245 kV GIS bus duct | 180 | M | 1.2 | 245kV, 3150A, 50 kA, 3 sec, single phase, SF6 gas Insulated Bus Duct outside GIS Hall alongwith associated Support structure arrangement bends, joints,accessories, & its earthing arrangement with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification etc. | Meter | 180 | 45894.639 | 4130.5175 | 4130.5175 | 54155.674 | 9748021.3236 | Technical Sanction Order no. - 82 , dated. 12.08.2025 of SGM(P) II, OPTCL
1000000461 | 245 kV SF6 to air bushing | 6 | SET | 1.3 | 245kV, 3150A, 50 kA SF6/Air BUSHING ( Bushing shall be of Polymer / composite insulator type and shall be seamless sheath of a silicone rubber compound. The hollow silicone composite insulators shall comply as per IEC 61462 and the relevant parts of IEC 62217. The design of the composite insulators shall be tested and verified according to IEC 61462 ) FOR CONNECTING GIS TO AIS along with support structure. | SET | 6 | 307694.8875 | 27692.5399 | 27692.5399 | 363079.9672 | 2178479.8035 | Technical Sanction Order no. - 82 , dated. 12.08.2025 of SGM(P) II, OPTCL
1000000585 | 245 kV 3 core IVT | 6 | SET | 3 | 245 KV, 3CORE, SINGLE PHASE Inductive VOLTAGE TRANSFORMER (AIS) | SET | 6 | 231909.18 | 20871.8262 | 20871.8262 | 273652.8324 | 1641916.9944 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  | 0 | NOS | 4 | 245 KV,2000A,50KA,ISOLATOR
1000000096 | 220KV SI WITH DB With ES OF 2000A | 2 |  | 4.1 | 245 KV,2000A,50KA,ISOLATOR (single Isolator with earth switch including post insulators)(for feeder) (AIS) | Sets | 2 | 378121.38 | 34030.9242 | 34030.9242 | 446183.2284 | 892366.4568 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000000945 | 220KV Bus Post Insulator | 0 | SET | 5 | 245 KV solid core Bus Post Insulators {AIS) | NOS | 0 | 20313.2278 | 1828.1905 | 1828.1905 | 23969.6088 | 0
1000000671 | 245 kV SM surge arrestor | 6 | NOS | 6 | 220 KV. METAL OXIDE SURGE ARRESTOR.10 K.A. class III | NOS | 6 | 70578.02 | 6352.0218 | 6352.0218 | 83282.0636 | 499692.3816 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  | 0 | NOS | 7 | BUS BAR & CIRCUIT MATERIALS
|  | 0 |  | 7.1 | Porcelain Long Rod INSULATOR
3000000950 | 160KN 220 KV PORCELAIN LONG ROD INSULATO | 6 |  | 7.1.1 | 160 KN Long rod Insulator for 220 KV tension purpose | NOS | 6 | 14593.68 | 1313.4312 | 1313.4312 | 17220.5424 | 103323.2544 | CD TL 60
3000000953 | 90KN 220KV PORCELAIN LONG ROD | 6 | NOS | 7.1.2 | 90 KN Long rod Insulator for 220 KV Suspension purpose | NOS | 6 | 11187.5 | 1006.875 | 1006.875 | 13201.25 | 79207.5 | CD TL 60
1000000018 | ACSR MOOSE CONDUCTOR | 1 | NOS | 7.1.3 | ACSR MOOSE CONDUCTOR ( Twin Moose ) | km | 1 | 409923 | 36893.07 | 36893.07 | 483709.14 | 483709.14 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  |  |  | 7.2 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | [6 empty] | 0
3000000879 | Single Tension H/W Fitting ACSR Moose | 6 |  | 7.2.1 | 220 KV Single Tension H/W fitting for single moose ACSR | NOS | 6 | 2823.38 | 254.1042 | 254.1042 | 3331.5884 | 19989.5304 | CD TL 9
3000000867 | CLAMP OF SS HWF FOR ACSR MOOSE | 6 | SET | 7.2.2 | 220 KV Single Suspension H/W fitting for single moose ACSR | Sets | 6 | 3465.33 | 311.8797 | 311.8797 | 4089.0894 | 24534.5364 | CD TL 7
3000004408 | Clamps,connectors & HW: 220 kV system | 1 | NOS | 7.3 | Clamps & connectors etc (inline with the arrangement of the conductor type, suitable for maximum load with respect to the connected Equipment) suitable for 220 KV: T- clamp for ACSR ZEBRA urn to ACSR MOOSE drop,BPI clamp suitable for ACSR Moose,Isolator pad clamp suitable for ACSR Moose conductor,3 bolted PG clamp suitable for ACSR Moose conductor,LA Clamp suitable for ACSR Moose, IVT Clamp suitable for ACSR Moose etc as required. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | Market Rate
|  | 0 | LOT | 8 | SUBSTATION EARTHING SYSTEMS | [6 empty] | 0
3000004033 | Earthing Conductor for Earth Mat: 75 x 10 mm GI Flat. | 2 |  | 8.1 | EARTHING CONDUCTOR FOR BURRIAL : 75X10 mm GI Flat for laying (spacing maximum 5m both way) | Mtrs | 2000 | 575 | 51.75 | 51.75 | 678.5 | 1357000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000004001 | Earthing Conductor for risers: 50 x 6 mm GI Flat | 1.5 | KM | 8.2 | EARTHING CONDUCTOR; 50X6 mm Gl Flat for Raiser from the burial earth mat to equipment, structure, building lightning protection etc) | Mtrs | 1500 | 231 | 20.79 | 20.79 | 272.58 | 408870
3000000592 | 50 mm Heavy Duty GI Perforated Pipes, 3 mtrs long for treated earth pit | 25 | MT | 8.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty Gl PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 25 | 3675.65 | 330.8085 | 330.8085 | 4337.267 | 108431.675
[5 empty] | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained & High Quality ISI mark PVC-U selfit Pipe, PVC elbow bend,PVC Tee etc suitable for under ground burrial (HARD CONDUIT INCLUDING of adequate tensile strength minimum 7kg/sqmm or better) as per TS. | [6 empty] | 0
3000004065 | G.I Cable Trays(size: 450x75x2500mm) | 150 |  | 9.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 150 | 638.14 | 57.4326 | 57.4326 | 753.0052 | 112950.78 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000004066 | G.I Cable Trays(size: 300x75x2500mm) | 150 | Mtrs | 9.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 150 | 478.61 | 43.0749 | 43.0749 | 564.7598 | 84713.97
3000004067 | G.I Cable Trays(size: 150x75x2500mm) | 250 | Mtrs | 9.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 250 | 319.07 | 28.7163 | 28.7163 | 376.5026 | 94125.65
3000003565 | Support G. I angle 50x50x6 mm for cable tray | 2 | Mtrs | 9.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 2 | 92260.97 | 8303.4873 | 8303.4873 | 108867.9446 | 217735.8892
|  |  |  | 9.5 | 250mm dia PVC Pipe | MTRS | 50 | 294.35 | 26.4915 | 26.4915 | 347.333 | 17366.65
1000000930 | 110mm dia PVC Pipe | 100 | Mtr. | 9.6 | 110mm dia PVCPipe | MTRS | 100 | 967.2966 | 87.0567 | 87.0567 | 1141.4099 | 114140.9945
3000004564 | PVC pipe bends for 250mm,110mm & 50mmDia | 1 | NOS | 9.7 | PVC pipe bends,Tee,Elbow etc suitable for 110mm dia as above | LS | 1 | 5000 | 450 | 450 | 5900 | 5900 | MR
|  |  |  | 10 | SUB STATION SWITCYARD HDG type Boxes (BMK,AC CONSOLE & OTHER MB) as per Tech Spec. | [6 empty] | 0
3000001310 | Console Box for Switchyard Lighting | 1 |  | 10.1 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 1 | 54087.06 | 4867.8354 | 4867.8354 | 63822.7308 | 63822.7308 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000000992 | CT/IVT/CVT CONSOLE BOX | 2 | NOS | 10.2 | IVT OUT DOOR CONSOLE BOXES | NOS | 2 | 44533.64 | 4008.0276 | 4008.0276 | 52549.6952 | 105099.3904
|  |  |  | 11 | SWITCH YARD STRUCTURES HDG TYPE ( INCLUDING FOUNDATION BOLTS) FOR 220/132/33 KV CLASS | [6 empty] | 0
|  |  |  | 11.1 | DIFFERENT TYPE OF LATICE TYPE COLUMNS WITH DETAILS & DIFFERENT TYPE OF BEAMS WITH DETAILS | [6 empty] | 0
|  |  |  | 11.1.1 | P1S TYPE COLUMN,- HEIGHT-21.5 MTRS,WEIGHT-4.464MT{2 Nos) | Nos | 2 |  |  |  | 0 | 0
|  |  |  | 11.1.2 | Q1 TYPE BEAM,-LENGTH-18 MTRS, WEIGHT-1.473MT (2 Nos) | Nos | 2 |  |  |  | 0 | 0
3000003445 | HDG MS SS equipment Structures | 11.874 | MT | 11.1.3 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 11.874 | 92260.97 | 8303.4873 | 8303.4873 | 108867.9446 | 1292697.9742 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  | 0 |  | 11.2 | DIFFERENT TYPE OF TUBULAR SUPPORT STRUCTURES HDG TYPE FOR ALL 220KV EQUIPMENT INCLUDING FOUNDATION BOLT - ITS NUTS, ITS WASHERS, ITS PLATE ETC )
|  | 2 |  | 11.2.1 | 245 KV Isolator (2*1.5) | set | 2
|  | 6 |  | 11.2.2 | 245 KV Surge Arrester (for Line feeders: Low level-6 Nos) (6*.35) | Nos | 6
|  | 6 |  | 11.2.3 | 245 KV IVT(6 *.35) | Nos | 6
|  | 0 |  | 11.2.4 | 245 KV Post Insulator | Nos | 0
|  | 7.2 |  | 11.2.5 | TOTAL WEIGHT OF TUBULAR SUPPORT STRUCTURE FOR ABOVE EQUIPMENT INCLUDING GI FOUNDATION BOLTS, ITS NUTS, WASHERS PLATE ETC | MT | 7.2 | 92260.97 | 8303.4873 | 8303.4873 | 108867.9446 | 783849.2011 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000004093 | G.I. nuts & bolts | 1 |  | 11.2.6 | Gl bolts ,Nuts, washers plainn & spring etc for the above structures | MT | 1 | 117049.77 | 10534.4793 | 10534.4793 | 138118.7286 | 138118.7286
|  | 0 | MT | 12 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES | [6 empty] | 0
|  | 0 |  | 12.1 | POWER CABLES,1.1KV,XLPE & PVC .ARMOURED, ALUMINIUM CONDUCTOR (As per Specification) including Power cable termination & other materials
3000004051 | 3.5CX35 Sq. mm. Al cable (XLPE) | 300 |  | 12.1.1 | 3.5 CX35 mm² PVC | MTRS | 300 | 145.63 | 13.1067 | 13.1067 | 171.8434 | 51553.02 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
|  | 0 |  | 12.2 | CONTROL CABLES,1.1 KV, PVC armoured Stranded Copper (As per specification) including control cable termination & other materials. | [6 empty] | 0
3000004056 | 4 CX 2.5 mm2 | 1000 | Mtrs | 12.2.1 | 4 CX 2.5 mm2 | MTRS | 1000 | 122.09 | 10.9881 | 10.9881 | 144.0662 | 144066.2 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
3000000108 | 2.5SQMM 5C CONTROL CABLE | 0.5 | KM | 12.2.2 | 5 CX 2.5 mm2 | MTRS | 800 | 122.09 | 10.9881 | 10.9881 | 144.0662 | 115252.96
3000004058 | 7CX 2.5 mm2 | 500 | MTR | 12.2.3 | 7CX 2.5 mm² | MTRS | 500 | 184.82 | 16.6338 | 16.6338 | 218.0876 | 109043.8
3000004059 | 10 CX 2.5 mm2 | 500 | MTR | 12.2.4 | 10 CX 2.5 mm2 | MTRS | 500 | 251.17 | 22.6053 | 22.6053 | 296.3806 | 148190.3
3000000111 | 12C X 2.5 Sqmm control cable | 1 | KM | 12.2.5 | 12 CX 2.5 mm2 | MTRS | 1000 | 251.17 | 22.6053 | 22.6053 | 296.3806 | 296380.6
3000004061 | 16 CX 2.5 mm2 | 200 | MTR | 12.2.6 | 16 CX 2.5 mm2 | MTRS | 200 | 382.1 | 34.389 | 34.389 | 450.878 | 90175.6
3000000113 | 19C X 2.5 Sqmm control cable | 1 | KM | 12.2.7 | 19 CX 2.5 mm2 | MTRS | 1000 | 443.11 | 39.8799 | 39.8799 | 522.8698 | 522869.8
|  | 0 | KM | 13 | FIRE FIGHTING SYSTEM(PORTABLE /TROLLEY/ WHEEL MOUNTED FIRE EXTINGUSHERS SETS FOR CONTROL ROOM, EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC (REFER TS-VOUIIA-SCOPE OF WORKAT SL NO. 15-ANNEXURE -1)
4000000087 | Foam 09 Litres Fire Extinguishers | 2 |  | 13.1 | FOAM TYPE-9 LTRS | NOS | 2 | 2000 | 180 | 180 | 2360 | 4720 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
4000000093 | DRY CHEMICAL POWDER - 22.5 KGS | 2 | NOS | 13.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22 5 KGS | NOS | 2 | 13000 | 1170 | 1170 | 15340 | 30680
4000000085 | CO2 TYPE 9 KG FIRE EXTINGUISHER | 4 | NOS | 13.3 | CO₂ - 9 KGS | NOS | 4 | 120000 | 10800 | 10800 | 141600 | 566400
4000000084 | CO2 TYPE 22.5 KG FIRE EXTINGUISHER | 2 | NOS | 13.4 | CO₂ (TROLLY MOUNTED)- 22.5 KGS | NOS | 2 | 25000 | 2250 | 2250 | 29500 | 59000
4000000207 | Foam FE 50 kg | 1 | NOS | 13.5 | 50 Litres Mechanical Foam type | NOS | 1 | 10000 | 900 | 900 | 11800 | 11800
4000000232 | Fire bucket with stand | 1 | NOS | 13.6 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND & ITS COVER ON THE TOP | SET | 1 | 5000 | 450 | 450 | 5900 | 5900
3000003561 | DANGER BOARD | 2 | SET | 13.7 | Supply of Danger Board | Nos. | 2 | 236.77 | 21.3093 | 21.3093 | 279.3886 | 558.7772 | CD TL 9
|  | 0 | NOS | 14 | 220 KV SIDE PROTECTION & OTHER PANELS
3000001290 | 220kv FP Relay panelDistance portection | 2 |  | 14.1 | FEEDER PROTECTION PANEL (MAIN-I , MAIN-II & BACK-UP PROTECTION WITH AUTO RECLOSURE DISTANCE PROTECTION with Bay control unit (BCU) with all other relays & component required for complete prtection,control etc as per TS and also suitable for substation automation system. | NOS | 2 | 2850000 | 256500 | 256500 | 3363000 | 6726000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
2000000246 | BEST QUALITY INSULATING MAT | 4 | NOS | 14.2 | BEST QUALITY & APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | NOS | 4 | 1960 | 176.4 | 176.4 | 2312.8 | 9251.2
|  |  | NOS |  | TOTAL OF PART-I _SCHEDULE VIIA_SUPPLY COMPONENT OF THE WORKS CONTRACT FOR SUBSTATION. | [6 empty] | 76272286.3477
Note on A30: PRASANTA: 3000004065
Note on A31: PRASANTA: 3000004066
Note on A32: PRASANTA:

## BAY Erection Balianta
(ERECTION BAY EXTENSION) |  |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
Construction of 02 nos. of 220kV GIS bay Extension work at existing 220/132/33kV GIS Balianta.
PART -I | DESCRIPTION OF ITEMS (BAY) | UNITS | Quantity | IN INR |  |  |  |  | Remarks
SL. No. | SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) |  |  | BASIC PRICE PER UNIT (Taxable Value) IN INR | CGST @ 9% PER UNIT IN INR | OGST @ 9% PER UNIT IN INR | TOTAL PRICE PER UNIT IN INR | TOTAL PRICE for for the Quantity
ELECTRICAL ERECTION WORKS (PART-A)
1 | 245KV GIS EQUIPMENT as per latest IEC standard & type tested equipment as per technical specification, with open future proof & flexible system in line with IEC 61850 & IEC 62271-203. (Circuit breaker shall be C2 - M2 class as per IEC 62271-100). (Compatible with existing GIS)
1 | 245kV, 3150A,50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T & P.T), SF6 gas insulated line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer,Line Potential Transformer (3 core), bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Stand alone Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct (inside the GIS room) & its termination arrangement,PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete line feeder bay module & its earthing arrangement with earthing strips of adequate size and SF6 gas Insulated Bus Duct inside GIS Hall alongwith associated Support structure arrangement as per the technical specification. | SET | 2 | 325000 | 29250 | 29250 | 383500 | 767000 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Park Project.
1.1 | 245kV, 3150A, 50 kA, 3 sec, single phase, SF6 gas Insulated Bus Duct outside GIS Hall alongwith associated Support structure arrangement bends, joints,accessories, & its earthing arrangement with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification etc. | Meter | 180 | 1150.87 | 103.5783 | 103.5783 | 1358.0266 | 244444.788 | Technical Sanction Order no. - 82 , dated. 12.08.2025 of SGM(P) II, OPTCL
1.2 | 245kV, 3150A, 50 kA SF6/Air BUSHING ( Bushing shall be of Polymer / composite insulator type and shall be seamless sheath of a silicone rubber compound. The hollow silicone composite insulators shall comply as per IEC 61462 and the relevant parts of IEC 62217. The design of the composite insulators shall be tested and verified according to IEC 61462 ) FOR CONNECTING GIS TO AIS along with support structure. | NOS | 6 | 12656.49 | 1139.0841 | 1139.0841 | 14934.6582 | 89607.9492
3 | 245 KV, 3CORE, SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER (AIS) | NOS | 6 | 12207.78 | 1098.7002 | 1098.7002 | 14405.1804 | 86431.0824 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
4 | 245 KV,2000A,50KA,ISOLATOR | [6 empty] | 0
4.1 | 245 KV,2000A,50KA,ISOLATOR (single Isolator with earth switch including post insulators)(for feeder) | Sets | 2 | 25786.48 | 2320.7832 | 2320.7832 | 30428.0464 | 60856.0928 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
4.2 | 245 KV solid core Bus Post Insulators {AIS) | NOS | 0 | 3042.8432 | 273.8559 | 273.8559 | 3590.555 | 0
5 | 220 KV. METAL OXIDE SURGE ARRESTOR.10 K.A. class III | NOS | 6 | 4047.57 | 364.2813 | 364.2813 | 4776.1326 | 28656.7956 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
6 | BUS BAR STRINGING/HOISTING OF INSULATORS/ERECTION OF HW FITTINGS CLAMPS & CONNECTORS: Supply of labour,T&P and other necessary arrangements for stringing of bus bar conductors, hoisting of single or double insulator strings, erection of Single or Double; Suspension/Tension Hard-wares Fittings, Erection of Clamp & connectors, as per requirements, Jumpers, connections to Equipments, testing, commissioning etc. as per the instruction of Engineer-in charge.
6.1 | Twin Conductor /Phase/Mtr. (ACSR Moose) | Mtrs | 1000 | 196.04 | 17.6436 | 17.6436 | 231.3272 | 231327.2 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
7 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | [6 empty] | 0
7.1 | Erection of all type of hardwares, Insulators,Clamps & connectors etc suitable for 220 KV: Tension & suspension insulators, Hardwares, T- clamp for ACSR ZEBRA urn to ACSR MOOSE drop,Isolator pad clamp suitable for ACSR Moose conductor,3 bolted PG clamp suitable for ACSR Moose conductor,LA Clamp suitable for ACSR Moose,CVT Clamp suitable for ACSR Moose etc as required. | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | MR
8 | SUBSTATION EARTHING SYSTEMS: Substation earth mat Design, engineering, supply(except the GI Flats, only erection) inclusive of corrosion protection measures,laying of earth mat conductors of Hot dip galvanised flats of size 75X10 mm to the approval of Engineer in charge, excavation, welding/jointing of ground conductors along with risers (a) upto Finished level from the mat size 75X10 mm & b) from the finished ground level to the top of the structure and equipment shall be with 75X10 or 50X6 mm GI Flats as per the standard practice, with back filling and good compaction,perforated 50 mm Heavy duty GI pipes for treated earth pits (with details of treatment as per IS). The spacing between the earth conductor not more than 5 mtrs(both way) and to be buried at depth of 700mm from the finished ground level. For provision of treated earth pit and refer the specification for designing(only bentonite soil shall be used for the treatment). Provision of water taps inside the switch yard areas and peripheral treated earth pit are required to be provided for watering the treated earth pits. The no. of treated are to be done as per the practice and as indicated in the drawing for different equipments. This is as per approved drawing and specification. Provision water taps to each pit (supply ,laying of different size PVC water pipe of ISI mark,other materials like bends,T joints,elbow,taps for control,Valves and main water pipe line from the water overhead tank etc
8.1 | EARTHING CONDUCTOR FOR BURRIAL : 75X10 mm GI Flat for laying (spacing maximum 5m both way) | Mtrs | 2000 | 85.77 | 7.7193 | 7.7193 | 101.2086 | 202417.2 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
8.2 | EARTHING CONDUCTOR; 50X6 mm Gl Flat for Raiser from the burial earth mat to equipment, structure, building lightning protection etc) | Mtrs | 1500 | 67.39 | 6.0651 | 6.0651 | 79.5202 | 119280.3
8.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty Gl PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 25 | 2327.91 | 209.5119 | 209.5119 | 2746.9338 | 68673.345
9 | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained & High Quality ISI mark PVC-U selfit Pipe, PVC elbow bend,PVC Tee etc suitable for under ground burrial (HARD CONDUIT INCLUDING of adequate tensile strength minimum 7kg/sqmm or better) as per TS.
9.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 150 | 35 | 3.15 | 3.15 | 41.3 | 6195 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
9.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 150 | 35 | 3.15 | 3.15 | 41.3 | 6195
9.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 250 | 35 | 3.15 | 3.15 | 41.3 | 10325
9.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 2 | 10000 | 900 | 900 | 11800 | 23600
9.4 | PVC pipe bends for 250mm,110mm & 50mm dia a | Lot | 1 | 3000 | 270 | 270 | 3540 | 3540 | LS
10 | SUB STATION SWITCYARD HDG type Boxes (BMK,AC CONSOLE & OTHER MB) as per Tech Spec.
10.1 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 2 | 5900 | 531 | 531 | 6962 | 13924 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
10.2 | CVT IVT OUT DOOR CONSOLE BOXES | NOS | 4 | 2037 | 183.33 | 183.33 | 2403.66 | 9614.64
11 | SWITCH YARD STRUCTURES HDG TYPE ( INCLUDING FOUNDATION BOLTS) FOR 220/132/33 KV CLASS
11.1 | DIFFERENT TYPE OF LATICE TYPE COLUMNS WITH DETAILS & DIFFERENT TYPE OF BEAMS WITH DETAILS
11.1.1 | P1S TYPE COLUMN,- HEIGHT-21.5 MTRS,WEIGHT-4.464MT{2 Nos) | Nos | 2
11.1.2 | Q1 TYPE BEAM,-LENGTH-18 MTRS, WEIGHT-1.473MT (2 Nos) | Nos | 2
11.1.3 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 11.874 | 4533.3 | 407.997 | 407.997 | 5349.294 | 63517.517 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
11.2 | DIFFERENT TYPE OF TUBULAR SUPPORT STRUCTURES HDG TYPE FOR ALL 220KV EQUIPMENT INCLUDING FOUNDATION BOLT - ITS NUTS, ITS WASHERS, ITS PLATE ETC )
11.2.1 | 245 KV Isolator (2*1.5) | set | 2
11.2.2 | 245 KV Surge Arrester (for Line feeders: Low level-6 Nos) (6*.35) | Nos | 6
11.2.3 | 245 KV CVT IVT (6 *.35) | Nos | 6
11.2.4 | 245 KV Post Insulator | Nos | 0
11.2.5 | TOTAL WEIGHT OF TUBULAR SUPPORT STRUCTURE FOR ABOVE EQUIPMENT INCLUDING GI FOUNDATION BOLTS, ITS NUTS, WASHERS PLATE ETC | MT | 7.2 | 4533.3 | 407.997 | 407.997 | 5349.294 | 38514.9168 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
11.2.6 | Gl bolts ,Nuts, washers plainn & spring etc for the above structures | MT | 1 | 4533.3 | 407.997 | 407.997 | 5349.294 | 5349.294
12 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES | [6 empty] | 0
12.1 | Laying of Power Cable including fixing of cable with terminal connections both at equipments and control panels with supply of and fixing of lugs, Ferrules, clamps, connectors, glands, fixing of cable trays, including supply of N&B, Link plates, Cable Markers, Plaster of Paris, M-Seal compounds etc for sealing purpose and all necessary arrangements, laying of Earthing Flats, earthing ,laying of Cable trench slabs and chequered plate etc for the cable trench,Cable scheduled and cable diagram to be prepared by the contractor. Note: Supply & fixing of Modular Multi-diameter flexible Cable sealing system consisting of frames, blocks and accessories to be installed wherever the electrical / control / communication cables over-ground enter or leave from control room building. Cable sealing to be done with Multi-diameter type flexible modular based sealing blocks of different sizes (refer the Vol-II Scope.)
12.1.1 | 3.5 CX35 mm² PVC | MTRS | 300 | 404.32 | 36.3888 | 36.3888 | 477.0976 | 143129.28 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
12.2 | Laying of Control Cable including fixing of cable with terminal connections both at equipments and control panels with supply of and fixing of lugs, Ferrules, clamps, connectors, glands, fixing of cable trays, including supply of N&B, Link plates, Cable Markers, Plaster of Paris, M-Seal compounds etc for sealing purpose and all necessary arrangements, laying of Earthing Flats, earthing ,laying of Cable trench slabs and chequered plate etc for the cable trench,Cable scheduled and cable diagram to be prepared by the contractor. Note: Supply & fixing of Modular Multi-diameter flexible Cable sealing system consisting of frames, blocks and accessories to be installed wherever the electrical / control / communication cables over-ground enter or leave from control room building. Cable sealing to be done with Multi-diameter type flexible modular based sealing blocks of different sizes (refer the Vol-II Scope.
12.2.1 | 4 CX 2.5 mm2 | MTRS | 1000 | 42.88 | 3.8592 | 3.8592 | 50.5984 | 50598.4 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
12.2.2 | 5 CX 2.5 mm2 | MTRS | 800 | 42.88 | 3.8592 | 3.8592 | 50.5984 | 40478.72
12.2.3 | 7CX 2.5 mm² | MTRS | 500 | 42.88 | 3.8592 | 3.8592 | 50.5984 | 25299.2
12.2.4 | 10 CX 2.5 mm2 | MTRS | 500 | 49 | 4.41 | 4.41 | 57.82 | 28910
12.2.5 | 12 CX 2.5 mm2 | MTRS | 1000 | 49 | 4.41 | 4.41 | 57.82 | 57820
12.2.6 | 16 CX 2.5 mm2 | MTRS | 200 | 49 | 4.41 | 4.41 | 57.82 | 11564
12.2.7 | 19 CX 2.5 mm2 | MTRS | 1000 | 61.27 | 5.5143 | 5.5143 | 72.2986 | 72298.6
13 | FIRE FIGHTING SYSTEM(PORTABLE /TROLLEY/ WHEEL MOUNTED FIRE EXTINGUSHERS SETS FOR CONTROL ROOM, EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC (REFER TS-VOUIIA-SCOPE OF WORKAT SL NO. 15-ANNEXURE -1)
13.1 | FOAM TYPE-9 LTRS | NOS | 2 | 146 | 13.14 | 13.14 | 172.28 | 344.56 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
13.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22 5 KGS | NOS | 2 | 336 | 30.24 | 30.24 | 396.48 | 792.96
13.3 | CO₂ - 9 KGS | NOS | 4 | 146 | 13.14 | 13.14 | 172.28 | 689.12
13.4 | CO₂ (TROLLY MOUNTED)- 22.5 KGS | NOS | 2 | 146 | 13.14 | 13.14 | 172.28 | 344.56
13.5 | 50 Litres Mechanical Foam type | NOS | 1 | 224 | 20.16 | 20.16 | 264.32 | 264.32
13.6 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND & ITS COVER ON THE TOP | SET | 1 | 224 | 20.16 | 20.16 | 264.32 | 264.32
13.7 | Supply of Danger Board | Nos. | 2 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 376.3492 | Autonagar
14 | 220 KV SIDE PROTECTION & OTHER PANELS | [6 empty] | 0
14.1 | FEEDER PROTECTION PANEL (MAIN-I , MAIN-II & BACK-UP PROTECTION WITH AUTO RECLOSURE DISTANCE PROTECTION with Bay control unit (BCU) with all other relays & component required for complete prtection,control etc as per TS and also suitable for substation automation system. | NOS | 2 | 24807.25 | 2232.6525 | 2232.6525 | 29272.555 | 58545.11 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
15 | BEST QUALITY & APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | NOS | 4 | 20 | 1.8 | 1.8 | 23.6 | 94.4
| TOTAL ELECTRICAL WORKS (PART-A) | [6 empty] | 2630284.02
CIVIL ERECTION WORKS (PART-B)
1 | Foundations : Design, engineering, supply of all labour, material (Cement-OPC-43 Grade,MS Rod(FE-500), coarse and fine aggregates(Sand and Metal Chips) etc) for construction of RCC ( 1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including soil investigation, excavation,concreting, shuttering, grouting, underpinning and back filling of foundations etc complete for the following switch yard gantry/ portal structures and equipment support & others as per the technical specification and approved drawings.(RCC RATIO 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge.
1.1 | EXCAVATION FOR PREPARATION OF FOUNDATION WORK FOR THE SWITCHYARD COLUMN,EQUIPMENT etc.:This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge.
1.1.1 | Normal Soil(SOFT/LOOSE) | Cum | 200 | 156.68 | 14.1012 | 14.1012 | 184.8824 | 36976.48 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
1.1.2 | Hard Soil | Cum | 300 | 248.08 | 22.3272 | 22.3272 | 292.7344 | 87820.32 |  | 54
1.1.3 | Soft Rock/Disintegrated rock (not requiring blasting) | Cum | 200 | 554.9 | 49.941 | 49.941 | 654.782 | 130956.4
1.1.4 | Hard Rock required blasting | Cum | 150 | 913.95 | 82.2555 | 82.2555 | 1078.461 | 161769.15
1.2 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 200 | 5237.8 | 471.402 | 471.402 | 6180.604 | 1236120.8
1.3 | Open cast foundation or piling as per the site requirement for the above column/equipment/marshalling box foundations with RCC: 1:1.5:3 (Grade M-20),including supply of Labour all materials like Cement, coarse and fine aggregates,shoring & shuttering,proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. | Cum | 300 | 7565.71 | 680.9139 | 680.9139 | 8927.5378 | 2678261.34
1.4 | MS Rod:cutting,bending,binding ,placing in position of M.S.Rod including supply of different size of MS rod & binding wire for foundation concreting including supply of labours and T&P in line with the Specification and as per direction of Engineer in Charge. | MT | 25 | 68623.36 | 6176.1024 | 6176.1024 | 80975.5648 | 2024389.12
2 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in cable trench as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing),including supply of Labour all materials like MS Rod,Cement, coarse and fine aggregates,shuttering,cutting,bending,binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Fly ash Brickwork with fly ash Fly ash Brick ,plastering (!:6 Ratio) & curing, wherever required including the supply of labour,material, cement, etc. (5) Fabrication & Fixing of MS Angle(G.I) for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the plate fixed on the trench wall for better rigidity. The plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. (6) Precast of RCC covers (1:1.5:3) and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (7) CABLE TRENCHES INSIDE THE CONTROL ROOM SHALL BE COVERED WITH M.S CHEQUERED PLATE(Duly painted as per instruction of Engg in charge) INCLUDING STANDARD SUPPORT STAND {HD Galvanised (M.S JOIST ,CHANNEL,ANGLE)}.
2.1 | Cable trench with covers
2.1.1 | Section 3-3 | Mtrs | 150 | 12019.23 | 1081.7307 | 1081.7307 | 14182.6914 | 2127403.71 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
2.1.2 | Section 4-4 | Mtrs | 100 | 7211.54 | 649.0386 | 649.0386 | 8509.6172 | 850961.72
3 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:3:6 (M10) using 20 mm nominal metal over a lair of good quality river sand of 25 mm and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. Provision of pockets for water perculation into the yard atleast in two meters (both way) appart eachother for the entire PCC area & the pocket shall be provided with 75mm hard PVC pipe having minimum length of 300mm completely burried in the ground. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth from the Switch yard area. As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. | CUM | 150 | 5145.91 | 463.1319 | 463.1319 | 6072.1738 | 910826.07 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
4 | Metal Spreading: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size metals consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:3:6). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 200 | 2867 | 258.03 | 258.03 | 3383.06 | 676612
5 | CONTOUR SURVEY,AND LEVELING, BACK FILLING
5.1 | Contour survey of the entire sub-station area including Supply of all labour & T&P by contractor. | SQM | 2000 | 4.57 | 0.4113 | 0.4113 | 5.3926 | 10785.2 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
6 | COLOUR CODING, BAY MARKING Etc:Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof sticker may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. MS sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Lot | 1 | 30000 | 2700 | 2700 | 35400 | 35400 | LS |  | 81
7 | Anti-Weed Treatment
7.1 | Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treat of the switch-yard areas,controlroom etc. as per the instruction of Engineer-in-Charge.The chemical to be sprayed as per the standard practice adopted for antiweed treatment of sub-station area & as per the technical specification. | Sq Mtrs | 2000 | 17.84 | 1.6056 | 1.6056 | 21.0512 | 42102.4 | Rate as per Technical Sanction No.- 62/2024-25 , dated. 25.10.2024 of ED, CZ BBSR- For Aluminium Project
| TOTAL(PART-B) | [6 empty] | 11010384.71
| TOTAL (PART A+B) | [6 empty] | 13640668.73

## Bidanasi Bay Supply_SC
Supply of Materials and Equipments for Construction of Two nos. of 220kV AIS Bay Extension at Bidanasi Grid Sub-station
PART -I | DESCRIPTION OF ITEMS | UNITS | TOTAL SCOPE |  |  |  | GST |  | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE TENDER QUANTITY | Remarks
SL. No. | SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) |  | Quantity | BASIC PRICE PER UNIT (Taxable Value) In Rs | % variation in PV (IEEMA) | BASIC PRICE PER UNIT inclusive of PV (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8= (7x9%) | 9= (7x9%) | 10= (7+8+9) | 11= (10x4) | 12
SUPPLY
1 | 245 kV,1200-600-300 A,50 KA,5Core Single Phase Current Transformer (4nos. PS class & 1 No. 0.2 Cl;ass)With Clamps & Connectors | Nos. | 6 | 382298.97 | 4.37% | 399005.435 | 35910.4891 | 35910.4891 | 470826.4133 | 2824958.4797 | COST DATA 2024-25
2 | 245 KV,2000A,50KA,ISOLATORS (with support insulators and clamps & connectors) |  |  |  |  | 0 | 0 | 0 | 0
2.1 | 245KV Single Isolator without Earth switch | Set | 2 | 596680.16 | 0% | 596680.16 | 53701.2144 | 53701.2144 | 704082.5888 | 1408165.1776 | COST DATA 2024-25
2.2 | 245KV Single Isolator with Earth switch (1 no each at both Grid end) | Set | 2 | 775865.96 | 0% | 775865.96 | 69827.9364 | 69827.9364 | 915521.8328 | 1831043.6656 |  | Qty of SI with ES at Chandaka B shall be -1 | 1
2.3 | 245KV Tandem Isolator without Earth switch | Nos | 0 | 633063.08 | 0% | 633063.08 | 56975.6772 | 56975.6772 | 747014.4344 | 0
3 | 245KV, 3 Core, Single Phase Inductive Volatage Transformer (2 core 3P class & 1 core 0.2 class) (AIS) (1 no each at both Grid end | Nos | 6 | 379430 | 4.37% | 396011.091 | 35640.9982 | 35640.9982 | 467293.0874 | 2803758.5243 | COST DATA 2024-25 | At Chandaka B side: GIS-indoor termination- 220KV cable- ourdoor termination kit- 220KV Single Isolator with ES-220KV IVT-220KV LA- 220KV outdoor termination kit-220KV Cable to Mendhasal The equipment lisetd here may be included in the BOQ. | 3
4 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS (1 no each at both Grid end | Nos | 6 | 71489.05 | 10.76% | 79181.2718 | 7126.3145 | 7126.3145 | 93433.9007 | 560603.4042 |  |  | 3
5 | 245KV, 1 phase solid core Bus Post Insulator (8 kN) (AIS) as per Technical Specification. | Nos | 10 | 20931.02 | 0% | 20931.02 | 1883.7918 | 1883.7918 | 24698.6036 | 246986.036
6 | 245KV, 3150A, 50KA, SF6 Circuit Braker with supporting Structure. Facilities for integration with SAS as per the site requirement. | SET | 2 | 1365681.73 | 7.47% | 1467698.1552 | 132092.834 | 132092.834 | 1731883.8232 | 3463767.6463 | COST DATA 2024-25
8 | BUS BAR & CIRCUIT MATERIALS
8.1 | TENSION & SUSPENSION ANTI FOG TYPE INSULATOR STRING | [10 empty] | The main bus shall be twin ACSR moose. Accordingly the hardware fittings and insulator strings for 220KV shall be included
7.1.1 | 160 kN Porcelain Long Rod INSULATOR for Single Moose cond(TENSION)-220 KV | Strings | 36 | 14593.68 |  | 14593.68 | 1313.4312 | 1313.4312 | 17220.5424 | 619939.5264
7.1.2 | 90 kN Porcelain Long Rod INSULATOR for Single Moose cond (SUSPENSION)-220 KV | Strings | 6 | 11187.5 |  | 11187.5 | 1006.875 | 1006.875 | 13201.25 | 79207.5
8.2 | ACSR MOOSE CONDUCTOR | Km. | 3 | 446927.69 | 13.07% | 505341.1391 | 45480.7025 | 45480.7025 | 596302.5441 | 1788907.6324 | cost data
8.3 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS
7.3.1 | 220kV Single Tension Hardware fitting for single moose ACSR | Nos. | 12 | 4814.14 |  | 4814.14 | 433.2726 | 433.2726 | 5680.6852 | 68168.2224
7.3.2 | 220kV Single Suspension Hardware fitting for single moose ACSR | Nos. | 6 | 1080.21 |  | 1080.21 | 97.2189 | 97.2189 | 1274.6478 | 7647.8868
7.3.3 | 220kV Double Tension Hardware fitting for Twin moose ACSR | Nos. | 12 | 12752.61 |  | 12752.61 | 1147.7349 | 1147.7349 | 15048.0798 | 180576.9576
7.3.4 | 220kV Double Suspension Hardware fitting for Twin moose ACSR | Nos. | 0 | 2849.06 |  | 2849.06 | 256.4154 | 256.4154 | 3361.8908 | 0
7.3.5.1 | Clamp for Post Insulator (Twin Moose) | Set | 1 |  |  | 0 | 0 | 0 | 0 | 0 | Rate considered from CPC W.O- 785, 23.11.2022
7.3.5.2 | Clamp for Post Insulator (Single Moose) | Set | 1 |  |  | 0 | 0 | 0 | 0 | 0
7.3.5.3 | Spacer Clamps for Twin Moose | Set | 20 |  |  | 0 | 0 | 0 | 0 | 0
7.3.5.4 | PG clamp for Moose | Lot | 1 |  |  | 0 | 0 | 0 | 0 | 0
7.3.5.5 | PG clamp for Twin Moose | Lot | 1 |  |  | 0 | 0 | 0 | 0 | 0
7.3.5.6 | T clamp for Moose | Lot | 1 |  |  | 0 | 0 | 0 | 0 | 0
7.3.5.7 | Flexible Copper Bond & other required accessories | Lot | 2 |  |  | 0 | 0 | 0 | 0 | 0
8.3.1 | Compression Type Clamps & Connectors etc: There shall be conductor grip of atleast 100mm. The pad clamps shall be atleast 100x100x10mm with hole spacing of 50mm). This includes all types of clamps and connectors required to complete the work, (confirming with IS 5561:2108 with amendements and revisions and other applicable standards) as per approved drawing and direction of engineer in charge. (for both Mendhasal & Chandaka-B) | Lot | 1 | 300000 | 0% | 300000 | 27000 | 27000 | 354000 | 354000 | Rate considered from RTSS Champapur
9 | Supply of Danger Board | Nos. | 8 | 236.77 | 0% | 236.77 | 21.3093 | 21.3093 | 279.3886 | 2235.1088 | cost data
10 | SUBSTATION EARTHING SYSTEMS |  |  |  |  | 0 | 0 | 0 | 0
10.1.1 | EARTHING CONDUCTOR FOR BURRIAL : 75X10 mm GI Flat for laying (spacing maximum 5m both way) and for Raiser from the burial earth mat to equipment, structure etc upto the finished level) (for both Mendhasal & Chandaka-B) | Mtr | 2000 | 611 | 0% | 611 | 54.99 | 54.99 | 720.98 | 1441960 | Rate considered from CPC W.O- 250(14), 14.03.2024( UG Puri Samagara)
10.1.2 | EARTHING CONDUCTOR: 50x6 mm GI Flat for Raiser from the finished level to equipment,structure etc)(for both Mendhasal & Chandaka-B) | Mtr | 800 | 326 | 0% | 326 | 29.34 | 29.34 | 384.68 | 307744
10.1.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long treated earth pit)(for both Mendhasal & Chandaka-B) | Nos. | 40 | 5399 | 0% | 5399 | 485.91 | 485.91 | 6370.82 | 254832.8
11 | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained & High Quality ISI mark PVC-U selfit Pipe, PVC elbow bend,PVC Tee etc suitable for under ground burrial (HARD CONDUIT INCLUDING of adequate tensile strength minimum 7kg/sqmm or better) as per TS. |  |  |  |  | 0 | 0 | 0 | 0
11.1 | complete Section:3-3 | Mtr | 300 | 1007.23 | 0% | 1007.23 | 90.6507 | 90.6507 | 1188.5314 | 356559.42 | Package CPC- 08/2024-26
11.2 | complete Section:4-4 | Mtr | 400 | 678.24 | 0% | 678.24 | 61.0416 | 61.0416 | 800.3232 | 320129.28
11.3 | Support G. I angle 50x50x6 mm for cable tray | MT | 1 | 107556.27 | 0% | 107556.27 | 9680.0643 | 9680.0643 | 126916.3986 | 126916.3986
11.4 | 110mm dia PVCPipe | Mtr | 50 | 294.35 | 0% | 294.35 | 26.4915 | 26.4915 | 347.333 | 17366.65
11.5 | PVC pipe bends,Tee,Elbow etc suitable for 110mm dia as above | Lot | 2 | 4912.26 | 0% | 4912.26 | 442.1034 | 442.1034 | 5796.4668 | 11592.9336
12 | SUB STATION SWITCHYARD BMK, AC CONSOLE & OTHER MARSHALLING BOXES |  |  |  |  | 0 | 0 | 0 | 0
12.1 | BAY MARSHALLING KIOSK | Nos. | 1 | 150362.04 | 0% | 150362.04 | 13532.5836 | 13532.5836 | 177427.2072 | 177427.2072 | Cost data 24-25
12.2 | SWITCHYARD AC CONSOLE FOR LIGHTING | Nos. | 1 | 47997 | 0% | 47997 | 4319.73 | 4319.73 | 56636.46 | 56636.46 | Rate considered from CPC W.O- 250(14), 14.03.2024( UG Puri Samagara)
12.3 | CT & IVT Out Door Console Boxes (HDG type) each one no.(for both Mendhasal & Chandaka-B) | Nos. | 2 | 45108.48 | 0% | 45108.48 | 4059.7632 | 4059.7632 | 53228.0064 | 106456.0128 | Cost data 24-25 | CT & IVT Out Door Console Boxes (HDG type) each one no.
13 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220/132/33 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS. |  |  |  |  | 0 | 0 | 0 | 0
13.1 | DIFFERENT TYPES OF COLUMNS/ BEAMS WITH DETAILS |  |  |  |  | 0 | 0 | 0 | 0
13.1.1 | P1S - 220 KV(NOMINAL UNIT WT- 4.5 MT) | Set | 11 |  |  | 0 | 0 | 0 | 0 |  |  | Is there columns and beams available at Mendhasal? Column and beam qty is zero here? If new bay extension work is required, Columns & beam are required and accordingly the qty may be mentioned.
13.1.2 | Q1- 220 KV(NOMINAL UNIT WT- 1.5 MT) | Set | 4 |  |  | 0 | 0 | 0 | 0
13.1.3 | Q1X - 220 KV(NOMINAL UNIT WT- 1.95 MT) | Set | 2 |  |  | 0 | 0 | 0 | 0
13.1.4 | Q3 - 220 KV(NOMINAL UNIT WT- 2.5 MT) | Set | 4 |  |  | 0 | 0 | 0 | 0
13.1.5 | TOTAL WEIGHT OF COLUMN & BEAM INCLUDING FOUNDATION BOLTS | MT | 69.4 | 82451 | 0% | 82451 | 7420.59 | 7420.59 | 97292.18 | 6752077.292 | Cost data for structure 25-26
13.2 | SUPPORT STRUCTURES (LATTICE) FOR ALL 220 KV EQUIPMENT |  |  |  |  | 0 | 0 | 0 | 0
13.2.1 | ISOLATORS-220KV (Tandem = 1.5 MT, S/I = 1.5 MT, SI with Earth switch= 1.65MT) | Nos. | 4 |  |  | 0 | 0 | 0 | 0
13.2.2 | CT-220 KV (0.35 MT) | Nos. | 6 |  |  | 0 | 0 | 0 | 0
13.2.3 | IVT-220 KV (0.35 MT) | Nos. | 6 |  |  | 0 | 0 | 0 | 0 |  |  | Line IVTs are required on both sides of the cable. Qty 6
13.2.5 | Surge Arrester-220 kV (0.35 MT) | Nos. | 6 |  |  | 0 | 0 | 0 | 0 |  |  | Surge arresetres shall be 6
13.2.6 | BPI-220 KV (0.31 MT) | Nos. | 10 |  |  | 0 | 0 | 0 | 0
13.2.7 | TOTAL WEIGHT OF EQUIPMENT STRUCTURE (incl. beam mounting channels) | MT | 15.7 | 82451 | 0% | 82451 | 7420.59 | 7420.59 | 97292.18 | 1527487.226 | Cost data for structure 25-26
13.2.8 | Total weight of GI Nuts and bolts (incl. foundation bolts) for the above structures | MT | 3 | 102000 | 0% | 102000 | 9180 | 9180 | 120360 | 361080
14 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES |  |  |  |  | 0 | 0 | 0 | 0
14.1 | POWER CABLES,1.1KV, PVC ,ARMOURED, ALUMINIUM CONDUCTOR as per the sizes given above (As per Specification) |  |  |  |  | 0 | 0 | 0 | 0
14.1.1 | PVC 3.5C X 35 mm2 | Mtr | 1000 | 147.505 | 1.28% | 149.3931 | 13.4454 | 13.4454 | 176.2838 | 176283.8155 | Cost data 24-25
14.1.2 | PVC 4 CX 6 mm2 | Mtr | 1500 | 287 | 0.32% | 287.9184 | 25.9127 | 25.9127 | 339.7437 | 509615.568 | Rate considered from CPC W.O- 250(14), 14.03.2024( UG Puri Samagara)
14.1.3 | PVC 2CX 6 mm2 | Mtr | 1200 | 143 | 0.19% | 143.2717 | 12.8945 | 12.8945 | 169.0606 | 202872.7272
14.2 | CONTROL CABLES,1.1 KV, PVC, STRANDED COPPER, ARMOURED FRLS (As per specification) |  |  |  |  | 0 | 0 | 0 | 0
14.2.1 | 2 CX 2.5 mm2 | Mtr | 2000 | 78.41 | 1.25% | 79.3901 | 7.1451 | 7.1451 | 93.6803 | 187360.695 | Cost data 24-25
14.2.2 | 4 CX 2.5 mm2 | Mtr | 3000 | 123.67 | 2.53% | 126.7989 | 11.4119 | 11.4119 | 149.6226 | 448867.9325
14.2.3 | 7CX 2.5 mm2 | Mtr | 5000 | 187.201 | 1.11% | 189.2789 | 17.0351 | 17.0351 | 223.3491 | 1116745.6935
14.2.4 | 10 CX 2.5 mm2 | Mtr | 5000 | 254.413 | 1.59% | 258.4582 | 23.2612 | 23.2612 | 304.9806 | 1524903.1835
14.2.5 | 16 CX 2.5 mm2 | Mtr | 3000 | 387.03 | 5.12% | 406.8459 | 36.6161 | 36.6161 | 480.0782 | 1440234.6134
15 | PROTECTION, CONTROL & METERING PANEL AS PER TECH SPEC. |  |  |  |  | 0 | 0 | 0 | 0
15.1 | 220 KV SIDE |  |  |  |  | 0 | 0 | 0 | 0
15..1.1 | 220KV FEEDER PROTECTION PANEL: Line Differential Relay (Main-I & Main-II of different make) with auto reclosure, Numerical Backup Protection Relay, Bay control unit (BCU) with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Shall be compatible with the SAS at both the substations. | NOS | 2 | 2895582.64 | 0% | 2895582.64 | 260602.4376 | 260602.4376 | 3416787.5152 | 6833575.0304 | Cost data 24-25
16 | Insulating Mat: Best Quality & approved make (Confirming to IS:15652:2006) to be kept infront of all panels, boards etc.(2000X1000X3mm Size) | Nos. | 4 | 3599 | 0% | 3599 | 323.91 | 323.91 | 4246.82 | 16987.28 | Rate considered from CPC W.O- 250(14), 14.03.2024( UG Puri Samagara
40515677.9874

## Bidanasi Bay Erection_SC
Erection of Materials and Equipments for Construction of Two nos. of 220kV AIS Bay Extension at Bidanasi Grid Sub-station
PART -II | DESCRIPTION OF ITEMS |  |  |  | GST
SL. No. | ERECTION,TESTING & COMMISSIONING INCLUDING CIVIL WORKS OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) | UNITS | Quantity | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE TENDER QUANTITY | Remarks
1 | 2 | 3 | 4 | 5 | 6= (5x9%) | 7= (5x9%) | 8= (5+6+7) | 9= (8x4) | 10
PART-A | ELECTRICAL ERECTION WORKS: FOR 220 KV BAY EXTENSION FOR BAY EXTN. One no. at MENDHASAL Grid Sub-station & One no. at CHANDAKA Grid Sub-station (PART-A)
1 | 245 kV,1200-600-300 A,50 KA,5Core Single Phase Current Transformer (4nos. PS class & 1 No. 0.2 Cl;ass)With Clamps & Connectors | Nos. | 6 | 15695.55 | 1412.5995 | 1412.5995 | 18520.749 | 111124.494 | Latest RC Rate_04.10.2025
2 | 245 KV,2000A,50KA,ISOLATORS (with support insulators and clamps & connectors)
2.1 | 245KV Single Isolator without Earth switch | Set | 2 | 29880.28 | 2689.2252 | 2689.2252 | 35258.7304 | 70517.4608 | Latest RC Rate_04.10.2025 | 245KV Single Isolator without Earth switch | Nos | 2 | 23240.47
2.2 | 245KV Single Isolator with Earth switch | Set | 2 | 33153.68 | 2983.8312 | 2983.8312 | 39121.3424 | 78242.6848 |  | 245KV Single Isolator with Earth switch | Nos | 1 | 25786.48
2.3 | 245KV Tandem Isolator without Earth switch | Nos | 0 | 29880.28 | 2689.2252 | 2689.2252 | 35258.7304 | 0 |  | 245KV Tandem Isolator without Earth switch | Nos | 1 | 18279.02
3 | 245KV, 3 Core, Single Phase Inductive Volatage Transformer (2 core 3P class & 1 core 0.2 class) (AIS) | Nos. | 6 | 15695.55 | 1412.5995 | 1412.5995 | 18520.749 | 111124.494
4 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos. | 6 | 5203.87 | 468.3483 | 468.3483 | 6140.5666 | 36843.3996
5 | 245KV, 1 phase solid core Bus Post Insulator (8 kN) (AIS) as per Technical Specification. | Nos. | 10 | 2853.73 | 256.8357 | 256.8357 | 3367.4014 | 33674.014
6 | 245KV, 3150A, 50KA, SF6 Circuit Braker with supporting Structure. Facilities for integration with SAS as per the site requirement. | Nos. | 2 | 97698.43 | 8792.8587 | 8792.8587 | 115284.1474 | 230568.2948
8 | Jumpering to Equipments with supply of Labour and T & P, excluding supply of clamps, conductor & pipe etc.(For Both Chandaka B and Mendhasal GSS)
8.1 | ACSR Moose [Single] | Mtr. | 1000 | 134.3 | 12.087 | 12.087 | 158.474 | 158474 | Latest RC Rate_04.10.2025
8.2 | ACSR Moose (Twin) | Mtr. | 200 | 184.65 | 16.6185 | 16.6185 | 217.887 | 43577.4
8.3 | Danger Board | Nos. | 8 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 1505.3968
9 | SUBSTATION EARTHING SYSTEMS: Substation earth mat Design, engineering, supply(except the GI Flats, only erection) inclusive of corrosion protection measures,laying of earth mat conductors of Hot dip galvanised flats of size 75X10 mm to the approval of Engineer in charge, excavation, welding/jointing of ground conductors along with risers (a) upto Finished level from the mat size 75X10 mm & b) from the finished ground level to the top of the structure and equipment shall be with 75X10 or 50X6 mm GI Flats as per the standard practice, with back filling and good compaction,perforated 50 mm Heavy duty GI pipes for treated earth pits (with details of treatment as per IS). The spacing between the earth conductor not more than 5 mtrs(both way) and to be buried at depth of 700mm from the finished ground level. For provision of treated earth pit and refer the specification for designing(only bentonite soil shall be used for the treatment). | Mtr. | 2000 | 110.27 | 9.9243 | 9.9243 | 130.1186 | 260237.2 | Latest RC Rate_04.10.2025
9.1 | EARTHING CONDUCTOR; 50X6 mm Gl Flat for Raiser from the burial earth mat to equipment, structure, building lightning protection etc) | Mtr | 800 | 86.64 | 7.7976 | 7.7976 | 102.2352 | 81788.16 | Latest RC Rate_04.10.2025
9.2 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | Nos. | 40 | 3780.63 | 340.2567 | 340.2567 | 4461.1434 | 178445.736 | Latest RC Rate_04.10.2025
10 | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS suitable for different sections i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories & GI Pipe & bend as per TS.
10.1 | complete Section:3-3 | Mtr | 300 | 269 | 24.21 | 24.21 | 317.42 | 95226 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
10.2 | complete Section:4-4 | Mtr | 400 | 269 | 24.21 | 24.21 | 317.42 | 126968
10.3 | Support G. I angle 50x50x6 mm for cable tray | MT | 1 | 26913 | 2422.17 | 2422.17 | 31757.34 | 31757.34
10.4 | 110mm dia PVCPipe | Mtr | 50 | 148 | 13.32 | 13.32 | 174.64 | 8732
10.5 | PVC pipe bends,Tee,Elbow etc suitable for 110mm dia as above | Lot | 2 | 1345 | 121.05 | 121.05 | 1587.1 | 3174.2
11 | SUB STATION SWITCHYARD BMK, AC CONSOLE & OTHER MARSHALLING BOXES
11.1 | BAY MARSHALLING KIOSK | Nos. | 1 | 9904.14 | 891.3726 | 891.3726 | 11686.8852 | 11686.8852 | Latest RC Rate_04.10.2025
11.2 | SWITCHYARD AC CONSOLE FOR LIGHTING | Nos. | 1 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 3605.1006
11.3 | CT & CVT Out Door Console Boxes (HDG type) | Nos. | 2 | 3055.69 | 275.0121 | 275.0121 | 3605.7142 | 7211.4284
12 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220/132/33 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS.
12.1 | SUPPORT STRUCTURES (LATTICE) FOR ALL 220 KV EQUIPMENT
12.1.1 | ISOLATORS-220KV (Tandem = 1.5 MT, S/I = 1.5 MT, SI with Earth switch= 1.65MT) | Nos. | 4
12.1.2 | CT-220 KV (0.35 MT) | Nos. | 6
12.1.3 | IVT-220 KV (0.35 MT) | Nos. | 6
12.1.5 | Surge Arrester-220 kV (0.35 MT) | Nos. | 10
12.1.6 | BPI-220 KV (0.31 MT) | Nos. | 10
12.1.7 | TOTAL WEIGHT OF EQUIPMENT STRUCTURE (incl. beam mounting channels) | MT | 15.7 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 107978.2352 | Latest RC Rate_04.10.2025
12.1.8 | Total weight of GI Nuts and bolts (incl. foundation bolts) for the above structures | MT | 3 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 20632.7838
13 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
13.1 | Laying of Power Cable including fixing of cable with terminal connections both at equipments and control panels with supply of and fixing of lugs, Ferrules, clamps, connectors, glands, fixing of cable trays, including supply of N&B, Link plates, Cable Markers, Plaster of Paris, M-Seal compounds etc for sealing purpose and all necessary arrangements, laying of Earthing Flats, earthing ,laying of Cable trench slabs and chequered plate etc for the cable trench,Cable scheduled and cable diagram to be prepared by the contractor.
13.1.1 | PVC 3.5C X 35 mm2 | Mtr | 1000 | 519.83 | 46.7847 | 46.7847 | 613.3994 | 613399.4 | Latest RC Rate_04.10.2025
13.1.2 | PVC 4 CX 6 mm2 | Mtr | 1500 | 157.53 | 14.1777 | 14.1777 | 185.8854 | 278828.1
13.1.3 | PVC 2CX 6 mm2 | Mtr | 1200 | 157.53 | 14.1777 | 14.1777 | 185.8854 | 223062.48
13.2 | Laying of Control Cable including fixing of cable with terminal connections both at equipments and control panels with supply of and fixing of lugs, Ferrules, clamps, connectors, glands, fixing of cable trays, including supply of N&B, Link plates, Cable Markers, Plaster of Paris, M-Seal compounds etc for sealing purpose and all necessary arrangements, laying of Earthing Flats, earthing ,laying of Cable trench slabs and chequered plate etc for the cable trench,Cable scheduled and cable diagram to be prepared by the contractor.
13.2.1 | 2 CX 2.5 mm2 | Mtr | 2000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 130130.4 | Latest RC Rate_04.10.2025
13.2.2 | 4 CX 2.5 mm2 | Mtr | 3000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 195195.6
13.2.3 | 7CX 2.5 mm2 | Mtr | 5000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 325326
13.2.4 | 10 CX 2.5 mm2 | Mtr | 5000 | 63 | 5.67 | 5.67 | 74.34 | 371700
13.2.5 | 16 CX 2.5 mm2 | Mtr | 3000 | 63 | 5.67 | 5.67 | 74.34 | 223020
14 | PROTECTION, CONTROL & METERING PANEL AS PER TECH SPEC.
14.1 | 220 KV SIDE
14.1.1 | 220KV FEEDER PROTECTION PANEL: Line Differential Relay (Main-I & Main-II of different make) with auto reclosure, Numerical Backup Protection Relay, Bay control unit (BCU) with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Shall be compatible with the SAS at both the substations. | Set | 2 | 25180.01 | 2266.2009 | 2266.2009 | 29712.4118 | 59424.8236 | Latest RC Rate_04.10.2025
14.1.2 | Integration with existing SAS of Chandaka-B and Mendhasal Substations including supply of materials and accessories for successful and smooth operation and control. | Set | 2 | 50000 | 4500 | 4500 | 59000 | 118000 | RTSS Khamar
| TOTAL ELECTRICAL ERECTION WORKS (Part-A) | [6 empty] | 4351181.5116
PART-B | CIVIL WORKS: FOR 220 KV BAY EXTENSION FOR BAY EXTN. One no. at MENDHASAL Grid Sub-station & One no. at CHANDAKA Grid Sub-station
1 | CONTOUR SURVEY,AND LEVELING, BACK FILLING
1.1 | Contour survey and furnishing contour map including supply of all materials, Labour and T&P | SQ.MTRS. | 600 | 5.87 | 0.5283 | 0.5283 | 6.9266 | 4155.96 | Latest RC Rate_04.10.2025
1.2 | Soil investigation : Supply of labour,T&Pand other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge. | PER POINT | 2 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 67348.12 | Latest RC Rate_04.10.2025
2 | OPEN CAST & PILE FOUNDATIONS WORK FOR THE SWITCHYARD COLUMN,EQUIPMENT etc: Design, engineering, supply of all labour, T&P, material (Cement-As Per TS,MS Rod ( FE-500 as per BIS-1786), coarse and fine aggregates (Sand and Metal Chips) etc) for construction of RCC ( 1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including , excavation,concreting, shuttering, grouting, underpinning and back filling of foundations etc complete for the following switch yard gantry/ portal structures and equipment support & others as per the technical specification and approved drawings. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. (a) For Switch yard gantry/portal structure foundations (b) For 220 KV Equipment foundations. (c) For other equipment foundations such as Lighting cum lightning mast, LT distribution boards etc
2.1 | EXCAVATION FOR PREPARATION OF FOUNDATION WORK FOR THE SWITCHYARD COLUMN,EQUIPMENT etc.:This also includes excavation in all types of soil or rocks including shoring and shuttering,supply of T & P,labour etc. and back filling(back filling shall be done in layers of 500mm sprinking of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after backfilling) & if required for fillling the foundation,borrowed earth/morrum/sand shall be brought for filling and compaction,including supply of sand,all T & P, labour as required as per the instruction of Engineer In charge.
2.1.1 | Normal Soil(SOFT/LOOSE) | Cum | 250 | 187.17 | 16.8453 | 16.8453 | 220.8606 | 55215.15 | Latest RC Rate_04.10.2025
2.1.2 | Dense/Compact Soil | Cum | 900 | 296.35 | 26.6715 | 26.6715 | 349.693 | 314723.7
2.1.3 | Soft/Disintegrated Rock(not Requiring Blasting) | Cum | 500 | 662.88 | 59.6592 | 59.6592 | 782.1984 | 391099.2
2.1.4 | Hard Rock(Requiring Blasting/Using breaker machinery) | Cum | 700 | 1091.81 | 98.2629 | 98.2629 | 1288.3358 | 901835.06
2.2 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in for the column/equipment/marshalling box foundations as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 90 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 643419.07 | Latest RC Rate_04.10.2025
2.3 | Open cast foundation for the above column/equipment/marshalling box foundations with RCC: 1:1.5:3 (Grade M-20) ,including supply of Labour all materials like cement, coarse and fine aggregates,shuttering,proper curing of the foundations/concrete and T&P in line with the Techinical Specification and as per direction of Engineer in Charge. ( without cost of steel) | Cum | 280 | 8751.26 | 787.6134 | 787.6134 | 10326.4868 | 2891416.3 | Latest RC Rate_04.10.2025
2.4 | Supply of steel different sizes(TATA/RINL/SAIL make only). No other make of steel shall be allowed. As per the design with cutting, bending, binding and placing in position of steel rods for foundation concreting including cost of binding wire. | MT | 30 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 2265048.47 | Latest RC Rate_04.10.2025
3 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling and disposal of excess earth as per the direction of Engineer In charge.
(2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in cable trench as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge.
(3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing), including supply of Labour all materials like MS Rod, Cement, coarse and fine aggregates, shuttering, cutting, bending, binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Fly ash Brickwork with fly ash Brick, plastering (1:6 Ratio) & curing, wherever required including the supply of labour, material, cement, etc.
(5) The outdoor cable trench wall top surface shall be "L" shaped and the cover slabs shall be placed with in the"L shaped" surface of both the walls. The top surface of the trench shall be smooth finished. (6)Supply,fabrication & Fixing of GI Angle for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the GI insert plate fixed on the trench wall for better rigidity. The Insert plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting.
(7) Precast of RCC covers (1:1.5:3) with MS sheet(2mm) frame and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (8) All the RCC cover slabs shall have the lifting hooks. The slabs without the MS sheet frame and Lifting hooks shall not be accepted.
(8) Cable Trenches Inside The Control Room Shall Be Covered With M.S Chequered Plate(Duly Painted As Per Instruction Of Engg In Charge) Including Standard Support Stand {Hd Galvanised (M.S Joist , Channel, Angle). Stoppers shall be fixed at the underneath so that the chequered shall not be falling into the cable trench in any case.
3.1 | Section 3-3 | Mtrs | 300 | 12019.23 | 1081.7307 | 1081.7307 | 14182.6914 | 4254807.42 | RTSS Khamar
3.2 | Section 4-4 | Mtrs | 500 | 7211.54 | 649.0386 | 649.0386 | 8509.6172 | 4254808.6
4 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:4:8 (M7.5) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. (Switch yard area) | CUM | 300 | 5952.27 | 535.7043 | 535.7043 | 7023.6786 | 2107103.58 | Latest RC Rate_04.10.2025
5 | Metal Spreading: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:4:8). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 300 | 3316.26 | 298.4634 | 298.4634 | 3913.1868 | 1173956.04 | Latest RC Rate_04.10.2025
6 | Switch yard fencing: Providing and fixing of G.I Goat mesh (2.5 mm dia) fencing ( the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, State and Central Government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous Brick Masonry work with ratio mortar (cement and sand)1:5 and cement pointing of the joints, for the fencing upto a height of 350 mm from the finished ground level) .This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing shall be as per specification. The fencing shall be continuous i.e. a GI flat of 50 x 6mm shall run continuous at top & at bottom all along the fence. The fencing shall be connected to the earth mat every 3 mtrs. | Mtr | 200 | 3500 | 315 | 315 | 4130 | 826000 | RTSS Khamar
7 | Colour coding for R,Y,B phase,Bay Marking,Earth pit marking,BMK marking & Switchyard Lighting kiosk and CR panel marking | Lot | 2 | 95392.5 | 8585.325 | 8585.325 | 112563.15 | 225126.3 | RTSS Khamar
| TOTAL PRICE FOR CIVIL WORK COMPONENT OF THE WORKS CONTRACT FOR SUBSTATION (Part-B) | [6 empty] | 20376062.97
24727244.4816

## Summary SS (hidden)
2X100 MVA, 220/33 KV GIS GSS WITH SAS AT PAHALA |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Construction of 2x100 MVA, 220KV GIS and 33KV AIS Sub-Station at Pahala with SAS along with 220 KV D/C line from existing 220/132/33KV GIS at Balianta through UG cabling length approx 8.805 Km & Over head length approx 1.135 Km.
(SUMMARY) |  | SUMMARY OF PRICE SCHEDULES
Sl. No. | DESCRIPTION OF SCHEDULES | PRICE IN INR
1 | Total Cost of materials SCHEDULE-VIIA (FOR S/S) | 672318711.812
2 | Stock,Storage & Insurance(@3% on Sl.No-1) | 20169561.3544
3 | Sub-Total (sl no. 1+2) | 692488273.1664
4 | Contigency 3% on Sl.No.3 | 20774648.195
5 | T&P cost @ 2% on Sl.No. 3 | 13849765.4633
6 | Transportation @5% on Sl.No.3 | 34624413.6583
7 | Erection Chages SCHEDULE-VIIB (FOR S/S) | 22820276.2596
8 | Civil Cost SCHEDULE-VIIC (FOR S/S) | 225361329.2916
9 | Grand Total (3+4+5+6+7+8) | 1009918706.0342
10 | Or say | 1009918706

## Summary TL (hidden)
220 KV D/C Line from existing 220/132/33KV GIS at Balianta to proposed 220/33KV GIS GSS at Pahala (Approx UG Line Length = 8.805 KM & Over Head line length= 1.135 KM) (SUMMARY) |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Construction of 2x100 MVA, 220KV GIS and 33KV AIS Sub-Station at Pahala with SAS along with 220 KV D/C line from existing 220/132/33KV GIS at Balianta through UG cabling length approx 8.805 Km & Over head length approx 1.135 Km.
SUMMARY OF PRICE SCHEDULES
Sl. No. | DESCRIPTION OF SCHEDULES | PRICE IN INR
1 | Total Cost of materials SCHEDULE-VIIA (FOR LINE) | #REF!
2 | Stock,Storage & Insurance(@3% on Sl.No-1) | #REF!
3 | Sub-Total (sl no. 1+2) | #REF!
4 | Contigency 3% on Sl.No.3 | #REF!
5 | T&P cost @ 2% on Sl.No. 3 | #REF!
6 | Transportation @5% on Sl.No.3 | #REF!
7 | Erection Chages SCHEDULE-VIIC (FOR LINE) | #REF!
8 | Civil Cost SCHEDULE-VIIC (FOR LINE) | 24545442.7388
9 | Grand Total (3+4+5+6+7+8) | #REF!
10 | Or say | #REF!

## Abstract (hidden)
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Construction of 2x100 MVA, 220KV GIS and 33KV AIS Sub-Station at Pahala with SAS along with 220 KV D/C line from existing 220/132/33KV GIS at Balianta through UG cabling length approx 8.805 Km & Over Head length approx 1.135 Km.
ABSTRACT
TOTAL COST OF SUB-STATION | 1009918706 | 690685383 | 319233323
TOTAL COST OF LINE | #REF! | 84706697 | #REF!
TOTAL COST | #REF! | 775392080 | #REF! | #REF!
OR SAY | #REF!
#NAME?

## SUMMARY (hidden)
Construction of 2x100 MVA, 220KV GIS and 33KV AIS Sub-Station at Pahala with SAS along with 220 KV D/C line from existing 220/132/33KV GIS at Balianta through UG cabling length approx 8.805 Km & Over Head length approx 1.135 Km.
SUMMARY
Sl. No. | Description | Amount(in Rs.)
1 | Total Cost of Materials (a+b+c below) | #REF!
a | Substation Cost | 660169945.8224
b | Mandatory Spares | 12148765.9896
c | Transmission Line | #REF!
2 | Stock, storage & Insurance(3% on Sl. No.-01) | #REF!
3 | Sub-Total(1+2) | #REF!
4 | Contigency @ 3% on sl. No.03 | #REF!
5 | T&P Cost @ 2% on Sl. No.03 | #REF!
6 | Transportation @ 5% on Sl. NO. 03 | #REF!
7 | Sub - Total Cost of Materials | #REF!
8 | Cost towards Erection (a+b) | #REF!
a | Substation Erection | 22820276.2596
b | Transmission Line Erection | #REF!
9 | Cost towards Civil (a+b) | 249906772.0304
a | Substation Civil Work | 225361329.2916
b | Transmission Line Civil Work | 24545442.7388
11 | Total Cost of Supply, Erection and Civil | #REF!
| Rounded off | #REF!
#NAME?

## Head (hidden)
ODISHA POWER TRANSMISSION CORPORATION LTD
| Province | ODISHA
| Division | EHT Construction Division, Angul
| Sub-Division | EHT Construction Sub-Division, Angul
| Name of the Work | Revised Estimate for Construction of 2x40 MVA , 220KV GIS and 33KV AIS Sub-Station at Angul(New), Aluminium Park with SAS along with 220 KV S/C LILO from existing 220KV Meramundali-Bhanjanagar D/C line Ckt-II (Line length - 6 Kms. approx.) for Proposed Aluminium Park at NALCO, Angul in Odisha State of India.
| Main Head of Classification | Departmental Work
| Estimate No. | 11 / 2024-2025
| Estimated Amount | Rs. | #REF!
#NAME?
Dy. General Manager (Elect.) EHT CONSTN:DIVISION:ANGUL
E.H.T Construction Division,Angul
REVISED ESTIMATE FRAMED BY Er. Kabi Chandra Pattanaik, Dy. GENERAL MANAGER (ELECT) EHT CONSTRUCTION DIVISION, ANGUL
R E P O R T
This estimate is framed in BPS format for an amount of Rs. 77,53,92,079/-(Rupees Seventy Seven Crores Fifty Three Lakhs Ninety Two Thousand Seventy Nine Only) Only to meet the probable expenditure for Construction 2x40 MVA, 220KV GIS and 33KV AIS Sub-Station at Angul(New), Aluminium Park with SAS along with 220 KV S/C LILO from existing 220KV Meramundali-Bhanjanagar D/C line Ckt-II (Line length - 6 Kms. approx.) for Proposed Aluminium Park at NALCO, Angul in Odisha State of India. As per instruction of competent authority of OPTCL and in consultation with E &Q wing, OPTCL, Bhubaneswar as per the current practice for standardization of Sub-Stations. The total scope includes 05 Nos. 220 KV Bays(02 X FDR +02 X TRF + 01 X B/C), 7 Nos. of 33KV Bays (04X FDR+02 X TRF+01X B/C). The 220KV line estimate has been done considering the approximate line length of 06 KM as the 220KV Meramundali -Bhanjanagar D/C line passes around 3.5KM from the proposed site of 220KV GIS and 33KV AIS Sub-Station Aluminium Park. Again OPGW has been considered instead of PLCC for commmunication as per standard practice of OPTCL. Also SAS has been considered for automation of the proposed 220KV GIS and 33KV AIS Sub-Station at Aluminium Park. The SAS kiosk are proposed for normal RCC building instead of prefabricated building for longevity. The construction of the above Sub-Station is essential to meet the future load growth mainly on account of village electrification and rapid industrialization in Chhendipada and adjecent area. The Cost of the materials & Erection charges depicted in the estimate are as per the rate contact for the year 2022-2023 issued vide Rate Contract Lr. No. Sr.GM-CPC-Rate Contract works - 36/2022 185(30) dated : 04.03.2023 of the Sr. GM(CPC), OPTCL, Bhubaneswar for Rate Contract for execution of Normal work on the OPTCL system and approved Cost Data for the year 2023-24 issued vide Lr. No. 914(16) Dated: 07.10.2023 of the CGM(CPC), OPTCL Bhubaneswar and Subsequent amendments respectively. The rate for the items which are not available in cost data/Rate Contract are considered from the prevailing market rate for similar material or work. GST @ 18% has been considered in both supply and Erection part of the present estimate.
Dy. GENERAL MANAGER (ELECT) EHT CONSTN:DIVISION:ANGUL

## TL Foundation (hidden)
Sl. No. | STRUCTURE | TYPE OF SOIL | EXCAVATION (in CUM) | RCC (in CUM) | PCC (in CUM) |  | Alluminium Park | EXC | RCC | PCC |  | STEEL
1 | PA Tower | Normal | 33.68 | 3.367 | 0.4495 | 0 | 0 | 0 | 0 | 0 | 0.7574 | 0 | 44 | WELDING OF NUTS & BOLTS
|  | Wet | 63.36 | 8.76 | 0.882 |  | 0 | 0 | 0 | 0 | 0.9921 | 0 |  | Sl No. | TYPE OF TOWER |  | Nos | Alluminium Park
|  | SS | 89.35 | 13.87 | 1.152 |  | 0 | 0 | 0 | 0 | 1.0407 | 0 |  | 1 | OA | NORMAL | 678 | 4 | 2712
|  | FS | 119.79 | 21.137 | 1.6245 |  | 0 | 0 | 0 | 0 | 1.0407 | 0 |  |  |  | +3 | 180 | 2 | 360
|  | Black cotton | 161.728 | 32.208 | 2.45 |  |  | 0 | 0 | 0 |  | 0 |  |  |  | +6 | 228 | 2 | 456
2 | With Extension | Normal | 38.332 | 3.847 | 0.4774 | 0 | 0 | 0 | 0 | 0 | 0.7574 | 0 |  | 2 | OB | NORMAL | 596 | 2 | 1192
|  | Wet | 70 | 9.72 | 0.968 |  | 0 | 0 | 0 | 0 | 0.9921 | 0 |  |  |  | +3 | 236 | 1 | 236
|  | SS | 97.47 | 15.28 | 1.352 |  | 0 | 0 | 0 | 0 | 1.0407 | 0 |  |  |  | +6 | 372 | 1 | 372
|  | FS | 129.472 | 23.059 | 1.7405 |  | 0 | 0 | 0 | 0 | 1.0407 | 0 |  | 3 | OC | NORMAL | 596 | 10 | 5960
3 | PB Tower | Normal | 50.43 | 5.406 | 0.7372 | 0 | 0 | 0 | 0 | 0 | 0.8138 | 0 |  |  |  | +3 | 254 | 6 | 1524
|  | Wet | 104.43 | 15.49 | 1.568 |  | 0 | 0 | 0 | 0 | 1.1255 | 0 |  |  |  | +6 | 402 | 2 | 804
|  | SS | 138.72 | 23.28 | 2.1125 |  | 0 | 0 | 0 | 0 | 1.1714 | 0 |  |  |  | +15 | 1038 | 2 | 2076 | 16868
|  | FS | 187.23 | 36.358 | 2.738 |  | 0 | 0 | 0 | 0 | 1.1714 | 0 |  | 4 | UR | NORMAL | 1217 | 0 | 0
4 | With Extension | Normal | 56.395 | 6.091 | 0.816 | 0 | 0 | 0 | 0 | 0 | 0.8138 | 0 |  |  |  | +3 | 357 | 0 | 0
|  | Wet | 113.49 | 17 | 1.682 |  | 0 | 0 | 0 | 0 | 1.1255 | 0 |  |  |  | +6 | 588 | 2 | 1176
|  | SS | 149.45 | 25.33 | 2.2445 |  | 0 | 0 | 0 | 0 | 1.1714 | 0 |  | 5 | PA | NORMAL | 514 | 0 | 0
|  | FS | 200.111 | 39.171 | 2.888 |  | 0 | 0 | 0 | 0 | 1.1714 | 0 |  |  |  | +3 | 142 | 0 | 0
5 | PC Tower | Normal | 72.124 | 7.6 | 1.1045 | 0 | 0 | 0 | 0 | 0 | 0.8851 | 0 |  |  |  | +6 | 276 | 0 | 0
|  | Wet | 141.54 | 20.64 | 2.45 |  | 0 | 0 | 0 | 0 | 1.235 | 0 |  | 6 | PB | NORMAL | 544 | 0 | 0
|  | SS | 188.44 | 31.33 | 3.362 |  | 0 | 0 | 0 | 0 | 1.3042 | 0 |  |  |  | +3 | 273 | 0 | 0
|  | FS | 236.376 | 43.972 | 4.05 |  | 0 | 0 | 0 | 0 | 1.3042 | 0 |  |  |  | +6 | 542 | 0 | 0
6 | With Extension | Normal | 72.124 | 7.6 | 1.1045 | 0 | 0 | 0 | 0 | 0 | 0.8851 | 0 |  | 7 | PC | NORMAL | 700 | 0 | 0
|  | Wet | 141.54 | 20.64 | 2.45 |  | 0 | 0 | 0 | 0 | 1.235 | 0 |  |  |  | +3 | 313 | 0 | 0
|  | SS | 188.44 | 31.33 | 3.362 |  | 0 | 0 | 0 | 0 | 1.3042 | 0 |  |  |  | +6 | 592 | 0 | 0 | 0
|  | FS | 236.376 | 43.972 | 4.05 |  | 0 | 0 | 0 | 0 | 1.3042 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 27
1 | OA Tower | Normal | 32.888 | 3.333 | 0.4176 | 10 | 0 | 0 | 0 | 0 | 1.197 | 0
|  | Wet | 64.512 | 8.796 | 0.882 |  | 4 | 258.048 | 35.184 | 3.528 | 1.718 | 6.872
|  | SS | 81.648 | 11.988 | 1.152 |  | 1 | 81.648 | 11.988 | 1.152 | 1.979 | 1.979
|  | FS | 111.132 | 18.495 | 1.6245 |  | 1 | 111.132 | 18.495 | 1.6245 | 2.495 | 2.495
|  | Black cotton | 161.728 | 32.208 | 2.45 |  | 0 | 0 | 0 | 0 | 0.434 | 0
2 | With Extension | Normal | 37.444 | 3.81 | 0.4774 |  | 0 | 0 | 0 | 0 | 1.197 | 0
|  | Wet | 71.25 | 9.765 | 0.968 |  | 3 | 213.75 | 29.295 | 2.904 | 1.718 | 5.154
|  | SS | 89.376 | 13.24 | 1.352 |  | 1 | 89.376 | 13.24 | 1.352 | 1.979 | 1.979
|  | FS | 120.412 | 20.236 | 1.7405 |  | 0 | 0 | 0 | 0 | 2.495 | 0
|  | Black cotton | 173.396 | 34.8 | 2.592 |  | 0 | 0 | 0 | 0 | 0.434 | 0
3 | OB Tower | Normal | 59.14 | 6.64 | 0.7372 | 4 | 0 | 0 | 0 | 0 | 1.045 | 0
|  | Wet | 119.16 | 17.9 | 1.568 |  | 2 | 238.32 | 35.8 | 3.136 | 2.515 | 5.03
|  | SS | 156.27 | 26.52 | 2.1125 |  | 0 | 0 | 0 | 0 | 3.115 | 0
|  | FS | 198.4 | 37.84 | 2.738 |  | 0 | 0 | 0 | 0 | 3.981 | 0
|  | Black cotton | 273.92 | 61.71 | 3.872 |  | 0 | 0 | 0 | 0 | 0.633 | 0
4 | With Extension | Normal | 65.67 | 7.4512 | 0.816 |  | 0 | 0 | 0 | 0 | 1.045 | 0
|  | Wet | 129.02 | 19.59 | 1.682 |  | 0 | 0 | 0 | 0 | 2.515 | 0
|  | SS | 167.36 | 28.65 | 2.2445 |  | 2 | 334.72 | 57.3 | 4.489 | 3.115 | 6.23
|  | FS | 211.81 | 40.73 | 2.888 |  | 0 | 0 | 0 | 0 | 3.981 | 0
|  | Black cotton | 290.3 | 65.76 | 4.05 |  | 0 | 0 | 0 | 0 | 0.633 | 0
5 | OC Tower | Normal | 95.506 | 11.026 | 1.1045 | 8 | 0 | 0 | 0 | 0 | 2.095 | 0
|  | Wet | 212.94 | 35.397 | 2.45 |  | 4 | 851.76 | 141.588 | 9.8 | 3.811 | 15.244
|  | SS | 271.04 | 51.357 | 3.362 |  | 1 | 271.04 | 51.357 | 3.362 | 4.25 | 4.25
|  | FS | 338.14 | 72.274 | 4.05 |  | 1 | 338.14 | 72.274 | 4.05 | 4.25 | 4.25
|  | Black cotton | 439.04 | 118.808 | 5.618 |  | 0 | 0 | 0 | 0 | 0.854 | 0
6 | With Extension | Normal | 104.36 | 12.227 | 1.2005 |  | 0 | 0 | 0 | 0 | 2.095 | 0
|  | Wet | 212.94 | 35.397 | 2.45 |  | 2 | 425.88 | 70.794 | 4.9 | 3.811 | 7.622
|  | SS | 271.04 | 51.357 | 3.362 |  | 0 | 0 | 0 | 0 | 4.25 | 0
|  | FS | 338.14 | 72.274 | 4.05 |  | 0 | 0 | 0 | 0 | 4.25 | 0
|  | Black cotton | 439.04 | 118.808 | 5.618 |  | 0 | 0 | 0 | 0 | 4.25 | 0
7 | UR Tower | Normal | 122.75 | 22.96 | 1.9531 | 2 | 0 | 0 | 0 | 0 | 4.25 | 0
|  | Wet | 216.75 | 52.12 | 3.4445 |  | 0 | 0 | 0 | 0 | 4.25 | 0
|  | SS | 276.48 | 73.6905 | 4.418 |  | 0 | 0 | 0 | 0 | 4.25 | 0
|  | FS | 346.687 |  | 5.5651 |  | 0 | 0 | 0 | 0 | 4.25 | 0
|  | Black cotton |  |  |  |  | 0 | 0 | 0 | 0 | 4.25 | 0
8 | With Extension | Normal | 122.75 | 22.96 | 1.9531 | 0 | 0 | 0 | 0 | 0 | 4.25 | 0
|  | Wet | 216.75 | 52.12 | 3.4445 |  | 2 | 433.5 | 104.24 | 6.889 | 4.25 | 8.5
|  | SS | 276.48 | 73.6905 | 4.418 |  | 0 | 0 | 0 | 0 | 4.25 | 0
|  | FS |  |  | 5.5651 |  | 0 | 0 | 0 | 0 | 4.25 | 0
|  | Black cotton |  |  |  |  | 0 | 0 | 0 | 0 | 4.25 | 0
9 | OC+15 Tower | Normal | 555.66 | 200 | 1.8 | 2 | 0 | 0 | 0 | 0 | 4.25 | 0
|  | Wet | 322.56 | 30.188 | 8.1 |  | 1 | 322.56 | 30.188 | 8.1 | 4.25 | 4.25
|  | SS |  |  |  |  | 0 | 0 | 0 | 0 | 4.25 | 0
|  | FS | 470.96 | 51.188 | 11.236 |  | 1 | 470.96 | 51.188 | 11.236 | 4.25 | 4.25
|  | Black cotton |  |  |  |  | 0 | 0 | 0 | 0
[5 empty] | total | 26 | 26 | 4440.834 | 722.931 | 66.5225 |  | 78.105

## Sheet1 (hidden)
1 | Pahala S/S Supply | 660169945.8224
2 | S/S Spare supply | 12148765.9896
3 | S/S Erection | 22820276.2596
4 | S/S Civil | 225361329.2916
5 | Line (OH+UG) Supply | 1508060745.2134
6 | Line Erection | 125710013.8025
7 | Line Civil | 110458086.4006
8 | Bay Extension Supply | 76272286.3477
9 | BayExtension Erection | 2859892.5
10 | Bay Extension Civil | 11010384.71
| Grand Total= | 2754871726.3374