## Pahala CBA
COST BENEFIT ANALYSIS
A. BENEFITS DUE TO ADDITIONAL SALE OF ENERGY ON ACCOUNT OF INSTALLATION OF 2X100 MVA, 220/33 KV GRID SUB-STATION AT PAHALA AND ASSOCIATED 220KV D/C LINE FROM BALIANTA THROUGH UG CABLING |  |  | Remarks
1 | Transformation Capacity considered for revenue calculation considering N-1 condition | 100
2 | Power factor (PF) | 0.9
3 | Diversity factor (DF=1.3 due to Mixed load) | 1.3
4 | Load factor (LF=0.7 due to Mixed load) | 0.7
5 | Additional avg. power available for sale on account of establishment of a new 220/33 KV Grid Sub-station at Pahala with 2x100 MVA transformers in MW (5 = 1 x 2 x 4 / 3) | 48.4615 | 0.9 : Power Factor 1.2: Diversity Factor
7 | Additional energy available for sale in LU | 4245.2308 | 8760 = 24*365
8 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 4117.8738 | 3% T.L is approved for FY 2025-26
9 | Anticipated revenue at a cost of Rs.0.24/ Unit in Lakhs | 988.2897 | Wheeling Cost 0.255/Unit
B. BENEFITS OF THE SCHEME DUE TO REDUCTION IN LOSSES
1 | Total losses before implementation of the scheme in MW | 1101.2117 | From Load Flow Analysis
2 | Total losses after implementation of the scheme in MW | 1100.4946
3 | Total reduction in losses in MW | 0.71714
4 | Load factor | 0.7
5 | Loss load factor (0.8 LF2 + 0.2 LF) | 0.532
6 | The energy available for sale per year in LU | 33.4209
7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 32.4183
8 | Anticipated revenue due to reduction in losses in lakhs @ Rs. 0.24/ Unit | 7.7804
C. CALCULATION OF REVENUE RETURN
1 | Anticipated revenue due to reduction in losses [Rs. Lakhs] | 7.7804
2 | Anticipated revenue due to sale of additional energy [Rs. lakhs] | 988.2897
3 | Total anticipated annual revenue [Rs. Cr.] | 9.9607
4 | Estimated Cost [Rs. Cr.] | 360.7506
5 | Average Annual Rate of Return in % | 2.7611

## NPV & IRR
Calculation of NPV and IRR : 2X100 MVA, 220/33 KV GRID SUB-STATION AT PAHALA AND ASSOCIATED 220KV D/C LINE FROM BALIANTA THROUGH UG CABLING
CoC (%) = | No Loan | x | 0 | + | No Equity | x | 0 | = | 0 |  |  | RoI on Loan P.a |  |  | = | 0 | IRR can't be computed due to 100% Grant. | [8 empty] | (Rs. in Crores)
Particulars | Constuction Period | [37 empty] | Total
Financial Year | 1 | 2 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
Cash Inflow (CI)
Govt Grant 100% | 72.15 | 180.38 | 108.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 360.76
Loan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0
Revenue | 0 | 0 |  | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 348.6245
Salvage Value | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 36.076 | 36.076
Total (CI) - (A) | 72.15 | 180.38 | 108.23 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 9.9607 | 46.0367 | 745.4605
Cash Outflow (CO)
CWIP | 72.15 | 180.38 | 108.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 360.76
IDC | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0
Loan Repayment | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0
Interest on Loan | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0
O&M exp. @3.0 % | 0 | 0 |  | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 378.7
Total (CO) - (B) | 72.15 | 180.38 | 108.23 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 739.46
Net Cash Inflow (B-A) | 0 | 0 | 0 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | -0.8593 | 35.2167 | 6.0005
DF @ CoC | 1 | 1 | 1 | bar: 4 to 38
Net Present value(NPV) | 0 | 0 | 0 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | -0.86 | 35.22 | 5.98
* CoC - Cost of Capital
IDC- Interest During Construction
CWIP- Capital Work in Progress
DF- Discounting Factor
IRR- Internal Rate of Return
ARR- Average Annual Rate of Return

## Data sheet
| Expenditure in Crores: | 360.7506
| Year: | 2026-27 | 2027-28 | 2028-29
| % of Expenditure: | 20% | 50% | 30%
| Year wise expenditure: | 72.1501 | 180.3753 | 108.2252
Loan | 0% | 0 | 0 | 0
Grant | 100% | 72.15 | 180.38 | 108.23
Total | 100% | 72.15 | 180.38 | 108.23