SYNOPSIS

The Odisha State with an area of nearly 1.56 lakh sq. kms. being the 10th largest state in India area wise, has a population of nearly 4.373 crores having 482 Kms. long sea beach along its territory. Out of the above population index almost 86% are based in the rural area. It is the 11th most populous state in the country.

The power system of the State has some low voltage pockets in certain remote zones fed as tail end, causing high system loss. Therefore, it has been proposed to bring out improvement in the system by way of installation of several new sub-stations in the transmission sector of the State.

This transmission project report has been prepared for “Conversion of 132kV Kutra Switching Station to 2X50MVA 132/33kV Grid Substation, Kutra" in the district of Sundargarh. In order to achieve stability and to cater qualitative uninterrupted power in the transmission system of the State as well as to meet the increasing load demand.

The main thrust and emphasis are laid on the following:

- This augmentation will enhance system reliability, reduce loading on existing substations, minimize technical losses, and ensure stable and quality power supply to industrial, agricultural, and domestic consumers in the region.

- It will help decongest the existing loads of TPWODL on nearby GSSs through diversion of some of the loads to proposed Kutra GSS.

- Minimize interruption of power supply to domestic consumers.

- Enhance power system reliability and deliver quality power to industrial consumers.

- Strengthening of transmission system of OPTCL 132 KV level network in the western part of Odisha.

- Improving the economic condition of the inhabitants.

- Will meet the load growth due to upcoming / existing industries.

INTRODUCTION

So far as the Electricity sector of the country is concerned, Odisha is the pioneer in implementing the Reforms & Restructuring of the State Electricity Board. In this process, the State is leading the whole Nation and other States are following its footsteps. As a result, the distribution sector has already been separated out and divided into four zones. The generating stations have also been isolated and working as State owned Company. The erstwhile GRIDCO [Grid Corporation of Orissa Ltd.] was vested with the functions of transmission and trading of bulk power. The same has been divided into two parts. While GRIDCO is vested with trading of bulk power, the business of wheeling of power is with Odisha Power Transmission Corporation Ltd (OPTCL).

Sundargarh district, constituted on 1 January 1948 through the merger of the erstwhile princely states of Gangapur and Bonai with Odisha, is one of the most important districts of the state in terms of natural resources, industrial development, and tribal heritage. Located in the north-western part of Odisha, the district is bounded by Jharkhand to the north and east, Chhattisgarh to the west and north-west, and the districts of Jharsuguda, Sambalpur, Angul, and Kendujhar within Odisha. Covering an area of about 9,712 sq. km, it is the second largest district in Odisha and has approximately 43% of its geographical area under forest cover. The district forms part of the Chhotanagpur Plateau and is characterized by undulating terrain, isolated hill ranges, extensive forests, and the river systems of the Brahmani and Ib. Rich deposits of iron ore, manganese, limestone, dolomite, and coal have made Sundargarh a major mining and industrial hub of eastern India. The district also has a significant urban population, with about 35% of its residents living in urban areas, making it one of the most urbanized districts in Odisha.

Kutra Tahasil is situated in the western part of Sundargarh district and occupies a prominent position in the mineral map of India owing to its abundant reserves of iron ore, manganese, limestone, dolomite, and coal. Located at approximately 22.23°N latitude and 84.47°E longitude along State Highway No. 10, Kutra serves as an important administrative and economic centre of the region. The availability of rich mineral resources has facilitated the establishment of several industrial units and mining operations in and around the tahasil, including OCL Cement, OCL Iron & Steel Pvt. Ltd., TISCO Dolomite Mines at Gomardih, Scan Steels Ltd. and Shiva Cement Factory. The area enjoys good connectivity with major industrial and commercial centres such as Rourkela and is strategically located near the neighbouring regions of Simdega, Kunkuri, and Jashpur. Owing to its mineral wealth, industrial presence, and growing infrastructure, Kutra has emerged as an important location for power infrastructure development, including the proposed 132/33 kV Grid Substation.

This transmission project report broadly contains the following parameters.

- Details of works.

- Need of the Project.

- Cost estimate.

- Least cost analysis.

- Status of works.

- Constraints.

- Costs benefit analysis.

- Phasing of outlay required.

- Drawings.

- System study analysis.

The works covered in this project have been programmed for completion during FY 2027-28 and accordingly the implementation program has been drawn up. The Total Project Cost comes to Rs. 34.30 Crores which will be executed through 30% equity support from Govt. of Odisha and 70% debt from suitable financial institutions. The annual revenue return (ARR) works out to 13.81% considering the anticipated financial benefits, which accrue due to implementation of scheme.

POWER SCENARIO OF THE STATE (As on 13.02.2024)

| AVAILABILITY OF POWER |  |  |  |
| --- | --- | --- | --- |
| TYPE OF GENERATION | STATE SHARE GENERATION | CENTRAL SHARE GENERATION | STATE SHARE + CENTRAL SHARE |
| TOTAL HYDRO | 2094.80 MW | 276.59 MW | 2371.39 MW |
| TOTAL THERMAL | 1740.00 MW | 1923.52 MW | 3663.52 MW |
| TOTAL IPP | 1013.70 MW | 0.00 MW | 1013.70 MW |
| RENEWABLE ENERGY |  |  |  |
| SMALL HYDRO | 109.15 MW | 0.00 MW | 109.15 MW |
| BIOMASS | 20.00 MW | 0.00 MW | 20.00 MW |
| WIND | 321.50 MW | 0.00 MW | 321.50 MW |
| SOLAR | 1466.65 MW | 0.00 MW | 1466.65 MW |
| TOTAL RENEWABLE | 1917.30 MW | 0.00 MW | 1917.30 MW |
| TOTAL | 6765.80 MW | 2200.11 MW | 8965.91 MW |
| * Data as on 13.02.2024 Source: Case no 115/2023 Gridco ARR page no: 31 & 32 |  |  |  |
| TRANSMISSION NETWORK OF OPTCL |  |  |  |
| VOLTAGE LEVEL | NO. OF SUB-STATIONS | NO OF TRANSFORMER | INSTALLED CAPACITY(MVA) |
| 400 KV | 5 | 11 | 3835 |
| 220 KV | 47 | 119 | 12272 |
| 132 KV | 142 | 353 | 10141 |
| TOTAL | 194 | 483 | 26248 |
| VOLTAGE LEVEL | NO. OF BAYS | ROUTE KMS | CIRCUIT KMS |
| 400 KV | 70 | 718.217 | 1196.872 |
| 220 KV | 439 | 3750.346 | 6831.365 |
| 132 KV | 1172 | 6492.274 | 8479.831 |
| 33 KV | 1459 |  |  |
| TOTAL | 3140 | 10960.837 | 16508.068 |
| * Data as on 31.03.2024 Source: Achievement report |  |  |  |
| DISTRIBUTION NETWORK OF DISCOM |  |  |  |
| NO OF PSS AND ITS INSTALLED MVA CAPACITY IN DISCOM |  |  |  |
| DISCOM’s | No of PSS | PTR 33/11 KV | DTR 11/.415 KV |
| TPCODL | 369 | 4863 MVA | 5702 MVA |
| TPNODL | 239 | 2527 MVA | 2708 MVA |
| TPSODL | 246 | 2518 MVA | 3878 MVA |
| TPWODL | 300 | 3350 MVA | 3488 MVA |
| TOTAL | 1154 | 13258 MVA | 15776 MVA |
| DISCOM LINES |  |  |  |
| DISCOM’s | 33 KV CKT KMS | 11 KV CKT KMS | LT CKT KMS |
| TPCODL | 4,082.00 | 39,350.00 | 50,050.00 |
| TPNODL | 3,007.00 | 38,339.00 | 67,117.30 |
| TPSODL | 3,883.00 | 43,450.00 | 40,000.00 |
| TPWODL | 5,632.00 | 52,870.00 | 62,858.00 |
| TOTAL | 16,604.00 | 1,74,009.00 | 2,20,025.30 |
| * Data as on 31.03.2024 Source: Discom Capex |  |  |  |

EXISTING SUPPLY SYSTEM

The existing 132 kV Kutra Switching Station in Sundargarh district is presently operating only as a switching point without any transformation facility. However, the region is experiencing significant growth in industrial activity, with major consumers such as M/s Scan Steels Ltd., M/s Shiva Cement Limited, M/s Uni Profiles Private Limited, M/s M R Engineers Private Limited, along with several emerging MSME units establishing operations in the area.

In addition to growing industrial demand, the station is expected to cater to the increasing agricultural and domestic load within the nearby TPWODL command areas. At present, power supply to these loads is being managed through long 33 kV feeders originating from distant substations, resulting in considerable voltage drops, reduced reliability, and frequent interruptions.

To address these issues and ensure quality power supply, it is proposed to upgrade the existing 132 kV Kutra Switching Station into a full-fledged 132/33 kV Grid Sub-Station by installing 2×50 MVA, 132/33 kV power transformers along with associated bays, switchgear, protection, control, and communication systems. This augmentation will enhance system reliability, reduce loading on existing substations, minimize technical losses, and ensure stable and quality power supply to industrial, agricultural, and domestic consumers in the region.

NEED OF THE PROJECT

- The proposal shall help to cater power supply to M/s. Scan Steels Ltd., M/s Sita Cement Limited, Uni Profiles Private Limited, M/s M R Engineers Private Limited and several other MSME enterprises in and around Kutra tahasil.

- Moreover, the implementation of this project will strengthen power availability for TPWODL consumers in nearby villages and towns. This would also encourage the establishment of additional small and medium-scale industries in the region, thereby fostering industrial growth and ultimately contributing to the overall economic development of the State of Odisha.

JUSTIFICATION OF THE PROJECT

The current infrastructure is inadequate to support the rising industrial, agricultural, and domestic demand, leading to persistent power quality issues and underscoring the need for establishing a dedicated 132/33 kV Grid Sub-Station at Kutra. In order to address these issues and ensure quality power supply, upgradation of the existing 132 kV Kutra Switching Station into a full-fledged 132/33 kV Grid Sub-Station by installing 2×50 MVA, 132/33 kV power transformers along with associated 33kV bays, switchgear, protection, control, and communication systems, shall be pertinent. This augmentation will enhance system reliability, reduce loading on existing substations, minimize technical losses, and ensure stable and quality power supply to industrial, agricultural, and domestic consumers in the region.

SCOPE OF NEW PROPOSAL

Proposed “Conversion of 132kV Kutra Switching Station to 2X50MVA 132/33kV Grid Substation, Kutra" in the district of Sundargarh.

The total scope of works as envisaged in the proposed project is detailed below.

- Installation of 50MVA, 132/33KV Transformers              	: 2 Nos.

- 132KV Transformer bay                   	                             	: 2 Nos.

- 33KV Transformer bays                                                    		: 2 Nos.

- 33KV Bus coupler bay                                                      		: 1 No.

- 33KV Line feeder bays                                                     		: 5 Nos.

- 250 KVA, 33 / 0.4KV station transformer with                 	: 1 Set

its auxiliaries

- Sub-station auxiliaries i.e., battery and                               	: 1 Set

battery charger, firefighting equipment etc.

- Land, Control room and other civil                                    	: As required.

## PROJECT IMPLEMENTATION PLAN

The project implementation plan for the works covered is given in the Bar Chart enclosed. The activity wise implementation schedule indicates that the project is programmed for completion by December 2027.

The CGM (Project), Odisha Power Transmission Corporation Limited, Bhubaneswar is the nodal authority for implementation of the project.

PROCUREMENT PROCEDURE

In accordance with the approved norms of OPTCL, the procurement of materials and services is to be taken up by way of National Competitive Bidding. The entire work for the proposed project shall be treated as a single package and is to be awarded on turn-key basis to a single party.

STATUS OF CLEARANCES

- ADMINISTRATIVE APPROVAL:

The Administrative Approval shall be accorded in line with DOP after approval from OERC

- TECHNO – ECONOMIC CLEARANCE:

Not required as the voltage level is less than 400 KV.

- ENVIRONMENT & FOREST CLEARANCE:

No forest is involved in the conversion of 132kV switching station to proposed 132/33 KV Sub-Station at Kutra

- STATE POLLUTION CONTROL BOARD:

Not required.

- INVESTMENT APPROVAL FROM OERC:

The investment proposal shall be placed in OERC for approval for which this DPR is being prepared.

As per the license condition 10 read with condition 23.1 of OPTCL approval of OERC is required for cost beyond 10 Crores. As per the prevailing practice/norms signing of the contract with successful bidder can only be made after due approval of the commission.

- POWER & TELECOMMUNICATION CO-ORDINATION COMMITTEE (PTCC)

The clearance in respect of PTCC would be obtained prior to charging of the line.

SOURCE OF FUNDING

The working capital would be made available through 30% equity support from Govt. of Odisha and 70% debt from suitable financial institutions as per the Govt. resolution dated 26.11.2025.

PRESENT STATUS OF WORK

- LoA will be issued after OERC approval.

# COST OF IMPLEMENTATION

The implementation of the Project will incur an expenditure of Rs. 34.30 Crores, the details of which are indicated separately.

# CERTIFICATE

Certified, that the Project report has been prepared by adopting the prevailing approved cost data of OPTCL.

PHASING OF EXPENDITURE:

Financial Year                               	     ₹ in Crores

2026-27                                         	₹ 10.29 Crores

2027-28                                         	₹ 24.01 Crores

# BENEFITS

Physical Benefits:

- This augmentation will enhance system reliability, reduce loading on existing substations, minimize technical losses, and ensure stable and quality power supply to industrial, agricultural, and domestic consumers in the region.

- It will help decongest the existing loads of TPWODL on nearby GSSs through diversion of some of the loads to proposed Kutra GSS.

- Minimize interruption of power supply to domestic consumers.

- Enhance power system reliability and deliver quality power to industrial consumers.

- Strengthening of transmission system of OPTCL 132 KV level network in the western part of Odisha.

- Improving the economic condition of the inhabitants.

- Will meet the load growth due to upcoming / existing industries.

Financial Benefit:

The project will yield a gross return of 13.81%.

ESTIMATED COST

| SL. NO. | DESCRIPTION | AMOUNT IN CRORES |
| --- | --- | --- |
| 1 | “Conversion of 132kV Kutra Switching Station to 2X50MVA 132/33kV Grid Substation, Kutra" | 34.30 |

The following percentages have been considered while framing the cost estimate.

Stock, storage & Insurance @ 3%

Contingency @ 3%

T&P Cost @ 2%

Transportation @ 5%

GST @ 18 %

LEAST COST ANALYSIS

The proposal is based on field studies conducted by OPTCL to arrive at the least cost option of attaining the objectives aimed in the Project. In order to achieve the system reliability, stability and to minimize interruption to the consumers, alternatives were examined at various stages of planning to arrive at the optimal solution based on technical as well as financial considerations.

CONSTRAINTS

This location is in the western part of the state and is termed to be one of the areas with extensive prospects for developing as an industrial, educational and trading hub. As this proposal is for upgradation of the existing 132kV switching station into a full-fledged Grid substation and no new construction of lines, hence, major constraints like ROW, forest clearance, etc. may not rise for this project. However, if any hurdles arise as per site condition, OPTCL’s proven expertise in managing ROW issues, departmental clearances, and shutdown planning provides confidence that these challenges can be effectively addressed

This area is suffering from uneven population distribution which poses a real challenge to the revenue authorities in implementing different govt. schemes. Further, this area has extensive potential for being an industrial hub owing to abundant mineral resources in and around Sundargarh. The project needs to be undertaken to help the inhabitants of this developing area.

ANNEXURES LIST: DOCUMENTS & DRAWINGS

The following documents are appended to this Project Report.

Annexure-I

- The detailed estimate for “Conversion of 132kV Kutra Switching Station to 2X50MVA 132/33kV Grid Substation, Kutra"

Annexure-II

- Project Implementation Schedule

Annexure-III

- Environmental Impact Assessment Study: Substation

Annexure-IV

- In-principle Approval for “Conversion of 132kV Kutra Switching Station to 2X50MVA 132/33kV Grid Substation, Kutra"

- Connectivity diagram of the proposed 132/33KV Sub-Station Kutra.

- Connectivity Arrangement before inclusion of proposed 132/33 KV Sub-station Kutra

- Connectivity Arrangement after inclusion of proposed 132/33 KV Sub-station Kutra

- Single Line Diagram of proposed 132/33 KV Sub-station Kutra

- Indicative Map of Sundargarh District

- Transmission Power Map of OPTCL in the state of Odisha.

- Schematic diagram of OPTCL network.

- Load flow study of proposed 132/33 KV Sub-station Kutra

- IRR of proposed 132/33 KV Sub-station Kutra

LOAD FLOW ANALYSIS

|:::::        LOAD FLOW ANALYSIS    :::::|

|-----CASE NO :  1     CONTINGENCY  : 0  SCHEDULE NO : 0-----|

|-----CONTINGENCY NAME : Base Case with 132kV  Switching station, Shiva Cement

line RATING CONSIDERED : NOMINAL -----|

-------------------------------------------------------------------------

|***** SUMMARY OF RESULTS *****|

TOTAL REAL POWER GENERATION (CONVENTIONAL)   :  42500.912 MW

TOTAL REAL POWER INJECTION (-ve LOAD)        :      0.000 MW

TOTAL REACT. POWER GENERATION (CONVENTIONAL) :   -836.272 MVAr

GENERATION p.f.                              :      1.000

TOTAL REAL POWER GENERATION (WIND)           :      0.000 MW

TOTAL REACT. POWER GENERATION (WIND)         :      0.000 MVAr

TOTAL REAL POWER GENERATION (SOLAR)          :      0.000 MW

TOTAL REACT. POWER GENERATION (SOLAR)        :      0.000 MVAr

TOTAL SHUNT REACTOR INJECTION                :      0.000 MW

TOTAL SHUNT REACTOR INJECTION                : -16617.102 MVAr

TOTAL SHUNT CAPACIT.INJECTION                :      0.000 MW

TOTAL SHUNT CAPACIT.INJECTION                :   3401.948 MVAr

TOTAL TCSC REACTIVE DRAWL                    :      0.000 MVAr

TOTAL SPS REACTIVE DRAWL                     :      0.000 MVAr

TOTAL UPFC INJECTION                         :     -0.000 MVAr

TOTAL SHUNT FACTS INJECTION                  :      0.000 MVAr

TOTAL SHUNT FACTS DRAWAL                     :    234.816 MVAr

TOTAL REAL POWER LOAD                        :  40690.535 MW

TOTAL REAL POWER DRAWAL (-ve gen.)           :    698.400 MW

TOTAL REACTIVE POWER LOAD                    :  13039.613 MVAr

LOAD p.f.                                    :      0.952

TOTAL COMPENSATION AT LOADS                  :      0.000 MVAr

TOTAL HVDC REACTIVE POWER                    :      0.000 MVAr

TOTAL REAL POWER LOSS (AC+DC)                :   1112.009421 MW (1112.009421+  0.000000)

PERCENTAGE REAL  LOSS (AC+DC)                :      2.616

TOTAL REACTIVE POWER  LOSS                   : -27331.595447 MVAr

|***** SUMMARY OF RESULTS *****|

|:::::        LOAD FLOW ANALYSIS    :::::|

|-----CASE NO :  1     CONTINGENCY  : 0  SCHEDULE NO : 0-----|

|-----CONTINGENCY NAME : with 132/33kV  Sub-station Shiva cement

line RATING CONSIDERED : NOMINAL -----|

-------------------------------------------------------------------------

TOTAL REAL POWER GENERATION (CONVENTIONAL)   :  42481.625 MW

TOTAL REAL POWER INJECTION (-ve LOAD)        :      0.000 MW

TOTAL REACT. POWER GENERATION (CONVENTIONAL) :   -862.618 MVAr

GENERATION p.f.                              :      1.000

TOTAL REAL POWER GENERATION (WIND)           :      0.000 MW

TOTAL REACT. POWER GENERATION (WIND)         :      0.000 MVAr

TOTAL REAL POWER GENERATION (SOLAR)          :      0.000 MW

TOTAL REACT. POWER GENERATION (SOLAR)        :      0.000 MVAr

TOTAL SHUNT REACTOR INJECTION                :      0.000 MW

TOTAL SHUNT REACTOR INJECTION                : -16617.779 MVAr

TOTAL SHUNT CAPACIT.INJECTION                :     -0.000 MW

TOTAL SHUNT CAPACIT.INJECTION                :   3402.091 MVAr

TOTAL TCSC REACTIVE DRAWL                    :      0.000 MVAr

TOTAL SPS REACTIVE DRAWL                     :      0.000 MVAr

TOTAL UPFC INJECTION                         :     -0.000 MVAr

TOTAL SHUNT FACTS INJECTION                  :      0.000 MVAr

TOTAL SHUNT FACTS DRAWAL                     :    235.955 MVAr

TOTAL REAL POWER LOAD                        :  40672.608 MW

TOTAL REAL POWER DRAWAL (-ve gen.)           :    698.400 MW

TOTAL REACTIVE POWER LOAD                    :  13037.919 MVAr

LOAD p.f.                                    :      0.952

TOTAL COMPENSATION AT LOADS                  :      0.000 MVAr

TOTAL HVDC REACTIVE POWER                    :      0.000 MVAr

TOTAL REAL POWER LOSS (AC+DC)                :   1110.649452 MW (1110.649452+  0.000000)

PERCENTAGE REAL  LOSS (AC+DC)                :      2.614

TOTAL REACTIVE POWER  LOSS                   : -27357.955154 MVAr

------------------------------------------------------------------

| COST BENEFIT ANALYSIS |  |  |
| --- | --- | --- |
| A. BENEFITS DUE TO SALE OF ENERGY ON ACCOUNT OF CONVERSION OF 132 KV SWITCHING STATION AT KUTRA TO 2 X 50 MVA, 132/33 KV GRID SUB-STATION |  |  |
| 1 | Transformation Capacity considered for revenue calculation considering N-1 condition (2x50 MVA= 100 MVA) | 50.00 |
| 2 | Power factor (PF) | 0.90 |
| 3 | Diversity factor (DF=1.4 due to mixed type industrial and commercial load) | 1.40 |
| 4 | Load factor (LF=0.7 due to mixed type industrial and commercial load) | 0.70 |
| 5 | Additional avg. power available for sale on account of establishment of a new 132/33 KV Grid Sub-station at Kutra with 2x50 MVA transformers in MW (5 = 1 x 2 x 4 / 3) | 22.50 |
| 6 | Additional energy available for sale in LU | 1971.00 |
| 7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 1911.87 |
| 8 | Anticipated revenue at a cost of Rs.0.24/ Unit in Lakhs | 458.85 |
| B. BENEFITS OF THE SCHEME DUE TO REDUCTION IN LOSSES |  |  |
| 1 | Total losses before implementation of the scheme in MW | 1112.009421 |
| 2 | Total losses after implementation of the scheme in MW | 1110.649452 |
| 3 | Total reduction in losses in MW | 1.36 |
| 4 | Load factor | 0.70 |
| 5 | Loss load factor (0.8 LF2 + 0.2 LF) | 0.53 |
| 6 | The energy available for sale per year in LU | 63.38 |
| 7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 61.48 |
| 8 | Anticipated revenue due to reduction in losses in lakhs @ Rs. 0.24/ Unit | 14.75 |
| C. CALCULATION OF REVENUE RETURN |  |  |
| 1 | Anticipated revenue due to reduction in losses [Rs. Lakhs] | 14.75 |
| 2 | Anticipated revenue due to sale of additional energy [Rs. lakhs] | 458.85 |
| 3 | Total anticipated annual revenue [Rs. Cr.] | 4.74 |
| 4 | Estimated Cost [Rs. Cr.] | 34.30 |
| 5 | Average Annual Rate of Return in % | 13.81 |
| 6 | Internal Rate of Return | 31.81% |

LIST OF FORMATS

| SL. NO. | DESCRIPTION | FORMAT NO. |
| --- | --- | --- |
| 1. | SANCTION AND CLEARANCES | FORMAT - I |
| 2. | SURVEY | FORMAT - II |
| 3. | ACQUISITION OF LAND FOR SUB-STATION | FORMAT - III |
| 4. | FOREST AND ENVIRONMENT CLEARANCE | FORMAT - IV |
| 5. | FINANCIAL BENEFITS | FORMAT – V |
| 6. | ANNUAL PLAN PROVISION | FORMAT – VI |
| 7. | EXPENDITURE INCURRED | FORMAT – VII |
| 8. | PROCUREMENT OF MATERIALS FOR SUB-STATION | FORMAT - VIII |
| 9. | PROCUREMENT OF MATERIALS FOR LINE | FORMAT - IX |

FORMAT - I

SANCTION AND CLEARANCES

| SL. NO. | NAME OF THE SCHEME | NAME OF FIVE YEAR PLAN IN WHICH INCLUDED | TECHNO-ECONOMIC CLEARANCE BY CEA | INVESTMENT APPROVAL | REMARKS |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |
| 1. | Conversion of 132kV Kutra Switching Station to 2X50MVA 132/33kV Grid Substation, Kutra | Shall be included in 15th Transmission Plan of OERC | Not required | Shall be obtained from OERC | ----------- |

FORMAT - II

SURVEY

| SL. NO. | GRID SUBSTATION | DATE OF TAKING UP SURVEY WORKS ORIGINAL DATE / REVISED DATE | COMPLETION OF SURVEY/ ORIGINAL DATE / REVISED DATE | WHETHER PTCC CLEARANCE RECEIVED | REMARKS |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |
| 1. | 2X50MVA 132/33kV Grid Substation, Kutra | Only upgradation of the existing switching station to grid substation is to be done. There is no involvement of line, hence, survey and PTCC clearance may not be required. |  |  |  |

FORMAT - III

ACQUISITION OF LAND FOR SUB-STATION

| SL. NO. | NAME OF THE SUB-STATION | WHETHER APPLICATION FOR ACQUISITION OF LAND FORWARDED TO COMPETENT AUTHORITY | WHETHER ORDERS ISSUED BY THE STATE GOVERNMENT | FINALLY WHETHER LAND HAS BEEN ACQUIRED | SPECIFY IF LAND IS AVAILABLE |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |
| 1. | 2X50MVA 132/33kV Grid Substation, Kutra | The proposed installation shall be constructed by conversion of the existing 132kV switching station land of OPTCL at Kutra into a 132/33kV, 2×50 MVA Grid Sub-station at Kutra |  |  |  |

FORMAT - IV

FOREST AND ENVIRONMENT CLEARANCE

| SL. NO. | DETAILS OF SCHEME | WHETHER SURVEY COMPLETED | WHETHER APPLICATION FOR CLEARANCE FORWARDED TO STATE GOVT. | WHETHER APPLICATION FORWARDED TO CENTRAL GOVT. | RECEIPT OF FOREST AND ENVIRONMENTAL CLEARANCE |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |  |
| 1. | Conversion of 132kV Kutra Switching Station to 2X50MVA 132/33kV Grid Substation, Kutra | No forest land involved in this project. The Environmental Impact Assessment Study report is annexed. |  |  |  |

FORMAT - V

FINANCIAL BENEFITS

| SL. NO. | NAME OF SCHEME | TOTAL LOSSES BEFORE IMPLEMENTATION OF THE SCHEME (MW) | TOTAL LOSSES AFTER IMPLEMENTATION OF THE SCHEME (MW) | REDUCTION IN TRANSMISSION LOSSES (MW) | UNITS TO BE SUPPLIED TO THE SYSTEM (LU) | 1] REVENUE DUE TO SALE OF ENERGY 2] REVENUE DUE TO REDUCTION OF LOSSES [Rs. IN LAKHS] | REMARKS |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| 1. | “Conversion of 132kV Kutra Switching Station to 2X50MVA 132/33kV Grid Substation, Kutra" | 1112.009421 | 1110.649452 | 1.36 | 1911.87 + 61.48 | 458.85 Lakhs 14.75 Lakhs | Total Anticipated Annual Revenue: Rs. 4.74 Cr. |

FORMAT - VI

ANNUAL PLAN PROVISION

| SL. NO. | NAME OF SCHEME | WHETHER NECESSARY PROVISIONS HAS BEEN MADE IN CURRENT FINANCIAL YEAR | IF NOT WHETHER PROVISION IS BEING MADE IN THE NEXT YEAR | REMARKS (ANNUAL PLAN PROVISION) |
| --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 |
| 1. | Conversion of 132kV Kutra Switching Station to 2X50MVA 132/33kV Grid Substation, Kutra | Provision has been made for FY 2026-27 & 2027-28. |  |  |

FORMAT - VII

EXPENDITURE STATEMENT

| SL. NO. | NAME OF THE SCHEME | ANTICIPATED EXPENDITURE TO BE INCURRED DURING THE FINANCIAL YEARS (RS. IN CRORES) |  | TOTAL |
| --- | --- | --- | --- | --- |
|  |  | 2026-27 | 2027-28 |  |
| 1 | 2 | 3 | 4 | 5 |
| 1. | Conversion of 132kV Kutra Switching Station to 2X50MVA 132/33kV Grid Substation, Kutra | 10.29 | 24.01 | 34.30 |
| TOTAL |  | ₹ 10.29 Crores | ₹ 24.01 Crores | ₹ 34.30 Crores |

FORMAT – VIII

PROCUREMENT OF MATERIAL FOR SUB-STATION

| SL. NO. | NAME OF MATERIAL | TOTAL QUANTITY | DETAILS OF ORDER | SUPPLY SCHEDULE FOR BALANCE QUANTITY |
| --- | --- | --- | --- | --- |
|  |  | 132 KV | 132 KV | 132 KV |
| 1. | As per cost estimate | As per cost estimate | The contract for Sub-Station shall be awarded to a single party on turnkey basis. |  |

FORMAT - IX

PROCUREMENT OF MATERIALS FOR LINE

| SL. NO. | NAME OF MATERIAL | TOTAL QUANTITY | DETAILS OF ORDER | POSITION OF RECEIPT OF MATERIALS | SUPPLY SCHEDULE FOR BALANCE QUANTITY |
| --- | --- | --- | --- | --- | --- |
| 1. | N.A | N.A | N.A |  |  |