## Data Sheet (hidden)
Sl No | Description | Value | Sl No | Description | Value
1 | No of Active 132KV feeder Bays |  | 1 | Bay Extension at Sonepur | 2
2 | No of Active 132KV Transformer Bays | 2
3 | No of Spare 132KV Transformer Bays
4 | No of 132KV Bus Coupler Bays
5 | No of Spare 132KV Bays
6 | No of Active 33KV feeder Bays | 4
7 | No of Active 33KV Transformer Bays | 2
8 | No of Spare 33KV Transformer Bays
9 | No of 33KV Bus Coupler Bays | 1
10 | No of Spare 33KV Bays
11 | No of sections in 132KV Main Bus
12 | No of sections in 132KV Reserve Bus
13 | No of sections in 33KV Main Bus | 1
14 | No of sections in 33KV Reserve Bus | 1
15 | No of Station Transformers | 1
16 | Insulators for 132KV | Disc
17 | Insulators for 33KV | Disc
18 | T1S | 10
19 | T4S | 7
20 | G1 | 26
21 | G2 | 6
22 | T8S | 8
23 | T9S | 6
24 | G4 | 4
25 | G4X | 4
26 | G6 | 2
27 | 132KV Switchyard Area | 1494
28 | 33KV Switchyard Area | 1575
29 | 7m Road Between the 132KV & 33KV Switchyard | 80
30 | Length of Switchyard | 80
31 | Breadth of switchyard | 100
30

## Summary Sheet
NAME OF THE WORK:- Construction of 2 x 50 MVA, 132/33 KV Grid Sub-station, Kutra with SAS
SUMMARY
Sl. No. | Description | Amount(in Rs.)
1 | Total Cost of Materials | 202301188.6055
2 | Stock, storage & Insurance(3% on Sl. No.-01) | 6069035.6582
3 | Sub-Total(1+2) | 208370224.2636
4 | Contigency @ 3% on sl. No.03 | 6251106.7279
5 | T&P Cost @ 2% on Sl. No.03 | 4167404.4853
6 | Transportation @ 5% on Sl. NO. 03 | 10418511.2132
7 | Sub - Total Cost of Materials | 229207246.69
8 | Cost towards Erection | 10654091.6266
9 | Cost towards Civil | 103116001.3948
10 | Total Cost of Supply, Erection and Civil | 342977339.7114

## Supply
(SUPPLY) |  |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Construction of 2 x 50 MVA, 132/33 KV Sub-station Kutra with SAS
| SUBSTATION EQUIPMENTS / MATERIALS |  |  |  | GST
Sl. No. | DESCRIPTION OF ITEMS(SCHEDULE-2A-SS) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNITS | QUANTITY: Construction of 132/33 KV Sub-station with SAS (132 KV Bay-02 Nos.: 02 TRF & (33 KV Bay-06 Nos.: 03 FDR, 02 TRF, 01 B/C | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | 145 KV, 800-400-200 A,40 KA, 4 core Single Phase Current Transformer (3 Nos PX CLASS & 1 No. 0.2s CLASS) | Nos | 6 | 232701.42 | 20943.1278 | 20943.1278 | 274587.6756 | 1647526.0536 | SM-24
2 | 145 KV, 1250A, 40KA, ISOLATORS
2.1 | Single Isolator without Earth Switch | Nos | 7 | 231941.65 | 20874.7485 | 20874.7485 | 273691.147 | 1915838.029 | SM-11
2.2 | Double Isolator with Earth Switch | Nos | 0 | 534828.58 | 48134.5722 | 48134.5722 | 631097.7244 | 0 | SM-12
2.3 | Double Isolator without Earth Switch | Nos | 2 | 431137.45 | 38802.3705 | 38802.3705 | 508742.191 | 1017484.382 | SM-13
3 | Metal oxide polymer housed surge arrrestor for 132 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 6 | 29179.14 | 2626.1226 | 2626.1226 | 34431.3852 | 206588.3112 | SM-31
4 | 145 KV, 2 Core, Single Phase IVT | Nos | 0 | 163753.99 | 14737.8591 | 14737.8591 | 193229.7082 | 0 | SM-55
5 | 132 KV Bus Post Insulator | Nos | 10 | 11759.87 | 1058.3883 | 1058.3883 | 13876.6466 | 138766.466 | Technical Sanction No: 967 dt. 03/06/2022 of ED , WZ, Burla with excalation of 5% of basic price upto FY 25-26
6 | 145KV, 3150A, 40KA, SF6 Circuit Breaker with supporting Structure. Facilities for integration with SAS as per the site requirement. | Nos | 2 | 571890.4 | 51470.136 | 51470.136 | 674830.672 | 1349661.344 | SM-3
7 | 33 KV CT 31.5 KA as per TS
7.1 | 36 KV,800-400-200, 3 core Single phase Current Transformer (2 Nos PX class & 1 No. 0.2s class) | Nos | 9 | 62012.84 | 5581.1556 | 5581.1556 | 73175.1512 | 658576.3608 | SM-25
7.2 | 36 KV, 1600-800-400, 3 core Single phase Current Transformer (2 Nos PX class & 1 No. 0.2s class) | Nos | 3 | 62012.84 | 5581.1556 | 5581.1556 | 73175.1512 | 219525.4536 | SM-25
7.3 | 36 KV, 1600-800-400, 4 core Single phase Current Transformer (3 Nos PX class & 1 No. 0.2s class) | Nos | 6 | 62012.84 | 5581.1556 | 5581.1556 | 73175.1512 | 439050.9072 | SM-25
8 | 36 KV, 31.5KA,ISOLATORS
8.1 | Single Isolator without Earth Switch (1250 A, feeder ) | Nos | 6 | 113696.64 | 10232.6976 | 10232.6976 | 134162.0352 | 804972.2112 | SM-16
8.2 | Single Isolator with Earth Switch (1250 A, feeder) | Nos | 3 | 162813.38 | 14653.2042 | 14653.2042 | 192119.7884 | 576359.3652 | SM-16+ differential of SM17-2*SM16
8.3 | Single Isolator without Earth Switch (1600 A, transformer and bus coupler ) | Nos | 8 | 113696.64 | 10232.6976 | 10232.6976 | 134162.0352 | 1073296.2816 | SM-16
8.4 | Beam Mounted Single Isolator without Earth Switch(1600 A, section isolator) | Nos | 2 | 113696.13 | 10232.6517 | 10232.6517 | 134161.4334 | 268322.8668 | SM-19
8.5 | Beam Mounted Single Isolator without Earth Switch(1250 A, station supply) | Nos | 1 | 113696.13 | 10232.6517 | 10232.6517 | 134161.4334 | 134161.4334 | SM-19
9 | Metal oxide polymer housed surge arrrestor for 33 kV system. Station Class Low Duty (SL) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor - As per TS | Nos | 18 | 9416.38 | 847.4742 | 847.4742 | 11111.3284 | 200003.9112 | SM-32
10 | 36 KV, 2 Core Single Phase IVT (1 core 3P & 1 core 0.2) | Nos | 3 | 31316.46 | 2818.4814 | 2818.4814 | 36953.4228 | 110860.2684 | SM-56
11 | 36 KV,31.5KA, Vacuum Circuit Breaker with supporting Structure. Facilities for integration with SAS as per the site requirement.
11.1 | 36 KV , 1600 A Vacuum Circuit breaker with supporting Structure. Facilities for integration with SAS as per the site requirement( transformer and bus coupler ) | Nos | 6 | 222305.73 | 20007.5157 | 20007.5157 | 262320.7614 | 1573924.5684 | SM-4
12 | 33 KV Bus Post Insulator | Nos | 20 | 5824.6807 | 524.2213 | 524.2213 | 6873.1233 | 137462.4657 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
13 | BUS BAR & CIRCUIT MATERIALS
13.1 | 132KV TENSION & SUSPENSION INSULATORS
13.1.1 | 120KN Porcelain Anti Fog type Disc Insulators | Nos | 120 | 720.04 | 64.8036 | 64.8036 | 849.6472 | 101957.664 | LM Accessories -54
13.1.2 | 90KN Porcelain Anti Fog type Disc Insulators | Nos | 27 | 668.53 | 60.1677 | 60.1677 | 788.8654 | 21299.3658 | LM Accessories -53
13.2 | 33KV TENSION & SUSPENSION INSULATORS
13.2.1 | 120KN Porcelain Anti Fog type Disc Insulators | Nos | 120 | 720.04 | 64.8036 | 64.8036 | 849.6472 | 101957.664 | LM Accessories -54
13.2.2 | 90KN Porcelain Anti Fog type Disc Insulators | Nos | 54 | 668.53 | 60.1677 | 60.1677 | 788.8654 | 42598.7316 | LM Accessories -53
13.3 | ACSR CONDUCTORS
13.3.1 | ACSR Moose Conductor | km | 2 | 446927.69 | 40223.4921 | 40223.4921 | 527374.6742 | 1054749.3484 | LM-19
13.3.2 | ACSR Panther Conductor (Station Transformer connections) | Mtrs | 75 | 192.28 | 17.3052 | 17.3052 | 226.8904 | 17016.78 | LM-17
13.4 | HARDWARES FITTINGS
13.4.1 | 132 KV Single Anchoring Double Tension H/W fitting (without Turn buckle) suitable for twin ACSR Moose conductor (300mm spacing) | Nos | 0 | 5056.93 | 455.1237 | 455.1237 | 5967.1774 | 0 | LM Accessories - 10
13.4.2 | 132 KV Single Tension H/W fitting without Turn buckle suitable for single ACSR Moose | Nos | 12 | 2823.38 | 254.1042 | 254.1042 | 3331.5884 | 39979.0608 | LM Accessories - 9
12.4.3 | 132 KV Single suspension H/W fitting suitable for single ACSR Moose | Nos | 3 | 3465.33 | 311.8797 | 311.8797 | 4089.0894 | 12267.2682 | LM Accessories - 7
13.4.4 | 33 KV Single Anchoring DoubleTension H/W fitting (without Turn buckle) suitable for twin ACSR Moose (250mm spacing) | Nos | 24 | 5056.93 | 455.1237 | 455.1237 | 5967.1774 | 143212.2576 | LM Accessories - 10
13.4.5 | 33 KV Single Suspension H/W fitting suitable for twin ACSR Moose | Nos | 15 | 3465.33 | 311.8797 | 311.8797 | 4089.0894 | 61336.341 | LM Accessories - 7
13.5 | CLAMPS & CONNECTORS (Compression Type)
13.5.1 | 132 KV 'T' Clamp for Twin Moose run with single Moose ACSR drop | Nos | 0 | 2491.65 | 224.2485 | 224.2485 | 2940.147 | 0 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
13.5.2 | 132 KV 'T' Clamp for Single Moose run with single Moose ACSR drop | Nos | 18 | 2491.65 | 224.2485 | 224.2485 | 2940.147 | 52922.646
13.5.3 | 132 KV 'T' Clamp for Single Panther run with single Moose ACSR drop | Nos | 0 | 2491.65 | 224.2485 | 224.2485 | 2940.147 | 0
13.5.4 | 132 KV IVT Clamp (Single Moose) | Nos | 0 | 2491.65 | 224.2485 | 224.2485 | 2940.147 | 0
13.5.5 | 132 KV CT Clamp (Bimetallic, Single Moose) | Nos | 12 | 3559.5 | 320.355 | 320.355 | 4200.21 | 50402.52
13.5.6 | 132 KV LA Clamp (Single Moose) | Nos | 6 | 2491.65 | 224.2485 | 224.2485 | 2940.147 | 17640.882
13.5.7 | 132 KV CB Clamp (Single Moose) | Nos | 12 | 6228.6 | 560.574 | 560.574 | 7349.748 | 88196.976
13.5.8 | 132 KV Isolater Pad Clamp (Single Moose) | Nos | 36 | 2491.65 | 224.2485 | 224.2485 | 2940.147 | 105845.292
13.5.9 | 132 KV Isolator pad clamp for Section Isolators (Twin Moose type) | Nos |  | 2491.65 | 224.2485 | 224.2485 | 2940.147 | 0
13.5.10 | 132 KV PI Clamp (Single Moose) | Nos | 10 | 2491.65 | 224.2485 | 224.2485 | 2940.147 | 29401.47
13.5.11 | Spacer for Twin 132 KV Bus (Moose) | Nos | 10 | 1769.39 | 159.2451 | 159.2451 | 2087.8802 | 20878.802 | LM-51
13.5.12 | 33 KV 'T' Clamp for Twin Moose run with single Moose ACSR drop | Nos | 69 | 2491.65 | 224.2485 | 224.2485 | 2940.147 | 202870.143 | Technical Sanction Order - ED (Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
13.5.14 | 33 KV IVT Clamp (Twin Moose) | Nos | 3 | 1339.8 | 120.582 | 120.582 | 1580.964 | 4742.892
13.5.15 | 33 KV CT Clamp (Bimetallic, Single Moose) | Nos | 30 | 1339.8 | 120.582 | 120.582 | 1580.964 | 47428.92
13.5.16 | 33 KV LA Clamp (Twin Moose) | Nos | 18 | 1339.8 | 120.582 | 120.582 | 1580.964 | 28457.352
13.5.17 | 33 KV CB Clamp (Twin Moose) | Nos | 0 | 2491.65 | 224.2485 | 224.2485 | 2940.147 | 0
13.5.18 | 33 KV Isolator pad clamp | Nos | 54 | 1339.8 | 120.582 | 120.582 | 1580.964 | 85372.056
13.5.19 | 33 KV Isolator pad clamp for Section Isolators (Twin Moose Type) | Nos | 0 | 1339.8 | 120.582 | 120.582 | 1580.964 | 0
13.5.20 | 33 KV Isolator pad clamp for Station Transformer Isolators ( Single ACSR Panther) | Nos | 0 | 1339.8 | 120.582 | 120.582 | 1580.964 | 0
13.5.21 | 33 KV PI Clamp | Nos | 20 | 1102.5 | 99.225 | 99.225 | 1300.95 | 26019
13.5.22 | Spacer for Twin 33 KV Bus (Moose) | Nos | 19 | 1769.39 | 159.2451 | 159.2451 | 2087.8802 | 39669.7238 | LM-51
13.5.23 | PG Clamp for ACSR Moose (Two Bolted) | Nos | 50 | 1102.5 | 99.225 | 99.225 | 1300.95 | 65047.5 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
14 | Substation Earthing Systems (The qty for the earthing materials shall be as per the approved earthing design calculations based on the soil resistivity of the project area). This also includes the the water piping network to each earth pit.
14.1.1 | Earthing Conductor for Earth Mat: 75 x 10 mm GI Flat. | MT | 22 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 2426011.0644 | LM-4
14.1.2 | Earthing Conductor for risers: 50 x 6 mm GI Flat | MT | 24 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 2646557.5248 | LM-4
14.1.3 | 50 mm Heavy Duty GI Perforated Pipes, 3 mtrs long for treated earth pit | Nos | 140 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 376817.896 | LM-8
14.1.4 | Supply of UPVC Pipes (2", 1.5", 1" & 1/2" etc), Joints, bends, Valves and all accessories for spreading the water network to each treated earth pit as per approved drawing. | LOT | 1 | 200000 | 18000 | 18000 | 236000 | 236000 | market price
14.1.5 | Switchyard buildings lightning protection (all materials & accessories like Shielding Wire, PG clamp, Test link, D shackle, Aluminium Flats & other required materials etc) as per IS/National Building code standard and as per approved drawing | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | market price
15 | G.I Cable Trays including G.I. support Angle suitable for different sections i.e. Section: 2-2, 3-3 & 4-4 along with its accessories as per TS. | [7 empty] | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
15.1 | G.I Cable Trays(size: 450x75x2500mm) | Mtrs | 400 | 781.2 | 70.308 | 70.308 | 921.816 | 368726.4
15.2 | G.I Cable Trays(size: 300x75x2500mm) | Mtrs | 500 | 624.75 | 56.2275 | 56.2275 | 737.205 | 368602.5
15.3 | G.I Cable Trays(size: 150x75x2500mm) | Mtrs | 300 | 469.35 | 42.2415 | 42.2415 | 553.833 | 166149.9
15.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 1.5 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 165409.8453 | LM-8
16 | SWITCH YARD STRUCTURES COLUMN & BEAM (LATTICE TYPE) FOR 132/33 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS. (Weight in brackets are only indicative - Actual weight shall be as per approved BOM. Measurement shall be done accordingly.)
16.1 | DIFFERENT TYPES OF COLUMNS WITH DETAILS - With Spike
16.1.1 | T1S - 132 KV(Nominal unit wt- 1.2 MT) =10 Sets | MT | 12
16.1.2 | T4S - 132KV (Nominal unit wt- 0.95 MT) =7 Sets | MT | 6.65
16.1.3 | T8S - 33KV(Nominal unit wt- 0.83 MT) = 8 Sets | MT | 6.64
16.1.4 | T9S - 33KV(Nominal unit wt- 0.6 MT)=6 Sets | MT | 3.6
16.2 | DIFFERENT TYPE OF BEAMS WITH DETAILS
16.2.1 | G1 - 132 KV(Nominal unit wt- 0.62 MT) = 26 Sets | MT | 16.12
16.2.2 | G2 - 132 KV(NOMINAL UNIT WT- 0.9 MT) =6 Sets | MT | 5.4
16.2.3 | G6 - 33KV (NOMINAL UNIT WT- 0.53 MT) = 2 Sets | MT | 1.06
16.2.4 | G4 - 33KV(NOMINAL UNIT WT- 0.4 MT) =4 Sets | MT | 1.6
16.2.5 | G4X - 33KV (NOMINAL UNIT WT- 0.52 MT) =4 Sets | MT | 2.08
16.3 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 55.15 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 6081568.6455 | LM-8
16.4 | SWITCH YARD EQUIPMENT STRUCTURES (LATTICE TYPE) FOR 132/33 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS.
16.4.1 | Structure for 132KV CT (Unit Weight - 214.546 Kg) =6 Nos | MT | 1.287
16.4.2 | Structure for 132KV IVTs (Unit Weight - 231.195 Kg) =0 Nos | MT | 0
16.4.3 | Structure for 132KV Surge Arrester (Unit Weight - 179.893 Kg) =6 Nos | MT | 1.0788
16.4.4 | 132 KV Single Isolator without Earth Switch (Unit weight - 658.767 Kg) = 7 Nos | MT | 4.6109
16.4.5 | 132 KV Double Isolator without Earth Switch (Unit Weight - 979.10 Kg) = 2 Nos | MT | 1.9582
16.4.6 | 132 KV Double Isolator with Earth Switch (Unit Weight - 1120.559 Kg) = 0 Nos | MT | 0
16.4.7 | Structure for 132KV BPI (Unit Weight - 309.883 Kg) =10 Nos | MT | 3.098
16.4.8 | Structure for 33KV CT (Unit Weight - 148.80 Kg) =9 Nos | MT | 1.3392
16.4.9 | Structure for 33KV IVTS (Unit Weight - 124.336 Kg) =3 Nos | MT | 0.3729
16.4.10 | Structure for 33KV LAs (Unit Weight - 148.8 Kg) =3 Nos | MT | 0.4464
16.4.11 | 33 KV Single Isolator without Earth Switch (1250 A, feeder ) (Unit weight - 294.893 Kg) = 6 Nos | MT | 1.7694
16.4.12 | 33 KV Single Isolator with Earth Switch (1250 A, feeder)(Unit weight - 324.8 Kg) = 3 Nos | MT | 0.9744
16.4.13 | Structure for 33KV BPI (Unit Weight - 148.80 Kg) =14 Nos | MT | 2.0832
16.4.14 | Structure for 33KV HG Fuse (Unit Weight - 245 Kg) =1 Sets | MT | 0.245
16.5 | TOTAL WEIGHT OF EQUIPMENT STRUCTURE | MT | 19.2634 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 2124237.3426 | LM-8
16.6 | Total weight of GI Nuts and bolts for the above Column, Beam & equipment structures and including different size of plain washer / spring washer for above structures. | MT | 3.7207 | 118560.66 | 10670.4594 | 10670.4594 | 139901.5788 | 520527.6072 | LM-5
17 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
17.1 | POWER CABLES, 1.1KV, FRLSH XLPE/PVC ARMOURED, ALUMINIUM CONDUCTOR (As per Specification)
17.1.1 | XLPE 3.5 CX300 mm2 | Mtrs | 320 | 1027.095 | 92.4385 | 92.4385 | 1211.9721 | 387831.072 | SM-134 | 800
17.1.2 | XLPE 3.5 CX185 mm2 | Mtrs | 320 | 488.679 | 43.9811 | 43.9811 | 576.6412 | 184525.1904 | SM-132 | 800
17.1.3 | XLPE 3.5 CX120 mm2 | Mtrs | 400 | 459.115 | 41.3203 | 41.3203 | 541.7557 | 216702.28 | SM-131 | 1000
17.1.4 | PVC 3.5 CX70 mm2 | Mtrs | 480 | 265.69 | 23.9121 | 23.9121 | 313.5142 | 150486.816 | SM-129 | 1200
17.1.5 | PVC 3.5 CX35 mm2 | Mtrs | 480 | 147.505 | 13.2754 | 13.2754 | 174.0559 | 83546.832 | SM-127 | 1200
17.1.6 | PVC 4 CX 16 mm2 | Mtrs | 400 | 115.785 | 10.4207 | 10.4207 | 136.6263 | 54650.52 | SM-125 | 1000
17.1.7 | PVC 4 CX 6 mm2 | Mtrs | 1000 | 116.172 | 10.4555 | 10.4555 | 137.083 | 137082.96 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024 | 2500
17.1.8 | PVC 2CX 6 mm2 | Mtrs | 640 | 102.9 | 9.261 | 9.261 | 121.422 | 77710.08 |  | 1600
17.2 | CONTROL CABLES, 1.1 KV, PVC, FRSLH Armoured, STRANDED COPPER (As per specification)
17.2.1 | 2 CX 2.5 mm2 | Mtrs | 1400 | 55.924 | 5.0332 | 5.0332 | 65.9903 | 92386.448 | SM-115 | 3500
17.2.2 | 4 CX 2.5 mm2 | Mtrs | 1000 | 103.221 | 9.2899 | 9.2899 | 121.8008 | 121800.78 | SM-118 | 2500
17.2.3 | 5 CX 2.5 mm2 | Mtrs | 1200 | 220.5 | 19.845 | 19.845 | 260.19 | 312228 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024 | 3000
17.2.4 | 7CX 2.5 mm2 | Mtrs | 1400 | 171.043 | 15.3939 | 15.3939 | 201.8307 | 282563.036 | SM-119 | 3500
17.2.5 | 10 CX 2.5 mm2 | Mtrs | 2600 | 264.2955 | 23.7866 | 23.7866 | 311.8687 | 810858.594 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024 | 6500
17.2.6 | 12 CX 2.5 mm2 | Mtrs | 2200 | 289.733 | 26.076 | 26.076 | 341.8849 | 752146.868 | SM-121 | 5500
17.2.7 | 16 CX 2.5 mm2 | Mtrs | 1400 | 366.057 | 32.9451 | 32.9451 | 431.9473 | 604726.164 | SM-122 | 3500
17.2.8 | 19 CX 2.5 mm2 | Mtrs | 640 | 440.548 | 39.6493 | 39.6493 | 519.8466 | 332701.8496 | SM-123 | 1600
17.3 | SINGLE CORE 1.1KV, PVC UN-ARMOURED COPPER CONDUCTOR: for connection from Battery Set to Battery Charger and from Battery Charger to DCDB on cable tray / HDPE pipe/PVC pipe etc
17.3.1 | 1CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | Mtrs | 240 | 666.75 | 60.0075 | 60.0075 | 786.765 | 188823.6 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024 | 600
18 | Supply of screened / Shielded Twisted pair copper cable for Analog Communication for showing winding temp, Oil temp,lighting, fire fighting, DG etc, LT current & LT voltage signals of sub-station auxiliary system in HMI
18.1 | 8PX1.5 mm2 screened copper cable | Mtrs | 200 | 296 | 26.64 | 26.64 | 349.28 | 69856 | Market | 500
18.2 | 2PX1.5 mm2 screened copper cable | Mtrs | 80 | 59.322 | 5.339 | 5.339 | 70 | 5600 |  | 200
19 | SUPPLY OF POWER TRANSFORMER, NCTs & OTHER ACCESSORIES AS PER TECHNICAL SPECIFICATION
19.1 | 132/33 KV, 63 MVA Yn Yn Power Transformer in cluding NCTs and other accessories & as per TS | Nos | 2 | 50750000 | 4567500 | 4567500 | 59885000 | 119770000
19.2 | The following type tests shall be carried out in presence of Purchaser’s representative on entire quantity of the Transformer. (a) Temperature Rise Test. (b) Measurement of Zero Sequence Impedance. (c) Auxiliary Power Consumption.. (d) Vacuum Test (e) Pressure Test (f) IP-55 Test | Lot | 1 | 1000000 | 90000 | 90000 | 1180000 | 1180000
19.3 | FIRE FIGHTING (Nitrogen Injection Type Fire Prevention & Extinguishing System): Suitable for 80 MVA, 132/33 KV Power Transformer as per Technical Specification & latest standard. | Lot | 2 | 2000000 | 180000 | 180000 | 2360000 | 4720000
19.4 | Online Drying out system for 80MVA, 132/33KV Power transformers | Set | 2 | 1500000 | 135000 | 135000 | 1770000 | 3540000
19.5 | Digital RTCC Panel: Having two integrated RTCC modules for OLTC control and transformer monitoring for two transformers. The RTCC modules shall be SAS compatible and as per TS. There shall be cutouts for two more RTCC modules in the panel. | Lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000
20 | SUPPLY OF STATION TRANSFORMER & OTHER MATERIALS FOR MEETING THE AUXILIARY SUPPLY OF THE SUB-STATION AS PER TECHNICAL SPECIFICATION
20.1 | Station Transformer - 33KV/433V, 250 KVA (As per Specification) | Nos | 1 | 621983.94 | 55978.5546 | 55978.5546 | 733941.0492 | 733941.0492 | SM-68
20.2 | HG Fuse set- for 33kV side of the station transformer including the mounting insulators, channels complete in all respect (each set comprises three single HG fuse) | Sets | 1 | 10047.45 | 904.2705 | 904.2705 | 11855.991 | 11855.991 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
21 | SUBSTATION AUTOMATION SYSTEM (IEC 61850)
21.1 | "SUBSTATION AUTOMATION SYSTEM (IEC 61850) Gateway Panel ( 2 layer type) : for Sub-Station Automation (in PRP on FO as per the specification) system (for All 132 & 33 KV side bays) and with other accessories, comprising: 1. Gateway (Non-Windows or Linus or Firmware based)- 2 nos. with 8 ethernet ports each 2. BCU for Substation Auxilliary System (Station AC, Station DC, Lighting, Fire fighting, Diesel generator etc.) 3. Ethernet Switches (with 20% spares Port) for bay & station level 4. LIU 5. Multimode glass fibre Doublle jacket armoured optical cables 6. Red boxes etc. including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. | Lot | 1 | 1650000 | 148500 | 148500 | 1947000 | 1947000 |  | 693904.07
21.2 | RTCC Communication Panel (3 layer type) ; comprising of: 1. Substation Ethernet Switches- 2 nos 2. Firewall cum Router-2 set 3. Station Data Concentrator (SDC)- 2 nos 5. LIU 6. Multimode glass fibre Double jacket armoured optical cables 7. Red boxes etc. 8. Provision for mounting the VMS switch etc including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect for remote communication & as per technical specification. | SET | 1 | 1650000 | 148500 | 148500 | 1947000 | 1947000 | 776764.74 | 346952.035
21.3 | Operator Workstations | Nos | 2 | 112548.85 | 10129.3965 | 10129.3965 | 132807.643 | 265615.286 | SM-39((Additional bay level cost data)
21.4 | Engineering workstation | Nos | 1 | 112548.85 | 10129.3965 | 10129.3965 | 132807.643 | 132807.643 | SM-39(Additional bay level cost data)
21.5 | Workstation for RAS (Remote Access System) | Nos | 1 | 112548.85 | 10129.3965 | 10129.3965 | 132807.643 | 132807.643 | SM-39(Additional bay level cost data)
21.6 | Colour Laser jet Printer-1Nos | Nos | 1 | 60420.96 | 5437.8864 | 5437.8864 | 71296.7328 | 71296.7328 | SM-40(Additional bay level cost data)
21.7 | Inverters - 3 KVA (Main & Stand by) | Nos | 2 | 183632.33 | 16526.9097 | 16526.9097 | 216686.1494 | 433372.2988 | SM-41(Additional bay level cost data)
21.8 | Furniture (Operator desk 3 Nos (for SAS, RAS, VMS) & Chair-6Nos) etc. | Lot | 1 | 250000 | 22500 | 22500 | 295000 | 295000 | Market price
21.9 | GPS System with IRIG-B/SNTP/PTP with VDU (Clock) | Nos | 1 | 124396.09 | 11195.6481 | 11195.6481 | 146787.3862 | 146787.3862 | SM - 42 (Additional bay level cost data)
21.1 | 132KV Level Protection Panel- Single Panel Type with IEC 61850-ED-2 PRP on FO
21.10.1 | 132KV feeder Protection: Numerical Distance protection relay, BCU, separate backup relay and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | Nos |  | 1219192.69 | 109727.3421 | 109727.3421 | 1438647.3742 | 0 | SM-42/2
21.10.2 | 132KV Transformer Protection: Numerical Differential protection relay, BCU, separate backup relay, separate Numerical REF relay (high impedance type) and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | Nos | 2 | 1523990.86 | 137159.1774 | 137159.1774 | 1798309.2148 | 3596618.4296 | SM-44/2 | SM-44
21.10.3 | 132KV Buscoupler Protection: BCU, separate backup realy and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | Nos |  | 711195.73 | 64007.6157 | 64007.6157 | 839210.9614 | 0 | SM-45
21.11 | 33KV Level Protection Panel- Single Panel Twin Bay Type (2 Bays in One Panel) with IEC 61850-ED-2 PRP on FO, 5 nos of line feeders, 2nos of transformer feeders and one bus coupler bay protection shall be accomodated in 4 nos of panels. The sequence of bays shall be as per the approved SLD.
21.11.1 | 33KV Feeder Protection: with BCPU & separate backup realy & with other Auxiliary relays as required as per the scheme compliant to IEC 61850 - ED-2 protocol with PRP on FO. Power Supply 220V DC. 33KV Transformer protection panel: with BCPU, separate backup realy, separate REF relay & with other Auxiliary relays as required as per the scheme, compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. 33KV Buscoupler Protection Panel: with BCPU & separate backup realy & with other Auxiliary relays as required as per the scheme compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | Nos | 3 | 1219192.6875 | 109727.3419 | 109727.3419 | 1438647.3712 | 4315942.1137 | (SM-47+SM48)/4
22 | AC & DC SYSTEM : All Indoor Panels with 2 mm CRCA sheet and 3 mm CRCA gland plate painted & as per TS All Outdoor Panels, Sub Station Swithyard Console Boxes, HDG type (86 micron), 3 mm thick CRCA, as per TS.
22.1 | AC SYSTEM
22.1.1 | MAIN AC DB ( Indoor Type): MAIN DB-1, MAIN DB-2 with B/C. The incomer & Bus coupler shall have 800 A, 50KA, drawout type with Numerical SAS compliant Relay (O/C, E/F, U/V, O/V protection).The ACDB shall be suitable for automatic switching OFF & ON during power failure. Facilities for integration with SAS as per the site requirement. | Set | 1 | 375905.74 | 33831.5166 | 33831.5166 | 443568.7732 | 443568.7732 | SM-78
22.1.2 | ACDB (Indoor Type): AC DB-1, AC DB-2 with B/C. Incomer-1 & 2, Bus coupler and DG set Incomer-1 shall have 400A Motorised MCCB for automatic operation. The ACDB shall be suitable for automatic switching OFF & ON , auto start of DG set etc during power failure. Facilities for integration with SAS as per the site requirement. | Set | 1 | 375905.74 | 33831.5166 | 33831.5166 | 443568.7732 | 443568.7732 | SM-78
22.1.3 | Main Lighting Distribution Board (Indoor Type): Having 250A MCCB for Incomers with source-1, Source-2 & Bus coupler. | Set | 1 | 375905.74 | 33831.5166 | 33831.5166 | 443568.7732 | 443568.7732 | SM-78
22.1.4 | Indoor Lighting Distribution Board (Indoor Type) | Set | 1 | 375905.74 | 33831.5166 | 33831.5166 | 443568.7732 | 443568.7732 | SM-78
22.1.5 | Emergency Lighting Distribution Board (Outdoor type): The ELDB should be supplying to 20% of switchyard lights, each of 132KV and 33KV Switchyard. | Set | 1 | 375905.74 | 33831.5166 | 33831.5166 | 443568.7732 | 443568.7732 | SM-78
22.1.6 | Indoor Receptacle Board | Set | 1 | 49758.44 | 4478.2596 | 4478.2596 | 58714.9592 | 58714.9592 | SM-34 (Additional bay level cost data)
22.1.7 | Bay Marshalling Kiosk (Outdoor type): 1 BMK for 2 nos 132KV bays and 1 BMK for 3 nos 33KV bays | Nos | 7 | 150362.04 | 13532.5836 | 13532.5836 | 177427.2072 | 1241990.4504 | SM-76
22.1.8 | Console Box for Switchyard Lighting (Outdoor type) | Nos | 2 | 45108.48 | 4059.7632 | 4059.7632 | 53228.0064 | 106456.0128 | SM-75
22.1.9 | Console Box for Street Lighting (Outdoor type) | Nos | 2 | 45108.48 | 4059.7632 | 4059.7632 | 53228.0064 | 106456.0128
22.1.10 | Console Box for Colony Supply (Outdoor type) | Nos | 1 | 45108.48 | 4059.7632 | 4059.7632 | 53228.0064 | 53228.0064
22.1.11 | Switchyard Receptacle Board for Transformer Oil Filtration (Outdoor type) | Nos | 1 | 49758.44 | 4478.2596 | 4478.2596 | 58714.9592 | 58714.9592 | SM-34 (Additional bay level cost data)
22.1.12 | Switchyard Receptacle Board for Welding & Other Emergency (Outdoor type) | Nos | 2 | 49758.44 | 4478.2596 | 4478.2596 | 58714.9592 | 117429.9184
22.1.13 | CT Out Door Console Boxes ( 132 KV CT-2 Nos, 33 KV CT-7 Nos) (Outdoor type) | Nos | 9 | 45108.48 | 4059.7632 | 4059.7632 | 53228.0064 | 479052.0576 | SM-75
22.1.14 | PT Out Door Console Boxes (132 KV IVT-0 No., 33 KV IVT-1 No.) (Outdoor type) | Nos | 1 | 45108.48 | 4059.7632 | 4059.7632 | 53228.0064 | 53228.0064 | SM-75
22.1.15 | Outdoor kiosk for Station Transformer (Outdoor type) | Nos | 2 | 150362.04 | 13532.5836 | 13532.5836 | 177427.2072 | 354854.4144 | SM-76
22.1.16 | ACDB for Yard Kiosk (Indoor Type): LT supply to Protection panels, Kiosk lighting, AC etc made of 2mm CR sheet | Nos | 2 | 49758.44 | 4478.2596 | 4478.2596 | 58714.9592 | 117429.9184 | SM-34 (Additional bay level cost data)
22.1.17 | DCDB for Yard Kiosk (Indoor Type): DC supply to Protection panels having source-1 & 2 with auto changeover facility, made of 2mm CR sheet. | Nos | 2 | 49758.44 | 4478.2596 | 4478.2596 | 58714.9592 | 117429.9184 | SM-35 (Additional bay level cost data)
22.2 | DC SYSTEM
22.2.1 | 220 V DC DISTRIBUTION BOARD (Indoor Type): Having 63A DC MCCB for Incomers, Bus Coupler with interlock, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE and shall be SAS compliant. | Set | 1 | 375905.74 | 33831.5166 | 33831.5166 | 443568.7732 | 443568.7732 | SM-79
22.2.2 | 220 V DC Emergency Lighting Distribution Board (Indoor Type) | Set | 1 | 375905.74 | 33831.5166 | 33831.5166 | 443568.7732 | 443568.7732 | SM-79
22.2.3 | Battery cells (2.2V), 350 AH Plante Type for 220 V DC (107 Nos + 3 Nos spare) | Set | 1 | 2043381.24 | 183904.3116 | 183904.3116 | 2411189.8632 | 2411189.8632 | SM-71
22.2.4 | Battery Charger For 350 Ah Plante Type Battery, 107 cells, 2.2V, Trickle charge volt-2.25V(Float & Float Cum Boost). The Charger ON/OFF status, input/output voltage, output current, associated charger protection signals shall be provided for integration with SAS. | Set | 1 | 400396.18 | 36035.6562 | 36035.6562 | 472467.4924 | 472467.4924 | SM-72
23 | ACCESSORIES FOR OPGW SYSTEM With OPGW cable
23.1 | 48 Fibre Optic Approach cable along with HDPE Pipes | Km | 1 | 215500 | 19395 | 19395 | 254290 | 254290 | Telecom -25
23.2 | Optical line Terminal Equipment(OLTE) -STM4 type SDH equipment with integrated MUX & tributary cards for speech & data ports for interfacing of Speech & data which should be compatible with existing OPTCL system including all accessories for successful commissioning. | No | 1 | 1745658.4 | 157109.256 | 157109.256 | 2059876.912 | 2059876.912 | Telecom-44
23.3 | Supply of FODP(Fibre Optic Distribution Panel)48 F: Indoor type,rack mounted with FCPC coupling and pig tails(DWSm Fibre) | No | 1 | 54256.95 | 4883.1255 | 4883.1255 | 64023.201 | 64023.201 | Telecom-29
23.4 | Digital tele-protection coupler with accessories compatible for interfacing with SDHMUX | Nos. | 2 | 395676 | 35610.84 | 35610.84 | 466897.68 | 933795.36 | Telecom-22
23.5 | 48 V, 300 AH, maintenance free VRLA Battery set. | Set | 1 | 119332.12 | 10739.8908 | 10739.8908 | 140811.9016 | 140811.9016 | Telecom-2
23.6 | SMPS based battery charger of 75A suitable for 48V VRLA battery. | No | 1 | 110881.51 | 9979.3359 | 9979.3359 | 130840.1818 | 130840.1818 | Telecom-18
23.7 | 48V DCDB | Nos | 1 | 49758.44 | 4478.2596 | 4478.2596 | 58714.9592 | 58714.9592 | SM-35 (Additional bay level cost data)
23.8 | Earth Flat, Cable Tray, Foundation rail, Junction Box,. | Set | 1 | 133969.5 | 12057.255 | 12057.255 | 158084.01 | 158084.01 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
24 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS) (Switch yard and other street area)
24.1 | SWITCHYARD LIGHTING- Includes supply of LED type Fixtures & Lamps of reputed make (Philips/CGL/Bajaj/Havells/Crompton/Wipro) with switch gear, GI Conduit etc. (Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved. | Set | 15 | 15406.65 | 1386.5985 | 1386.5985 | 18179.847 | 272697.705 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
24.2 | STREET LIGHTING: HDG Octagonal street lighting poles 7 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. The pole shall be manufactured in a single section with weight of galvanization 610 g/sqm or thickness of galvanization 86 micron. The pole shall be meant for installation in Wind Zone V. Poles should be suitable for installation on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes supply of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/ Havells/ Osram/Wipro), with switch gear, GI Conduit etc. & as per technical specification. The pole shall have separate or inbuilt GI junction box with suitable cover with (water/dust) ingress protection for housing electrical accessories. The JB shall have provision of fuses/MCB, buses, TBs as required for cable in and out. | Set | 20 | 32420.85 | 2917.8765 | 2917.8765 | 38256.603 | 765132.06 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
24.2 | Lighting provision for other Areas: Suitable for (a) Main Gate Lighting (2 nos of 70 Watt LED), (b) Garden Lighting (4 nos of 70W LED) with necessary post top lantern with pole , (c) Control Room Building peripheral Lighting (4 nos of 70W LED). | Lot | 1 | 157500 | 14175 | 14175 | 185850 | 185850 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
25 | AIR CONDIONER: Supply of 2T capacity Split Air Conditioning Units (Dual Inverter, five star or better type latest model) with copper condensor having remote temperature & operation control facility. AC Control Panel made of 2mm CR sheet, having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (As per specification) for Control/SAS Room, ACDC Room Communication room, office room & Conference room . The ACs in the ACDC Room(04 nos) shall run in tandem i.e 2 ACs at a time for 4 hours each. Suitable control arrangement shall be made using 24hr timer for start and stop. Similarly, for Control Room (2 ACs) and Communication Room (2ACs), one AC at a time for 4 hours each. One AC each in office rooms(2 nos), Conference Room, Transit Room.
25.1 | AC for Control Room Building | Set | 12 | 68250 | 6142.5 | 6142.5 | 80535 | 966420 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
25.2 | AC for Switchyard Kiosk | Set | 4 | 68250 | 6142.5 | 6142.5 | 80535 | 322140
25.3 | AC For Transit House | Set | 4 | 68250 | 6142.5 | 6142.5 | 80535 | 322140
26 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED Sets FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-INST TO BIDDER BEFORE DESIGN-SL NO 16-ANNEXURE - I)
26.1 | FOAM TYPE-9 LTRS | Nos | 4 | 5987.1 | 538.839 | 538.839 | 7064.778 | 28259.112 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
26.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 25 KGS | Nos | 4 | 46212.6 | 4159.134 | 4159.134 | 54530.868 | 218123.472
26.3 | DRY POWDER TYPE -6 KGS | Nos | 4 | 6434.4 | 579.096 | 579.096 | 7592.592 | 30370.368
26.4 | CO2 - 4.5 KGS | Nos | 10 | 13404.3 | 1206.387 | 1206.387 | 15817.074 | 158170.74
26.5 | CO2 - 9 KGS | Nos | 10 | 20590.5 | 1853.145 | 1853.145 | 24296.79 | 242967.9
26.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | Nos | 4 | 34505.1 | 3105.459 | 3105.459 | 40716.018 | 162864.072
26.7 | Water type- 9 LTRS | Nos | 4 | 5720.4 | 514.836 | 514.836 | 6750.072 | 27000.288
26.8 | Foam type - 50 LTR | Nos | 4 | 39196.5 | 3527.685 | 3527.685 | 46251.87 | 185007.48
26.9 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND With Canopy arrangement | Set | 6 | 8898.75 | 800.8875 | 800.8875 | 10500.525 | 63003.15
27 | Maintenance Testing Equipment (All equipment shall comply to the TS and as per list below) | Lot | 1 | 525000 | 47250 | 47250 | 619500 | 619500
27.1 | 100KV Automatic Transformer Oil Breakdown Voltage test set (Megger- OTS 100AF / Baur- DTA 100C) | Nos | 1
27.2 | 10KV Insulation Tester with 15m test lids (Megger- S1-1068 / Sonel-MIC 10K1) | Nos | 1
27.3 | Digital Earth Tester (Facility with soil resistivity measurement) (Megger-DET2/3 / Sonel MRU-120 / Fluke 1625) | Nos | 1
27.4 | Digital Multimeter (Megger / Fluke) | Nos | 2
27.5 | Digital Clamp meter (Megger/Fluke/Motwane) | Nos | 1
27.6 | Leakage current clamp meterAC & DC both (30mA / 300mA / 30A / 300A) (Megger/Fluke/Kyoritsu) | Nos | 1
27.7 | SF6 Gas Leakage Detector (Kika/DILO) | Nos | 1
27.8 | Oil sampling Bottle- Stainless Steel, Capacity- 1 Ltr (Make- Tosin) | Nos | 6
27.9 | Fibre Glass Discharge / Earth Rod: Grip up to 50mm, Min height-16ft, rubber grip, 35 sq.mm copper cable (1 set- 3 cables, 1 set of rod, carry bag) (Bemico) | Set | 6
27.1 | Electrical Rubber Hand Gloves | Pairs | 4
27.11 | Portable High Beam Light (rechargeable) | Nos | 2
27.12 | Desktop Computer: (HP/Lenovo/Dell) | Set | 2
Processor-Intel Core i5 10th Gen or better
RAM- 8GB DDR4 or More
ROM- 512GB SSD
Monitor- 21.5" FHD (1920 x 1080) or higher
Graphics- Intel UHD
OS- Genuine Windows 10 or 11 Pro
27.13 | Webcam- 720P Logitech | Nos | 2
27.14 | Speaker- 2 nos Stereo type | Nos | 2
27.15 | UPS 600VA (APC/V Guard) | Nos | 2
27.16 | Laser Printer, Black & White, Duplex printing (print, scan & copy) (HP/Canon/Epson) | Nos | 1
28 | Other Tools And Plants (T&P'S) Requirement (As Per details below). The T & P materials shall be of Taparia/Bosch/Stanley make. | lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | Market
28.1 | D Spanner Set (6mm – 42mm) | Set | 1
28.2 | Ring Spanner Set (6mm – 42mm) | Set | 1
28.3 | Box spanner set | Set | 1
28.4 | Pipe Wrench 24 " | Nos | 1
28.5 | Pipe Wrench 18 " | Nos | 1
28.6 | Adjustable spanner -12”(slide wrench) | Nos | 1
28.7 | Adjustable spanner -18”(slide wrench) | Nos | 1
28.8 | Insulated cutting plier (standard size) | Nos | 1
28.9 | Nose Plier (standard size) | Nos | 1
28.10 | Screw Driver set
28.10.1 | 12” Plain head | Nos | 2
28.10.2 | 12” star head | Nos | 2
28.10.3 | 8” Plain head | Nos | 2
28.10.4 | 6” plain head | Nos | 2
28.10.5 | 6” star head | Nos | 2
28.10.6 | Set of screw driver cum line tester | Set | 1
28.10.7 | Allen Key set | Set | 1
28.11 | Files
28.11.1 | Flat File-12” | Nos | 1
28.11.2 | Flat file-6” | Nos | 1
28.11.3 | Round file- 12” | Nos | 1
28.11.4 | Round file- 6” | Nos | 1
28.12 | Hammer with Handle
28.12.1 | 1 lb | Nos | 2
28.12.2 | 2 lb | Nos | 1
28.12.3 | ½ lb | Nos | 2
28.13 | Steel Tape (Any reputed make)
28.13.1 | 5Mtr | Nos | 1
28.13.2 | 30Mtr | Nos | 1
28.14 | Crow bar (Any reputed make)
28.14.1 | 5ft | Nos | 2
28.14.2 | 3ft | Nos | 2
28.15 | Oil Cane (Any reputed make) | Nos | 2
28.16 | Hand Drill Machine (impact drill) with key (Make-Bosch/Black & Decker) | Nos | 1
28.17 | Vacuum Cleaner (at least 15L) (Make-Eureka Forbes / Black & Decker / Phillips / Karcher) | No | 1 | [5 empty] | Market
28.18 | Stand Fan (450mm sweep,1400rpm, 240V AC) (Make-Crompton, Bajaj, Havells, Almonard, Usha) | Nos | 2
28.19 | Self supproted cum extendable Ladder-25ft (FRP) of Adequate Height to be used for Maintenance of Equipment Inside Switchyard. | Nos | 1 | [5 empty] | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
28.2 | Self supproted platform Ladder- 12feet (FRP) of Adequate Height to be used for Maintenance of Equipment Inside Switchyard. | Nos | 1
29 | De-Mineralised Plant of 50 L/Hr for Making Distilled Water for Battery Banks. (Cation and anion resin bed type) | Set | 1 | 50000 | 4500 | 4500 | 59000 | 59000
30 | Storage Water Cooler (Voltas/Bluestar only) with at least 20ltr storage | Nos | 1 | 40000 | 3600 | 3600 | 47200 | 47200 | Market
31 | Water Purifier (Kent/Aquaguard/ | Nos | 1 | 20000 | 1800 | 1800 | 23600 | 23600
32 | Supply of Office Furniture: Godrej make (As per details below). | Lot | 1 | 525000 | 47250 | 47250 | 619500 | 619500 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
32.1 | For Control Room, conference room, office rooms, Library, testing room etc
32.1.1 | 5ftX3ft executive table with drawer both sides | Nos | 4
32.1.2 | 4.5ft X 2.5ft Table with one side drawer | Nos | 7
32.1.3 | Computer table suitable keeping monitor, CPU, UPS and printer with two nos revolving arm chair suitable for computer use. | Set | 1
32.1.4 | Executive revolving, adjustable (height) chairs with arm | Nos | 4
32.1.5 | Cushion fixed “S” type steel chairs with arm | Nos | 16
32.1.6 | 6ftX3ft conference table | Nos | 1
32.1.7 | Cushion arm steel chairs for conference table purpose. | Nos | 6
32.1.8 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 3
32.1.9 | 6ft height steel almirah with glass doors for library purpose | Nos | 2
32.1.10 | 6ft height (having minimum 6 lockers facility) steel cupboard with locking arrangement. | Nos | 2
32.1.11 | 4ft steel rack (minimum three selves) for keeping the files and other items. | Nos | 8
32.2 | For Communication Room | [7 empty] | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
32.2.1 | 5ftX3ft executive table with drawer both sides | Nos | 1
32.2.2 | Executive revolving, adjustable (height) chairs with arm | Nos | 1
32.2.3 | Cushion fixed “S” type steel chairs with arm | Nos | 2
32.2.4 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 1
33 | Insulating Mat: Best Quality & approved make (Confirming to IS:15652:2006) to be kept infront of all panels, boards etc.(2000X1000X3mm Size) | Nos | 40 | 2625 | 236.25 | 236.25 | 3097.5 | 123900
34 | Visual Monitering System (VMS) with Connection to OPTCL Remote Control Center: Note: Any other requirement besides above to be explored & can be finalised during detail Engg. | Lot | 1 | 1050000 | 94500 | 94500 | 1239000 | 1239000
Design and Supply for IP Based VMS (Server Based with VMS software), which shall include ONVIF Compliant Colour Cameras with Night Vision(Bullet/DoMe/PTZ), PTZ Controller, Server (Rack mounted/Tower type) Based NVR with VMS Software,VMS Client PC, NAS Storage, Mounting arrangement for cameras, cables (Armoured/Un armoured FO/Ethernet/AC/DC/HDMI etc.), HDPE Pipes, Ethernet Switches, UPS, Battery, LIU,POE Injectors, Media Converters, Surge Protection Device (SPD), Ethernet Surge Protectors (ESP), Outdoor/Indoor Junction Boxes/Panels, Main display unit (32 inch Full HD), Keyboard, Mouse, Routers, Networking Rack etc. including any other hardware or software to complete the system as per TS.
An additional display unit (32 inch Full HD) shall also be provided in the security shed for monitoring purpose as per TS.
Any other materials (Hardware & Software) required at the substation for connection of VMS system with remote control center of OPTCL including configuration of the same are also included in the scope of supply. (Configuration at Remote Control Center not the scope of the Contractor.)
Network Topology: Ring
No. of such cameras (different type viz. PTZ, bullet or dome) are to be calculated as per standard practice & its installations at the strategic locations so as to avoid blind spots.
The following areas are to be covered without any blind spots:
1. Entry and exits of Store and Equipment storage Platforms/Open stockyard - Bullet cameras
2. All entry and exits of Control room building - Bullet cameras
3. All gates of substation and switchyard - Bullet cameras
4. Control Room Building (Inside Areas), Yard Kiosks - Panel Room, HMI Room, Communication Room, LT(AC/DC) Panel Room, Battery Room. - Bullet/Dome cameras
5. Entry and Exit of Security Shed cum main gate complex - Bullet cameras
6. Switchyard areas (All voltage levels) - PTZ Cameras
7. Transformers under present scope- Bullet/PTZ cameras
8. Substation boundary wall
Note: Any other requirement besides above to be explored & can be finalised during detail Engg.
| TOTAL OF SUBSTATION-2A (SUPPLY) | [6 empty] | 199095437.9997
SR. No. | DESCRIPTION OF ITEMS SUPPLY OF MANDATORY SPARES FOR THE FOLLOWING EQUIPMENTS. (As per Technical Specification) | Unit | Qty | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY
1 | 145 KV, 800-400-200 A, 31.5 KA, 4 core Single Phase Current Transformer (3 Nos PS CLASS & 1 No. 0.2s CLASS) | Nos | 2 | 232701.42 | 20943.1278 | 20943.1278 | 274587.6756 | 549175.3512 | SM-25
2 | 145 KV, 1250A, 31.5KA, ISOLATORS
2.1 | Fixed & Moving Contact Assembly set | Set | 1 | 172049.85 | 15484.4865 | 15484.4865 | 203018.823 | 203018.823 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
3 | 120 KV Metal Oxide Surge Arrester, 10 KA, Class III | Nos | 2 | 29179.14 | 2626.1226 | 2626.1226 | 34431.3852 | 68862.7704 | SM-31
4 | 145 KV, 2 CORE, Single Phase IVT | Nos | 2 | 163753.99 | 14737.8591 | 14737.8591 | 193229.7082 | 386459.4164 | SM-55
5 | 132 KV Bus Post Insulator | Nos | 2 | 11759.87 | 1058.3883 | 1058.3883 | 13876.6466 | 27753.2932 | Technical Sanction No: 967 dt. 03/06/2022 of ED , WZ, Burla with excalation of 5% of basic price upto FY 25-26
6 | 145KV, 3150A, 40KA, SF6, CIRCUIT BREAKER
6.1 | Density Monitoring System | Set | 1 | 7119 | 640.71 | 640.71 | 8400.42 | 8400.42 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
6.2 | Closing Coil | Nos | 4 | 8898.75 | 800.8875 | 800.8875 | 10500.525 | 42002.1
6.4 | Tripping Coil | Nos | 4 | 5339.25 | 480.5325 | 480.5325 | 6300.315 | 25201.26
6.5 | SF6 Gas Filling Device | Nos | 1 | 14238 | 1281.42 | 1281.42 | 16800.84 | 16800.84
7 | 33KV Current Transformer
7.1 | 36 KV,800-400-200,25KA,3 CORE SINGLE PHASE CURRENT TRANSFORMER(2 NOS PS CLASS & 1 NO. 0.2s CLASS) | Nos | 2 | 62012.84 | 5581.1556 | 5581.1556 | 73175.1512 | 146350.3024 | SM-25
7.2 | 36 KV, 800-400-200, 25KA, 4 CORE SINGLE PHASE CURRENT TRANSFORMER (3 NOS PS CLASS & 1 NO. 0.2s CLASS) | Nos | 2 | 62012.84 | 5581.1556 | 5581.1556 | 73175.1512 | 146350.3024 | SM-25
8 | 36 KV,1250A,25KA,ISOLATORS
8.1 | Fixed & Moving Contact Assembly set | Set | 1 | 100110.15 | 9009.9135 | 9009.9135 | 118129.977 | 118129.977 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
9 | 30 KV, Metal Oxide Surge Arrester, 10KA, class II | Nos | 2 | 9416.38 | 847.4742 | 847.4742 | 11111.3284 | 22222.6568 | SM-32
10 | 36 KV, 2 Core Single Phase IVT (1 core 3P & 1 core 0.2s) | Nos | 1 | 31316.46 | 2818.4814 | 2818.4814 | 36953.4228 | 36953.4228 | SM-56
11 | 36KV, 1250A,25KA,VACUUM CIRCUIT BREAKER
11.1 | Closing Coil | Nos | 2 | 1958.25 | 176.2425 | 176.2425 | 2310.735 | 4621.47 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
11.2 | Tripping Coil | Nos | 2 | 1958.25 | 176.2425 | 176.2425 | 2310.735 | 4621.47
12 | 33 KV Bus Post Insulators | Nos | 2 | 5824.6807 | 524.2213 | 524.2213 | 6873.1233 | 13746.2466
13 | BUS BAR & CIRCUIT MATERIALS
13.1 | 132KV TENSION & SUSPENSION INSULATORS
13.1.1 | 120KN Porcelain Anti Fog type Disc Insulators | Nos | 12 | 720.04 | 64.8036 | 64.8036 | 849.6472 | 10195.7664 | LM Accessories -54
13.1.2 | 90KN Porcelain Anti Fog type Disc Insulators | Nos | 3 | 668.53 | 60.1677 | 60.1677 | 788.8654 | 2366.5962 | LM Accessories -53
13.2 | 33KV TENSION & SUSPENSION INSULATORS
13.2.1 | 120KN Porcelain Anti Fog type Disc Insulators | Nos | 12 | 720.04 | 64.8036 | 64.8036 | 849.6472 | 10195.7664 | LM Accessories -54
13.2.2 | 90KN Porcelain Anti Fog type Disc Insulators | Nos | 5 | 668.53 | 60.1677 | 60.1677 | 788.8654 | 3944.327 | LM Accessories -53
14 | ACSR CONDUCTOR
14.1 | ACSR Moose Conductor | Mtrs | 150 | 446.93 | 40.2237 | 40.2237 | 527.3774 | 79106.61 | LM-19
14.2 | ACSR Panther Conductor (Station Transformer connections) | Mtrs | 50 | 192.28 | 17.3052 | 17.3052 | 226.8904 | 11344.52 | LM-17
15 | Clamps & Connectors for 132 KV & 33 KV (Each type Three Nos) for Sl No- 14.3.8 to 14.3.29 of Substation Sypply section. The exact qty of each item under this shall be mentioned by the agency and shall be incorporated in the P.O. | Set | 1 | 160115.34 | 14410.3806 | 14410.3806 | 188936.1012 | 188936.1012 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
16 | BATTERY CHARGER
16.1 | One complete set of Electronic cards of the Battery Charger for 300AH, 48V VRLA Battery Set. The exact qty of each item under this shall be mentioned by the agency and shall be incorporated in the P.O. | Set | 1 | 31144.05 | 2802.9645 | 2802.9645 | 36749.979 | 36749.979 | Technical Sanction Order - ED(Elect.) - 58/2023-24 vide Order No. ED/Bijepur/2131 dated 26.12.2023. with 5% Cost escalation for 2024
16.2 | One complete set of Electronic cards of the Battery Charger for 350AH, 220V Plante type Battery Set. The exact qty of each item under this shall be mentioned by the agency and shall be incorporated in the P.O. | Set | 1 | 26695.2 | 2402.568 | 2402.568 | 31500.336 | 31500.336
17 | Spares for Protection relay Panels (As installed in C/R Panels)
17.1 | Distance Protection Relay | Nos | 1 | 164809.31 | 14832.8379 | 14832.8379 | 194474.9858 | 194474.9858 | SM-86
17.2 | Differential Protection Relay | Nos | 1 | 225750.42 | 20317.5378 | 20317.5378 | 266385.4956 | 266385.4956 | SM-80
17.3 | BCU | Nos | 1 | 400000 | 36000 | 36000 | 472000 | 472000 | Market
17.4 | Other Auxiliary Relays (Each 1 No. of Different Type) the exact qty of each item under this shall be mentioned by the agency and shall be incorporated in the P.O. | Set | 1 | 66000 | 5940 | 5940 | 77880 | 77880
B | TOTAL SUPPLY OF MANDATORY SPARES FOR SUB-STATION | [6 empty] | 3205750.6058
C | TOTAL OF SUPPLY COMPONENT OF THE WORKS CONTRACT FOR SUBSTATION AND MANDATORY SPARE (A+B) | [6 empty] | 202301188.6055

## Erection
ERECTION |  |  | ODISHA POWER TRANSMISSION CORPORATION LTD
NAME OF THE WORK:- Construction of 2 x 50 MVA, 132/33 KV Sub-station Kuta with SAS
| ERECTION, INSTALLATION, TESTING & COMMISSIONING _SUBSTATION |  |  |  | GST
Sl. No. | DESCRIPTION OF ITEMS(SCHEDULE-VIIB-SS) ERECTION, INSTALLATION, TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT OF MEASUREMENT | QUANTITY: Construction of 132/33 KV Sub-station with SAS (132 KV Bay-02 Nos.: 02 TRF & (33 KV Bay-06 Nos.: 03 FDR, 02 TRF, 01 B/C | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY | RC SS ref.
1 | 2 | 3 | 4 | 5 | 6= {5*9%} | 7= {5*9%} | 8= {5+6+7} | 9= {8*4}
A | ELECTRICAL WORKS
SUB-STATION
1 | 145 KV, 800-400-200 A,40 KA, 4 core Single Phase Current Transformer (3 Nos PX CLASS & 1 No. 0.2s CLASS) | Nos | 6 | 7925.99 | 713.3391 | 713.3391 | 9352.6682 | 56116.0092 | E-1.2-(f)
2 | 145 KV, 1250A, 40KA, ISOLATORS
2.1 | Single Isolator without Earth Switch | Nos | 7 | 13829.2 | 1244.628 | 1244.628 | 16318.456 | 114229.192 | E-1.2-(b)
2.2 | Double Isolator with Earth Switch | Nos | 0 | 24355.92 | 2192.0328 | 2192.0328 | 28739.9856 | 0 | E-1.2-(e)
2.3 | Double Isolator without Earth Switch | Nos | 2 | 22291.86 | 2006.2674 | 2006.2674 | 26304.3948 | 52608.7896 | E-1.2-(d)
3 | Metal oxide polymer housed surge arrrestor for 132 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 6 | 4458.37 | 401.2533 | 401.2533 | 5260.8766 | 31565.2596 | E-1.2-(g)
4 | 145 KV, 2 Core, Single Phase IVT | Nos | 0 | 7925.99 | 713.3391 | 713.3391 | 9352.6682 | 0 | E-1.2-(f)
5 | 132 KV Bus Post Insulator | Nos | 10 | 1816.37 | 163.4733 | 163.4733 | 2143.3166 | 21433.166 | E-1.2-(h)
6 | 145KV, 3150A, 40KA, SF6 Circuit Braker with supporting Structure. Facilities for integration with SAS as per the site requirement. | Nos | 2 | 49537.46 | 4458.3714 | 4458.3714 | 58454.2028 | 116908.4056 | E-1.2-(a)
7 | 33 kV CT 31.5 kA as per TS
7.1 | 36 KV,800-400-200, 3 core Single phase Current Transformer (2 Nos PX class & 1 No. 0.2s class) | Nos | 9 | 2559.44 | 230.3496 | 230.3496 | 3020.1392 | 27181.2528 | E-1.4-(f)
7.2 | 36 KV, 1600-800-400, 3 core Single phase Current Transformer (2 Nos PX class & 1 No. 0.2s class) | Nos | 3 | 2559.44 | 230.3496 | 230.3496 | 3020.1392 | 9060.4176 | E-1.4-(f)
7.3 | 36 KV, 1600-800-400, 4 core Single phase Current Transformer (3 Nos PX class & 1 No. 0.2s class) | Nos | 6 | 2311.75 | 208.0575 | 208.0575 | 2727.865 | 16367.19 | E-1.4-(g)
8 | 36 KV,1250A,25KA,ISOLATORS
8.1 | Single Isolator without Earth Switch (1250 A, feeder ) | Nos | 6 | 6605 | 594.45 | 594.45 | 7793.9 | 46763.4 | E-1.4-(b)
8.2 | Single Isolator with Earth Switch (1250 A, feeder) | Nos | 3 | 6605 | 594.45 | 594.45 | 7793.9 | 23381.7 | E-1.4-(b)
8.3 | Single Isolator without Earth Switch (1600 A, transformer and bus coupler ) | Nos | 8 | 6605 | 490.4208 | 490.4208 | 6429.9616 | 51439.6928 | E-1.4-(b)
8.4 | Beam Mounted Single Isolator without Earth Switch(1600 A, section isolator) | Nos | 2 | 5449.12 | 490.4208 | 490.4208 | 6429.9616 | 12859.9232 | E-1.4-(c)
8.5 | Beam Mounted Single Isolator without Earth Switch(1250 A, station supply) | Nos | 1 | 5449.12 | 104.0283 | 104.0283 | 1363.9266 | 1363.9266 | E-1.4-(c)
9 | Metal oxide polymer housed surge arrrestor for 33 kV system. Station Class Low Duty (SL) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor - As per TS | Nos | 18 | 1155.87 | 104.0283 | 104.0283 | 1363.9266 | 24550.6788 | E-1.4-(j)
10 | 36 KV, 2 Core Single Phase IVT (1 core 3P & 1 core 0.2) | Nos | 3 | 2311.75 | 208.0575 | 208.0575 | 2727.865 | 8183.595 | E-1.4-(h)
11 | 36 KV,31.5KA, Vacuum Circuit Breaker with supporting Structure. Facilities for integration with SAS as per the site requirement. | Nos
11.1 | 36 KV , 1600 A Vacuum Circuit breaker with supporting Structure. Facilities for integration with SAS as per the site requirement( transformer and bus coupler ) | Nos | 6 | 23777.98 | 2140.0182 | 2140.0182 | 28058.0164 | 168348.0984 | E-1.4-(a)
12 | 33 KV Bus Post Insulator | Nos | 20 | 643.99 | 57.9591 | 57.9591 | 759.9082 | 15198.164 | E-1.4-(k)
13 | BUS BAR STRINGING: Supply of labour, T&P and other necessary arrangements for stringing of bus bar conductors, hoisting of single or double insulator strings, Single or Double Hard-wares Fittings, Clamp & connectors, as per requirements, Jumpers, connections to Equipments, testing, commissioning etc. as per the instruction of Engineer-in charge.
13.1 | Single moose conductor/Phase | Mtr | 2000 | 181.64 | 16.3476 | 16.3476 | 214.3352 | 428670.4 | F-1.0-(e)-i
13.2 | Twin moose Conductor /Phase | Mtr | 500 | 247.93 | 22.3137 | 22.3137 | 292.5574 | 146278.7 | F-1.0-(f)-i
13.3 | ACSR Panther Conductor (Station Transformer connections) | Mtr | 75 | 115.59 | 10.4031 | 10.4031 | 136.3962 | 10229.715 | F-1.0-(a)-i
14 | SUB-STATION EARTH-MAT
14.1 | Substation earth-mat: (a) The Soil resistivity for the substation area is to be measured and approved by OPTCL. (b) The Earth Mat design and layout is to prepared based on the soil resistivity and approved by OPTCL. (c) Laying of earth-mat conductors of Hot dip galvanized flats of size 75X10mm, excavation of earth for laying of earth flat as per approved design & drawing, welding/jointing, application of two coats of bituminous Paint, wrapping of HT Tape etc of ground conductors & etc with back filling and good compaction. The spacing between the earth conductor not more than 5 Mtrs (both way) and to be buried at depth of atleast 700mm from the finished ground level. (d) 50 mm,3 mtr long Heavy duty perforated GI pipes: for treated earth pits (with details of treatment as per IS). (e) Provision of water taps inside the switch yard areas and peripheral for treated earth pit for watering the treated earth pits. Note: The no. of treated and un treated earth pits are to be done as per the practice and as indicated in the drawing for different equipment. (f) The erection of risers of size 50 x 6 mm / 75 x 10 mm GI flats including welding/jointing, application of two coats of bituminous Paint, wrapping of HT Tape etc as per requirement. This is as per approved drawing and specification.
14.1.1 | 75x10 MM GI FLAT: for earth mat & subsoil risers. Subsoil flts to be laid from the earth mat up to the foundation level. | Mtrs | 3728 | 108.47 | 9.7623 | 9.7623 | 127.9946 | 477163.8688 | I-1.10-(vi)-(b)
14.1.2 | 50x6 MM GI FLAT: for Raiser from the foundation level to equipment, structure, columns and up to the bottom of spikes etc.). Each equipment strructure & Columns shall be connected to earth at two separate points. | Mtrs | 10156 | 85.22 | 7.6698 | 7.6698 | 100.5596 | 1021283.2976 | I-1.20-(v)-(b)
14.1.3 | 50MM GI Pipe for Treated Earth Pit: Electrode with chamber & cover, shall be connected to the main earth mat. The resistance of each earth pit shall be recorded in presence of the Engineer In charge. | Nos | 140 | 2944.11 | 264.9699 | 264.9699 | 3474.0498 | 486366.972 | I-1.3-(ii)
14.1.4 | Switchyard buildings lightning protection (all materials & accessories like Shielding Wire, PG clamp, Test link, D shackle, other required materials etc) as per IS/National Building code standard and as per approved drawing including associated civil works | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | market price
14.1.5 | Installation of water pipe network from the overhead tank to each treated earth pit as per approved drawing using the UPVC Pipes (2", 1.5", 1" & 1/2" etc), Joints, bends, Valves and all accessories, including the excavation, labour, T & P complete as per instruction of the Site engineer. | LOT | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | market price
15 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section: 2-2, 3-3 & 4-4 along with its accessories as per TS.
15.1 | G.I Cable Trays(size: 450x75x2500mm) | Mtrs | 400 | 82.95 | 7.4655 | 7.4655 | 97.881 | 39152.4 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
15.2 | G.I Cable Trays(size: 300x75x2500mm) | Mtrs | 500 | 58.8 | 5.292 | 5.292 | 69.384 | 34692 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
15.3 | G.I Cable Trays(size: 150x75x2500mm) | Mtrs | 300 | 53.55 | 4.8195 | 4.8195 | 63.189 | 18956.7 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
15.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 1.5 | 4347 | 391.23 | 391.23 | 5129.46 | 7694.19 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
16 | SWITCH YARD STRUCTURES COLUMN & BEAM (LATTICE TYPE) FOR 132/33 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS.
16.1 | DIFFERENT TYPES OF COLUMNS WITH DETAILS - With Spike
16.1.1 | T1S - 132 KV(Nominal unit wt- 1.2 MT) =10 Sets | MT | 12
16.1.2 | T4S - 132KV (Nominal unit wt- 0.95 MT) =7 Sets | MT | 6.65
16.1.3 | T8S - 33KV(Nominal unit wt- 0.83 MT) = 8 Sets | MT | 6.64
16.1.4 | T9S - 33KV(Nominal unit wt- 0.6 MT)=6 Sets | MT | 3.6
16.2 | DIFFERENT TYPE OF BEAMS WITH DETAILS
16.2.1 | G1 - 132 KV(Nominal unit wt- 0.62 MT) = 26 Sets | MT | 16.12
16.2.2 | G2 - 132 KV(NOMINAL UNIT WT- 0.9 MT) =6 Sets | MT | 5.4
16.2.3 | G6 - 33KV (NOMINAL UNIT WT- 0.53 MT) = 2 Sets | MT | 1.06
16.2.4 | G4 - 33KV(NOMINAL UNIT WT- 0.4 MT) =4 Sets | MT | 1.6
16.2.5 | G4X - 33KV (NOMINAL UNIT WT- 0.52 MT) =4 Sets | MT | 2.08
16.3 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 55.15 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 373104.0118 | F-3.10
16.4 | SWITCH YARD EQUIPMENT STRUCTURES (LATTICE TYPE) FOR 132/33 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS.
16.4.1 | Structure for 132KV CT (Unit Weight - 214.546 Kg) =6 Nos | MT | 1.287
16.4.2 | Structure for 132KV IVTs (Unit Weight - 231.195 Kg) =0 Nos | MT | 0
16.4.3 | Structure for 132KV Surge Arrester (Unit Weight - 179.893 Kg) =6 Nos | MT | 1.0788
16.4.4 | 132 KV Single Isolator without Earth Switch (Unit weight - 658.767 Kg) = 7 Nos | MT | 4.6109
16.4.5 | 132 KV Double Isolator without Earth Switch (Unit Weight - 979.10 Kg) = 2 Nos | MT | 1.9582
16.4.6 | 132 KV Double Isolator with Earth Switch (Unit Weight - 1120.559 Kg) = 0 Nos | MT | 0
16.4.7 | Structure for 132KV BPI (Unit Weight - 309.883 Kg) =10 Nos | MT | 3.098
16.4.8 | Structure for 33KV CT (Unit Weight - 148.80 Kg) =9 Nos | MT | 1.3392
16.4.9 | Structure for 33KV IVTS (Unit Weight - 124.336 Kg) =3 Nos | MT | 0.3729
16.4.10 | Structure for 33KV LAs (Unit Weight - 148.8 Kg) =3 Nos | MT | 0.4464
16.4.11 | 33 KV Single Isolator without Earth Switch (1250 A, feeder ) (Unit weight - 294.893 Kg) = 6 Nos | MT | 1.7694
16.4.12 | 33 KV Single Isolator with Earth Switch (1250 A, feeder)(Unit weight - 324.8 Kg) = 3 Nos | MT | 0.9744
16.4.13 | Structure for 33KV BPI (Unit Weight - 148.80 Kg) =14 Nos | MT | 2.0832
16.4.14 | Structure for 33KV HG Fuse (Unit Weight - 245 Kg) =1 Sets | MT | 0.245
16.4.15 | TOTAL WEIGHT OF EQUIPMENT STRUCTURE | MT | 19.2634 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 130321.8825 | F-3.10
16.5 | Total weight of GI Nuts and bolts for the above Column, Beam & equipment structures and including different size of plain washer / spring washer for above structures. | MT | 3.7207 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 25171.2947 | F-3.10
17 | Laying of Power and Control Cable including fixing of cable with terminal connections both at equipments and control panels with supply and fixing of lugs, Ferrules, clamps, connectors, glands, fixing of cable trays/ laying in ground in HDPE pipes, including supply of N & B, Link plates, Cable Markers, PVC pipes Bends, Plaster of Paris, M-Seal compounds etc for sealing purpose and all necessary arrangements, laying of Earthing Flats, earthing, laying of Cable trench slabs and chequered plate etc for the cable trench, Cable scheduled and cable diagram to be prepared by the contractor
17.1 | POWER CABLES, 1.1KV, FRLSH XLPE/PVC ARMOURED, ALUMINIUM CONDUCTOR (As per Specification)
17.1.1 | XLPE 3.5 CX300 mm2 | Mtrs | 320 | 2246.83 | 202.2147 | 202.2147 | 2651.2594 | 848403.008 | G-1.2-(xiv)
17.1.2 | XLPE 3.5 CX185 mm2 | Mtrs | 320 | 1704.48 | 153.4032 | 153.4032 | 2011.2864 | 643611.648 | G-1.2-(xii)
17.1.3 | XLPE 3.5 CX120 mm2 | Mtrs | 400 | 1007.2 | 90.648 | 90.648 | 1188.496 | 475398.4 | G-1.2-(x)
17.1.4 | PVC 3.5 CX70 mm2 | Mtrs | 480 | 674.05 | 60.6645 | 60.6645 | 795.379 | 381781.92 | G-1.2-(viii)
17.1.5 | PVC 3.5 CX35 mm2 | Mtrs | 480 | 511.34 | 46.0206 | 46.0206 | 603.3812 | 289622.976 | G-1.2-(vi)
17.1.6 | PVC 4 CX 16 mm2 | Mtrs | 400 | 271.16 | 24.4044 | 24.4044 | 319.9688 | 127987.52 | G-1.2-(iv)
17.1.7 | PVC 4 CX 6 mm2 | Mtrs | 1000 | 154.95 | 13.9455 | 13.9455 | 182.841 | 182841 | G-1.2-(ii)
17.1.8 | PVC 2CX 6 mm2 | Mtrs | 640 | 92.9355 | 8.3642 | 8.3642 | 109.6639 | 70184.8896 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
17.2 | CONTROL CABLES, 1.1 KV, PVC, FRSLH Armoured, STRANDED COPPER (As per specification)
17.2.1 | 2 CX 2.5 mm2 | Mtrs | 1400 | 54.25 | 4.8825 | 4.8825 | 64.015 | 89621 | G-1.1-(i)
17.2.2 | 4 CX 2.5 mm2 | Mtrs | 1000 | 54.25 | 4.8825 | 4.8825 | 64.015 | 64015 | G-1.1-(iii)
17.2.3 | 5 CX 2.5 mm2 | Mtrs | 1200 | 54.25 | 4.8825 | 4.8825 | 64.015 | 76818 | G-1.1-(iii)
17.2.4 | 7CX 2.5 mm2 | Mtrs | 1400 | 54.25 | 4.8825 | 4.8825 | 64.015 | 89621 | G-1.1-(iv)
17.2.5 | 10 CX 2.5 mm2 | Mtrs | 2600 | 61.98 | 5.5782 | 5.5782 | 73.1364 | 190154.64 | G-1.1-(vi)
17.2.6 | 12 CX 2.5 mm2 | Mtrs | 2200 | 61.98 | 5.5782 | 5.5782 | 73.1364 | 160900.08 | G-1.1-(vii)
17.2.7 | 16 CX 2.5 mm2 | Mtrs | 1400 | 61.98 | 5.5782 | 5.5782 | 73.1364 | 102390.96 | G-1.1-(viii)
17.2.8 | 19 CX 2.5 mm2 | Mtrs | 640 | 77.48 | 6.9732 | 6.9732 | 91.4264 | 58512.896 | G-1.1-(ix)
17.3 | SINGLE CORE 1.1KV, PVC UN-ARMOURED COPPER CONDUCTOR: for connection from Battery Set to Battery Charger and from Battery Charger to DCDB on cable tray / HDPE pipe/PVC pipe etc
17.3.1 | 1CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | Mtrs | 240 | 241.5 | 21.735 | 21.735 | 284.97 | 68392.8 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
18 | Supply of screened / Shielded Twisted pair copper cable for Analog Communication for showing winding temp, Oil temp,lighting, fire fighting, DG etc, LT current & LT voltage signals of sub-station auxiliary system in HMI
18.1 | 8PX1.5 mm2 screened copper cable | Mtrs | 200 | 49 | 4.41 | 4.41 | 57.82 | 28910 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
18.2 | 2PX1.5 mm2 screened copper cable | Mtrs | 80 | 42.88 | 3.8592 | 3.8592 | 50.5984 | 10119.68
19 | 132/33 KV, 50 MVA Transformer: Receiving the Transformers and its accessories & dragging and Installing on the plinth and placing in position, Erection of accessories of the Transformers, erection of NCTs on the Transformers, Earthing as per Standard (Including Supply of Materials), Vacuum Treatment of the tank and winding, Oil Filtration (Including Supply of Vacuum cum Oil Filter Machine), Supply & Laying of all types of Control & Power Cables Pertaining to Transformers, Testing and Commissioning including all tests of the Oil as per stipulation in the Standard Approved Testing Laboratory and as per the instruction of the Engineer in Charge. This include all related works for Erection, Testing and Commissioning of the Power Transformers/Auto Transformers. (Contractor to arrange Power Supply for Filtration And Vacuum Treatment works). It also includes supply of all materials required for erection Including T & P's. | Nos | 2 | 144886.72 | 13039.8048 | 13039.8048 | 170966.3296 | 341932.6592 | Item no.1.2.2-[b]-(i)
19.1 | Online Drying out system for 50MVA, 132/33KV Power transformers | Set | 2 | 20000 | 1800 | 1800 | 23600 | 47200 | market price
19.2 | Digital RTCC Panel: Having two integrated RTCC modules for OLTC control and transformer monitoring for two transformers. The RTCC modules shall be SAS compatible and as per TS. There shall be cutouts for two more RTCC modules in the panel. | Lot | 1 | 18163.73 | 1634.7357 | 1634.7357 | 21433.2014 | 21433.2014 | SS-H-1.20
20 | FIRE FIGHTING: Erection, Testing and commissioning of the NIFPES stystem complete with all accessories for successful operation including demonstaration of the NIFPES operational procedures for the 80 MVA, 132/33 KV Power Transformer as per the Technical Specification & latest standard.(1 lot for each transformer) | Lot | 2 | 210000 | 18900 | 18900 | 247800 | 495600 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
21 | Erection, Testing and commissioning of Station Transformer complete with all accessories & Other materials for meeting the auxiliary supply of the subsation as per technical Specification.
21.1 | Station Transformer - 33KV/433V, 250 KVA (As per specification) | Nos | 1 | 27452.22 | 2470.6998 | 2470.6998 | 32393.6196 | 32393.6196 | Item no.1.2.6-(iv)
21.2 | HG Fuse set- for 33kV side of the station transformer including the mounting insulators, channels complete in all respect (each set comprises three single HG fuse) | Set | 1 | 6195 | 557.55 | 557.55 | 7310.1 | 7310.1 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
22 | Substation Automation System(IEC 61850): Installation, Testing and commissioning of the Digital Substation equipment including imparting training (on Job/site) to atleast 6 Engineers of OPTCL regarding the softwares used, configuration of the devices & switches, testing, probable faults & tracing procedures. The items from Sl. No-22.1 to 22.3 sahll be considered complete only when the firm shall submit a successful training completion certificate from the nominated engineers. The firm shall intimate the training schedule to OPTCL sufficiently before commencing the training for nomination of engineers.
22.1 | Installation, Testing and Commissioning of Substation Automation Sytem System including integration with the existing SAS syatem This shall also include the integration with remote control center of OPTCL (STAMS) and SLDC including the supply of all material required at the substation for the integration work. (The integration work required at the remote control center along with the supply of any material are not in the scope.) "SUBSTATION AUTOMATION SYSTEM (IEC 61850) Gateway Panel ( 2 layer type) : for Sub-Station Automation (in PRP on FO as per the specification) system (for All 132 & 33 KV side bays) and with other accessories, comprising: 1. Gateway (Non-Windows or Linus or Firmware based)- 2 nos. with 8 ethernet ports each 2. BCU for Substation Auxilliary System (Station AC, Station DC, Lighting, Fire fighting, Diesel generator etc.) 3. Ethernet Switches (with 20% spares Port) for bay & station level 4. LIU 5. Multimode glass fibre Doublle jacket armoured optical cables 6. Red boxes etc. including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. . RTCC Communication Panel (3 layer type) ; comprising of: 1. Substation Ethernet Switches- 2 nos 2. Firewall cum Router-2 set 3. Station Data Concentrator (SDC)- 2 nos 5. LIU 6. Multimode glass fibre Doublle jacket armoured optical cables 7. Red boxes etc. 8. Provision for mounting the VMS switch etc including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect for remote communication & as per technical specification. 1.Operator Workstations 2.Engineering workstation 3.Workstation for RAS (Remote Access System) 4.Black & whiter Laser jet Printer-1Nos 5.Inverters - 3 KVA (Main & Stand by) 6.Furniture (Operator desk 3 Nos (for SAS, RAS, VMS) & Chair-6Nos) etc. GPS System with IRIG-B/SNTP/PTP with VDU (Clock) | Lot | 1 | 73500 | 6615 | 6615 | 86730 | 86730 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
22.2 | 132KV Level Protection Panel- Single Panel Twin Bay Type (2 Bays in One Panel) with IEC 61850-ED-2 PRP on FO
22.2.1 | 132KV feeder Protection Panel: Feeder-1 & 2 in one panel Numerical Distance protection relay, BCPU and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | Nos | 0 | 21466.23 | 1931.9607 | 1931.9607 | 25330.1514 | 0 | H-1.1-(v)
22.2.2 | 132KV Transformer Protection Panel: Transformer-1 & 2 in one panel Numerical Differential protection relay, BCPU and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | Nos | 2 | 21466.23 | 1931.9607 | 1931.9607 | 25330.1514 | 50660.3028 | H-1.1-(v)
22.2.3 | 132KV Buscoupler Protection Panel: BCPU and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | Nos | 1 | 21466.23 | 1931.9607 | 1931.9607 | 25330.1514 | 25330.1514 | H-1.1-(v)
22.3 | 33KV Level Protection Panel- Single Panel Twin Bay Type (2 Bays in One Panel) with IEC 61850-ED-2 PRP on FO
22.3.1 | 33KV Feeder Protection Panel: with BCPU & with other Auxiliary relays as required as per the scheme compliant to IEC 61850 - ED-2 protocol with PRP on FO. Power Supply 220V DC. 33KV Buscoupler Protection Panel: with BCPU & with other Auxiliary relays as required as per the scheme compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Note: 5 Nos. of Line Feeder Bays and 1 Bus coupler to be considered in 3 Panels. | Nos | 3 | 18741.68 | 1686.7512 | 1686.7512 | 22115.1824 | 66345.5472 | H-1.1-(vii)
22.3.2 | 33KV Transformer protection panel: with BCPU, numerical REF & with other Auxiliary relays as required as per the scheme, compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Note: 2 Nos. of Transformer Feeder Bays to be considered in one Panel. | Nos | 1 | 18741.68 | 1686.7512 | 1686.7512 | 22115.1824 | 22115.1824 | H-1.1-(vii)
23 | AC & DC SYSTEM : All Indoor Panels with 2 mm CRCA sheet and 3 mm CRCA gland plate painted & as per TS All Outdoor Panels, Sub Station Swithyard Console Boxes, HDG type (86 micron), 3 mm thick CRCA, as per TS.
23.1 | AC SYSTEM
23.1.1 | MAIN AC DB ( Indoor Type): MAIN DB-1, MAIN DB-2 with B/C. The incomer & Bus coupler shall have 800 A, 50KA, drawout type with Numerical SAS compliant Relay (O/C, E/F, U/V, O/V protection).The ACDB shall be suitable for automatic switching OFF & ON during power failure. Facilities for integration with SAS as per the site requirement. | Set | 1 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 12158.4722 | H-1.3
23.1.2 | ACDB (Indoor Type): AC DB-1, AC DB-2 with B/C. Incomer-1 & 2, Bus coupler and DG set Incomer-1 shall have 400A Motorised MCCB for automatic operation. The ACDB shall be suitable for automatic switching OFF & ON , auto start of DG set etc during power failure. Facilities for integration with SAS as per the site requirement. | Set | 1 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 12158.4722 | H-1.3
23.1.3 | Main Lighting Distribution Board (Indoor Type): Having 250A MCCB for Incomers with source-1, Source-2 & Bus coupler. | Set | 1 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 12158.4722 | H-1.3
23.1.4 | Indoor Lighting Distribution Board (Indoor Type) | Set | 1 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 12158.4722 | H-1.3
23.1.5 | Emergency Lighting Distribution Board (Outdoor type): The ELDB should be supplying to 20% of switchyard lights, each of 132KV and 33KV Switchyard. | Set | 1 | 9742.37 | 876.8133 | 876.8133 | 11495.9966 | 11495.9966 | H-1.4
23.1.6 | Indoor Receptacle Board | Set | 1 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 12158.4722 | H-1.3
23.1.7 | Bay Marshalling Kiosk (Outdoor type): 1 BMK for 2 nos 132KV bays and 1 BMK for 3 nos 33KV bays | Nos | 7 | 9742.37 | 876.8133 | 876.8133 | 11495.9966 | 80471.9762 | H-1.4
23.1.8 | Console Box for Switchyard Lighting (Outdoor type) | Nos | 2 | 3005.27 | 270.4743 | 270.4743 | 3546.2186 | 7092.4372 | H-1.6
23.1.9 | Console Box for Street Lighting (Outdoor type) | Nos | 2 | 3005.27 | 270.4743 | 270.4743 | 3546.2186 | 7092.4372 | H-1.6
23.1.10 | Console Box for Colony Supply (Outdoor type) | Nos | 1 | 3005.27 | 270.4743 | 270.4743 | 3546.2186 | 3546.2186 | H-1.6
23.1.11 | Switchyard Receptacle Board for Transformer Oil Filtration (Outdoor type) | Nos | 1 | 2138.85 | 192.4965 | 192.4965 | 2523.843 | 2523.843 | Electrical erection SL no.28.1.6 of Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
23.1.12 | Switchyard Receptacle Board for Welding & Other Emergency (Outdoor type) | Nos | 2 | 2138.85 | 192.4965 | 192.4965 | 2523.843 | 5047.686 | Electrical erection SL no.28.1.6 of Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
23.1.13 | CT Out Door Console Boxes ( 132 KV CT-2 Nos, 33 KV CT-7 Nos) (Outdoor type) | Nos | 9 | 3005.27 | 270.4743 | 270.4743 | 3546.2186 | 31915.9674 | H-1.6
23.1.14 | PT Out Door Console Boxes (132 KV IVT-0 No., 33 KV IVT-1 No.) (Outdoor type) | Nos | 1 | 3005.27 | 270.4743 | 270.4743 | 3546.2186 | 3546.2186 | H-1.6
23.1.15 | Outdoor kiosk for Station Transformer (Outdoor type) | Nos | 2 | 9742.37 | 876.8133 | 876.8133 | 11495.9966 | 22991.9932 | H-1.4
23.1.16 | ACDB for Yard Kiosk (Indoor Type): LT supply to Protection panels, Kiosk lighting, AC etc made of 2mm CR sheet | Nos | 2 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 24316.9444 | H-1.3
23.1.17 | DCDB for Yard Kiosk (Indoor Type): DC supply to Protection panels having source-1 & 2 with auto changeover facility, made of 2mm CR sheet. | Nos | 2 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 24316.9444 | H-1.3
23.2 | DC SYSTEM:
23.2.1 | 220 V DC DISTRIBUTION BOARD (Indoor Type): Having 63A DC MCCB for Incomers, Bus Coupler with interlock, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE and shall be SAS compliant. | Set | 1 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 12158.4722 | H-1.3
23.2.2 | 220 V DC Emergency Lighting Distribution Board (Indoor Type) | Set | 1 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 12158.4722 | H-1.3
23.2.3 | Battery cells (2.2V), 350 AH Plante Type for 220 V DC (107 Nos + 3 Nos spare) | Set | 1 | 16039.842 | 1443.5858 | 1443.5858 | 18927.0136 | 18927.0136 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
23.2.4 | Battery Charger For 350 Ah Plante Type Battery, 107 cells, 2.2V, Trickle charge volt-2.25V(Float & Float Cum Boost). The Charger ON/OFF status, input/output voltage, output current, associated charger protection signals shall be provided for integration with SAS. | Set | 1 | 4455.5175 | 400.9966 | 400.9966 | 5257.5107 | 5257.5107 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
24 | ACCESSORIES FOR OPGW SYSTEM With OPGW cable
24.1 | 48 Fibre Optic Approach cable along with HDPE Pipes | km | 1 | 61980 | 5578.2 | 5578.2 | 73136.4 | 73136.4 | B-1.0-(i)
24.2 | Optical line Terminal Equipment(OLTE) -STM4 type SDH equipment with integrated MUX & tributary cards for speech & data ports for interfacing of Speech & data which should be compatible with existing OPTCL system including all accessories for successful commissioning. | Nos | 1 | 309750 | 27877.5 | 27877.5 | 365505 | 365505 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
24.3 | Supply of FODP(Fibre Optic Distribution Panel)48 F: Indoor type,rack mounted with FCPC coupling and pig tails(DWSm Fibre) | Nos | 1 | 7434 | 669.06 | 669.06 | 8772.12 | 8772.12 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
24.4 | Digital tele-protection coupler with accessories compatible for interfacing with SDHMUX | Nos. | 2 | 4582.81 | 412.4529 | 412.4529 | 5407.7158 | 10815.4316 | annexure-III(Telecom)-2.0-(ii)
24.5 | 48 V, 300 AH, maintenance free VRLA Battery set. | Set | 1 | 5795.88 | 521.6292 | 521.6292 | 6839.1384 | 6839.1384 | Annex.II-H-1.5
24.6 | SMPS based battery charger of 75A suitable for 48V VRLA battery. | Nos | 1 | 5366.57 | 482.9913 | 482.9913 | 6332.5526 | 6332.5526
24.7 | 48V DCDB | Nos | 1 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 12158.4722 | Annex.II-H-1.3
24.8 | Earth Flat, Cable Tray, Foundation rail, Junction Box,. | Lot | 1 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 12158.4722 | Annex.II-H-1.3
25 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area): Design, engineering, procurement of labour, material including all associated works for construction of switch yard lightings as per technical specification and approved drawings. The Light fixture shall be of reputed make (Philips / CGL / Bajaj / Havells / Crompton) and fixtures shall be LED type and proper cabling from the lighting outdoor distribution boards to the junction boxes and from junction boxes to the fixtures. The lighting fixtures are to be installed on the switch yard structures & Street Light Poles. The quantity of such fixtures are to be designed and to be ascertained through the Lighting Design Calculation for acceptable Lux levels.
25.1 | Switchyard Lighting: Installation of 150W LED Fixtures in the Switchyard | Set | 15 | 2330.58 | 209.7522 | 209.7522 | 2750.0844 | 41251.266 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
25.2 | STREET LIGHTING: Installation of HDG Octagonal street lighting poles 7 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. Poles shall be installed on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes installation of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/ Havells/ Osram/Wipro), with switch gear, GI junction box, GI Conduit etc. & as per technical specification. | Set | 20 | 8787.71 | 790.8939 | 790.8939 | 10369.4978 | 207389.956
25.3 | Lighting provision for other Areas: Suitable for: (a) Main Gate Lighting (2 Nos of 70 Watt LED) (b) Garden Lighting (4 Nos of 70W LED) with necessary post top lantern with pole (c) Control Room Building peripheral Lighting (4 Nos of 70W LED). | Lot | 1 | 10500 | 945 | 945 | 12390 | 12390 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
26 | Air Conditioners
26.1 | AIR CONDIONER: Installation of 2T capacity Split Air Conditioning Units (Dual Inverter, five star or better type, latest model) with copper condensor having remote temperature & operation control facility. Installation of AC Control Panel made of 2mm CR sheet, having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (As per specification) for Control/SAS Room, ACDC Room Communication room, office room & Conference room . The ACs in the ACDC Room(04 nos) shall run in tandem i.e 2 ACs at a time for 4 hours each. Suitable control arrangement shall be made using 24hr timer for start and stop. Similarly, for Control Room (2 ACs) and Communication Room (2ACs), one AC at a time for 4 hours each. One AC each in office rooms(2 nos), Conference Room, Transit Room. | [7 empty] | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
26.1.1 | AC for Control Room Building | Set | 12 | 2349.9 | 211.491 | 211.491 | 2772.882 | 33274.584 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
26.1.2 | Air conditioners for Yard AC Kiosk with successful commissioning of the units as per TS. | Set | 4 | 21000 | 1890 | 1890 | 24780 | 99120 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
26.1.3 | Installation of AC and accessories in Transit House | Set | 4 | 2349.9 | 211.491 | 211.491 | 2772.882 | 11091.528 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
27 | Placement of Supplied Fire Exitinguishers at various locations of the substations as per instruction of Site Engineer.
27.1 | FOAM TYPE-9 LTRS | Nos | 4 | 153.3 | 13.797 | 13.797 | 180.894 | 723.576 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
27.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 25 KGS | Nos | 4 | 352.8 | 31.752 | 31.752 | 416.304 | 1665.216 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
27.3 | DRY POWDER TYPE -6 KGS | Nos | 4 | 141.75 | 12.7575 | 12.7575 | 167.265 | 669.06 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
27.4 | CO2 - 4.5 KGS | Nos | 10 | 153.3 | 13.797 | 13.797 | 180.894 | 1808.94 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
27.5 | CO2 - 9.0 KGS | Nos | 10 | 153.3 | 13.797 | 13.797 | 180.894 | 1808.94 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
27.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | Nos | 4 | 153.3 | 13.797 | 13.797 | 180.894 | 723.576 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
27.7 | Water type- 9 LTRS | Nos | 4 | 352.8 | 31.752 | 31.752 | 416.304 | 1665.216 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
27.8 | Foam type - 50 LTR | Nos | 4 | 235.2 | 21.168 | 21.168 | 277.536 | 1110.144 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
27.9 | FIRE BUCKET (6 Nos IN EACH STAND) WITH STAND With Canopy arrangement | Set | 6 | 235.2 | 21.168 | 21.168 | 277.536 | 1665.216 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
28 | Demonstration of the Maintenance Testing Equipment: The demo of performance and operation shall be made to a committee comprising of members from Constrction, O & M and EMR and a joint certificate shall be obtained for completion of the same. | Lot | 1 | 7048.65 | 634.3785 | 634.3785 | 8317.407 | 8317.407 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
28.1 | Demonstration of the 100KV Automatic Transformer Oil Breakdown Voltage test set (Megger- OTS 100AF / Baur- DTA 100C) | Nos | 1
28.2 | Demonstration of the 10KV Insulation Tester with 15m test lids (Megger- S1-1068 / Sonel-MIC 10K1) | Nos | 1
28.3 | Demonstration of the Digital Earth Tester (Facility with soil resistivity measurement) (Megger-DET2/3 / Sonel MRU-120 / Fluke 1625) | Nos | 1
28.4 | Demonstration of the Digital Multimeter (Megger / Fluke) | Nos | 2
28.5 | Demonstration of the Digital Clamp meter (Megger/Fluke/Motwane) | Nos | 1
28.6 | Demonstration of the Leakage current clamp meterAC & DC both (30mA / 300mA / 30A / 300A) (Megger/Fluke/Kyoritsu) | Nos | 1
28.7 | Demonstration of the SF6 Gas Leakage Detector (Kika/DILO) | Nos | 1
28.8 | Demonstration of the Oil sampling Bottle- Stainless Steel, Capacity- 1 Ltr (Make- Tosin) | Set | 6
28.9 | Demonstration of the Fibre Glass Discharge / Earth Rod: Grip up to 50mm, Min height-16ft, rubber grip, 35 sq.mm copper cable (1 set- 3 cables, 1 set of rod, carry bag) (Bemico) | Nos | 2
28.1 | Installation of the Desktop Computer: (HP/Lenovo/Dell) complete with all accessories including webcam and speakers and validation of the Genuine Windows Operating System | Set | 2
28.11 | Installation of the UPS 600VA (APC/V Guard) and verification of the backup | Nos | 2
28.12 | Installation of the Laser Printer, Black & White, Duplex printing (print, scan & copy) (HP/Canon/Epson) | Nos | 1
29 | Installation and demonstration of De Mineralised Plant. The capacity/Hr of the palnt and the sp gravity of the de-mineralised water shall be verified and certified by the site engineer. | Set | 1 | 2238 | 201.42 | 201.42 | 2640.84 | 2640.84 | market price
30 | Installation & demo of the Storage Water Cooler (Voltas/Bluestar only) with at least 20ltr storage for performance |  | 1 | 1000 | 90 | 90 | 1180 | 1180 | market price
31 | Installation and demo of the Water Purifier (Kent/Aquaguard/ for performance |  | 1 | 1000 | 90 | 90 | 1180 | 1180 | market price
32 | Office Furniture: Godrej make (As per details below). Placing In Control Room, Communication Room, Conference Room, Office Rooms, Library, Testing Lab etc. | Lot | 1 | 7048.65 | 634.3785 | 634.3785 | 8317.407 | 8317.407 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
32.1 | For Control Room, conference room, office rooms, Library, testing room etc
32.2 | 5ftX3ft executive table with drawer both sides | Nos | 4
32.3 | 4.5ft X 2.5ft Table with one side drawer | Nos | 7
32.4 | Computer table suitable keeping monitor, CPU, UPS and printer with two nos revolving arm chair suitable for computer use. | Set | 1
32.5 | Executive revolving, adjustable (height) chairs with arm | Nos | 4
32.6 | Cushion fixed “S” type steel chairs with arm | Nos | 16
32.7 | 6ftX3ft conference table | Nos | 1
32.8 | Cushion arm steel chairs for conference table purpose. | Nos | 6
32.9 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 3
32.1 | 6ft height steel almirah with glass doors for library purpose | Nos | 2
32.11 | 6ft height (having minimum 6 lockers facility) steel cupboard with locking arrangement. | Nos | 2
32.12 | 4ft steel rack (minimum three selves) for keeping the files and other items. | Nos | 8
32.13 | For Communication Room
32.14 | 5ftX3ft executive table with drawer both sides | Nos | 1
32.15 | Executive revolving, adjustable (height) chairs with arm | Nos | 1
32.16 | Cushion fixed “S” type steel chairs with arm | Nos | 2
32.17 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 1
33 | Insulating Mat: Best Quality & approved make (Confirming to IS:15652:2006) to be placed infront & backside of all panels, boards etc.(2000X1000X3mm Size) | Nos | 40 | 21 | 1.89 | 1.89 | 24.78 | 991.2 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
34 | Installation , Testing and commissioning of Visual Monitering System (VMS) with Connection to OPTCL Remote Control Center: | Lot | 1 | 47250 | 4252.5 | 4252.5 | 55755 | 55755 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
PART-A | ERECTION COMPONENT OF THE WORKS CONTRACT FOR SUBSTATION | [6 empty] | 10654091.6266
Note on B110: Optcl: Revised

## Civil
CIVIL WORKS |  |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Construction of 2 x 80 MVA, 132/33 KV Sub-station Kutra with SAS
CIVIL WORKS _SUBSTATION
Sl. No. | DESCRIPTION OF ITEMS(SCHEDULE-VIIC-SS) CIVIL WORK COMPONENT OF THE WORKS CONTRACT OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT OF MEASUREMENT | QUANTITY: Construction of 132/33 KV Sub-station with SAS (132 KV Bay-02 Nos.: 02 TRF & (33 KV Bay-06 Nos.: 03 FDR, 02 TRF, 01 B/C | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY
1 | 2 | 3 |  | 5 | 6= {5*9%} | 7= {5*9%} | 8= {5+6+7} | 9= {8*4}
1 | 2 | 3 | 4 | 5 | 6= {5*9%} | 7= {5*9%} | 8= {5+6+7} | 9= {8*4}
PART A | CIVIL WORKS
1 | CONTOUR SURVEY,AND LEVELING, BACK FILLING
1.1 | Contour survey and furnishing contour map including supply of all materials, Labour and T&P | SQ.MTRS. | 11200 | 5.78 | 0.5202 | 0.5202 | 6.8204 | 76388.48 | Annexure - II SSN-1.10
1.2 | Soil investigation : Supply of labour,T&P and other necessary arrangements for Soil investigation/testing (7mtrs) for the Switchyard, control Room, Quarters area etc.as per the site requirement, Technical specification & instruction of Engineer-in-Charge. | PER POINT | 2 | 37978.72 | 3418.0848 | 3418.0848 | 44814.8896 | 89629.7792 | Annexure - I TLN Survey -1.5 (b)
2 | Excavation for OPEN CAST foundation including shoring and back filling of columns, Equipments foundations, including supply of all labours,T&P,and materials and as per the direction of the Engineer-in-Charge.
2.1 | Normal Soil(SOFT/LOOSE) | Cum | 200 | 205.895 | 18.5306 | 18.5306 | 242.9561 | 48591.22 | Annexure - II B SSN -4 & 5 Avg.
2.2 | Hard Soil | Cum | 400 | 316.47 | 28.4823 | 28.4823 | 373.4346 | 149373.84
2.3 | Soft Rock | Cum | 320 | 678.68 | 61.0812 | 61.0812 | 800.8424 | 256269.568
2.4 | Hard Rock(Requiring Blasting/Using breaker machinery) | Cum | 80 | 1128.59 | 101.5731 | 101.5731 | 1331.7362 | 106538.896
3 | OPEN CAST/SHALLOW FOUNDATION CONCRETE WORKS
3.1 | Foundations: Design, engineering, supply of all labour, material and construction(open cast foundation) of PCC, RCC footings of any depth, pedestal including the cost of concreting, cement, reinforcement steel, shuttering, grouting, underpinning and back filling of foundations etc complete for the switchyard gantry/ portal /column structures and equipment support as per the technical specification and approved drawings & disposal of excess earth as per direction of Engineer In charge. (a) For Switch yard gantry/portal structure foundations (b) For 132 & 33 KV Equipment foundations. (c) For other equipment foundations.
3.1.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in for the above column/equipment/marshalling box foundations for column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 80 | 5907.71 | 531.6939 | 531.6939 | 6971.0978 | 557687.824 | Annexure - II SSN Foundation Work Sl. No. 1.20 (i)
3.1.2 | Open cast foundation for the above column/equipment/marshalling box foundations with RCC: 1:1.5:3 (Grade M-20) ,including supply of Labour all materials like cement, coarse and fine aggregates, shuttering, proper curing of the foundations/concrete and T&P in line with the Techinical Specification and as per direction of Engineer in Charge. ( without cost of steel) | Cum | 1000 | 8533.36 | 768.0024 | 768.0024 | 10069.3648 | 10069364.8 | Annexure - II SS Foundation Work Sl. No. 1.40 (i)
3.1.3 | Supply of steel different sizes(TATA/RINL/SAIL make). No other make of steel shall be allowed. (as per the design) with cutting, bending, binding and placing in position of steel rods for foundation concreting including cost of binding wire. | MT | 25 | 65511.29 | 5896.0161 | 5896.0161 | 77303.3222 | 1932583.055 | Annexure - II SSN Foundation and Reinforcement Sl. No. 1.10 (i) with steel
4 | Cutting, Filling and Leveling of Sub-station area including supply of labour and T&P
4.1 | LEVELLING OF S/S AREA:Providing, neatly dressing up and levelling of substation area including switchyard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification.
4.1.1 | CUTTING of substation area, utilising the usable soil for filling and compaction and disposing the unsuable soil from site
4.1.1.1 | Soft/loose soil | Cum | 200 | 183.02 | 16.4718 | 16.4718 | 215.9636 | 43192.72 | Annexure - II SSN Cutting Filling and Leveling Work Sl. No. 1(i) | 500
4.1.1.2 | Dense/ Compact soil | Cum | 200 | 289.77 | 26.0793 | 26.0793 | 341.9286 | 68385.72 | Annexure - II SSN Cutting Filling and Leveling Work Sl. No. 1(ii) | 500
4.1.1.3 | Soft/Disintegrated rock[not requiring blasting] | Cum | 200 | 594.8 | 53.532 | 53.532 | 701.864 | 140372.8 | Annexure - II SSN Cutting Filling and Leveling Work Sl. No. 1(iii) | 500
4.1.1.4 | Hard rock[requiring blasting or by using concrete breaker machinery] | Cum | 0 | 1128.58 | 101.5722 | 101.5722 | 1331.7244 | 0 | Annexure - II SSN Cutting Filling and Leveling Work Sl. No. 1(iv) | 0
4.1.2 | FILLING of substation area with borrowed earth with supply of all labour,T & P. |  | 0
4.1.2.1 | Up to 30 mtr lead | Cum | 0 | 415.04 | 37.3536 | 37.3536 | 489.7472 | 0 | Annexure - II SSN Cutting Filling and Leveling Work Sl. No. 2(i) | 0
4.1.2.2 | Beyond 30 mtr & up to 100mtr lead | Cum | 200 | 644.03 | 57.9627 | 57.9627 | 759.9554 | 151991.08 | Annexure - II SSN Cutting Filling and Leveling Work Sl. No. 2(ii) | 500
4.1.2.3 | Beyond 100mtr lead | Cum | 16000 | 1144.94 | 103.0446 | 103.0446 | 1351.0292 | 21616467.2 | Annexure - II SSN Cutting Filling and Leveling Work Sl. No. 2(iii) | 40000
5 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in cable trench as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing),including supply of Labour all materials like MS Rod,Cement, coarse and fine aggregates,shuttering,cutting,bending,binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) The outdoor cable trench wall top surface shall be "L" shaped and the cover slabs shall be placed with in the"L shaped" surface of both the walls. The top surface of the trench shall be smooth finished. (5)Supply,fabrication & Fixing of GI Angle for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the GI insert plate fixed on the trench wall for better rigidity. The Insert plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. (6) Precast of RCC covers (1:1.5:3) with MS sheet (2mm thick) and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (7) All the RCC cover slabs shall have the lifting hooks. The slabs without the MS sheet frame and Lifting hooks shall not be accepted. (8)Cable trenches inside the control room building shall be covered M.S Chequered plate (Duly painted as per instruction of Engg in charge) including standard support stand {HD Galvanised (M.S JOIST, CHANNEL, ANGLE)}.
5.1 | Section 2- 2 | Mtrs | 60 | 10500 | 945 | 945 | 12390 | 743400 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
5.2 | Section 3-3 | Mtrs | 140 | 9450 | 850.5 | 850.5 | 11151 | 1561140 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
5.3 | Section 4-4 | Mtrs | 100 | 5202.75 | 468.2475 | 468.2475 | 6139.245 | 613924.5 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
6 | Rain water harvesting system as per Technical specification and approval of drawing and as per the direction of the Engineer in charge. | Nos | 1.6 | 210000 | 18900 | 18900 | 247800 | 396480 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
7 | Cable trench crossing:Design,engineering,construction including supply of labour,materials,cement,reinforcement steel,formwork etc,and all associated works for construction of trench crossing as per technical specification and approved drawing.(Road crossing )
7.1 | Section 2-2 | Nos | 1 | 82195.05 | 7397.5545 | 7397.5545 | 96990.159 | 96990.159 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
7.2 | Section 3-3 | Nos | 2 | 70490.7 | 6344.163 | 6344.163 | 83179.026 | 166358.052 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
8 | Out door bay kiosks: Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The indicative drawing provided in the TS may be referred to. As per approved drawings and specification. Doors shall be heat insulated and hinge type. The area given is for reference only and may vary according to requirement of the equipment to be installed inside. The contractor shall finalize the dimensions according to the equipment offered by them providing enough space & access for erection, operation and maintenance & future expansion.
8.1 | Switchyard Kiosk for 132KV -inside dimensions- 8m (L)x 5m (W) x 3.3m(H)
8.1.1 | Excavation in all type of soil(including Hard Rock) upto all depth,PCC and RCC volume including MS rods (FE-500-TATA/ RINL/ Sail) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. ( including for Pile foundation if required with cost of boring, Column ,Beams and roofs etc. ) | Lot | 1 | 166956.88 | 15026.1192 | 15026.1192 | 197009.1184 | 197009.1184 | Market price
8.1.2 | Fly Ash Brick masonry work in cement sand mortar 1: 5 with bricks of class designation 75kg/mm2 as per technical spec & approved drawings. | Lot | 1 | 100174.13 | 9015.6717 | 9015.6717 | 118205.4734 | 118205.4734 | Market price
8.1.3 | Flooring shall be with vitrified digital double charged tiles (Kajaria/Johnson/Somany/Varmora/Cera) with dado as per technical spec & approved drawings. | Lot | 1 | 33391.38 | 3005.2242 | 3005.2242 | 39401.8284 | 39401.8284 | Market price
8.1.4 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 1 | 16695.7 | 1502.613 | 1502.613 | 19700.926 | 19700.926 | Market price
8.1.5 | Doors shall be of hinge operated openable and window shall be sliding type with adequate locking facility. The door window frame shall be of UPVC (Fenesta make) heavy sections with double layer toughened glaze of 6mm (min.) & windows shall have anodised aluminium grills. As per technical spec & approved drawing. | Lot | 1 | 33391.38 | 3005.2242 | 3005.2242 | 39401.8284 | 39401.8284 | Market price
8.1.6 | Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make) ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 66782.75 | 6010.4475 | 6010.4475 | 78803.645 | 78803.645 | Market price
8.1.7 | Provision of smoke and fire detection & Alarm system of the kiosks - to be integrated with the system in the main CRB. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 | 75825.04 | 6824.2536 | 6824.2536 | 89473.5472 | 89473.5472 | Market price
8.2 | Switchyard Kiosk for 33KV -inside dimensions- 5m (L)x 5m (W) x 3.3m(H)
8.2.1 | Excavation in all type of soil(including Hard Rock) upto all depth,PCC and RCC volume including MS rods (FE-500-TATA/ RINL/ Sail) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. ( including for Pile foundation if required with cost of boring, Column ,Beams and roofs etc. ) | Lot | 1 | 104348.05 | 9391.3245 | 9391.3245 | 123130.699 | 123130.699
8.2.2 | Fly Ash Brick masonry work in cement sand mortar 1: 5 with bricks of class designation 75kg/mm2 as per technical spec & approved drawings. | Lot | 1 | 62608.83 | 5634.7947 | 5634.7947 | 73878.4194 | 73878.4194
8.2.3 | Flooring shall be with vitrified digital double charged tiles (Kajaria/Johnson/Somany/Varmora/Cera) with dado as per technical spec & approved drawings. | Lot | 1 | 20869.61 | 1878.2649 | 1878.2649 | 24626.1398 | 24626.1398
8.2.4 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 1 | 10434.81 | 939.1329 | 939.1329 | 12313.0758 | 12313.0758
8.2.5 | Doors shall be of hinge operated openable and window shall be sliding type with adequate locking facility. The door window frame shall be of UPVC (Fenesta make) heavy sections with double layer toughened glaze of 6mm (min.) & windows shall have anodised aluminium grills. As per technical spec & approved drawing. | Lot | 1 | 20869.61 | 1878.2649 | 1878.2649 | 24626.1398 | 24626.1398
8.2.6 | Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make) ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 41739.22 | 3756.5298 | 3756.5298 | 49252.2796 | 49252.2796
8.2.7 | Provision of smoke and fire detection & Alarm system of the kiosks - to be integrated with the system in the main CRB. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 | 47390.65 | 4265.1585 | 4265.1585 | 55920.967 | 55920.967
9 | Roads: Design, supply of all labour, materials & construction of roads and walkways/ shoulders within sub-station (Switch yard area,colony area/transit house, approach road, control room building area, main gate to the switch yard gate etc) as per specification, layout and approved drawings in complete shape. This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Engineer In charge.
9.1 | Approach Road: 7 mtrs concrete road with shoulder (600mm) at both the side as per technical specification indicated in the civil section(from the switch yard main gate to the govt road.) | Mtrs | 75 | 13006.35 | 1170.5715 | 1170.5715 | 15347.493 | 1151061.975 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
9.2 | 7 mtrs concrete road with shoulder (600mm) at both the side as per technical specification indicated in the civil section(from the switch yard main gate to power transformer & infront of GIS cum control room building) | Mtrs | 200 | 13006.35 | 1170.5715 | 1170.5715 | 15347.493 | 3069498.6 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
9.3 | 3.75 mtrs concrete road with shoulder (500mm) at both the side as per technical specification indicated in the civil section( Periphery roads outside switch yard fencing and colony roads) | Mtrs | 750 | 4699.8 | 422.982 | 422.982 | 5545.764 | 4159323 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
10 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme (RCC type), road-culverts,Shall have drain on both side of the road and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. All the switch yard bays , roads water drainage shall be connected to the main surface drain. As per approved drawing and specification. All the drainage system shall be RCC type with M20 grade concrete.
10.1 | Storm water drain (RCC type) as per design above and subsequent approval | Mtrs. | 200 | 2800 | 252 | 252 | 3304 | 660800
10.2 | Road side drains(RCC type)-on each side of the 3.75 mtr and 7 mtr concrete roads as per design above & subsequent apporval | Mtrs | 1500 | 2800 | 252 | 252 | 3304 | 4956000
10.3 | Road-culverts, drain crossings (RCC type) | Lots | 1 | 525000 | 47250 | 47250 | 619500 | 619500 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
11 | Foundations for transformers: Design, engineering, supply of labour, material, equipments and construction of Auto-transformer/Transformer foundation including piling if required, all associated works, rail tracks, jacking pads,anchor block RCC and PCC, miscellaneous structural steel including oil collection pits, MS grating(if required), gravel filling, and other items etc. not mentioned herein, but specifically required for the completion of the work as per technical specification and approved drawing. (Rate shall be inclusive of cement, reinforcement steel, angles,flats and form work etc.)(all cement concrete shall have RCC ratio 1:1.5:3). Transformer RCC foundation and Rail Track should be extended upto the approach road (However, the height of RCC foundation beyond transformer main plinth area should be same as height of concrete road ). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth.
11.1 | 50 MVA 132/33KV Transformer a) Overall dimension of transformer(appox) Length:12420 mmX Width 7200 mmX Height 6200 mm b) Total weight with oil and tank: 150 MT (appox) | Nos | 2 | 650278.65 | 58525.0785 | 58525.0785 | 767328.807 | 1534657.614 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
11.2 | OIL SUMP PIT (150% of tfr oil capacity of one transformer): Design, engineering, supply of labour, material, equipments and construction of oil sump pit (RCC with ratio 1:1.5:3) including piling if any, all associated works & suitable connectivity oil collector pit provisioned near the transformer to the main oil sump pit and with provision of pump (suitable for handling transformer oil having capacity of 5 HP, with auto level control , including cabling, fixing of control gear & provision of a pump shed (of sufficient size to allow person to install, dismantle, make cable connection & maintain etc) over the oil sump pit). This oil sump pit shall be as per CIGRE standard for the oil collection pit inorder to separate oil from the water. Other piping with necessary valves arrangement shall also be provided to remove water from the oil sump pit. As per spec and approved drawing. | Nos | 1 | 286122.9 | 25751.061 | 25751.061 | 337625.022 | 337625.022 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
12 | FIRE FIGHTING (Nitrogen Injection Type Fire Prevention & Extinguishing System) SYSTEM WITH DETAILED DESIGN SUITABLE FOR 80 MVA, 132/33 KV POWER TRANSFORMER etc AS PER THE TECHNICAL SPEC. & LATEST STANDARD.
12.1 | All civil works related to NIFPES as per approved drawing including excavation in all type of soil, PCC, RCC, Steel , backfilling, compaction etc complete in all respect as per instruction of site in-charge. | Lot | 2 | 210000 | 18900 | 18900 | 247800 | 495600 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
13 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:4:8 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. (Switch yard area) | CUM | 400 | 5804.07 | 522.3663 | 522.3663 | 6848.8026 | 2739521.04 | Annexure - II SSN Foundation Work Sl. No. 1.30 (i)
14 | METAL SPREADING IN THE SWITCH-YARD: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:4:8).The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 600 | 3233.69 | 291.0321 | 291.0321 | 3815.7542 | 2289452.52 | Annexure - II SSN Foundation Work Sl. No. 3.10
15 | Anti-Weed Treatment :Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treat of the switch-yard areas,controlroom etc. as per the instruction of Engineer-in-Charge.The chemical to be sprayed as per the standard practice adopted for antiweed treatment of sub-station area & as per the technical specification. | Sq Mtrs | 5000 | 18.732 | 1.6859 | 1.6859 | 22.1038 | 110518.8 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
16 | CONTROL ROOM cum office BUILDING: Design, engineering and construction of switch yard buildings including excavation, construction of foundations (open cast or pile as per soil conditions), construction of RCC super structure, brick wall, plastering,painting, Flooring etc.The cost of material, supply of labour, cement, reinforcement- steel and form work as per the enclosed drawing and technical specification ( The RCC structure frame and the foundations should be in the ratio 1:1.5:3). The indicative drawings of the building is provided and the foundation of the building shall be designed based on the actual soil condition. It shall be ensured that the various room sizes are sufficient to accomodate the offered equipment.
16.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 | 472218.55 | 42499.6695 | 42499.6695 | 557217.889 | 557217.889 | Market price
16.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 399089.82 | 35918.0838 | 35918.0838 | 470925.9876 | 470925.9876 | Market price
16.3 | Providing & laying Plain cement concrete (1:2:4) (in sunken slab areas)using 12mm size black hard crusher broken granite chips of approved quality from approved quarry including hoisting, lowering and laying concrete in layers, watering, curing etc. complete including cost, conveyance, royalties and taxes of all materials with labour, cess and T&P etc. required for the work complete. | Lot | 1 | 33311.04 | 2997.9936 | 2997.9936 | 39307.0272 | 39307.0272 | Market price
16.4 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations, columns, Beams, lintels, chhajas, roof slabs, stair case etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 3166323.25 | 284969.0925 | 284969.0925 | 3736261.435 | 3736261.435 | Market price
16.5 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 4139142.58 | 372522.8322 | 372522.8322 | 4884188.2444 | 4884188.2444 | Market price
16.6 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) for foundation and plinth and in cement mortar of mix (1:4) for other area in ground floor, first floor & head room with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 952316.33 | 85708.4697 | 85708.4697 | 1123733.2694 | 1123733.2694 | Market price
16.7 | Providing 16 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 307132.95 | 27641.9655 | 27641.9655 | 362416.881 | 362416.881 | Market price
16.8 | Providing 18mm C.P. in two coats underlayer 12mm C.P. 1:5 and top layer 6mm thick C.P. 1:6 finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 161769.49 | 14559.2541 | 14559.2541 | 190887.9982 | 190887.9982 | Market price
16.9 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 124675.99 | 11220.8391 | 11220.8391 | 147117.6682 | 147117.6682 | Market price
16.1 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 551821.51 | 49663.9359 | 49663.9359 | 651149.3818 | 651149.3818 | Market price
16.11 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 75635.64 | 6807.2076 | 6807.2076 | 89250.0552 | 89250.0552 | Market price
16.12 | Supplying, fitting and Fixing Matt finish full body vitrified Acid proof tiles in floor and in dado upto lintel level of Battery room of 10MM thick, size 300mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 150000 | 13500 | 13500 | 177000 | 177000 | Market price
16.13 | Providing, fitting & fixing anti-skid ceramic floor tiles in flooring in toilets using special plain/ printed series anti-skid ceramic floor tile of premium grade (having minimum thickness 7 mm to 8 mm & size 300 mm x 300 mm confirming to IS 13755 of approved quality and shade of Somany/ Kajaria / Johnson on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened & washed sharp river sand for mortar ceramic floor tiles with neat white cement slurry, mixed with required (tiles are to be immersed in the water for required time before use) quantities of pigments of approved marks to match the shades of the anti-skid ceramic floor tiles if required including cost, conveyance, loading, unloading, stacking, royalties of all material, cost of all labour, sundries, T&P required for the work, watering, complete in all respect as per specification excluding GST as per specification as directed by Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 39320.66 | 3538.8594 | 3538.8594 | 46398.3788 | 46398.3788 | Market price
16.14 | Providing & Fixing tiles of size 30cm x 45 cm glazed ceramic wall tiles (All Toilet walls) of premium grade of approved quality and shade having thickness 8mm to 10mm confirming to IS 13755 in dados skirting and risers of steps on 12mm thick cement plaster (1:3) to proper slope, line and level including cutting to required size and shape, fixing at corners and splays etc including filling the joints with neat white cement slurry mixed with pigments to match the shade of the tiles including cost, Conveyance, loading, unloading, stacking, royalities of all materials, cost of all labour,T&P, sundries, watering and curing for the required period for the work complete in all respect excluding GST as directed by the Engineer-in-charge.(Note- Sample of tiles shall be approved before procurement and use.) | Lot | 1 | 149553.44 | 13459.8096 | 13459.8096 | 176473.0592 | 176473.0592 | Market price
16.15 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 212776.97 | 19149.9273 | 19149.9273 | 251076.8246 | 251076.8246 | Market price
16.16 | Providing Granite stone prepolished 10mm thick in dado of approved quality, colour and size in dado, riser of steps and dado of landings in all floors at all height on 12mm thick bed of cement mortar of mix (1:3) with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 32408.47 | 2916.7623 | 2916.7623 | 38241.9946 | 38241.9946 | Market price
16.17 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 172573.2 | 15531.588 | 15531.588 | 203636.376 | 203636.376 | Market price
16.18 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board and pasting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. (In toilets, rest rooms) | Lot | 1 | 94601.43 | 8514.1287 | 8514.1287 | 111629.6874 | 111629.6874 | Market price
16.19 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board, Vision glass panel (1.5ft x 1ft) and paisting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. (All except in toilets & rest rooms) | Lot | 1 | 581918.03 | 52372.6227 | 52372.6227 | 686663.2754 | 686663.2754 | Market price
16.2 | Supplying, fitting and fixing of M.S grills, Grill window (as per I.S. specification and as per approved drawings) in proper position in all floors as per TS, approved drawing, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 118410.72 | 10656.9648 | 10656.9648 | 139724.6496 | 139724.6496 | Market price
16.21 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge. | [7 empty] | Market price
16.21.1 | Inside walls and Ceiling: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 523170.83 | 47085.3747 | 47085.3747 | 617341.5794 | 617341.5794 | Market price
16.21.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 101515.94 | 9136.4346 | 9136.4346 | 119788.8092 | 119788.8092 | Market price
16.21.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 9298.75 | 836.8875 | 836.8875 | 10972.525 | 10972.525 | Market price
16.22 | Supplying, fitting and fixing of Stainless steel of 304 grade in hand railing using 50mm dia of 2mm thick circular pipe with Balustrade of size 32mm x 32mm x 2mm @ 0.90mtr. C/C and stainless square pipe bracing of size 32mm x 32mm x 2mm in 3 rows in stair case as per approved design and specification, buffing, polishing etc with cost, conveyance, cost of all labour,labour cess, T&P etc. required for the work complete in all respect as per direction of the Engineer-in-charge. | Lot | 1 | 50521.27 | 4546.9143 | 4546.9143 | 59615.0986 | 59615.0986 | Market price
16.23 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 100978.98 | 9088.1082 | 9088.1082 | 119155.1964 | 119155.1964 | Market price
16.24 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 66936.46 | 6024.2814 | 6024.2814 | 78985.0228 | 78985.0228 | Market price
16.25 | Providing and fixing of UPVC sliding windows in the Control room Building as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 574776 | 51729.84 | 51729.84 | 678235.68 | 678235.68 | Market price
16.26 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 173473.8 | 15612.642 | 15612.642 | 204699.084 | 204699.084 | Market price
16.27 | Water proofing to the sunken slab including providing and filling it with 40mm size brick bat as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 12652.79 | 1138.7511 | 1138.7511 | 14930.2922 | 14930.2922 | Market price
16.28 | Providing and fixing removable Raised/False Flooring System in the control room as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 364390 | 32795.1 | 32795.1 | 429980.2 | 429980.2 | Market price
16.29 | Plinth Potection for control room building as per the provided drawing and as per sepcification in TS. | Lot | 1 | 92194.88 | 8297.5392 | 8297.5392 | 108789.9584 | 108789.9584 | Market price
16.3 | Construction of covered drain for control room building as per the provided drawing and as per specification in TS. | Lot | 1 | 330956.09 | 29786.0481 | 29786.0481 | 390528.1862 | 390528.1862 | Market price
16.31 | Provision of PHD and other fittings of Jaguar make for the control room building (in Toilets, wash room, overhead water tank of adequate capacity etc) of reputed make, provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing. Provision of rain water discharge pipes at different locations and two nos of over head water tank of 2000 ltrs capacity etc as per requirement and approved drawing. All bath room & toilet shall have water & termite proof doors and provision of sliding louvers with exhaust fan. | Lot | 1 | 776921.44 | 69922.9296 | 69922.9296 | 916767.2992 | 916767.2992 | Market price
16.32 | Construction of septic tank and soak pit for control room building as per the provided drawing and as per specification in TS. | Lot | 1 | 255823.4 | 23024.106 | 23024.106 | 301871.612 | 301871.612 | Market price
16.33 | Construction of borewell for control room building as per the specification in TS. | Lot | 1 | 210940.68 | 18984.6612 | 18984.6612 | 248910.0024 | 248910.0024 | Market price
16.34 | Provision for Electrical Work:Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make), fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 1108185.91 | 99736.7319 | 99736.7319 | 1307659.3738 | 1307659.3738 | Market price
16.35 | Provision of Fire alarm system for the control room building as per the provided drawing and as per specification in TS. | Lot | 1 | 93565 | 8420.85 | 8420.85 | 110406.7 | 110406.7 | Market price
16.36 | Provision of false ceiling in the control room building (Control room, Office space, Cabins, rest rooms, Communication room, ACDC room & lobby) as per specification mentioned in the civil section & approved drawings including, relay panel room, office room, SAS room, conference room, transit room etc as per direction of the engineer in charge. | Lot | 1 | 250000 | 22500 | 22500 | 295000 | 295000 | Market price
17 | MAIN GATE, WICKET GATE & SECURITY SHED (GATE COMPLEX): The Main gate, wicket gate and the Secirity shed shall be constructed as per the drawing provided and technical specification, complete in all respect and as per instruction of Engineer in charge. The foundation shall be designed as per actual site soil condition and shall be constructed as per approved drawing. | [7 empty] | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil & rock as per drawing and technical specification complete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the surplus earth/unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. This includes cost, conveyance of all materials, all labour, T&P articles required for the work, stacking the useful materials separately, including shoring, shuttering, propping and dewatering if required etc. | Lot | 1 | 35532.43 | 3197.9187 | 3197.9187 | 41928.2674 | 41928.2674 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.2 | Providing and lying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 30322.32 | 2729.0088 | 2729.0088 | 35780.3376 | 35780.3376 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.3 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundation & base of column work, all column, all beam, all pedestal, all lintel, all chajja, all slab, all projection etc.), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 443372.68 | 39903.5412 | 39903.5412 | 523179.7624 | 523179.7624 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.4 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, including cost of binding wires, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 565359.94 | 50882.3946 | 50882.3946 | 667124.7292 | 667124.7292 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.5 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 90680.42 | 8161.2378 | 8161.2378 | 107002.8956 | 107002.8956 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.6 | Providing 12 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 14705.25 | 1323.4725 | 1323.4725 | 17352.195 | 17352.195 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.7 | Providing 16mm thick cement plaster ( 1:6) finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 16080.99 | 1447.2891 | 1447.2891 | 18975.5682 | 18975.5682 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.8 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 8988.68 | 808.9812 | 808.9812 | 10606.6424 | 10606.6424 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.9 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 8613.92 | 775.2528 | 775.2528 | 10164.4256 | 10164.4256 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.10 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 2071.9 | 186.471 | 186.471 | 2444.842 | 2444.842 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.11 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 2782.87 | 250.4583 | 250.4583 | 3283.7866 | 3283.7866 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.12 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 6003.88 | 540.3492 | 540.3492 | 7084.5784 | 7084.5784 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.13 | Providing and fixing of 35mm thick WPC Door Shutter(Solid) with teak edge leaping to the periphery of the shutter with pilishing as per detailed drawing with including, all hardwares & fixtures, SS tower bolt(150mm), Door stopper, SS aldrop(250mm), SS handle(200mm length), ss handle (150mm length) & SS Butt hinges -125mm x 65mm x2.12mm .including cost, conveyance, loading, T&P required for the work etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 12476.16 | 1122.8544 | 1122.8544 | 14721.8688 | 14721.8688 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.14 | Supplying, fitting and fixing of M.S grills for windows, Main Gate, wicket gate etc. (as per I.S. specification and as per approved drawings ) in proper position in all floors and at all height including making holes to brick walls/ R.C.C structure/wood work etc. and making good to the damaged walls/ structures with cement concrete (1:2:4) with black hard crusher broken granite stone chips of 12mm to 20mm size ( 20mm size not to exceeds 25% ) including watering and curing etc. complete in all respect as directed by the Engineer in charge. (W.I. / M.S. windows grills, grill gates, collapsible gates with top and bottom rails, steel windows, steel doors, steel frames for doors and windows, staircase and parapet railings square bar along with required nos. of nails and screws and other required materials of approved quality and approved size shall be supplied by the contractor at his own cost.) | Lot | 1 | 136012.19 | 12241.0971 | 12241.0971 | 160494.3842 | 160494.3842 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.15 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge. | [7 empty] | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.15.1 | Inside walls and Ceiling: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 36222.67 | 3260.0403 | 3260.0403 | 42742.7506 | 42742.7506 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.15.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 14163.64 | 1274.7276 | 1274.7276 | 16713.0952 | 16713.0952 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.15.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 5032.84 | 452.9556 | 452.9556 | 5938.7512 | 5938.7512 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.16 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 14502.83 | 1305.2547 | 1305.2547 | 17113.3394 | 17113.3394 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.17 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 6770.36 | 609.3324 | 609.3324 | 7989.0248 | 7989.0248 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.18 | Providing and fixing of UPVC sliding windows in the Transit house as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 26280 | 2365.2 | 2365.2 | 31010.4 | 31010.4 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.19 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 24914.7 | 2242.323 | 2242.323 | 29399.346 | 29399.346 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.20 | GFRC Letter: Manufacturing, providing and installation of GFRC mouldings (Glass Fiber Reinforced Concrete) of approved make of thickness 230mm±5mm with pattern, design and colour of approved make to be fixed on/beteween RCC/ block work column or structural work with dry fixing method with all required T & P , manpower and all other material as required for completion of work in all respect.
17.20.1 | Per Letter (450mm(h) x 40mm (d) x 50mm (w)) | Nos | 50 | 800 | 72 | 72 | 944 | 47200 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.20.2 | OPTCL Logo | Nos | 1 | 1000 | 90 | 90 | 1180 | 1180 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.21 | Electrical works of Main Gate, Wicket gate and Security Shed: As per the provided drawing and as per specification in TS. This also includes supply of all electrical materials (of specified manufacturer as indicated in the TS) for main gate, wicket gate & security shed to complete the work as as per description provided in the relevant section of TS. | Lot | 1 | 244423.62 | 21998.1258 | 21998.1258 | 288419.8716 | 288419.8716 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
17.22 | Supply of the following materials: a) First Aid Box - 1 set b) Shock Treatment Chart (Odia, Hindi & English) - 1 set c) Insulating mat - 6 sq. m. d) Danger Board - 1 set | Lot | 1 | 6015 | 541.35 | 541.35 | 7097.7 | 7097.7 | Sanctioned estimate-09/25-26 dt.03.06.25 vide order no.EHTC/CLE/SBP/T-412/404 Dt.13.06.2025 of G.M(Ele) Const. Circle,Sambalpur
18 | BOUNDARY WALL (RCC structure, Brickwall type)
18.1 | BOUNDARY WALL: The boundary wall shall be constructed to a height of 2 mtrs above finished ground level of the substation area with 10” wide brick masonry work with RCC(1:1.5:3) ground tie beam to be rested on the RCC pillars (pillar to pillar distance @ 3mtrs) as per specification. | RM | 150 | 7875 | 708.75 | 708.75 | 9292.5 | 1393875 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
18.1.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil and rock as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plinth with sand, compaction, carriage & disposal of the unsuable earth material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1
18.1.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1
18.1.3 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations & bases of column, Beams, pedestal & column, rcc band etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour, Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1
18.1.4 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1
18.1.5 | Providing Brick work with Fly ash bricks 25cm x 12cm x 8cm size having crushing strength not less than 75 kg/cm2 with dimensional tolerance +/ - 2 percent in cement mortar (1:6) ( 1 cement: 6 sand), with all necessary projection, splay cutting, circular moulding, corbelling, etc., including cost of all materials, labour, conveyance, loading ,and unloadining, royalties, scaffolding, watering, curing, sundries, tools and plants, etc., as per the direction of the Engineer-in-charge. | Lot | 1
18.1.6 | Providing 16 mm. thick cement plaster in all floors at all height with cement mortar of mix (1:6) with portland slag cement (PSC) finished smooth to inside rough surface of brick masonry walls after racking out joints including watering and curing rounding of corners etc. complete with cost, coveyance, loading and unloading, royalties and ,es of all materials and cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. (Inside) | Lot | 1
18.1.7 | Painting of wall surface with weather coat two coats over a coat of primer of approved shade and quality of approved design after cleaning by watering & removing the dirts etc. to the surface to be painted including watering, curing, cost, conveyance of all materials, cost of all labour, brushes, T&P etc. and necessary scaffolding work complete as directed by the Engineer-in-charge. | Lot | 1
18.1.8 | Providing and fixing of GI 'Y' angles over the boundary wall at every 1m rigdly & sufficently (at least 200mm) grouted inside the wall for the support of the concertina wire. | Lot | 1
18.1.9 | Providing and fixing concertina coil fencing with punched tape concertina coil 600mm dia 10metr openable length (total length90m), having 50nos rounds per 6m length, upto 3m height of wall with existing angle iron 'Y' shaped placed 2.4m or 3m apart and with 9 horizontal R.B.T. reinforced barbed wire, stud tied with G.I. staples and G.I. clips to retain horizontal, including necessary bolts or G.I. barbed wire tied to angle iron, all complete as per direction of Engineer-in-charge, with reinforced barbed tape(R.B.T.) / Spring core (2.5mm thick) wire of high tensile strength of 165kg/sq.mm with tape (0.52mm thick) and weight 43.478 gm/meter. | Lot | 1
19 | SWITCHYARD GATE: Design, engineering, procurement of labour, material including all associated works for construction and fixing of switch yard gates and switchyard wicket gates as per specification and approved drawing. Switchyard gates shall have RCC pillars on both sides having open or pile founfdation and the gate shall be of stainless steel square pipes of 304 grade. The main entrance gate to switchyard shall have a wicket gate made of the same material. This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth, PCC/RCC concreting, supply of cement aggregates, rebar rod etc as per the direction of Engineer In charge. It includes supply of all materials and all other associated works required to complete works as per specification and approved drawings and instruction of engineer in charge.
19.1 | Switchyard gate (On both sides of 7 m. road of switchyard) | NOS | 2 | 74318 | 6688.62 | 6688.62 | 87695.24 | 175390.48 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
19.2 | Wicket gate( The wicket gate shall have biometric authentication system) | NOS | 1 | 400000 | 36000 | 36000 | 472000 | 472000 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
20 | STATION TRANSFORMER:Design, engineering, procurement of labour, material including all associated works for construction of foundation(RCC) for the station transformers 2X 33/0.415 KV,250 KVA (plinth mounted) and foundation for 4P structure including piling if any as per approved drawing and specification. It includes other accessories & materials as required need to be supplied for complete installation of transformer as per the instruction of Engineer In charge and as per the specification and approved drawing. | Nos | 2 | 24676.68 | 2220.9012 | 2220.9012 | 29118.4824 | 58236.9648 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
21 | RCC Foundations for Octagonal Lighting Poles: Design, engineering, procurement of labour, material including piling if any, all associated works for construction of foundations for octagonal lighting poles as per approved drawings (RCC ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawing and specification. Pcc padding ratio (1:4:8). The MS Rod (FE-500-TATA/ RINL/ Sail) as per BIS-1786 to be used. | Nos | 10 | 10000 | 900 | 900 | 11800 | 118000 | Market price
22 | COLOUR CODING, BAY MARKING Etc: Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (Red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof sticker (fluorescent type) may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. Stainless Steel sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Lot | 1 | 210000 | 18900 | 18900 | 247800 | 247800 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
23 | STORE SHED+OPEN STOCKYARD: Design, engineering, construction of store shed with the cost of all required material, procurement of labour, all T&P etc. This includes supply of all materials and all associated works for construction of store shed and open stockyard, complete in all respect as per technical specification and enclosed drawing. This also includes, excavation in all type soil and rocks, backfilling and disposal of excavated soil, (cement, reinforcement steel, form work for) PCC, RCC(1:1.5:3), reinforcement steel (FE-500 as per BIS-1786) (SAIL, RINL, TATA, Jindal), Fly Ash Brick work with mortar 1:5, Plastering, Flooring, External and Internal Painting, all electrical works/items (Including but not limited to wires, conduits, GI boxes, switches, regulators, luminaires (Phillips/Crompton/Bajaj/Havells/Wipro) , fans, electrical fixtures and all other switchgear etc.), rolling shutter etc. and any other works required for completion of the work in all respect. Foundation shall be as per actual soil condition as per soil test, including piling where required. The indicative drawing provided in the TS may be referred to. | Lot | 1 | 1155000 | 103950 | 103950 | 1362900 | 1362900 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
24 | VEHICLE PARKING SHED: as per Technical specification, provided drawing and as per the direction of the Engineer in charge. Design, engineering, construction of store shed with the cost of all required material, procurement of labour, all T&P etc. This includes supply of all materials and all associated works for construction of vehicle parking shed, complete in all respect as per technical specification and enclosed drawing. This also includes, excavation in all type soil and rocks, backfilling and disposal of excavated soil, (cement, reinforcement steel, form work for) PCC, RCC (1:1.5:3), M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal), Fly ash Brick work with mortar 1:5, Plastering, Flooring, External and Internal Painting, all electrical works (Including but not limited to wires, conduits, GI boxes, switches, luminaires (Phillips/Crompton/Bajaj/Havells/Wipro), electrical fixtures and all other switchgear etc.)etc. and any other works required for completion of the work in all respect. Foundation shall be as per actual soil condition as per soil test, including piling where required. The indicative drawing provided in the TS may be referred to. | Lot | 1 | 367500 | 33075 | 33075 | 433650 | 433650 | Sanctioned estimate-58/23-24 dt.22.12.23 of ED,WZ for Bijepur GSS considering cost escalation of 5%
25 | PROVISION OF SAND BED:Design, engineering, procurement of labour, material including all associated works for construction of sand bed as per specification and approved drawing. This also includes excavation in all types of soil or rocks, back fillin ,and disposal of excess earth as per the direction of Engineer In charge. The sand bed size shall be of 10m x 5m constructed with bricks, plastered and the filled with river sand for storing of Transformer Bushings and other Insulators. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000
26 | Switch yard fencing: Providing and fixing of G.I Goat mesh fencing (the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings and as required under the safety regulation of local, State and Central Government bodies and as per instruction of the Engineer-in-Charge. This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing shall be as per specification. The fencing shall be continuous i.e. a GI flat of 50 x 6mm shall run continuous at top & at bottom all along the fence. The fencing shall be connected to the earth mat every 3 mtrs. | Mtr | 250 | 2593.18 | 233.3862 | 233.3862 | 3059.9524 | 764988.1 | Technical Sanction No: 967 dt. 03/06/2022 of ED , WZ, Burla with excalation of 5% of basic price upto FY 25-26
27 | TRANSIT HOUSE: Design, engineering and construction of switch yard buildings including excavation, construction of foundations (open cast or pile as per soil conditions), construction of RCC super structure, brick the cost of material, supply of labour, cement, reinforcement- steel and form work as per the enclosed drawing and technical specification ( The RCC structure frame and the foundations should be in the ratio 1:1.5:3). The indicative drawings of the building is provided and the foundation of the building shall be designed based on the actual soil condition. Foundation shall be as per actual soil condition as per soil test, including piling where required. | [7 empty] | Market price
27.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 | 301211.02 | 27108.9918 | 27108.9918 | 355429.0036 | 355429.0036 | Market price
27.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 260559.34 | 23450.3406 | 23450.3406 | 307460.0212 | 307460.0212 | Market price
27.3 | Providing & laying Plain cement concrete (1:2:4) using 12mm size black hard crusher broken granite chips of approved quality from approved quarry including hoisting, lowering and laying concrete in layers, watering, curing etc. complete including cost, conveyance, royalties and taxes of all materials with labour, cess and T&P etc. required for the work complete. | Lot | 1 | 9942.65 | 894.8385 | 894.8385 | 11732.327 | 11732.327 | Market price
27.4 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations, columns, Beams, lintels, chhajas, roof slabs, stair case etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 1676113.36 | 150850.2024 | 150850.2024 | 1977813.7648 | 1977813.7648 | Market price
27.5 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 2232941.16 | 200964.7044 | 200964.7044 | 2634870.5688 | 2634870.5688 | Market price
27.6 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) for foundation and plinth and in cement mortar of mix (1:4) for other area in ground floor, first floor & head room with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 385242.08 | 34671.7872 | 34671.7872 | 454585.6544 | 454585.6544 | Market price
27.7 | Providing 16 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 177975.53 | 16017.7977 | 16017.7977 | 210011.1254 | 210011.1254 | Market price
27.8 | Providing 18mm C.P. in two coats underlayer 12mm C.P. 1:5 and top layer 6mm thick C.P. 1:6 finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 104882.42 | 9439.4178 | 9439.4178 | 123761.2556 | 123761.2556 | Market price
27.9 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 52842.74 | 4755.8466 | 4755.8466 | 62354.4332 | 62354.4332 | Market price
27.1 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 239188.36 | 21526.9524 | 21526.9524 | 282242.2648 | 282242.2648 | Market price
27.11 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 51802.87 | 4662.2583 | 4662.2583 | 61127.3866 | 61127.3866 | Market price
27.12 | Providing, fitting & fixing anti-skid ceramic floor tiles in flooring in toilets using special plain/ printed series anti-skid ceramic floor tile of premium grade (having minimum thickness 7 mm to 8 mm & size 300 mm x 300 mm confirming to IS 13755 of approved quality and shade of Somany/ Kajaria / Johnson on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened & washed sharp river sand for mortar ceramic floor tiles with neat white cement slurry, mixed with required (tiles are to be immersed in the water for required time before use) quantities of pigments of approved marks to match the shades of the anti-skid ceramic floor tiles if required including cost, conveyance, loading, unloading, stacking, royalties of all material, cost of all labour, sundries, T&P required for the work, watering, complete in all respect as per specification excluding GST as per specification as directed by Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 12140.52 | 1092.6468 | 1092.6468 | 14325.8136 | 14325.8136 | Market price
27.13 | Providing & Fixing tiles of size 30cm x 45 cm glazed ceramic wall tiles (All Toilet walls) of premium grade of approved quality and shade having thickness 8mm to 10mm confirming to IS 13755 in dados skirting and risers of steps on 12mm thick cement plaster (1:3) to proper slope, line and level including cutting to required size and shape, fixing at corners and splays etc including filling the joints with neat white cement slurry mixed with pigments to match the shade of the tiles including cost, Conveyance, loading, unloading, stacking, royalities of all materials, cost of all labour,T&P, sundries, watering and curing for the required period for the work complete in all respect excluding GST as directed by the Engineer-in-charge.(Note- Sample of tiles shall be approved before procurement and use.) | Lot | 1 | 65578.7 | 5902.083 | 5902.083 | 77382.866 | 77382.866 | Market price
27.14 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 123268.36 | 11094.1524 | 11094.1524 | 145456.6648 | 145456.6648 | Market price
27.15 | Providing Granite stone prepolished 10mm thick in dado of approved quality, colour and size in dado, riser of steps and dado of landings in all floors at all height on 12mm thick bed of cement mortar of mix (1:3) with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 19217.93 | 1729.6137 | 1729.6137 | 22677.1574 | 22677.1574 | Market price
27.16 | Providing,Fixing 16m thick Kota stone in floors treads or steps and landing on 20mm thick cement mortar (1:4) (1cement : 4 course and) and filling joints with of approved quality including cost, conveyance, taxes, cost of all labour etc. complete. Providing,Fixing 16m thick Kota stone in dado ,riser on 12mm thick cement mortar (1:3) (1cement : 3 course and) and filling joints with of approved quality including cost, conveyance, taxes, cost of all labour etc. complete. | Lot | 1 | 44895.68 | 4040.6112 | 4040.6112 | 52976.9024 | 52976.9024 | Market price
27.17 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 125157.9 | 11264.211 | 11264.211 | 147686.322 | 147686.322 | Market price
27.18 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board and pasting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. | Lot | 1 | 448363.08 | 40352.6772 | 40352.6772 | 529068.4344 | 529068.4344 | Market price
27.19 | Supplying, fitting and fixing of M.S grills, Grill window ( as per I.S. specification and as per approved drawings ) in proper position in all floorsas per TS, approved drawing, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 91241.08 | 8211.6972 | 8211.6972 | 107664.4744 | 107664.4744 | Market price
27.2 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge.
27.20.1 | Inside walls: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 280619.13 | 25255.7217 | 25255.7217 | 331130.5734 | 331130.5734 | Market price
27.20.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 65795.51 | 5921.5959 | 5921.5959 | 77638.7018 | 77638.7018 | Market price
27.20.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 607.66 | 54.6894 | 54.6894 | 717.0388 | 717.0388 | Market price
27.21 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 71130.56 | 6401.7504 | 6401.7504 | 83934.0608 | 83934.0608 | Market price
27.22 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 44317.83 | 3988.6047 | 3988.6047 | 52295.0394 | 52295.0394 | Market price
27.23 | Providing and fixing of UPVC sliding windows in the Transit house as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 424584 | 38212.56 | 38212.56 | 501009.12 | 501009.12 | Market price
27.24 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. \ | Lot | 1 | 122196.6 | 10997.694 | 10997.694 | 144191.988 | 144191.988 | Market price
27.25 | Water proofing to the sunken slab including providing and filling it with 40mm size brick bat as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 3348 | 301.32 | 301.32 | 3950.64 | 3950.64 | Market price
27.26 | Providing and laying tactile tile (for vision impaired persons as per standards) of size 300x300x9.8 mm having with water absorption less than 0.5% and conforming to IS:15622 of approved make in all colours and shades in for outdor floors such as footpath, courtyard, multi modals location etc., laid on 20mm thick base of cement mortar 1:4 (1 cement : 4 coarse sand) in all shapes & patterns including grouting the joints with white cement mixed with matching pigments etc. complete as per direction of Engineer-in-Charge | Lot | 1 | 21505.13 | 1935.4617 | 1935.4617 | 25376.0534 | 25376.0534 | Market price
27.27 | Supplying, fitting and fixing in position 16mm thick chequred tile of approved make and quality, colour and size in all floors at all height on 25mm thick bed of cement mortar of mix (1:1) laid in proper slope and gradient with screened and washed sharp sand for mortar and with Portland Slag Cement (PSC) grouted with neat white cement slurry with required quantities of pigments of approved marks watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 15829.76 | 1424.6784 | 1424.6784 | 18679.1168 | 18679.1168 | Market price
27.28 | Plinth Potection for Transit house as per the provided drawing and as per sepcification in TS. | Lot | 1 | 71707.51 | 6453.6759 | 6453.6759 | 84614.8618 | 84614.8618 | Market price
27.29 | Construction of covered drain for Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 257416.05 | 23167.4445 | 23167.4445 | 303750.939 | 303750.939 | Market price
27.3 | Provision of PH work for the Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 570758.62 | 51368.2758 | 51368.2758 | 673495.1716 | 673495.1716 | Market price
27.31 | Construction of septic tank and soak pit for Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 255823.4 | 23024.106 | 23024.106 | 301871.612 | 301871.612 | Market price
27.32 | Provision of Electrical works the Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 467669.25 | 42090.2325 | 42090.2325 | 551849.715 | 551849.715 | Market price
27.33 | Furnishings for Transit House: Supply and installation of the following items- 1. 55 inch Full HD LED TV set of Sony/LG/Samsung make with supply of Set up Box for the television unit with 1 year recharge from the date of commissioning (1set) 2. Durian make Sofa set (3+1+1) with center table for lobby (1 set) 3. Durian make King size cot with mattress & all other amenities like study table with 2 chair (Godrej) in all the bed rooms, bed sheets, pillow etc (Bombay Dyeing/Raymond Home) make. 2 Person wardrobe (Godrej Interio), hangers for hanging cloths in each room for storage of Baggages and Cloths etc. Bathing requirements like Bath Towels, Hand Towels etc. (02 sets for all the bed rooms). Decoratives Such as wall ceinic Hangers, Doors and Windows Curtains (02 Sets for all doors and Windows) - Total 4 sets for 4 guest rooms 4. Geyser-3 Ltr capacity of Bajaj/V-Guard/Phillips/Crompton make (4 set) 5. Dining table with 6 chairs of Durian/Godrej make (1 set) 6. Modular kitchen with exhaust chimney system, gas stove, and required utensils (1. 02 Cook Ware and Dinner Sets for 08 persons 2. Induction cooking heaters for cooking capacity of 10 persons at a stretch) 7. RO & UV Water purifier with cooling water system of Aquaguard/Bluestar/Kent make (1 set) 8. 3 star inverter compressor frost free Refrigerator of 230 Ltr or above capacity, double door type (LG/Samsung/Whirlpool/Godrej/Panasonic Make) (1 set) | LOT | 0 | 2000000 | 180000 | 180000 | 2360000 | 0 | Market price
28 | Land scaping & provision for platform for hoisting of National Flags and Provision of Garden: As per site condition of the substation and approval of the gardening layout. The qty may vary as per the approved layout and instrcution of engineer in charge.
28.1 | Provision of gardens/ lawn area with garden grass in front of the control room building & other areas that can be developed as a garden as per the site Engineer's instruction. This include the all required work including the soil treatment for laying of the lawn grass. | sqm |  | 500 | 45 | 45 | 590 | 0 | Market price
28.2 | Motorised fountain at a suitable location as per instrcution of Engineer in charge. | Nos |  | 50000 | 4500 | 4500 | 59000 | 0 | Market price
28.3 | Sprinkler arrangement in the lawn to cover all the lawn area and water tap arrangement at different location to all areas of plantation. | Lot |  | 50000 | 4500 | 4500 | 59000 | 0 | Market price
28.4 | Flowering plants (Rose, jasmine, hibiscus or as per instruction of Engineer in Charge at least 50 each | Nos |  | 50 | 4.5 | 4.5 | 59 | 0 | Market price
28.5 | Fruit bering Non Fruit bearing Plants (Mango, guava, Neem, Acacia) as per instruction of Engineer in Charge. 25 nos of each type of trees to be plantedin the free areas immediately after the substation layout paln is finalised. It must be ensured that the plants survive till hand over. Therefore, proper care shall be taken by the contractor. | Nos |  | 50 | 4.5 | 4.5 | 59 | 0 | Market price
28.6 | Decorative Plants for Lawn/garden (varieties of Hedge, thuja) as per instruction of Engineer in Charge | Nos |  | 50 | 4.5 | 4.5 | 59 | 0 | Market price
28.7 | Decorative plants (foxtail palm of at least 5 ft height) for both side of the 7m road from the main gate as per instruction of the Engineer in charge. | Nos |  | 1100 | 99 | 99 | 1298 | 0 | Market price
28.8 | Construction of platform & suitable GI pipe & other attachment for hoisting of National Flags as per the direction of Engineer incharge. | Nos |  | 10000 | 900 | 900 | 11800 | 0 | Market price
29 | STONE PITCHING & TOE WALL:Stone pitching including making of toe walls both at top and bottom, including surface drain both at top and bottom and partition wall in every 10 mtrs by using boulders and RR masonry walls respectively. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth and supply of materials and labour as per the direction of Engineer In charge and as per approved drawing and specification.
29.1 | Excavation in all type of Soil | Cum | 150 | 316.47 | 28.4823 | 28.4823 | 373.4346 | 56015.19 | Annexure - II B SSN -4(ii) & 5(ii) Avg.
29.2 | P.C.C (1:3:6): Lean Concrete Grade M-10 | Cum | 10 | 5907.71 | 531.6939 | 531.6939 | 6971.0978 | 69710.978 | Annexure - II SSN Foundation Work Sl. No. 1.20 (i)
29.3 | RR Masonry (1:5) | Cum | 150 | 2933.92 | 264.0528 | 264.0528 | 3462.0256 | 519303.84 | Annexure - II SSN Masonary Work Sl. No. 1.30 (i)
29.4 | P.C.C (1:2:4): Lean Concrete Grade M-15 | Cum | 2 | 7186 | 646.74 | 646.74 | 8479.48 | 16958.96 | Annexure - II SSN Foundation Work Sl. No. 1.10 (i)
30 | RETAINING WALL: Construction of RCC retaining wall below the FGL and from NSL as per the site condition to sustain the earth pressure. The depth and length of RCC wall shall be designed as per site requirement. This includes excavation in all type of soil, RCC (1:1.5:3) with supply of steel(Fe-500), cement ,sand etc. including cutting, bending, binding, backfilling in layers after concreting for soil compaction and also supply of other required materials and labour . The work shall be executed as per the approved design , drawing as per direction of Engineer In charge
30.1 | Exacavation all type of soil | Cum | 500 | 316.47 | 28.4823 | 28.4823 | 373.4346 | 186717.3 | Annexure - II B SSN -4(ii) & 5(ii) Avg.
30.2 | P.C.C (1:3:6): Lean Concrete Grade M-10 | Cum | 30 | 5907.71 | 531.6939 | 531.6939 | 6971.0978 | 209132.934 | Annexure - II SSN Foundation Work Sl. No. 1.20 (i)
30.3 | RCC volume (M20) | Cum | 200 | 8533.36 | 768.0024 | 768.0024 | 10069.3648 | 2013872.96 | Annexure - II SS Foundation Work Sl. No. 1.40 (i)
30.4 | Steel ( Fe 500) | MT | 15 | 65511.29 | 5896.0161 | 5896.0161 | 77303.3222 | 1159549.833 | Annexure - II SSN Foundation and Reinforcement Sl. No. 1.10 (i) with steel
| TOTAL OF Civil Work (PART-A)_SUBSTATION | [6 empty] | 103116001.3948