## ARR Kutra
COST BENEFIT ANALYSIS
A. BENEFITS DUE TO SALE OF ENERGY ON ACCOUNT OF CONVERSION OF 132 KV SWITCHING STATION AT KUTRA TO 2 X 50 MVA, 132/33 KV GRID SUB-STATION
1 | Transformation Capacity considered for revenue calculation considering N-1 condition (2x50 MVA= 100 MVA) | 50
2 | Power factor (PF) | 0.9
3 | Diversity factor (DF=1.4 due to mixed type industrial and commercial load) | 1.4
4 | Load factor (LF=0.7 due to mixed type industrial and commercial load) | 0.7
5 | Additional avg. power available for sale on account of establishment of a new 132/33 KV Grid Sub-station at Kutra with 2x50 MVA transformers in MW (5 = 1 x 2 x 4 / 3) | 22.5
6 | Additional energy available for sale in LU | 1971
7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 1911.87
8 | Anticipated revenue at a cost of Rs.0.24/ Unit in Lakhs | 458.8488
B. BENEFITS OF THE SCHEME DUE TO REDUCTION IN LOSSES
1 | Total losses before implementation of the scheme in MW | 1112.0094
2 | Total losses after implementation of the scheme in MW | 1110.6495
3 | Total reduction in losses in MW | 1.36
4 | Load factor | 0.7
5 | Loss load factor (0.8 LF2 + 0.2 LF) | 0.532
6 | The energy available for sale per year in LU | 63.3789
7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 61.4775
8 | Anticipated revenue due to reduction in losses in lakhs @ Rs. 0.24/ Unit | 14.7546
C. CALCULATION OF REVENUE RETURN
1 | Anticipated revenue due to reduction in losses [Rs. Lakhs] | 14.7546
2 | Anticipated revenue due to sale of additional energy [Rs. lakhs] | 458.8488
3 | Total anticipated annual revenue [Rs. Cr.] | 4.736
4 | Estimated Cost [Rs. Cr.] | 34.3
5 | Average Annual Rate of Return in % | 13.8077
6 | Internal Rate of Return | 31.81%

## IRR Kutra
Calculation of NPV and IRR : CONVERSION OF 132 KV SWITCHING STATION AT KUTRA TO 2 X 50 MVA, 132/33 KV GRID SUB-STATION
CoC (%) = | 70% | x | 8.03 | + | 30% | x | 15.5 | = | 6.58 |  | RoI on Loan P.a |  |  | = | 7.75 |  | IRR = | 31.81% | [16 empty] | Rs in Crores
Particulars | Constuction Period |  | Benefits Period | [34 empty] | Total
Financial Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
Cash Inflow (CI)
Equity | 3.09 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.29
Loan(Principal) | 7.2 | 16.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.01
Loan (Interest) | 0.58 | 1.93 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.51
Revenue | 0 | 0 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 165.7612
Salvage Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.681 | 3.681
Total (CI) - (A) | 10.87 | 25.94 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 4.736 | 8.417 | 206.2522
Cash Outflow (CO)
CWIP | 10.29 | 24.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.3
IDC | 0.58 | 1.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.51
Loan Repayment | 0 | 0 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.52
Interest on Loan | 0 | 0 | 2.04 | 1.86 | 1.69 | 1.51 | 1.33 | 1.15 | 0.98 | 0.8 | 0.62 | 0.44 | 0.27 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.78
R&M exp. @ 3 % PC | 0 | 0 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 38.5
Total (CO) - (B) | 10.87 | 25.94 | 5.35 | 5.17 | 5 | 4.82 | 4.64 | 4.46 | 4.29 | 4.11 | 3.93 | 3.75 | 3.58 | 3.4 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 114.61
Net Cash Inflow (A-B) | 0 | 0 | -0.61397 | -0.43397 | -0.26397 | -0.083966 | 0.096034 | 0.27603 | 0.44603 | 0.62603 | 0.80603 | 0.98603 | 1.156 | 1.336 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 3.636 | 7.317 | 91.6422
DF @ CoC | 1 | 0.938 | 0.88 | 0.826 | 0.775 | 0.727 | 0.682 | 0.64 | 0.601 | 0.564 | 0.529 | 0.496 | 0.465 | 0.437 | 0.41 | 0.384 | 0.361 | 0.338 | 0.318 | 0.298 | 0.28 | 0.262 | 0.246 | 0.231 | 0.217 | 0.203 | 0.191 | 0.179 | 0.168 | 0.158 | 0.148 | 0.139 | 0.13 | 0.122 | 0.115 | 0.107 | 0.101 | 14.666
Net Present value(NPV) | 0 | 0 | -0.54 | -0.36 | -0.2 | -0.06 | 0.07 | 0.18 | 0.27 | 0.35 | 0.43 | 0.49 | 0.54 | 0.58 | 1.49 | 1.4 | 1.31 | 1.23 | 1.16 | 1.08 | 1.02 | 0.95 | 0.89 | 0.84 | 0.79 | 0.74 | 0.69 | 0.65 | 0.61 | 0.57 | 0.54 | 0.51 | 0.47 | 0.44 | 0.42 | 0.39 | 0.74 | 20.68
NPV at IRR | 0 | 0 | -0.35 | -0.19 | -0.09 | -0.02 | 0.02 | 0.04 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.04 | 0.08 | 0.06 | 0.04 | 0.03 | 0.03 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.01
**
CoC - Cost of Capital
IDC- Interest During Construction
CWIP- Capital Work in Progress
DF- Discounting Factor
IRR- Internal Rate of Return
ARR- Average Annual Rate of Return
Opening Balance |  |  | 26.52 | 24.31 | 22.1 | 19.89 | 17.68 | 15.47 | 13.26 | 11.05 | 8.84 | 6.63 | 4.42 | 2.21
Repayment |  |  | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21
Closing Balance |  |  | 24.31 | 22.1 | 19.89 | 17.68 | 15.47 | 13.26 | 11.05 | 8.84 | 6.63 | 4.42 | 2.21 | 0
Agerage Loan |  |  | 25.415 | 23.205 | 20.995 | 18.785 | 16.575 | 14.365 | 12.155 | 9.945 | 7.735 | 5.525 | 3.315 | 1.105
Interest |  |  | 2.0408 | 1.8634 | 1.6859 | 1.5084 | 1.331 | 1.1535 | 0.97605 | 0.79858 | 0.62112 | 0.44366 | 0.26619 | 0.088731
|  |  | -0.0008245 | -0.0033615 | 0.0041015 | 0.0015645 | -0.0009725 | -0.0035095 | 0.0039535 | 0.0014165 | -0.0011205 | -0.0036575 | 0.0038055 | 0.0012685

## Data Sheet
| Expenditure in Crores: | 34.3
| Year: | 2026-27 | 2027-28
| % of Expenditure: | 30% | 70%
| Year wise expenditure: | 10.29 | 24.01
Equity | 30% | 3.09 | 7.2
Loan | 70% | 7.2 | 16.81
Grant | 0% | 0 | 0
Total | 100% | 10.29 | 24.01