## Basic (hidden)
Name of Package | Supply and Services for Diversion of 400 KV transmission lines of POWERGRID at various locations in NR1 due to infringement with upcoming Greenfield Haryana Orbital Rail Corridor of HRIDC
Tender Enquiry Ref No.: | NR1/NT/W-TW/DOM/I00/23/00932 Dated 11.04.2023 (Rfx-5002002632)
0

## Sch-2 (hidden)
#REF! | [6 empty] | Schedule - 2
#REF! | [9 empty] | As per Lum-sum |  | 0
(SCHEDULE OF RATES AND PRICES ) | [9 empty] | AS per Percent |  | #REF!
[10 empty] | As per lum-sum on Sch-2 |  | 0%
Bidder’s Name and Address | [5 empty] | To: |  |  |  | As per Percent on Sch-2 |  | #REF!
[6 empty] | Contract & Materials deprtament |  |  |  | Total Discount |  | #REF!
Name : | #REF! |  | Power Grid Corporation of India Ltd.,
Address : |  |  |  | Northern Region –I, Regional Headquarter,
| #REF! |  |  |  |  | SCO Bay No. 5 to 10, Sector 16A |  |  |  | Multipackage Discount |  | #REF!
| #REF! |  |  |  |  | Faridabad-121002, Haryana
Local Transportation, In-transit Insurance, loading and unloading
[7 empty] | All Prices are in Indian Rupees. |  |  |  | Amount after Discount (Rs.) |  | Dis Alert | Amount after MPD (Rs.)
SI. No. | Description | Location | Unit | Quantity | FOR destination | Unit Freight, Insurance, loading & unloading Charges including GST | Total Freight, Insurance, loading & unloading Charges including GST |  |  |  | Unit Freight & Insurance Charges | Total Freight & Insurance Charges |  | Unit Freight & Insurance Charges | Total Freight & Insurance Charges
| Freight, Insurance, loading & unloading Charges for Supply of following as per requirement mentioned in Technical Specification | [6 empty] | #REF!
1
| Total F&I charges including GST | [5 empty] | 0 |  | #REF!
Date : | #REF!
Place : | #REF! |  |  |  | Printed Name : | #REF!
[5 empty] | Designation : | #REF!

## Sch-5 (hidden)
NR1/NT/W-TW/DOM/I00/23/00932 Dated 11.04.2023 (Rfx-5002002632) | [9 empty] | Schedule - 5
Supply and Services for Diversion of 400 KV transmission lines of POWERGRID at various locations in NR1 due to infringement with upcoming Greenfield Haryana Orbital Rail Corridor of HRIDC
[14 empty] | As per Lum-sum |  | 0
(SCHEDULE OF RATES AND PRICES ) | [13 empty] | AS per Percent |  | #REF!
[14 empty] | As per lum-sum on Sch-2 |  | 0%
[9 empty] | To: |  |  |  |  | As per Percent on Sch-2 |  | #REF!
Bidder’s Name and Address | [7 empty] | Contracts & Material | [5 empty] | Total Discount |  | #REF!
Name : | #REF! | [6 empty] | Power Grid Corporation of India Ltd.,
Address : | #REF! | [6 empty] | Northern Region –I, Regional Headquarter,
| #REF! | [6 empty] | SCO Bay No. 5 to 10, Sector 16A | [5 empty] | Multipackage Discount |  | #REF!
| #REF! | [6 empty] | Faridabad-121002, Haryana
Dismantling Charges
[10 empty] | All Prices are in Indian Rupees. |  |  |  |  | Amount after Discount (Rs.) |  | Dis Alert | Amount after MPD (Rs.)
SI. No. | Description | Location | Unit | Quantity | SAC Code | WhetherHSN in column ‘5’ is confirmed. If not indicate applicable theHSNC # | Rate of GST applicable ( in %) | Whether rate of GST in column ‘7’ is confirmed. If not indicate applicable rate of GST # (Select suitable GST rate from Dropdown) | Unit Dismantling Charges (Excluding GST) | Total Buy-Back Chargess (excluding GST) |  |  |  |  | Unit Freight & Insurance Charges | Total Freight & Insurance Charges |  | Unit Freight & Insurance Charges | Total Freight & Insurance Charges
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10=9X4 |  |  | #REF! |  | 5 | 6 = 4 x 5 |  | 5 | 6 = 4 x 5
1 | Dismantling of existing old 200 MM pipe | Bassi | RMT | 303 | 995429 |  | 18% |  |  | Included | 18% | #VALUE!
2 | Dismantling of existing old 150 MM Pipe | Bassi | RMT | 273 | 995429 |  | 18% |  |  | Included | 18% | #VALUE!
3 | Dismantling of existing old 100 MM Pipe | Bassi | RMT | 250 | 995429 |  | 18% |  |  | Included | 18% | #VALUE!
4 | Dismantling of all pipe line, Pump, etc in Pump room. | Bassi | LS | 1 | 998736 |  | 18% |  |  | Included | 18% | #VALUE!
| Total Dismantling charges (Excluding GST) |  | 10=9X4: 0 |  |  | #REF!
| Total GST on Dismantling |  | 10=9X4: #VALUE! |  |  | #REF!
Total charges
| Total Dismantling charges (including GST) |  | 10=9X4: #VALUE!
Date : | #REF!
Place : | #REF! |  | 8: Printed Name :; 9: #REF!
[8 empty] | Designation : | #REF!

## Sch-6 (hidden)
NR1/NT/W-TW/DOM/I00/23/00932 Dated 11.04.2023 (Rfx-5002002632) | [9 empty] | Schedule - 6
Supply and Services for Diversion of 400 KV transmission lines of POWERGRID at various locations in NR1 due to infringement with upcoming Greenfield Haryana Orbital Rail Corridor of HRIDC
[14 empty] | As per Lum-sum |  | 0
(SCHEDULE OF RATES AND PRICES ) | [13 empty] | AS per Percent |  | #REF!
[14 empty] | As per lum-sum on Sch-2 |  | 0%
[9 empty] | To: |  |  |  |  | As per Percent on Sch-2 |  | #REF!
Bidder’s Name and Address | [7 empty] | Contracts & Material | [5 empty] | Total Discount |  | #REF!
Name : | #REF! | [6 empty] | Power Grid Corporation of India Ltd.,
Address : | #REF! | [6 empty] | Northern Region –I, Regional Headquarter,
| #REF! | [6 empty] | SCO Bay No. 5 to 10, Sector 16A | [5 empty] | Multipackage Discount |  | #REF!
| #REF! | [6 empty] | Faridabad-121002, Haryana
Buy-Back Charges
[10 empty] | All Prices are in Indian Rupees. |  |  |  |  | Amount after Discount (Rs.) |  | Dis Alert | Amount after MPD (Rs.)
SI. No. | Description | Location | Unit | Quantity | HSN Code | WhetherHSN in column ‘5’ is confirmed. If not indicate applicable theHSNC # | Rate of GST applicable ( in %) | Whether rate of GST in column ‘7’ is confirmed. If not indicate applicable rate of GST # (Select suitable GST rate from Dropdown) | Unit Buy-Back Charges (Excluding GST) | Total Buy-Back Chargess (excluding GST) |  |  |  |  | Unit Freight & Insurance Charges | Total Freight & Insurance Charges |  | Unit Freight & Insurance Charges | Total Freight & Insurance Charges
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10=9X4 |  |  | #REF! |  | 5 | 6 = 4 x 5 |  | 5 | 6 = 4 x 5
1 | Buyback of dismantled Pipes (200 mm Dia) | Bassi | 3: Mtr; 4: 303; 5: 73041011; 7: 18% | 18% | 0
2 | Buyback of dismantled Pipes (150 mm Dia) | Bassi | 3: Mtr; 4: 273; 5: 73041011; 7: 18% | 18% | 0
3 | Buyback of dismantled Pipes (100 mm Dia) | Bassi | 3: Mtr; 4: 250; 5: 73041011; 7: 18% | 18% | 0
4 | Buyback of dismantled Pipes (300 mm Dia) | Bassi | 3: Mtr; 4: 18; 5: 73041011; 7: 18% | 18% | 0
| Total Buy-Back charges (Excluding GST) |  | 10=9X4: 0 |  |  | #REF!
| Total GST on Total Buy-Back Price |  | 10=9X4: 0 |  |  | #REF!
Total charges
| Total Buy-Back charges (including GST) |  | 10=9X4: 0
Date : | #REF!
Place : | #REF! |  | 8: Printed Name :; 9: #REF!
[8 empty] | Designation : | #REF!

## Discount (hidden)
This letter of discount is optional. Bidder may / may not offer any discount.
#REF! |  |  |  |  | Letter of Discount
LETTER OF DISCOUNT
To:
Contract & Materials deprtament
Power Grid Corporation of India Ltd.,
Northern Region –I, Regional Headquarter,
SCO Bay No. 5 to 10, Sector 16A
Faridabad-121002, Haryana
Subject : |  | #REF!
Dear Sir
With reference to the subject tender, we hereby offer unconditional discount on the prices quoted by us as per details given here below : | [6 empty] | Final Discount Factor
| 1 | Discount on lum-sum basis on total price quoted by us . [The discount shall be proportionately applicable on all the items of all the Schdules i.e. Sch-1,3] In Rs. |  |  |  | #REF! | #REF!
| 2 | Discount on percent basis on total price quoted by us [The discount shall be proportionately applicable on all the items of all the Schdules i.e. Sch-1,3] In Percent (%) |  |  |  | #REF! | 0%
| 3 | Discount on lum-sum basis on the Schedules as given below : [The discount shall be proportionately applicable on all the relevent items of the respective Schdules.] In Rs.
|  | Schedule-1 : Ex works prices |  | In Rs. |  | #REF! | #REF! | Schedule-1 : Ex works prices | #REF!
|  | Schedule-1 : Ex works prices (Bought Out Only) |  | In Rs. |  | #REF! | #REF! | Schedule-1 : (Bought Out Only) | #REF!
|  | Schedule-2 : Freight & Insurance |  | In Rs. |  | 0 | 0% | Schedule-2 : Freight & Insurance | #REF!
|  | Schedule-3 : Supervision Charges |  | In Rs. |  | #REF! | #REF! | Schedule-3 : AMC Charges | #REF!
|  | Schedule-7 : Type Test Charges |  | In Rs. |  | #REF! |  | Schedule-6 : Type Test Charges | #REF!
| 4 | Discount on percent basis on the Schedules as given below : [The discount shall be proportionately applicable on all the relevent items of the respective Schdules.] In Percent (%)
|  | Schedule-1 : Ex works prices |  | In Percent (%) |  | #REF! | 0%
|  | Schedule-1 : Ex works prices (Bought Out Only) |  | In Percent (%) |  | #REF! | 0%
|  | Schedule-2 : Freight & Insurance |  | In Percent (%) |  | 0 | 0%
|  | Schedule-3 : Service Charges |  | In Percent (%) |  | #REF! | 0%
|  | Schedule-7 : Type Test Charges |  | In Percent (%) |  | #REF!
| 3 | Multipackage discount on Total Price on LS Basis quoted without T&D (Applicable on this package only if other package covered under the same bidding Document is also awarded to us, Discount) |  |  |  | #REF!
| 4 | Multipackage discount on Total Price on percent Basis quoted without T&D (Applicable on this package only if other package covered under the same bidding Document is also awarded to us, Discount) |  |  |  | #REF!
Discount(s) offered at sl. No. 1 to 4 will automatically get displayed and accounted for in the respective items of the Schedules.
| 5 | We hereby offer Multi-package discount as given below:
Multi-Package Discount(s) offered at sl. No. 3 & 4 will not get automatically accounted for in the respective items of the Schedules. The same shall be worked out saparately for evaluation.
Please consider this letter of discount as the integral part of our price bid.
Thanking you, we remain,
Yours faithfully,
#REF!
Date : |  | #REF! | Printed Name : | #REF!
Place : |  | #REF! | Designation : | #REF!
Click for Bid Form

## Sch-6B After Discount (hidden)
#REF! |  |  | Schedule - 6B After Discount
#REF!
(GRAND SUMMARY : AFTER DISCOUNT)
Bidder’s Name and Address |  |  | To:
Contract & Materials deprtament
Name : | #REF! |  | Power Grid Corporation of India Ltd.,
Address : | #REF! |  | Northern Region –I, Regional Headquarter,
| #REF! |  | SCO Bay No. 5 to 10, Sector 16A
| #REF! |  | Faridabad-121002, Haryana
Sl. No. | Description |  | Total Price (INR)
1 | TOTAL SCHEDULE NO. 1 |  | #REF! | #REF!
Ex-works price
2 | TOTAL SCHEDULE NO. 2 |  | #REF!
Local Transportation, In-transit Insurance, loading and unloading
3 | TOTAL SCHEDULE NO.3 |  | #REF!
Installation Charges
4 | TOTAL SCHEDULE NO. 4 |  | #REF!
Total GST for Schedule-1 and 3
5 | TOTAL SCHEDULE NO. 5 |  | #REF!
Total Dismantling Charges (including GST)
6 | TOTAL SCHEDULE NO. 6 |  | #REF!
Total Buy Back Charges (including GST)
7 | GRAND TOTAL [1+3+4+5-6] |  | #REF!
Date : | #REF! | Printed Name : | #REF!
Place : | #REF! | Designation : | #REF!

## Front Page
ODISHA POWER TRANSMISSION CORPORATION LTD
| Province | ODISHA
| Division | EHT Project Division,Rayagada
| Sub-Division | EHT Project Sub-Division, Rayagada
| Name of the Work | Construction of 400 KV Indravati-Therubali D/C LINE from proposed 400 KV PSP Sub-Station at Mukhiguda to proposed 400/220 KV GSS Therubali (RE-02)
Main Head of Classification
| Estimate No. | 32 / 2025-2026
| Estimated Amount | Rs. | 3674138349
(Rupees Three Hundred Sixty Seven Crores Forty One Lakhs Thirty Eight Thousand Three Hundred Forty Nine Only)
Dy. General Manager (Elect.) E.H.T Project Division,Rayagada

## Report
R E P O R T
This Revised estimate has been framed in BPS format for an amount of Rs. 3,67,41,38,349.00(Rupees Three Hundred Sixty seven Crores Forty one Lakhs Thirty Eight Thousand Three Hundred Fouty Nine Only)to meet the probable expenditure for Construction of 400 KV Indravati-Therubali D/C LINE from proposed 400 KV PSP Sub-Station at Mukhiguda to proposed 400/220 KV GSS Therubali in the state of Odisha. As per Letter received from Director(Projects) vide L.No- 431 on Dated:13.11.2025 and as per instruction of competent authority of OPTCL, the estimate has been framed as per the current practice for standardization of Sub-Stations . Further, modification has been made as per the Note # 8 recieved from E&Q cell basically considering the following: (i) Transmission Line is to be strung as Twin moose type in Quad Moose designed EHT Tower for 400 kV. Accordingly Supply/Erection qty changed and Line foundation qty also changed. (ii) Counterpoise earthing wire is changed from 50 x 6 GI flat to 7/3.66mm steel wire. (iii)Damper spacers used in place of Vibration dampers & pacers separately. (iv) Supply of GI earth wire changed from 7/3.14 mm to 7/3.66 mm type. (v) Hardware fittings qty changed as per actual derived. (v) Insulator Qty changed as per actual derived with 5% extra for breakage & wastage. (vi) Route KM changed from 93.25 to 93.204 KMs as per approved detailed survey report. (vii) High Resolution Binacular make specified as per instruction. Apart from this, in this estimate the Reserve/Revenua Forest area has been escalated from 55 Ha. to 65 Ha. as per data recieved from M/s CEEP after finalisation of Route and this has been incorporated in the statutory fees in the summary sheet of this estimate. The total scope includes construction of 270 Nos of 400 kV Towers out of which 57 Nos are of suspension type and 213 Nos are of Tension type towers. Further, the scope also incluides stringing of twin ACSR moose Line of Approx. 93.204 KMs. The scope also includes stringing of OPGW and earth wire in double peak towers of 400 kV in the entire length of Line. The construction of the above Transmission line infrastructure is essential to evacuate the green energy power generated from proposed Pumped Storage Plant, Indravati at Mukhiguda. The Cost of the materials & Erection charges depicted in the estimate are as per the rate contact for the year 2025-26 issued vide Rate Contract vide Lr. No. Sr.GM-CPC-Rate Contract works-1294 dated. 14.11.2025 of the Sr. GM(CPC),OPTCL,Bhubaneswar for RATE CONTRACT for execution of Normal work on OPTCL system and approved Cost Data for the year 2024-25 issued vide Lr. No. 84 Dated:16.01.2025 of the CGM(CPC),OPTCL,Bhubaneswar and subsequent amendments. The rate for the items which are not availbale in cost data/Rate Contract are considered form the preveiling market rate for similar materials or work and from the sanctioned estimate of Basudevpur Project and for new materials whose rates are unavailable, has been scaled up to some considerable percentage . GST @ 18% has been considered in both supply and Erection part of the present estimate. The Estimate also includes the statutory fees requirement for the purpose of deposit in expediting Forest Diversion proposal of the Line.
Dy. GENERAL MANAGER (ELECT) EHT PROJECTS DIVISION, RAYAGADA

## SUMMARY LINE ABSTRACT
ODISHA POWER TRANSMISSION CORPORATION LIMITED
SUMMARY
Name of of Works: Construction of 400 KV Indravati-Therubali D/C LINE from proposed 400 KV PSP Sub-Station at Mukhiguda to proposed 400/220 KV GSS Therubali Conductor- ACSR MOOSE (Twin), Towers- Suitable for Quad ACSR Moose Type
Sl.No. | Description | Amount (inRs.)
1 | Total Cost of materials (FOR 400 KV Indravati-Therubali D/C LINE from proposed 400 KV PSP Sub-Station at Mukhiguda to proposed 400/220 KV GSS Therubali ) | 2193920503.7372
2 | Stock,Storage & Insurance(@3% on Sl.No-1) | 65817615.1121
3 | Sub-Total (sl no. 1+2) | 2259738118.8494
4 | Contigency 3% on Sl.No.3 | 67792143.5655
5 | T&P cost @ 2% on Sl.No. 3 | 45194762.377
6 | Transportation @5% on Sl.No.3 | 112986905.9425
7 | Sub-Total of Supply (Sl No 03 to 06) | 2485711930.7343
8 | Total erection Chages | 204715016.2006
9 | Total Civil Work Charges | 625711401.8786
10 | Arrangement for obtaining of the Project License for the project from ELBO office,by arranging EHT Licence holder,HT License,Lineman A & other etc,OPTCL drawing preparation, submission,estimate preparation & approval from the competent Authority of CEI &OPTCL,Arrangement of CEI Inspection etc. | 500000
11 | Statutory fees for payment towards forest diversion proposal in the line (considered 55 lakhs per hectare & approx 65 hectares of forest involvement in the corridor) | 357500000
12 | Grand Total (7+8+9+10+11) | 3674138349
(Rupees Three Hundred Sixty seven Crores Forty one Lakhs Thirty Eight Thousand Three Hundred Fouty Nine Only)

## Supply
Name of of Works: Construction of 400 KV Indravati-Therubali D/C LINE from proposed 400 KV PSP Sub-Station at Mukhiguda to proposed 400/220 KV GSS Therubali (SUPPLY)
Conductor- ACSR MOOSE (Twin), Towers- Suitable for Quad ACSR Moose Type |  |  | Total length of over head line- 93.204 RKM.
Earth wire- OPGW |  |  | Total towers- 270
No. of Ciruit- DC line on DC tower -93.204 KMs |  |  | Angle towers- 213 Nos, Suspension tower-57
Sl. No. | SUBSTATION EQUIPMENTS / MATERIALS
DESCRIPTION OF ITEMS(SCHEDULE-VIIA-TL) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification)
TOTAL FORD Price except Entry Tax IN INR
Construction of 400kv Indrabati-Therubali line (Twin Moose) (SUPPLY)
| SUPPLY_LINE EQUIPMENT & MATERIALS |  |  | IN INR
S. No. | SUPPLY OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT | QTY | UNIT PRICE | OGST @9% | CGST@9% | TOTAL UNIT PRICE With GST | Total Price | Remarks | PRICE REFERENCE
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8=5+6+7 | 9=4x8 | 10=7X10
1 | SUPPLY of Following type tested Lattice type Galvanized steel tangent / Angle tower(MS and HT) with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification.
1.1 | DA TYPE (0 deg ANGLE ) TOWERS- 57 nos | MT | 903.45
1.1.1 | +0 mtr Body Extension of DA - 57 Nos | MT | 193.287
1.1.2 | +3 mtr Body Extension of DA- 8 nos | MT | 19.072
1.1.3 | +6 mtr Body Extension of DA---13 Nos | MT | 51.35
1.1.4 | +9 mtr Body Extension of DA 16 Nos | MT | 83.68
1.2 | DB TYPE (15 deg ANGLE ) TOWERS- 90 Nos | MT | 2102.76
1.2.1 | +0 mtr Body Extension of DB - 90 Nos | MT | 455.4
1.2.2 | +3 mtr Body Extension of DB- 11 Nos | MT | 77.33
1.2.3 | +6 mtr Body Extension of DB- 15 Nos | MT | 89.85
1.2.4 | +9 mtr Body Extension of DB-24 Nos | MT | 192.12
1.3 | DC TYPE (30 deg ANGLE ) TOWERS- 41 Nos | MT | 1146.77
1.3.1 | +0 mtr Body Extension of DC - 41 Nos | MT | 239.03
1.3.2 | +3 mtr Body Extension of DC- 4 Nos | MT | 33.6
1.3.3 | +6 mtr Body Extension of DC- 07 nos | MT | 52.71
1.3.4 | +9 mtr Body Extension of DC- 5 Nos | MT | 48.15
1.4 | DD TYPE (60 deg ANGLE ) TOWERS- 82 nos | MT | 2781.44
1.4.1 | +0 mtr Body Extension of DD - 77 Nos | MT | 611.38
1.4.2 | +3 mtr Body Extension of DD- 5 Nos | MT | 52.575
1.4.3 | +6 mtr Body Extension of DD- 15 nos | MT | 141.45
1.4.4 | +9 mtr Body Extension of DD- 17 Nos | MT | 213.078
1.4.5 | +18 mtr Body Extension of DD- 1 Nos | MT | 28.042
1.4.6 | +25 mtr Body Extension of DD- 7 Nos | MT | 249.69
1.5 | STUBS
1.5.1 | DA - 57No. | MT | 37.107
1.5.2 | DB -90 nos | MT | 113.49
1.5.3 | DC - 41 No. | MT | 60.68
1.5.4 | DD -74 No. | MT | 146.298
1.5.5 | DD +18/25 8 Nos | MT | 17.464
1.6 | TEMPLATES
1.6.1 | DA - 6 no | MT | 9.9
1.6.2 | DB 10 Nos | MT | 21.8
1.6.3 | DC - 4 no | MT | 8.76
1.6.4 | DD - 7 no | MT | 16.38
1.6.5 | DD +18/25 - 1 no | MT | 2.34
1.7 | TOTAL WEIGHT OF STRUCTURES WITH STUBS INCLUDING MS & HT MATERIALS |  | 10141.253 | 85000 | 7650 | 7650 | 100300 | 1017167675.9 |  | Structure rate contract 767 Dtd. 24.06.2025 | ok | 862006505 | 77580585.45 | 77580585.45 | 1017167675.9 | 1017167675.9 | 0
1.8 | WEIGHT OF TEMPLATES | MT | 59.18 | 63712 | 5734.08 | 5734.08 | 75180.16 | 4449161.8688 |  | Structure rate contract 767 Dtd. 24.06.2025 | ok | 3770476.16 | 339342.8544 | 339342.8544 | 4449161.8688 | 4449161.8688 | 0
1.9 | Weight of different type G.I Nuts and Bolts | MT | 510.0217 | 102000 | 9180 | 9180 | 120360 | 61386205.794 |  | Structure rate contract 767 Dtd. 24.06.2025 | ok | 52022208.3 | 4681998.747 | 4681998.747 | 61386205.794 | 61386205.794 | 0
2 | Supply of the following tower accessories as per technical specification and as directed by the engineer in charge. |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2.1 | EARTHING DEVICE | Nos. | 540 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 1453440.456 |  | CD 24-25 Line sl.8 | ok | 1231729.2 | 110855.628 | 110855.628 | 1453440.456 | 1453440.456 | 0
2.2 | DANGER BOARD | Nos. | 270 | 236.77 | 21.3093 | 21.3093 | 279.3886 | 75434.922 |  | CD 24-25 Line sl.9 | ok | 63927.9 | 5753.511 | 5753.511 | 75434.922 | 75434.922 | 0
2.3 | NUMBER PLATE | Nos. | 540 | 129.38 | 11.6442 | 11.6442 | 152.6684 | 82440.936 |  | CD 24-25 Line sl.10 | ok | 69865.2 | 6287.868 | 6287.868 | 82440.936 | 82440.936 | 0
2.4 | PHASE PLATE | Nos. | 1620 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 192918.672 |  | CD 24-25 Line sl.11 | ok | 163490.4 | 14714.136 | 14714.136 | 192918.672 | 192918.672 | 0
2.5 | BIRD GUARD | Nos. | 342 | 524.7398 | 47.2266 | 47.2266 | 619.193 | 211764.0083 |  | Sanctioned Estimate of Basudevpur Project | ok | 179461.024 | 16151.4922 | 16151.4922 | 211764.0083 | 211764.0083 | 0
2.6 | ANTICLIMBING DEVICE | SET | 270 | 4400.23 | 396.0207 | 396.0207 | 5192.2714 | 1401913.278 |  | CD 24-25 Line sl.13 | ok | 1188062.1 | 106925.589 | 106925.589 | 1401913.278 | 1401913.278 | 0
2.7 | CIRCUIT PLATE | Nos. | 540 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 64306.224 |  | CD 24-25 Line sl.12 | ok | 54496.8 | 4904.712 | 4904.712 | 64306.224 | 64306.224 | 0
2.8 | COUNTERPOISE EARTHING wire -7/3.66 mm | Mtrs | 8100 | 32764.47 | 2948.8023 | 2948.8023 | 38662.0746 | 313162804.26 |  | Sanctioned Estimate of Basudevpur Project | ok | 265392207 | 23885298.63 | 23885298.63 | 313162804.26 | 313162804.26 | 0
1: 3; 2: Supply of following POWER CONDUCTORS in the proposed 400 KV lines as per the technical specification and as per the instruction of the engineer in charge. |  |  | 0 | 0 | 0 | 0 | 0 | 0
3.1 | ACSR Moose (54+7/3.53/3.66 mm) | Kms. | 1136 | 428317.61 | 38548.5849 | 38548.5849 | 505414.7798 | 574151189.8528 |  | Biennial PO placed on 26.09.2025 | ok | 486568804.96 | 43791192.4464 | 43791192.4464 | 574151189.8528 | 574151189.8528 | 0
4 | POWER CONDUCTOR ACESSORIES FOR ACSR MOOSE |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
4.1 | MID SPAN JOINT | Nos. | 950 | 1058 | 95.22 | 95.22 | 1248.44 | 1186018 |  | CD 24-25 Line sl.37 | ok | 1005100 | 90459 | 90459 | 1186018 | 1186018 | 0
4.2 | REPAIR SLEEVE | Nos. | 631 | 464.09 | 41.7681 | 41.7681 | 547.6262 | 345552.1322 |  | CD 24-25 Line sl.43 | ok | 292840.79 | 26355.6711 | 26355.6711 | 345552.1322 | 345552.1322 | 0
4.3 | PG CLAMP FOR ACSR MOOSE | Nos. | 800 | 612 | 55.08 | 55.08 | 722.16 | 577728 |  | Sanctioned Estimate of Basudevpur Project | ok | 489600 | 44064 | 44064 | 577728 | 577728 | 0
4.4 | SPACER DAMPER TWIN ACSR MOOSE | Nos. | 18650 | 563 | 50.67 | 50.67 | 664.34 | 12389941 |  | Sanctioned Estimate of Basudevpur Project | ok | 10499950 | 944995.5 | 944995.5 | 12389941 | 12389941 | 0
4.5 | RIGID SPACER ACSR MOOSE | Nos. | 5112 | 563 | 50.67 | 50.67 | 664.34 | 3396106.08 |  | Sanctioned Estimate of Basudevpur Project | ok | 2878056 | 259025.04 | 259025.04 | 3396106.08 | 3396106.08 | 0
5 | Supply of the GI earth wire of size 7/3.66 mm as per the technical specification and as per the direction of Engineer in charge. | Kms. | 94.6021 | 32764.47 | 2948.8023 | 2948.8023 | 38662.0746 | 3657511.901 |  | CD SL No- 16 | ok | 3099586.3568 | 278962.7721 | 278962.7721 | 3657511.901 | 3657511.901 | 0
1: 6; 2: EARTH CONDUCTOR ACESSORIES |  |  | 0 | 0 | 0 | 0 | 0 | 0
6.1 | VIBRATION DAMPER | Nos. | 540 | 361.62 | 32.5458 | 32.5458 | 426.7116 | 230424.264 |  | CD SL No- 44 | ok | 195274.8 | 17574.732 | 17574.732 | 230424.264 | 230424.264 | 0
6.2 | FLEXIBLE COPPER EARTH BOND | Nos. | 540 | 278.17 | 25.0353 | 25.0353 | 328.2406 | 177249.924 |  | CD SL No- 46 | ok | 150211.8 | 13519.062 | 13519.062 | 177249.924 | 177249.924 | 0
6.3 | SUSPENSION CLAMP | Nos. | 57 | 465.77 | 41.9193 | 41.9193 | 549.6086 | 31327.6902 |  | CD SL No- 48 | ok | 26548.89 | 2389.4001 | 2389.4001 | 31327.6902 | 31327.6902 | 0
6.4 | TENSION CLAMP | Nos. | 213 | 562.22 | 50.5998 | 50.5998 | 663.4196 | 141308.3748 |  | CD SL No- 50 | ok | 119752.86 | 10777.7574 | 10777.7574 | 141308.3748 | 141308.3748 | 0
6.5 | MID SPAN COMPRESSION JOINT | Nos. | 45 | 37.52 | 3.3768 | 3.3768 | 44.2736 | 1992.312 |  | CD SL No- 47 | ok | 1688.4 | 151.956 | 151.956 | 1992.312 | 1992.312 | 0
6.6 | REPAIR SLEEVE | Nos. | 20 | 37.52 | 3.3768 | 3.3768 | 44.2736 | 885.472 |  | CD SL No- 47 considerd | ok | 750.4 | 67.536 | 67.536 | 885.472 | 885.472 | 0
7 | Supply of OPGW Fibre Optic Cable & Hard ware for Speech , data & protection |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 48 fibre (DWSM) OPGW fibre optic cable. | Km | 94.6021 | 215500 | 19395 | 19395 | 254290 | 24056357.8374 |  | CD24-25-TEL-25 | ok | 20386743.93 | 1834806.9537 | 1834806.9537 | 24056357.8374 | 24056357.8374 | 0
7.2 | OPGW hardware set like suspension Assembly,Tensin Assembly(Dead end assembly, Pass through assembly) ,Vibration Damper,Down Lead Clamp Assemblies for 48 Fibre(DWSM) OPGW,Earth bond,Link plates | Km | 94.6021 | 22597.72 | 2033.7948 | 2033.7948 | 26665.3096 | 2522593.2187 |  | CD24-25-TEL-26 | ok | 2137790.8633 | 192401.1777 | 192401.1777 | 2522593.2187 | 2522593.2187 | 0
7.3 | Joint Box (splice enclosure),48F | Nos | 35 | 6491 | 584.19 | 584.19 | 7659.38 | 268078.3 |  | CD24-25-TEL-28 | ok | 227185 | 20446.65 | 20446.65 | 268078.3 | 268078.3 | 0
8 | Supply of the following Anti fog type porcelain disc insulators as per the technical specification and as per the instruction of the Engineer in charge. |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 160KN Porcelain Antifog Disc Insulator | Nos. | 124035 | 920 | 82.8 | 82.8 | 1085.6 | 134652396 |  | 4100000045 Dtd. 19.11.2025 | ok | 114112200 | 10270098 | 10270098 | 134652396 | 134652396 | 0
8.2 | 120 KN Porcelain Antifog Disc Insulator | Nos. | 17751 | 833 | 74.97 | 74.97 | 982.94 | 17448167.94 |  | 4100000045 Dtd. 19.11.2025 | ok | 14786583 | 1330792.47 | 1330792.47 | 17448167.94 | 17448167.94 | 0
1: 9; 2: Supply of the following hard ware fittings suitable for ACSR Moose conductors as per the technical specification. |  |  | 0 | 0 | 0 | 0 | 0 | 0
1: 9.1; 2: For ACSR Moose |  |  | 0 | 0 | 0 | 0 | 0 | 0
9.1.1 | Double suspension Hardware fittings.(AGS type) (2 x 120kN) | Nos | 342 | 5275.69 | 474.8121 | 474.8121 | 6225.3142 | 2129057.4564 |  | CD SL No-08 | ok | 1804285.98 | 162385.7382 | 162385.7382 | 2129057.4564 | 2129057.4564 | 0
9.1.2 | Double tension Hardware fittings. (2 x 160kN) | Nos. | 2568 | 5056.93 | 455.1237 | 455.1237 | 5967.1774 | 15323711.5632 |  | CD SL No-10 | ok | 12986196.24 | 1168757.6616 | 1168757.6616 | 15323711.5632 | 15323711.5632 | 0
9.1.3 | Single suspension Pilot Insulator Hardware fittings (1 x 120kN) | Nos. | 51 | 3465.33 | 311.8797 | 311.8797 | 4089.0894 | 208543.5594 |  | CD SL No-07 | ok | 176731.83 | 15905.8647 | 15905.8647 | 208543.5594 | 208543.5594 | 0
9.1.4 | “D” Shackle | Nos. | 2568 | 310 | 27.9 | 27.9 | 365.8 | 939374.4 |  | Sanctioned Estimate of Basudevpur Project | ok | 796080 | 71647.2 | 71647.2 | 939374.4 | 939374.4 | 0
9.1.5 | Hanger | Nos. | 342 | 592 | 53.28 | 53.28 | 698.56 | 238907.52 |  | Sanctioned Estimate of Basudevpur Project | ok | 202464 | 18221.76 | 18221.76 | 238907.52 | 238907.52 | 0
9.1.6 | U'-Bolt. | Nos | 57 | 137 | 12.33 | 12.33 | 161.66 | 9214.62 |  | Sanctioned Estimate of Basudevpur Project | ok | 7809 | 702.81 | 702.81 | 9214.62 | 9214.62 | 0
10 | High Resolution Binacular(Nikon Monarch 20x56 (M511)) | Nos | 2 | 80000 | 7200 | 7200 | 94400 | 188800 |  | Market price | ok | 160000 | 14400 | 14400 | 188800 | 188800 | 0
1: B; 2: TOTAL -SCHEDULE VIIA - 400KV LINE; 9=4x8: 2193920503.7372 | [5 empty] | 2193920503.7372 | 2193920503.7372 | 0
|  |  |  | 1098514.0698 | 98866.2663 | 98866.2663 | 1296246.6024
[5 empty] | 0.09 | 0.09 | 1.18

## Erection
Name of of Works: Construction of 400 KV Indravati-Therubali D/C LINE from proposed 400 KV PSP Sub-Station at Mukhiguda to proposed 400/220 KV GSS Therubali (ERECTION Schedule)
Conductor- ACSR MOOSE (Twin), Towers- Suitable for Quad ACSR Moose Type |  |  | Total length of over head line- 93.204 RKM.
Earth wire- OPGW |  |  | Total towers- 270
No. of Ciruit- DC line on DC tower -93.204 KMs |  |  | Angle towers- 213 Nos, Suspension tower-57
Construction of 400kv Indrabati-Therubali line (Twin Moose) (ERECTION Schedule)
| ERECTION_LINE EQUIPMENT & MATERIALS (SCHEDULE-VIIB) |  |  | IN INR
S. No. | ERECTION OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT | QTY | UNIT PRICE | OGST @9% | CGST@9% | TOTALUNIT PRICE With GST | TOTAL PRICE | PRICE REFERENCE
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8=5+6+7 | 9=4X8
1 | Erection, Testing and commissioning of following type tested Lattice type Galvanized steel tangent / Angle tower(MS and HT) with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). This includes supply of all labourers, T&P, headloading (if required) of all type of structures, & other materials required for erection.All Erection should confirm to the Technical Specification laid there in the Tender Specification.
1.1 | DA TYPE (0 deg ANGLE ) TOWERS- 57 nos | MT | 903.45
1.1.1 | +0 mtr Body Extension of DA - 57 Nos |  | 193.287
1.1.2 | +3 mtr Body Extension of DA- 8 nos | MT | 19.072
1.1.3 | +6 mtr Body Extension of DA---13 Nos | MT | 51.35
1.1.4 | +9 mtr Body Extension of DA 16 Nos | MT | 83.68
1.2 | DB TYPE (15 deg ANGLE ) TOWERS- 90 Nos | MT | 2102.76
1.2.1 | +0 mtr Body Extension of DB - 90 Nos |  | 455.4
1.2.2 | +3 mtr Body Extension of DB- 11 Nos | MT | 77.33
1.2.3 | +6 mtr Body Extension of DB- 15 Nos | MT | 89.85
1.2.4 | +9 mtr Body Extension of DB-24 Nos | MT | 192.12
1.3 | DC TYPE (30 deg ANGLE ) TOWERS- 41 Nos | MT | 1146.77
1.3.1 | +0 mtr Body Extension of DC - 41 Nos |  | 239.03
1.3.2 | +3 mtr Body Extension of DC- 4 Nos | MT | 33.6
1.3.3 | +6 mtr Body Extension of DC- 07 nos | MT | 52.71
1.3.4 | +9 mtr Body Extension of DC- 5 Nos | MT | 48.15
1.4 | DD TYPE (60 deg ANGLE ) TOWERS- 82 nos | MT | 2781.44
1.4.1 | +0 mtr Body Extension of DD - 77 Nos |  | 611.38
1.4.2 | +3 mtr Body Extension of DD- 5 Nos | MT | 52.575
1.4.3 | +6 mtr Body Extension of DD- 15 nos | MT | 141.45
1.4.4 | +9 mtr Body Extension of DD- 17 Nos | MT | 213.078
1.4.5 | +18 mtr Body Extension of DD- 1 Nos | MT | 28.042
1.4.6 | +25 mtr Body Extension of DD- 7 Nos | MT | 249.69
1.5 | STUBS
1.5.1 | DA - 57No. | MT | 37.107
1.5.2 | DB -90 nos | MT | 113.49
1.5.3 | DC - 41 No. | MT | 60.68
1.5.4 | DD -74 No. | MT | 146.298
1.5.5 | DD +18/25 8 Nos | MT | 17.464
1.6 | TEMPLATES
1.6.1 | DA - 57 no | MT | 94.05
1.6.2 | DB - 90 Nos | MT | 196.2
1.6.3 | DC - 41 no | MT | 89.79
1.6.4 | DD - 74 no | MT | 173.16
1.6.5 | DD +18/25 - 8 no | MT | 18.72
1.7 | ERECTION OF EHT SUPER STRUCTURES TOTAL WEIGHT OF STRUCTURES WITHOUT STUBS INCLUDING MS & HT MATERIALS | MT | 9766.214 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 85118856.1713 | RC 25-26, TL Sl. No. 9(i) | ok | 85118856.1713 | 85118856.1713 | 0
1.8 | WEIGHT OF Stubs, cleats & templates | MT | 946.959 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 8253358.6629 | RC 25-26, TL Sl. No. 9(i) | ok | 8253358.6629 | 8253358.6629 | 0
1.9 | Weight of different type G.I Nuts and Bolts | MT | 535.6586 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 4668610.7417 | RC 25-26, TL Sl. No. 9(i) | ok | 4668610.7417 | 4668610.7417 | 0
1: 2; 2: Erection of the following tower accessories as per technical specification and as directed by the engineer in charge. |  |  | 0 | 0 | 0
2.1 | EARTHING DEVICE | Nos. | 540 | 3859.4 | 347.346 | 347.346 | 4554.092 | 2459209.68 | RC25-26 TL 8.20(ii) | ok | 2459209.68 | 2459209.68 | 0
2.2 | DANGER BOARD | Nos. | 270 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 50807.142 | RC25-26 TL-11(ii) | ok | 50807.142 | 50807.142 | 0
2.3 | NUMBER PLATE | Nos. | 540 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 101614.284 | RC25-26 TL-11(i) | ok | 101614.284 | 101614.284 | 0
2.4 | PHASE PLATE | Nos. | 1620 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 304842.852 | RC25-26 TL-11(iii) | ok | 304842.852 | 304842.852 | 0
2.5 | BIRD GUARD | Nos. | 342 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 64355.7132 | RC25-26 TL-11(iv) | ok | 64355.7132 | 64355.7132 | 0
2.6 | ANTICLIMBING DEVICE | SET | 270 | 3441.28 | 309.7152 | 309.7152 | 4060.7104 | 1096391.808 | RC25-26 TL-H-11(v) | ok | 1096391.808 | 1096391.808 | 0
2.7 | CIRCUIT PLATE | Nos. | 540 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 101614.284 | RC 25-26 TL-11(i) | ok | 101614.284 | 101614.284 | 0
2.8 | COUNTERPOISE EARTHING wire -7/3.66 mm | Mtrs | 8100 | 94.52 | 8.5068 | 8.5068 | 111.5336 | 903422.16 | RC 25-26 TL, 8.3(i) | ok | 903422.16 | 903422.16 | 0
1: 3; 2: Hoisting and fixing of insulators with required accessories, paying out of conductor, jointing, stringing, sagging & Jumpering etc. of power conductor with G.I. Earth wire & OPGW in the proposed lines with all required accessories including scaffolding/other required arrangements for 33 KV,11 KV, LT , P&T lines, NH/roads, railway line, river etc and using own required T&P and compression jointing machines etc. as per the direction of Engineer in charge. |  |  | 0 | 0 | 0
3.1 | ACSR Double Moose with one Earth Wire and one OPGW | Route Kms. | 93.204 | 283694.75 | 25532.5275 | 25532.5275 | 334759.805 | 31200952.8652 | RC 25-26 Stringing SL No-10.10 (i- ©) | ok | 31200952.8652 | 31200952.8652 | 0
3.2 | Additional charges for Stringing EHT Line crossing/Railway/NH | Route Kms. | 10 | 99293.17 | 8936.3853 | 8936.3853 | 117165.9406 | 1171659.406 | RC 25-26 Stringing SL No-10.10 (i- (c ) i) | ok | 1171659.406 | 1171659.406 | 0
3.3 | Additional Crossing for stringing at river crossings with special towers beyond +6 mtr extension | Route Kms. | 1.5 | 198586.32 | 17872.7688 | 17872.7688 | 234331.8576 | 351497.7864 | RC 25-26 StringingSL No-10.10 (i- (c ) iv) | ok | 351497.7864 | 351497.7864 | 0
3.4 | Additional charges for stringing of line in towers placed in hilly terrain | Route Kms. | 35 | 156032.12 | 14042.8908 | 14042.8908 | 184117.9016 | 6444126.556 | RC 25-26 Stringing SL No-10.10 (i- (c ) v) | ok | 6444126.556 | 6444126.556 | 0
3.5 | Additional charges for stringing in special towers beyond +6 metres extension | Route Kms. | 50 | 99293.17 | 8936.3853 | 8936.3853 | 117165.9406 | 5858297.03 | RC 25-26 Stringing SL No-10.10 (i- (c ) iii) | ok | 5858297.03 | 5858297.03 | 0
1: 4; 2: WELDING OF TOWER BOLTS/NUTS |  |  | 0 | 0 | 0
5 | Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods, welding generator machine (diesel engine operator.), application of required zinc rich paints around the welding portion after welding (two coats),fuel,lubricants,T&P and labours and other arrangements etc. | Nos. | 25000 | 10.24 | 0.9216 | 0.9216 | 12.0832 | 302080 | RC25-26 TL-Fabrication-16.20(i) | ok | 302080 | 302080 | 0
1: 6; 2: ERECTION OF OPGW CABLE |  |  | 0 | 0 | 0
6.1 | 24F/48F OPGW stringing without supply of required HWF, tension assembly set, suspension assembly set, vibration damper set etc.(Under offline condition) | Km | 0 | 45000 | 4050 | 4050 | 53100 | 0 | CPC RC Sl.No.4 (OrderNo.171, DT.28.02.2023) | ok | 0 | 0 | 0
1: 7; 2: Head loading |  |  |  | 0 | 0
7.1 | Head loading quantity in MT-mtrs ( Includes head loading of all foundation materials as well as supply materials) | Per Ton/Per Mtr. | 3595835.51 | 13.26 | 1.1934 | 1.1934 | 15.6468 | 56263319.0579 | CPC RC Line works Sl.no.18 |  |  | 56263319.0579 | 0
1: B; 2: TOTAL -SCHEDULE VIIB - 400KV LINE; 9=4X8: 204715016.2006 |  | 869202360.1988 |  | 204715016.2006 | 0
5: 912260.74; 6: 82103.4666; 7: 82103.4666; 8=5+6+7: 1076467.6732 |  |  | 148451697.1428
[5 empty] | 0.09 | 0.09 | 1.18

## Civil
Name of of Works: Construction of 400 KV Indravati-Therubali D/C LINE from proposed 400 KV PSP Sub-Station at Mukhiguda to proposed 400/220 KV GSS Therubali Civil Works schedule
Conductor- ACSR MOOSE (Twin), Towers- Suitable for Quad ACSR Moose Type |  |  | Total length of over head line- 93.204 RKM.
Earth wire- OPGW |  |  | Total towers- 270
No. of Ciruit- DC line on DC tower -93.204 KMs |  |  | Angle towers- 213 Nos, Suspension tower-57
Sl. No. | DESCRIPTION OF ITEMS (SCHEDULE VIIC) | UNITS |  | IN INR
| ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) |  | TOTAL | UNIT PRICE | OGST @9% | CGST@9% | TOTAL UNIT PRICE With GST | Total Price | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8=5+6+7 | 9=4x8 | 10=7X10
PART A | CIVIL WORKS
1 | SURVEY OF LINE & PREPARATION LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting
1.1 | Preliminary survey, Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | KM. | 0 | 5036 | 453.24 | 453.24 | 5942.48 | 0 | RC25-26 TL-Survey-1.1 | ok | 0 |  | 0 | 0
1.2 | Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | KM. | 0 | 14268.67 | 1284.1803 | 1284.1803 | 16837.0306 | 0 | RC25-26 TL-Survey-1.2 | ok | 0 |  | 0 | 0
1.3 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | KM. | 93.204 | 6714.67 | 604.3203 | 604.3203 | 7923.3106 | 738484.2412 | RC25-26 TL-Survey-1.4 | ok | 738484.2412 |  | 738484.2412 | 0
1.4 | Preparation of land schedule with HAL & SAVIK classification on revenue maps indicating alignment therein duly authenticated by Revenue Inspector & Tahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 400KV line. Final route to be plotted on 1:50000 topo sheet for approval. | KM. | 0 | 10911.34 | 982.0206 | 982.0206 | 12875.3812 | 0 | RC25-26 TL-Survey-1.3 | ok | 0 |  | 0 | 0
1.5 | Soil Testing in complete shape along with submission of report etc. up to the depth of 07 Mtrs. | Per Loc. | 20 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 673481.224 | RC25-26 TL-Survey-1.5(a) | ok | 673481.224 |  | 673481.224 | 0
1.6 | Soil Testing in complete shape along with submission of report etc. up to the depth of 15 Mtrs. | Per Loc. | 30 | 38609.34 | 3474.8406 | 3474.8406 | 45559.0212 | 1366770.636 | RC25-26 TL-Survey-1.5(b) | ok | 1366770.636 |  | 1366770.636 | 0
1.7 | Soil Testing in complete shape along with submission of report etc. upto the depth of 30 mtrs for River bed pile. | Per Loc. | 5 | 75540.02 | 6798.6018 | 6798.6018 | 89137.2236 | 445686.118 | RC25-26 TL-Survey-1.5(c) | ok | 445686.118 |  | 445686.118 | 0
1: 2; 2: EXCAVATION WORKS FOR OPEN CAST/SHALLOW TYPE FOUNDATIONS, PILE CAPPINGS, RIVETMENT WORKS ETC; 6: 0; 7: 0 |  | 0 |  | 0 | 0
1: 2.1; 2: Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposal of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge. (675000cum); 6: 0; 7: 0 |  | 0 |  | 0 | 0
2.1.1 | Soft/Loose soil | CUM | 60795.7272 | 233.97 | 21.0573 | 21.0573 | 276.0846 | 16784764.0257 | RC25-26 TL-EXC-2(i) | ok | 16784764.0257 |  | 16784764.0257 | 0
2.1.2 | Dense/Compact soil | CUM | 22798.3977 | 366.54 | 32.9886 | 32.9886 | 432.5172 | 9860699.1377 | RC25-26 TL-EXC-2(ii) | ok | 9860699.1377 |  | 9860699.1377 | 0
2.1.3 | Partial Submerged soil | CUM | 15198.9318 | 421.13 | 37.9017 | 37.9017 | 496.9334 | 7552856.8557 | RC25-26 TL-EXC-2(vi) | ok | 7552856.8557 |  | 7552856.8557 | 0
2.1.4 | Fully submerged soil | CUM | 7599.4659 | 421.13 | 37.9017 | 37.9017 | 496.9334 | 3776428.4279 | RC25-26 TL-EXC-2(v) | ok | 3776428.4279 |  | 3776428.4279 | 0
2.1.5 | Soft/Disintegrated rock(Not requiring Blasting) | CUM | 22798.3977 | 701.88 | 63.1692 | 63.1692 | 828.2184 | 18882052.4657 | RC25-26 TL-EXC-2(iii) | ok | 18882052.4657 |  | 18882052.4657 | 0
2.1.6 | Hard Rock(Requiring Blasting/Using breaker machinery) | CUM | 22798.3977 | 1403.75 | 126.3375 | 126.3375 | 1656.425 | 37763835.9102 | RC25-26 TL-EXC-2(iv) | ok | 37763835.9102 |  | 37763835.9102 | 0
1: 3; 2: FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge. This includes the open cast foundations, Piles, Pile cappings, risers, chimney, rivetment works etc.; 6: 0; 7: 0 |  | 0 |  | 0 | 0
3.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower open foundations, pile cappings and rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P, head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 2947.308 | 6377.44 | 573.9696 | 573.9696 | 7525.3792 | 22179610.3192 | RC25-26 TL-FDN-6.2(iii) | ok | 22179610.3192 |  | 22179610.3192 | 0
3.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1.5:3) of grade M20 for open cast foundation, 500mm under ream piles, pile caps, chimney, risers (if any) with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement for tower open foundations, 500mm Under-reamed piles, all pile cappings risers, chimey etc. and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, dewatering, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P, head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 22351.7944 | 9103.72 | 819.3348 | 819.3348 | 10742.3896 | 240111683.7039 | RC25-26 TL-FDN-6.4(i) | ok | 240111683.7039 |  | 240111683.7039 | 0
3.3 | Cutting bending hooking, fixing and binding in poisition of MS bars for rainforcement of all foundations (open or pile types) concrete of towers including supply of wire for binding With supply of steel rod(TATA/RINL/SAIL Make) and head loading. No other make of steel shall be allowed. | MT | 1900.7157 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 143507106.1463 | RC25-26 TL-FDN-6.5(i) | ok | 143507106.1463 |  | 143507106.1463 | 0
1: 4; 2: PILE FOUNDATION BORING & CONCRETE WORKS |  | 0 |  | 0 | 0
1: 4.1; 2: 500mm Dia Under reamed Pile foundation as per approved design and drawing |  | 0 |  | 0 | 0
4.2 | Boring for under ream cast-in-Situ piling (500mm dia), with Manual Auger method or by using Motor driven Machinery ,including supply of Bentonite required for as per required procedure depending on the length of the bore stabilization. | Mtrs. | 100 | 3058.24 | 275.2416 | 275.2416 | 3608.7232 | 360872.32 | RC 25-26, TL Sl. No. 7.5(i) | ok | 360872.32 |  | 360872.32 | 0
1: 5; 2: 1000mm Dia Pile Foundation in the River bed as per approved design and drawing |  | 0 |  | 0 | 0
5.1 | Boring of 1000mm dia pile by DMC method or motor driven machinery etc., including supply of all equipments with labours and T&P as per specification with supply of Bentonite required for stabilization of bore. | Mtrs. | 100 | 7475.69 | 672.8121 | 672.8121 | 8821.3142 | 882131.42 | RC 25-26, TL Sl. No. 7.5(ii) | ok | 882131.42 | 11.8315 | 882131.42 | 0
5.2 | Fixing charges of MS Liner including the supply of materials like MS Sheet of adequate thickness, fabrication, cutting, bending, binding, putting the liner in appropriate position and other related works | MT | 12 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 906019.3872 | RC 25-26, TL, Sl. No. 7.6(i) |  | 906019.3872 |  | 906019.3872 | 0
1: 6; 2: REVETMENT: (including Benching) Supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge. |  | 0 |  | 0 | 0
6.3 | PCC in the ratio 1:2:4 as above Design, Engineering, Providing and laying of plain cement concrete (PCC 1:2:4) with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 800 | 7723.79 | 695.1411 | 695.1411 | 9114.0722 | 7291257.76 | RC25-26 TL-FDN-6.3(i) | ok | 7291257.76 |  | 7291257.76 | 0
6.4 | RR masonary work in the ratio 1:5 including supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge. | CUM | 3500 | 3805.47 | 342.4923 | 342.4923 | 4490.4546 | 15716591.1 | RC25-26 TL-15.10(i) | ok | 15716591.1 |  | 15716591.1 | 0
1: 6; 2: ROW (Right Of Way):- The agency shall pay the compensation @100% of the bench mark value of the land for construction of tower foundation and erection and 15% of bench mark value for acquisition of ROW in the land required for transmission line corridor as per the required width as per the letter no-RDM-LRGEA-POLICY-0003/43341/R&DM Dated 21.12.2022 of Additional Chief Secretary to Govt, R&DM Department, Govt. of Odisha. The agency shall also pay the crops compensation if any during the construction of transmission line in the own cost. The agency is sole responsible for obtaining ROW clearance. The agency shall pay all the cost for obtaining the ROW clearance for construction of Tower foundation, Erection and stringing of said line.; 6: 0; 7: 0 |  | 0 |  | 0 | 0
7.1 | Compensation for construction of Tower foudation & erection of transmission line including crops compensation & etc. (100% Bench mark cost plus other compensation) | Per location | 270 | 200000 | 18000 | 18000 | 236000 | 63720000 | Tentative Market Price |  | 63720000 |  | 63720000 | 0
7.2 | Compensation for or acquisition of ROW in the land required & trees & crops compensation to owners for transmission line corridor as per the required width (15% Bench mark cost plus other compensation if any) | RKM | 93.25 | 150000 | 13500 | 13500 | 177000 | 16505250 |  |  | 16505250 |  | 16505250 | 0
8 | Approval for PTCC, railway crossing, NHAI, Water and other atatutory bodies clearances (except payment of statutory fees) has to be obtained by submitting the required documents to the concerned department through OPTCL. Way-Leave blockade charges and any other charges are to be borne by the bidders. The documents for PTCC clearance & Railway clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | LS | 1 | 2145526 | 193097.34 | 193097.34 | 2531720.68 | 2531720.68 | Sanctioned Estimate of Basudevpur Project | ok | 2531720.68 |  | 2531720.68 | 0
9 | Forest Clearance work including preparation of Land Schedule (as per requirement ), DGPS Survey, authentication by concerned offices, preparation of complete Forest Diversion Proposal, obtaining Stage-I clearance, grant of working premission, submission of Stage-I compliances and obtaining Stahge-II clearance etc. Any other requirement of documents as per the prevailing norms of Forest department from time to time shall also be complied. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 06 months of award of contract. The contractor have to pay the DGPS authnetication & base point fees and all other payments to ORSAC. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | Per Hectare | 0 | 302193.28 | 27197.3952 | 27197.3952 | 356588.0704 | 0 |  | ok | 0 |  | 0 | 0
10 | Barbed wire fencing with spike to avoid wild animals, elephants from electrocution in Reserve Forest area including supply of barbed wire and all other materials as per approved TS and drawings ans as per recommendation of site Engineer-In -Charge as per condition of MOEF. GOI | Per Loc. | 100 | 115000 | 10350 | 10350 | 135700 | 13570000 | Tentative Market Price | ok | 13570000 |  | 13570000 | 0
11 | Supply & Installation of Dynamic Bird Flight Diverter LED type for installation in Top conductor & Earth wire under Forest stretch as per condition of MOEF. GOI | Nos. | 200 | 2475 | 222.75 | 222.75 | 2920.5 | 584100 | Wor Order No.ED-NZ-BLS-1040,Dt.23.05.2025 | ok | 584100 |  | 584100 | 0
2: TOTAL SCHEDULE VIIC OF 400KV LINE INCLUDING GST; 9=4x8: 625711401.8786 |  |  |  | 625711401.8786 | 0
5: 3263873.25; 6: 293748.5925; 7: 293748.5925; 8=5+6+7: 3851370.435 |  | 625711401.8786
[5 empty] | 0.09 | 0.09 | 1.18
Note on B17: OPTCL: River oile required?

## Schedule 3 Civil Works (hidden)
400/220/33 KV Sub-Station at NEULPOI & Associated 400 KV LILO LINE (CIVIL WORKS) |  |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK: Construction of 2X500 MVA,2X63 MVA 400/220/33 KV Sub-Station with SAS at Neulpoi with associated 400 KV D/C LILO LINE from 400KV Meramandali-New Duburi D/C line (CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi and 400 KV D/C LILO LINE from 400KV Meramandali-Mendhasal D/C line(CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi in Dhenkanal District on EPC contract basis
NOTICE INVITING TENDER-NIT NO. -
PRICE BID FOR WORKS CONTRACT : SCHEDULE -3 CIVIL WORKS COMPONENT OF THE WORKS CONTRACT-
NAME OF BIDDER
400/220 kV Substation Neulpoi: 400 KV Bays-[21 Nos (10 Fdr+2 ICT+7Tie+2Reactor)] In 1 & 1/2 CB System, 220KV Bay-7 Nos.(FDR-2,ICT-2+ TRF -2, B/C-1) 33KV Bay-9 Nos.(FDR-6,TFR-2, B/C -1]
Sl. No. | ERECTION, INSTALLATION, TESTING & COMMISSIONING _SUBSTATION |  |  |  |  | RUPEES IN INR
| DESCRIPTION OF ITEMS(SCHEDULE-2C) ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) | UNIT | Quantity (Neulpoi GSS) |  |  | UNIT PRICE | GST PER UNIT |  | TOTAL PER UNIT PRICE | AMOUNT
[7 empty] | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 |  |  | 5 | 6=5x9% | 7=5x9% | 8=5+6+7 | 9=4X8
B | CIVIL WORKS
1 | CONTOUR SURVEY AND LEVELING, BACK FILLING
1.1 | Contour survey and furnishing contour map including supply of all materials, Labour and T&P | SQ.MTRS. | 150000 |  |  | 5 | 0.45 | 0.45 | 5.9 | 885000
1.2 | Soil investigation : Supply of labour,T&P and other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge. (7.00mtrs) | PER POINT | 7 |  |  | 22595 | 2033.55 | 2033.55 | 26662.1 | 186634.7
2 | Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge.
2.1 | Normal Soil(SOFT/LOOSE) | Cum | 12500 |  |  | 136 | 12.24 | 12.24 | 160.48 | 2006000
2.2 | Hard Soil | Cum | 3200 |  |  | 192 | 17.28 | 17.28 | 226.56 | 724992
2.3 | Soft Rock | Cum | 3200 |  |  | 395 | 35.55 | 35.55 | 466.1 | 1491520
2.4 | Hard Rock(Requiring Blasting/Using breaker machinery) | Cum | 5500 |  |  | 621 | 55.89 | 55.89 | 732.78 | 4030290
3 | OPEN CAST/SHALLOW FOUNDATION CONCRETE WORKS Foundations: Design, engineering, supply of all labour, material and construction(open cast foundation) of PCC, RCC footings of any depth, pedestal including the cost of soil investigation, concreting, cement, reinforcement steel, fine and coarse aggregated, shoring & shuttering, grouting, underpinning and back filling of foundations etc complete for the switchyard gantry/ portal /column structures and equipment support as per the technical specification and approved drawings & disposal of excess earth as per direction of Engineer In charge. (a) For Switch yard gantry/portal structure foundations (b) For 400KV, 220KV, 33 KV Equipment foundations. (c) For other equipment foundations.
3.1 | Plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement in for the above column/ equipment/marshalling box foundations for column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all required materials, labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 900 |  |  | 5646 | 508.14 | 508.14 | 6662.28 | 5996052
3.2 | Open cast foundation for the above column/equipment/marshalling box foundations with RCC: 1:1.5:3 (Grade M-20) ,including supply of Labour all materials like cement, coarse and fine aggregates, shuttering, proper curing of the foundations/concrete and T&P in line with the Techinical Specification and as per direction of Engineer in Charge. ( without cost of steel) | Cum | 8000 |  |  | 7002 | 630.18 | 630.18 | 8262.36 | 66098880
3.3 | Supply of steel different sizes(TATA/RINL/SAIL make only). No other make of steel shall be allowed. As per the design with cutting, bending, binding and placing in position of steel rods for foundation concreting including cost of binding wire. | MT | 250 |  |  | 72149 | 6493.41 | 6493.41 | 85135.82 | 21283955
4 | Cutting, Filling and Leveling of Sub-station area including supply of labour and T&P Providing, neatly dressing up and levelling of substation area including switchyard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification.
4.1 | CUTTING of substation area and utilising the usable soil for filling and compaction and disposing the unsuable soil from site
4.1.1 | Soft/loose soil | Cum | 12000 |  |  | 136 | 12.24 | 12.24 | 160.48 | 1925760
4.1.2 | Dense/ Compact soil | Cum | 5000 |  |  | 192 | 17.28 | 17.28 | 226.56 | 1132800
4.1.3 | Soft/Disintegrated rock[not requiring blasting] | Cum | 3000 |  |  | 395 | 35.55 | 35.55 | 466.1 | 1398300
4.1.4 | Hard rock[requiring blasting or by using concrete breaker machinery] | Cum | 0 |  |  | 986 | 88.74 | 88.74 | 1163.48 | 0
4.2 | FILLING of substation area with borrowed earth with supply of all labour,T & P.
4.2.1 | Up to 30 mtr lead | Cum | 0 |  |  | 282 | 25.38 | 25.38 | 332.76 | 0
4.2.2 | Beyond 30 mtr & up to 100mtr lead | Cum | 10000 |  |  | 339 | 30.51 | 30.51 | 400.02 | 4000200
4.2.3 | Beyond 100mtr lead | Cum | 15000 |  |  | 452 | 40.68 | 40.68 | 533.36 | 8000400
5 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling and disposal of excess earth as per the direction of Engineer In charge.
(2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in cable trench as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge.
(3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing), including supply of Labour all materials like MS Rod, Cement, coarse and fine aggregates, shuttering, cutting, bending, binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Fly ash Brickwork with fly ash Brick, plastering (1:6 Ratio) & curing, wherever required including the supply of labour, material, cement, etc.
(5) The outdoor cable trench wall top surface shall be "L" shaped and the cover slabs shall be placed with in the"L shaped" surface of both the walls. The top surface of the trench shall be smooth finished. (6)Supply,fabrication & Fixing of GI Angle for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the GI insert plate fixed on the trench wall for better rigidity. The Insert plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting.
(7) Precast of RCC covers (1:1.5:3) with MS sheet(2mm) frame and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (8) All the RCC cover slabs shall have the lifting hooks. The slabs without the MS sheet frame and Lifting hooks shall not be accepted.
(9) Cable Trenches Inside The Control Room Shall Be Covered With M.S Chequered Plate(Duly Painted As Per Instruction Of Engg In Charge) Including Standard Support Stand {Hd Galvanised (M.S Joist , Channel, Angle). Stoppers shall be fixed at the underneath so that the chequered shall not be falling into the cable trench in any case.
5.1 | Section 1-1 | Mtrs | 800 |  |  | 22566 | 2030.94 | 2030.94 | 26627.88 | 21302304
5.2 | Section 2-2 | Mtrs | 600 |  |  | 15886 | 1429.74 | 1429.74 | 18745.48 | 11247288
5.3 | Section 3-3 | Mtrs | 600 |  |  | 14288 | 1285.92 | 1285.92 | 16859.84 | 10115904
5.4 | Section 4-4 (inside dimensions- width- 400mm, height- 400mm), wall- 75mm, bottom concrete-75mm, two 150mm trays shall be laid side by side in one layer. | Mtrs | 600 |  |  | 7578 | 682.02 | 682.02 | 8942.04 | 5365224
6 | Cable trench crossing:Design,engineering,construction including supply of labour,materials,cement,reinforcement steel,formwork etc,and all associated works for construction of trench crossing as per technical specification and approved drawing.(Road crossing )
6.1 | Section 1-1 | Nos | 1 |  |  | 221052 | 19894.68 | 19894.68 | 260841.36 | 260841.36
6,2 | Section 2-2 | Nos | 1 |  |  | 197825 | 17804.25 | 17804.25 | 233433.5 | 233433.5
6,3 | Section 3-3 | Nos | 1 |  |  | 141129 | 12701.61 | 12701.61 | 166532.22 | 166532.22
7 | Roads: Design, construction of roads and walkways/ shoulders within sub-station(Switch yard area,colony area,approach road,control room building area, main gate to the switch yard gate etc) as per specification, layout and approved drawings complete. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge.
7.1 | 7 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section(from the switch yard main gate to power transformer & infront of GIS cum control room building. | Mtrs | 1200 |  |  | 20516 | 1846.44 | 1846.44 | 24208.88 | 29050656
7.2 | Approach Road: 7 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section(from the switch yard main gate to the govt road. | Mtrs | 300 |  |  | 17786 | 1600.74 | 1600.74 | 20987.48 | 6296244
7.3 | 3.75 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section( Periphery roads outside switch yard fencing and colony roads) | Mtrs | 1200 |  |  | 12494 | 1124.46 | 1124.46 | 14742.92 | 17691504
8 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme (RCC type), road-culverts,Shall have drain on both side of the road and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. All the switch yard bays , roads water drainage shall be connected to the main surface drain. As per approved drawing and specification. All the drainage system shall be RCC type with M20 grade concrete.
8.1 | Storm water drain (RCC type) as per design above and subsequent approval | Mtrs. | 1000 |  |  | 3870 | 348.3 | 348.3 | 4566.6 | 4566600
8.2 | Road side drains(RCC type)-on each side of the 3.75 mtr and 7 mtr concrete roads as per design above & subsequent apporval | Mtrs | 2400 |  |  | 3317 | 298.53 | 298.53 | 3914.06 | 9393744
8.3 | Road-culverts, drain crossings (RCC type) | Lots | 2 |  |  | 334530 | 30107.7 | 30107.7 | 394745.4 | 789490.8
9 | Rain water harvesting system as per Technical specification and approval of drawing and as per the direction of the Engineer in charge. | Nos | 3 |  |  | 210848 | 18976.32 | 18976.32 | 248800.64 | 746401.92
10 | Foundations for transformers: Design, engineering, supply of labour, material, equipments and construction of Auto-transformer/Transformer foundation including piling if any, all associated works, rail tracks, jacking pads,anchor block RCC and PCC, miscellaneous structural steel including oil collection pits (for 30% of the tfr oil capacity) below the transformer, MS grating(if required), gravel filling, and other items etc. not mentioned herein, but specifically required for the completion of the work as per technical specification and approved drawing. (Rate shall be inclusive of cement, reinforcement steel, angles,flats and form work etc.)(all cement concrete shall have RCC ratio 1:1.5:3). Transformer RCC foundation and Rail Track should be extended upto the approaching road (However,the height of RCC foundation beyond transformer main plinth area should be same as height of concrete road ). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth.
10.1 | 500 MVA, 400/220kV transformers/ 125MVAr, 400KV Reactors a) Overall dimension of transformer(appox) Length:11500 mmX Width 7000 mmX Height 7500 mm b) Total weight with oil and tank: 300 MT (appox) | Nos | 4 |  |  | 2856133 | 257051.97 | 257051.97 | 3370236.94 | 13480947.76
10.2 | 63 MVA, 220/33 KV Power Transformer a) Overall dimension of transformer(appox) Length:7200 mmX Width 6000 mmX Height 7000 mm b) Total weight with oil and tank: 128 MT (appox) | Nos | 2 |  |  | 1295659 | 116609.31 | 116609.31 | 1528877.62 | 3057755.24
10.3 | OIL SUMP PIT (150% of tfr oil capacity of one transformer): Design, engineering, supply of labour, material, equipments and construction of oil sump pit (RCC with ratio 1:1.5:3) including piling if any, all associated works & suitable connectivity oil collector pit provisioned near the transformer to the main oil sump pit and with provision of pump (suitable for handling transformer oil having capacity of 5 HP, with auto level control , including cabling, fixing of control gear & provision of a pump shed (of sufficient size to allow person to install, dismantle, make cable connection & maintain etc) over the oil sump pit). This oil sump pit shall be as per CIGRE standard for the oil collection pit inorder to separate oil from the water. Other piping with necessary valves arrangement shall also be provided to remove water from the oil sump pit. As per spec and approved drawing.
10.3.1 | Oil capacity of each ICT-500 MVA, 400/220 KV :100000 ltrs. (approx) | Lot | 1 |  |  | 196083.22 | 17647.4898 | 17647.4898 | 231378.1996 | 231378.1996
10.3.2 | Oil capacity of each Reactor-125 MVAR, 400 KV :100000 ltrs. (approx) | Lot | 1 |  |  | 196083.22 | 17647.4898 | 17647.4898 | 231378.1996 | 231378.1996
10.3.3 | Oil capacity of each Transformer 63 MVA, 220/33 KV: 26500 ltrs. (approx) | Lot | 1 |  |  | 76414.78 | 6877.3302 | 6877.3302 | 90169.4404 | 90169.4404
11 | FIRE FIGHTING (Nitrogen Injection Type Fire Prevention & Extinguishing System) All civil works related to NIFPES as per approved drawing including excavation in all type of soil, PCC, RCC, Steel , backfilling, compaction etc complete in all respect as per instruction of site in-charge.
11.1 | For 500MVA, 400/220 KV ICT | Lot | 2 |  |  | 100000 | 9000 | 9000 | 118000 | 236000
11.2 | For 125MVAr, 400KV Reactor | Lot | 2 |  |  | 100000 | 9000 | 9000 | 118000 | 236000
11.2 | For 63MVA, 220/33KV Power Transformer | Lot | 2 |  |  | 100000 | 9000 | 9000 | 118000 | 236000
12 | Fire wall: Design, engineering, procurement of labour, material including all associated works for construction of fire-walls as per technical specification and approved drawings(column shall be RCC ratio 1:1.5:3 and the walls are of fire resistant bricks).This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Enginer In charge. As per approved drawing and specification. The MS Rod FE-500 as per BIS-1786 to be used .Painting of the walls as per direction of the Engineer in charge. | NO. | 3 |  |  | 200000 | 18000 | 18000 | 236000 | 708000
13 | STATION TRANSFORMER:Design, engineering, procurement of labour, material including all associated works for construction of foundation(RCC) for the station transformers 2X 33/0.415 KV,1000 KVA (plinth mounted) including piling if any as per approved drawing and specification. It includes other accessories & materials as required need to be supplied for complete installation of transformer as per the instruction of Engineer In charge and as per the specification and approved drawing. | Nos | 2 |  |  | 250000 | 22500 | 22500 | 295000 | 590000
14 | Out door bay kiosks : Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The indicative drawing provided in the TS may be referred to. As per approved drawings and specification. The internal dimensions of the Bay Kiosks are as mentioned against the switchyards below. Doors shall be heat insulated and hinge type.
14.1 | For 400KV & 220KV Switchyards (4 Lots for 400KV + 1 Lot for 220KV = 5 Lots) Internal Dimensions for the Kiosk - 8m x 5.5m x 3.3m
14.1.1 | RCC volume including MS rods (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. ( including for Pile foundation if required with cost of boring, Column ,Beams and roofs etc. ) | Lot | 5 |  |  | 125217.66 | 11269.5894 | 11269.5894 | 147756.8388 | 738784.194
14.1.2 | Fly Ash Brick masonry work in cement sand mortar 1: 5 with bricks of class designation 75kg/mm2 as per technical spec & approved drawings. | Lot | 5 |  |  | 75130.596 | 6761.7536 | 6761.7536 | 88654.1033 | 443270.5164
14.1.3 | Flooring shall be with vitrified digital double charged tiles (Kajaria/Johnson/Somany/Varmora/Cera) with dado as per technical spec & approved drawings. | Lot | 5 |  |  | 25043.532 | 2253.9179 | 2253.9179 | 29551.3678 | 147756.8388
14.1.4 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 5 |  |  | 12521.772 | 1126.9595 | 1126.9595 | 14775.691 | 73878.4548
14.1.5 | Doors shall be of hinge operated openable and window shall be sliding type with adequate locking facility. The door window frame shall be of UPVC (Fenesta make) heavy sections with double layer toughened glaze of 6mm (min.) & windows shall have anodised aluminium grills. As per technical spec & approved drawing. | Lot | 5 |  |  | 25043.532 | 2253.9179 | 2253.9179 | 29551.3678 | 147756.8388
14.1.6 | Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make) ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 5 |  |  | 50087.064 | 4507.8358 | 4507.8358 | 59102.7355 | 295513.6776
14.1.7 | Provision of smoke and fire detection & Alarm system of the kiosks - to be integrated with the system in the main CRB. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 5 |  |  | 56868.78 | 5118.1902 | 5118.1902 | 67105.1604 | 335525.802
14.2 | For 33KV Switchyard (1 lot) of internal size-5m x 5m x 3.3m
14.2.1 | RCC volume including MS rods (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. ( including for Pile foundation if required with cost of boring, Column ,Beams and roofs etc. ) | Lot | 1 |  |  | 104348.05 | 9391.3245 | 9391.3245 | 123130.699 | 123130.699
14.2.2 | Fly Ash Brick masonry work in cement sand mortar 1: 5 with bricks of class designation 75kg/mm2 as per technical spec & approved drawings. | Lot | 1 |  |  | 62608.83 | 5634.7947 | 5634.7947 | 73878.4194 | 73878.4194
14.2.3 | Flooring shall be with vitrified digital double charged tiles (Kajaria/Johnson/Somany/Varmora/Cera) with dado as per technical spec & approved drawings. | Lot | 1 |  |  | 20869.61 | 1878.2649 | 1878.2649 | 24626.1398 | 24626.1398
14.2.4 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 1 |  |  | 10434.81 | 939.1329 | 939.1329 | 12313.0758 | 12313.0758
14.2.5 | Doors shall be of hinge operated openable and window shall be sliding type with adequate locking facility. The door window frame shall be of UPVC (Fenesta make) heavy sections with double layer toughened glaze of 6mm (min.) & windows shall have anodised aluminium grills. As per technical spec & approved drawing. | Lot | 1 |  |  | 20869.61 | 1878.2649 | 1878.2649 | 24626.1398 | 24626.1398
14.2.6 | Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make) ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 |  |  | 41739.22 | 3756.5298 | 3756.5298 | 49252.2796 | 49252.2796
14.2.7 | Provision of smoke and fire detection & Alarm system of the kiosks - to be integrated with the system in the main CRB. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 |  |  | 47390.65 | 4265.1585 | 4265.1585 | 55920.967 | 55920.967
15 | Anti-Weed Treatment :Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treat of the switch-yard areas,controlroom etc. as per the instruction of Engineer-in-Charge.The chemical to be sprayed as per the standard practice adopted for antiweed treatment of sub-station area & as per the technical specification. | Sq Mtrs | 8000 |  |  | 17.84 | 1.6056 | 1.6056 | 21.0512 | 168409.6
16 | PCC before site surfacing: Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:4:8 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. (Switch yard area) | CUM | 3000 |  |  | 5145.91 | 463.1319 | 463.1319 | 6072.1738 | 18216521.4
17 | METAL SPREADING IN THE SWITCH-YARD: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:4:8). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 4000 |  |  | 2867 | 258.03 | 258.03 | 3383.06 | 13532240
18 | Switch yard fencing: Providing and fixing of G.I Goat mesh fencing (the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings and as required under the safety regulation of local, State and Central Government bodies and as per instruction of the Engineer-in-Charge. This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing shall be as per specification. The fencing shall be continuous i.e. a GI flat of 50 x 6mm shall run continuous at top & at bottom all along the fence. The fencing shall be connected to the earth mat every 3 mtrs. | Mtr | 3000 |  |  | 2240 | 201.6 | 201.6 | 2643.2 | 7929600
19 | SWITCHYARD GATE: Design, engineering, procurement of labour, material including all associated works for construction and fixing of switch yard gates and switchyard wicket gates as per specification and approved drawing. Switchyard gates shall have RCC pillars on both sides having open or pile founfdation and the gate shall be of stainless steel square pipes of 304 grade. The main entrance gate to switchyard shall have a wicket gate made of the same material. This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth, PCC/RCC concreting, supply of cement aggregates, rebar rod etc as per the direction of Engineer In charge. It includes supply of all materials and all other associated works required to complete works as per specification and approved drawings and instruction of engineer in charge.
19.1 | Switchyard gate (On both sides of 7 m. road of switchyard) | NOS | 3 |  |  | 150000 | 13500 | 13500 | 177000 | 531000
19.2 | Wicket gate | NOS | 4 |  |  | 50000 | 4500 | 4500 | 59000 | 236000
20 | STONE PITCHING & TOE WALL:Stone pitching including making of toe walls both at top and bottom, including surface drain both at top and bottom and partition wall in every 10 mtrs by using boulders and RR masonry walls respectively. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth and supply of materials and labour as per the direction of Engineer In charge and as per approved drawing and specification.
20.1 | Excavation of Soil | Cum | 1000 |  |  | 248.08 | 22.3272 | 22.3272 | 292.7344 | 292734.4
20.2 | P.C.C (1:3:6): Lean Concrete Grade M-10 | Cum | 30 |  |  | 5237.8 | 471.402 | 471.402 | 6180.604 | 185418.12
20.3 | RR Masonry (1:5) | Cum | 400 |  |  | 2511.7 | 226.053 | 226.053 | 2963.806 | 1185522.4
20.4 | P.C.C (1:2:4): Lean Concrete Grade M-15 | Cum | 5 |  |  | 6371.13 | 573.4017 | 573.4017 | 7517.9334 | 37589.667
20.5 | Brick masonary in ratio 1:5 with supply of first class K.B bricks,good quality river sand, cement, labour & T&P etc. as required. | Cum | 200 |  |  | 4533.3 | 407.997 | 407.997 | 5349.294 | 1069858.8
21 | RETAINING WALL: Construction of RCC retaining wall below the FGL and from NSL as per the site condition to sustain the earth pressure. The depth and length of RCC wall shall be designed as per site requirement. This includes excavation in all type of soil, RCC (1:1.5:3) with supply of steel(Fe-500), cement ,sand etc. including cutting, bending, binding, backfilling in layers after concreting for soil compaction and also supply of other required materials and labour . The work shall be executed as per the approved design , drawing as per direction of Engineer In charge
21.1 | Exacavation all type of soil | Cum | 1200 |  |  | 5237.8 | 471.402 | 471.402 | 6180.604 | 7416724.8
21.2 | PCC (1:3:6) | Cum | 50 |  |  | 5237.8 | 471.402 | 471.402 | 6180.604 | 309030.2
21.3 | RCC volume (M20) | Cum | 200 |  |  | 7565.71 | 680.9139 | 680.9139 | 8927.5378 | 1785507.56
22 | STORE SHED+OPEN STOCKYARD:Design, engineering, procurement of labour, material including all associated works for construction of store shed & open stockyard as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the specification,approved drawing and direction of Engineer In charge. One no store shed of floor size 10X10 mtr having Fly ash Brick walls and plastering with RCC roof. The flooring shall be of 75 mm thickness PCC (mix ratio1:2:4) over RR masonry works (as per standard practice of flooring). Provision of adequate nos of MS racks (proper paintings also to be done as per the direction of site in charge) for keeping the spare materials. The height of the shed shall be 4mtrs above the plinth. Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc),fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators( including supply) and provision of incoming AC supply from the main ACDB/outdoor kiosks installed for street light or colony quarters. Foundation shall be as per actual soil condition as per soil test, including piling where required. | Lot | 1 |  |  | 1100000 | 99000 | 99000 | 1298000 | 1298000
Also includes painting of the building (in side and out side) as per recommended for colony building in the specification.Store shed door shall have access control system which is sensor operated with key card for entry. Log of all the persons accessing the store shed with date and time stamp shall be kept in the system. There shall be provision for manual override of the system for exigencies as per direction of engineer in charge. Installation of smoke and fire detection & Alarm system of the building. Provision of conventional fire fighting equipment (including supply of FFE) at strategic location suitable for wall hanging as per direction of engineer in charge. The MS Rod ( FE-500 as per BIS-1786 ) to be used in the building. (* REMARKS : FOR SUPPLY OF ALL THE CABLES AS INDICATED ARE COVERED IN THE supply)}
23 | VEHICLE PARKING SHED: Design, engineering, construction of parking area shall be with the cost of all required material, procurement of labour, all T&P etc. This includes supply of all materials and all associated works for construction of vehicle parking shed, complete in all respect as per technical specification and enclosed drawing. This also includes, excavation in all type soil and rocks, backfilling and disposal of excavated soil, (cement, reinforcement steel, form work for) PCC, RCC (1:1.5:3), M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal), Fly ash Brick work with mortar 1:5, Plastering, Flooring, External and Internal Painting, all electrical works (Including but not limited to wires, conduits, GI boxes, switches, luminaires (Phillips/Crompton/Bajaj/Havells/Wipro), electrical fixtures and all other switchgear etc.)etc. and any other works required for completion of the work in all respect. Foundation shall be as per actual soil condition as per soil test, including piling where required. Note:The provision is to be made for three cars and two space for two wheelers (the indicative drawing is for two cars and two spaces for two wheelers). | Lot | 1 |  |  | 500000 | 45000 | 45000 | 590000 | 590000
24 | PROVISION OF SAND BED:Design, engineering, procurement of labour, material including all associated works for construction of sand bed as per specification and approved drawing. This also includes excavation in all types of soil or rocks, back fillin ,and disposal of excess earth as per the direction of Engineer In charge. The sand bed size shall be of 10m x 10m constructed with bricks, plastered and the filled with river sand for storing of Transformer Bushings and other Insulators. | Lot | 1 |  |  | 100000 | 9000 | 9000 | 118000 | 118000
25 | RCC Foundations for Octagonal Lighting Poles: Design, engineering, procurement of labour, material including piling if any, all associated works for construction of foundations for octagonal lighting poles as per approved drawings (RCC ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawing and specification. Pcc padding ratio (1:4:8). The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 to be used. | Nos | 50 |  |  | 10000 | 900 | 900 | 11800 | 590000
26 | COLOUR CODING, BAY MARKING Etc: Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (Red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof sticker (fluorescent type) may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. Stainless Steel sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Lot | 1 |  |  | 200000 | 18000 | 18000 | 236000 | 236000
27 | CONTROL ROOM cum office BUILDING: Design, engineering and construction of switch yard buildings including excavation, construction of foundations (open cast or pile as per soil conditions), construction of RCC super structure, with the cost of material, supply of labour, cement, reinforcement- steel and form work as per the enclosed drawing and technical specification ( The RCC structure frame and the foundations should be in the ratio 1:1.5:3). The indicative drawings of the building is provided and the foundation of the building shall be designed based on the actual soil condition. It shall be ensured that the various room sizes are sufficient to accomodate the offered equipment.
27.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plinth with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 |  |  | 472218.55 | 42499.6695 | 42499.6695 | 557217.889 | 557217.889
27.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 |  |  | 399089.82 | 35918.0838 | 35918.0838 | 470925.9876 | 470925.9876
27.3 | Providing & laying Plain cement concrete (1:2:4) (in sunken slab areas)using 12mm size black hard crusher broken granite chips of approved quality from approved quarry including hoisting, lowering and laying concrete in layers, watering, curing etc. complete including cost, conveyance, royalties and taxes of all materials with labour, cess and T&P etc. required for the work complete. | Lot | 1 |  |  | 33311.04 | 2997.9936 | 2997.9936 | 39307.0272 | 39307.0272
27.4 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations, columns, Beams, lintels, chhajas, roof slabs, stair case etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 |  |  | 3166323.25 | 284969.0925 | 284969.0925 | 3736261.435 | 3736261.435
27.5 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 |  |  | 4139142.58 | 372522.8322 | 372522.8322 | 4884188.2444 | 4884188.2444
27.6 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) for foundation and plinth and in cement mortar of mix (1:4) for other area in ground floor, first floor & head room with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 |  |  | 952316.33 | 85708.4697 | 85708.4697 | 1123733.2694 | 1123733.2694
27.7 | Providing 16 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 |  |  | 307132.95 | 27641.9655 | 27641.9655 | 362416.881 | 362416.881
27.8 | Providing 18mm C.P. in two coats underlayer 12mm C.P. 1:5 and top layer 6mm thick C.P. 1:6 finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 |  |  | 161769.49 | 14559.2541 | 14559.2541 | 190887.9982 | 190887.9982
27.9 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 |  |  | 124675.99 | 11220.8391 | 11220.8391 | 147117.6682 | 147117.6682
27.1 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 |  |  | 551821.51 | 49663.9359 | 49663.9359 | 651149.3818 | 651149.3818
27.11 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 |  |  | 75635.64 | 6807.2076 | 6807.2076 | 89250.0552 | 89250.0552
27.12 | Supplying, fitting and Fixing Matt finish full body vitrified Acid proof tiles in floor and in dado upto lintel level of Battery room of 10MM thick, size 300mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 |  |  | 150000 | 13500 | 13500 | 177000 | 177000
27.13 | Providing, fitting & fixing anti-skid ceramic floor tiles in flooring in toilets using special plain/ printed series anti-skid ceramic floor tile of premium grade (having minimum thickness 7 mm to 8 mm & size 300 mm x 300 mm confirming to IS 13755 of approved quality and shade of Somany/ Kajaria / Johnson on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened & washed sharp river sand for mortar ceramic floor tiles with neat white cement slurry, mixed with required (tiles are to be immersed in the water for required time before use) quantities of pigments of approved marks to match the shades of the anti-skid ceramic floor tiles if required including cost, conveyance, loading, unloading, stacking, royalties of all material, cost of all labour, sundries, T&P required for the work, watering, complete in all respect as per specification excluding GST as per specification as directed by Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 |  |  | 39320.66 | 3538.8594 | 3538.8594 | 46398.3788 | 46398.3788
27.14 | Providing & Fixing tiles of size 30cm x 45 cm glazed ceramic wall tiles (All Toilet walls) of premium grade of approved quality and shade having thickness 8mm to 10mm confirming to IS 13755 in dados skirting and risers of steps on 12mm thick cement plaster (1:3) to proper slope, line and level including cutting to required size and shape, fixing at corners and splays etc including filling the joints with neat white cement slurry mixed with pigments to match the shade of the tiles including cost, Conveyance, loading, unloading, stacking, royalities of all materials, cost of all labour,T&P, sundries, watering and curing for the required period for the work complete in all respect excluding GST as directed by the Engineer-in-charge.(Note- Sample of tiles shall be approved before procurement and use.) | Lot | 1 |  |  | 149553.44 | 13459.8096 | 13459.8096 | 176473.0592 | 176473.0592
27.15 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 |  |  | 212776.97 | 19149.9273 | 19149.9273 | 251076.8246 | 251076.8246
27.16 | Providing Granite stone prepolished 10mm thick in dado of approved quality, colour and size in dado, riser of steps and dado of landings in all floors at all height on 12mm thick bed of cement mortar of mix (1:3) with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 |  |  | 32408.47 | 2916.7623 | 2916.7623 | 38241.9946 | 38241.9946
27.17 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 |  |  | 172573.2 | 15531.588 | 15531.588 | 203636.376 | 203636.376
27.18 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board and pasting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. (In toilets, rest rooms) | Lot | 1 |  |  | 94601.43 | 8514.1287 | 8514.1287 | 111629.6874 | 111629.6874
27.19 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board, Vision glass panel (1.5ft x 1ft) and paisting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. (All except in toilets & rest rooms) | Lot | 1 |  |  | 581918.03 | 52372.6227 | 52372.6227 | 686663.2754 | 686663.2754
27.2 | Supplying, fitting and fixing of M.S grills, Grill window (as per I.S. specification and as per approved drawings) in proper position in all floors as per TS, approved drawing, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 118410.72 | 10656.9648 | 10656.9648 | 139724.6496 | 139724.6496
27.21 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge.
27.21.1 | Inside walls and Ceiling: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 |  |  | 523170.83 | 47085.3747 | 47085.3747 | 617341.5794 | 617341.5794
27.21.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 |  |  | 101515.94 | 9136.4346 | 9136.4346 | 119788.8092 | 119788.8092
27.21.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 |  |  | 9298.75 | 836.8875 | 836.8875 | 10972.525 | 10972.525
27.22 | Supplying, fitting and fixing of Stainless steel of 304 grade in hand railing using 50mm dia of 2mm thick circular pipe with Balustrade of size 32mm x 32mm x 2mm @ 0.90mtr. C/C and stainless square pipe bracing of size 32mm x 32mm x 2mm in 3 rows in stair case as per approved design and specification, buffing, polishing etc with cost, conveyance, cost of all labour,labour cess, T&P etc. required for the work complete in all respect as per direction of the Engineer-in-charge. | Lot | 1 |  |  | 50521.27 | 4546.9143 | 4546.9143 | 59615.0986 | 59615.0986
27.23 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 100978.98 | 9088.1082 | 9088.1082 | 119155.1964 | 119155.1964
27.24 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 66936.46 | 6024.2814 | 6024.2814 | 78985.0228 | 78985.0228
27.25 | Providing and fixing of UPVC sliding windows in the Control room Building as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 574776 | 51729.84 | 51729.84 | 678235.68 | 678235.68
27.26 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 173473.8 | 15612.642 | 15612.642 | 204699.084 | 204699.084
27.27 | Water proofing to the sunken slab including providing and filling it with 40mm size brick bat as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 12652.79 | 1138.7511 | 1138.7511 | 14930.2922 | 14930.2922
27.28 | Providing and fixing removable Raised/False Flooring System in the control room as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 364390 | 32795.1 | 32795.1 | 429980.2 | 429980.2
27.29 | Plinth Potection for control room building as per the provided drawing and as per sepcification in TS. | Lot | 1 |  |  | 92194.88 | 8297.5392 | 8297.5392 | 108789.9584 | 108789.9584
27.3 | Construction of covered drain for control room building as per the provided drawing and as per specification in TS. | Lot | 1 |  |  | 330956.09 | 29786.0481 | 29786.0481 | 390528.1862 | 390528.1862
27.31 | Provision of PHD and other fittings of Jaguar make for the control room building (in Toilets, wash room, overhead water tank of adequate capacity etc) of reputed make, provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing. Provision of rain water discharge pipes at different locations and two nos of over head water tank of 2000 ltrs capacity etc as per requirement and approved drawing. All bath room & toilet shall have water & termite proof doors and provision of sliding louvers with exhaust fan. | Lot | 1 |  |  | 776921.44 | 69922.9296 | 69922.9296 | 916767.2992 | 916767.2992
27.32 | Construction of septic tank and soak pit for control room building as per the provided drawing and as per specification in TS. | Lot | 1 |  |  | 255823.4 | 23024.106 | 23024.106 | 301871.612 | 301871.612
27.33 | Construction of borewell for control room building as per the specification in TS. | Lot | 1 |  |  | 210940.68 | 18984.6612 | 18984.6612 | 248910.0024 | 248910.0024
27.34 | Provision for Electrical Work:Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make), fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 |  |  | 1108185.91 | 99736.7319 | 99736.7319 | 1307659.3738 | 1307659.3738
27.35 | Provision of Fire alarm system for the control room building as per the provided drawing and as per specification in TS. | Lot | 1 |  |  | 93565 | 8420.85 | 8420.85 | 110406.7 | 110406.7
27.36 | Provision of false ceiling in the control room building (Control room, Office space, Cabins, rest rooms, Communication room, ACDC room & lobby) as per specification mentioned in the civil section & approved drawings including, relay panel room, office room, SAS room, conference room, transit room etc as per direction of the engineer in charge. | Lot | 1 |  |  | 250000 | 22500 | 22500 | 295000 | 295000
28 | MAIN GATE, WICKET GATE & SECURITY SHED (GATE COMPLEX): The Main gate, wicket gate and the Secirity shed shall be constructed as per the drawing provided and technical specification, complete in all respect and as per instruction of Engineer in charge. The foundation shall be designed as per actual site soil condition and shall be constructed as per approved drawing.
28.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil & rock as per drawing and technical specification complete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the surplus earth/unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. This includes cost, conveyance of all materials, all labour, T&P articles required for the work, stacking the useful materials separately, including shoring, shuttering, propping and dewatering if required etc. | Lot | 1 |  |  | 35532.43 | 3197.92 | 3197.92 | 41928.27 | 41928.27
28.2 | Providing and lying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 |  |  | 30322.32 | 2729.01 | 2729.01 | 35780.34 | 35780.34
28.3 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundation & base of column work, all column, all beam, all pedestal, all lintel, all chajja, all slab, all projection etc.), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 |  |  | 443372.68 | 39903.54 | 39903.54 | 523179.76 | 523179.76
28.4 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, including cost of binding wires, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 |  |  | 565359.94 | 50882.39 | 50882.39 | 667124.72 | 667124.72
28.5 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 |  |  | 90680.42 | 8161.24 | 8161.24 | 107002.9 | 107002.9
28.6 | Providing 12 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 |  |  | 14705.25 | 1323.47 | 1323.47 | 17352.19 | 17352.19
28.7 | Providing 16mm thick cement plaster ( 1:6) finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 |  |  | 16080.99 | 1447.29 | 1447.29 | 18975.57 | 18975.57
28.8 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 |  |  | 8988.68 | 808.98 | 808.98 | 10606.64 | 10606.64
28.9 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 |  |  | 8613.92 | 775.25 | 775.25 | 10164.42 | 10164.42
28.1 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 |  |  | 2071.9 | 186.47 | 186.47 | 2444.84 | 2444.84
28.11 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 |  |  | 2782.87 | 250.46 | 250.46 | 3283.79 | 3283.79
28.12 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 |  |  | 6003.88 | 540.35 | 540.35 | 7084.58 | 7084.58
28.13 | Providing and fixing of 35mm thick WPC Door Shutter(Solid) with teak edge leaping to the periphery of the shutter with pilishing as per detailed drawing with including, all hardwares & fixtures, SS tower bolt(150mm), Door stopper, SS aldrop(250mm), SS handle(200mm length), ss handle (150mm length) & SS Butt hinges -125mm x 65mm x2.12mm .including cost, conveyance, loading, T&P required for the work etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 |  |  | 12476.16 | 1122.85 | 1122.85 | 14721.86 | 14721.86
28.14 | Supplying, fitting and fixing of M.S grills for windows, Main Gate, wicket gate etc. (as per I.S. specification and as per approved drawings ) in proper position in all floors and at all height including making holes to brick walls/ R.C.C structure/wood work etc. and making good to the damaged walls/ structures with cement concrete (1:2:4) with black hard crusher broken granite stone chips of 12mm to 20mm size ( 20mm size not to exceeds 25% ) including watering and curing etc. complete in all respect as directed by the Engineer in charge. (W.I. / M.S. windows grills, grill gates, collapsible gates with top and bottom rails, steel windows, steel doors, steel frames for doors and windows, staircase and parapet railings square bar along with required nos. of nails and screws and other required materials of approved quality and approved size shall be supplied by the contractor at his own cost.) | Lot | 1 |  |  | 136012.19 | 12241.1 | 12241.1 | 160494.39 | 160494.39
28.15 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge.
28.15.1 | Inside walls and Ceiling: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 |  |  | 36222.67 | 3260.04 | 3260.04 | 42742.75 | 42742.75
28.15.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 |  |  | 14163.64 | 1274.73 | 1274.73 | 16713.1 | 16713.1
28.15.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 |  |  | 5032.84 | 452.96 | 452.96 | 5938.76 | 5938.76
28.16 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 14502.83 | 1305.25 | 1305.25 | 17113.33 | 17113.33
28.17 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 6770.36 | 609.33 | 609.33 | 7989.02 | 7989.02
28.18 | Providing and fixing of UPVC sliding windows in the security shed as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 26280 | 2365.2 | 2365.2 | 31010.4 | 31010.4
28.19 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 24914.7 | 2242.32 | 2242.32 | 29399.34 | 29399.34
28.2 | GFRC Letter: Manufacturing, providing and installation of GFRC mouldings (Glass Fiber Reinforced Concrete) of approved make of thickness 230mm±5mm with pattern, design and colour of approved make to be fixed on/beteween RCC/ block work column or structural work with dry fixing method with all required T & P , manpower and all other material as required for completion of work in all respect.
i | Per Letter (450mm(h) x 40mm (d) x 50mm (w)) | Nos | 20 |  |  | 800 | 72 | 72 | 944 | 18880
ii | OPTCL Logo | Nos | 1 |  |  | 1000 | 90 | 90 | 1180 | 1180
28.21 | Electrical works of Main Gate, Wicket gate and Security Shed: As per the provided drawing and as per specification in TS. This also includes supply of all electrical materials (of specified manufacturer as indicated in the TS) for main gate, wicket gate & security shed to complete the work as as per description provided in the relevant section of TS. | Lot | 1 |  |  | 244423.62 | 21998.13 | 21998.13 | 288419.88 | 288419.88
28.22 | Supply of the following materials: a) First Aid Box - 1 set b) Shock Treatment Chart (Odia, Hindi & English) - 1 set c) Insulating mat - 6 sq. m. d) Danger Board - 1 set | Lot | 1 |  |  | 6015 | 541.35 | 541.35 | 7097.7 | 7097.7
29 | BOUNDARY WALL (RCC structure, Brickwall type & Precast type)
29.1 | BOUNDARY WALL: The boundary wall shall be constructed to a height of 2 mtrs above finished ground level of the substation area with 10” wide brick masonry work with RCC(M25) ground tie beam to be rested on the RCC pillars (pillar to pillar distance @ 3mtrs) as per specification. | RM | 3000 |  |  | 10000 | 900 | 900 | 11800 | 35400000
29.1.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil and rock as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plinth with sand, compaction, carriage & disposal of the unsuable earth material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1
29.1.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1
29.1.3 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations & bases of column, Beams, pedestal & column, rcc band etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour, Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1
29.1.4 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1
29.1.5 | Providing Brick work with Fly ash bricks 25cm x 12cm x 8cm size having crushing strength not less than 75 kg/cm2 with dimensional tolerance +/ - 2 percent in cement mortar (1:6) ( 1 cement: 6 sand), with all necessary projection, splay cutting, circular moulding, corbelling, etc., including cost of all materials, labour, conveyance, loading ,and unloadining, royalties, scaffolding, watering, curing, sundries, tools and plants, etc., as per the direction of the Engineer-in-charge. | Lot | 1
29.1.6 | Providing 16 mm. thick cement plaster in all floors at all height with cement mortar of mix (1:6) with portland slag cement (PSC) finished smooth to inside rough surface of brick masonry walls after racking out joints including watering and curing rounding of corners etc. complete with cost, coveyance, loading and unloading, royalties and ,es of all materials and cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. (Inside) | Lot | 1
29.1.7 | Painting of wall surface with weather coat two coats over a coat of primer of approved shade and quality of approved design after cleaning by watering & removing the dirts etc. to the surface to be painted including watering, curing, cost, conveyance of all materials, cost of all labour, brushes, T&P etc. and necessary scaffolding work complete as directed by the Engineer-in-charge. | Lot | 1
29.1.8 | Providing and fixing of GI 'Y' angles over the boundary wall at every 1m rigdly & sufficently (at least 200mm) grouted inside the wall for the support of the concertina wire. | Lot | 1
29.1.9 | Providing and fixing concertina coil fencing with punched tape concertina coil 600mm dia 10metr openable length (total length90m), having 50nos rounds per 6m length, upto 3m height of wall with existing angle iron 'Y' shaped placed 2.4m or 3m apart and with 9 horizontal R.B.T. reinforced barbed wire, stud tied with G.I. staples and G.I. clips to retain horizontal, including necessary bolts or G.I. barbed wire tied to angle iron, all complete as per direction of Engineer-in-charge, with reinforced barbed tape(R.B.T.) / Spring core (2.5mm thick) wire of high tensile strength of 165kg/sq.mm with tape (0.52mm thick) and weight 43.478 gm/meter. | Lot | 1
29.2 | Precast Boundary Wall: Supplying and fixing precast RCC/ SFRC boundary wall precast RCC/ SFRC fencing compound wall pole having finished dimension of 200mmx200mmx3000mm (long) made of M 30 grade concrete with 10 nos of 4mm dia HTPC (High Tension Pre Coated) wire, fixed in cast-in-situ PCC M-20 concrete in Foundation footing of size 600 mm dia 300mm depth from top and P.C.C. of proportion in CC(1:4:8) of size 600 mm dia 300mm depth at bottom Inside the RCC collar pipe of 600mm internal dia placed over a base of plain cement concrete of proportion with C.C. (1:4:8) of size 680 mm dia 100mm depth including excavating foundation pit for each pole in hard stony earth of size 680 mm dia 700mm depth including providing cast-in-situ PCC of proportion in CC.(1:4:8) of size 1520 mm length, 150 mm width & 100mm depth below slab panel including watering & curing for required days, along with supplying, fixing befitting precast RCC/SFRC slab having dimension of 2100mm (long) x 300mm (wide) x 50mm (thick) made with M-30 grade concrete having 4mm dia GI wire 3 nos covering the top of the compound wall poles with a precast RCC/SFRC cover of size (300x300x150) mm in order to prevent the slab panels from removing. All complete as a set to be measured in term of running meter including such precast RCC/SFRC top cover, slab, pole, including painting two coats of approved cement paint over a coat of cement wash including curing, cost and conveyance of all materials, royalties, taxes, all labour, labour cess, T & P required for the work etc. complete including dewatering if required as per the direction of the Engineer-in-charge excluding cost of GST. | Mtr | 1000 |  |  | 5411.02 | 486.99 | 486.99 | 6385 | 6385000
30 | TRANSIT HOUSE: Design, engineering and construction of switch yard buildings including excavation, construction of foundations (open cast or pile as per soil conditions), construction of RCC super structure, brick the cost of material, supply of labour, cement, reinforcement- steel and form work as per the enclosed drawing and technical specification ( The RCC structure frame and the foundations should be in the ratio 1:1.5:3). The indicative drawings of the building is provided and the foundation of the building shall be designed based on the actual soil condition. Foundation shall be as per actual soil condition as per soil test, including piling where required.
30.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 |  |  | 301211.02 | 27108.99 | 27108.99 | 355429 | 355429
30.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 |  |  | 260559.34 | 23450.34 | 23450.34 | 307460.02 | 307460.02
30.3 | Providing & laying Plain cement concrete (1:2:4) (in sunken slab areas) using 12mm size black hard crusher broken granite chips of approved quality from approved quarry including hoisting, lowering and laying concrete in layers, watering, curing etc. complete including cost, conveyance, royalties and taxes of all materials with labour, cess and T&P etc. required for the work complete. | Lot | 1 |  |  | 9942.65 | 894.84 | 894.84 | 11732.33 | 11732.33
30.4 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations, columns, Beams, lintels, chhajas, roof slabs, stair case etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 |  |  | 1676113.36 | 150850.2 | 150850.2 | 1977813.76 | 1977813.76
30.5 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 |  |  | 2232941.16 | 200964.7 | 200964.7 | 2634870.56 | 2634870.56
30.6 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) for foundation and plinth and in cement mortar of mix (1:4) for other area in ground floor, first floor & head room with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 |  |  | 385242.08 | 34671.79 | 34671.79 | 454585.66 | 454585.66
30.7 | Providing 16 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 |  |  | 177975.53 | 16017.8 | 16017.8 | 210011.13 | 210011.13
30.8 | Providing 18mm C.P. in two coats underlayer 12mm C.P. 1:5 and top layer 6mm thick C.P. 1:6 finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 |  |  | 104882.42 | 9439.42 | 9439.42 | 123761.26 | 123761.26
30.9 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 |  |  | 52842.74 | 4755.85 | 4755.85 | 62354.44 | 62354.44
30.1 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 |  |  | 239188.36 | 21526.95 | 21526.95 | 282242.26 | 282242.26
30.11 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 |  |  | 51802.87 | 4662.26 | 4662.26 | 61127.39 | 61127.39
30.12 | Providing, fitting & fixing anti-skid ceramic floor tiles in flooring in toilets using special plain/ printed series anti-skid ceramic floor tile of premium grade (having minimum thickness 7 mm to 8 mm & size 300 mm x 300 mm confirming to IS 13755 of approved quality and shade of Somany/ Kajaria / Johnson on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened & washed sharp river sand for mortar ceramic floor tiles with neat white cement slurry, mixed with required (tiles are to be immersed in the water for required time before use) quantities of pigments of approved marks to match the shades of the anti-skid ceramic floor tiles if required including cost, conveyance, loading, unloading, stacking, royalties of all material, cost of all labour, sundries, T&P required for the work, watering, complete in all respect as per specification excluding GST as per specification as directed by Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 |  |  | 12140.52 | 1092.65 | 1092.65 | 14325.82 | 14325.82
30.13 | Providing & Fixing tiles of size 30cm x 45 cm glazed ceramic wall tiles (All Toilet walls) of premium grade of approved quality and shade having thickness 8mm to 10mm confirming to IS 13755 in dados skirting and risers of steps on 12mm thick cement plaster (1:3) to proper slope, line and level including cutting to required size and shape, fixing at corners and splays etc including filling the joints with neat white cement slurry mixed with pigments to match the shade of the tiles including cost, Conveyance, loading, unloading, stacking, royalities of all materials, cost of all labour,T&P, sundries, watering and curing for the required period for the work complete in all respect excluding GST as directed by the Engineer-in-charge.(Note- Sample of tiles shall be approved before procurement and use.) | Lot | 1 |  |  | 65578.7 | 5902.08 | 5902.08 | 77382.86 | 77382.86
30.14 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 |  |  | 123268.36 | 11094.15 | 11094.15 | 145456.66 | 145456.66
30.15 | Providing Granite stone prepolished 10mm thick in dado of approved quality, colour and size in dado, riser of steps and dado of landings in all floors at all height on 12mm thick bed of cement mortar of mix (1:3) with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 |  |  | 19217.93 | 1729.61 | 1729.61 | 22677.15 | 22677.15
30.16 | Providing,Fixing 16m thick Kota stone in floors treads or steps and landing on 20mm thick cement mortar (1:4) (1cement : 4 course and) and filling joints with of approved quality including cost, conveyance, taxes, cost of all labour etc. complete. Providing,Fixing 16m thick Kota stone in dado ,riser on 12mm thick cement mortar (1:3) (1cement : 3 course and) and filling joints with of approved quality including cost, conveyance, taxes, cost of all labour etc. complete. | Lot | 1 |  |  | 44895.68 | 4040.61 | 4040.61 | 52976.9 | 52976.9
30.17 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 |  |  | 125157.9 | 11264.21 | 11264.21 | 147686.32 | 147686.32
30.18 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board and pasting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. | Lot | 1 |  |  | 448363.08 | 40352.68 | 40352.68 | 529068.44 | 529068.44
30.19 | Supplying, fitting and fixing of M.S grills, Grill window ( as per I.S. specification and as per approved drawings ) in proper position in all floorsas per TS, approved drawing, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 91241.08 | 8211.7 | 8211.7 | 107664.48 | 107664.48
30.2 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge.
30.20.1 | Inside walls: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 |  |  | 280619.13 | 25255.72 | 25255.72 | 331130.57 | 331130.57
30.20.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 |  |  | 65795.51 | 5921.6 | 5921.6 | 77638.71 | 77638.71
30.20.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 |  |  | 607.66 | 54.69 | 54.69 | 717.04 | 717.04
30.21 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 71130.56 | 6401.75 | 6401.75 | 83934.06 | 83934.06
30.22 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 44317.83 | 3988.6 | 3988.6 | 52295.03 | 52295.03
30.23 | Providing and fixing of UPVC sliding windows in the Transit house as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 424584 | 38212.56 | 38212.56 | 501009.12 | 501009.12
30.24 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 122196.6 | 10997.69 | 10997.69 | 144191.98 | 144191.98
30.25 | Water proofing to the sunken slab including providing and filling it with 40mm size brick bat as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 |  |  | 3348 | 301.32 | 301.32 | 3950.64 | 3950.64
30.26 | Providing and laying tactile tile (for vision impaired persons as per standards) of size 300x300x9.8 mm having with water absorption less than 0.5% and conforming to IS:15622 of approved make in all colours and shades in for outdor floors such as footpath, courtyard, multi modals location etc., laid on 20mm thick base of cement mortar 1:4 (1 cement : 4 coarse sand) in all shapes & patterns including grouting the joints with white cement mixed with matching pigments etc. complete as per direction of Engineer-in-Charge | Lot | 1 |  |  | 21505.13 | 1935.46 | 1935.46 | 25376.05 | 25376.05
30.27 | Supplying, fitting and fixing in position 16mm thick chequred tile of approved make and quality, colour and size in all floors at all height on 25mm thick bed of cement mortar of mix (1:1) laid in proper slope and gradient with screened and washed sharp sand for mortar and with Portland Slag Cement (PSC) grouted with neat white cement slurry with required quantities of pigments of approved marks watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work complete in all respect as directed by the Engineer-in-charge | Lot | 1 |  |  | 15829.76 | 1424.68 | 1424.68 | 18679.12 | 18679.12
30.28 | Plinth Potection for Transit house as per the provided drawing and as per sepcification in TS. | Lot | 1 |  |  | 71707.51 | 6453.68 | 6453.68 | 84614.87 | 84614.87
30.29 | Construction of covered drain for Transit house as per the provided drawing and as per specification in TS. | Lot | 1 |  |  | 257416.05 | 23167.44 | 23167.44 | 303750.93 | 303750.93
30.3 | Provision of PH work for the Transit house as per the provided drawing and as per specification in TS. | Lot | 1 |  |  | 570758.62 | 51368.28 | 51368.28 | 673495.18 | 673495.18
30.31 | Construction of septic tank and soak pit for Transit house as per the provided drawing and as per specification in TS. | Lot | 1 |  |  | 255823.4 | 23024.11 | 23024.11 | 301871.62 | 301871.62
30.32 | Provision of Electrical works the Transit house as per the provided drawing and as per specification in TS. This also includes supply of all electrical materials (of specified manufacturer as indicated in the TS) to complete the work as as per description provided in the relevant section of TS. | Lot | 1 |  |  | 467669.25 | 42090.23 | 42090.23 | 551849.71 | 551849.71
30.3 | Furnishings for Transit House: Supply and installation of the following items- 1. 55 inch Full HD LED TV set of Sony/LG/Samsung make with supply of Set up Box for the television unit with 1 year recharge from the date of commissioning (1set) 2. Durian make Sofa set (3+1+1) with center table for lobby (1 set) 3. Durian make King size cot with mattress & all other amenities like study table with 2 chair (Godrej) in all the bed rooms, bed sheets, pillow etc (Bombay Dyeing/Raymond Home) make. 2 Person wardrobe (Godrej Interio), hangers for hanging cloths in each room for storage of Baggages and Cloths etc. Bathing requirements like Bath Towels, Hand Towels etc. (02 sets for all the bed rooms). Decoratives Such as wall ceinic Hangers, Doors and Windows Curtains (02 Sets for all doors and Windows) - Total 4 sets for 4 guest rooms 4. Geyser-3 Ltr capacity of Bajaj/V-Guard/Phillips/Crompton make (4 set) 5. Dining table with 6 chairs of Durian/Godrej make (1 set) 6. Modular kitchen with exhaust chimney system, gas stove, and required utensils (1. 02 Cook Ware and Dinner Sets for 08 persons 2. Induction cooking heaters for cooking capacity of 10 persons at a stretch) 7. RO & UV Water purifier with cooling water system of Aquaguard/Bluestar/Kent make (1 set) 8. 3 star inverter compressor frost free Refrigerator of 230 Ltr or above capacity, double door type (LG/Samsung/Whirlpool/Godrej/Panasonic Make) (1 set) | LOT | 1 |  |  | 2000000 | 180000 | 180000 | 2360000 | 2360000
31 | Construction of borewell for Transit house as per the specification in TS (as in control room building). The starter is to be installed in the transit house as per the instruction of the site Engineer. The deliveries of borewell of transit house and the cotrol room building shall also be connected with each other through gate valves to use any one borewell for the entire substation premises in case of exigencies, including supply of all materials such as UPVC Pipes, joints, valves etc for completion of the work as per instruction of site Engineer. | Lot | 1 |  |  | 220940.68 | 19884.6612 | 19884.6612 | 260710.0024 | 260710.0024
32 | Land scaping & provision for platform for hoisting of National Flags and Provision of Garden: As per site condition of the substation and approval of the gardening layout. The qty may vary as per the approved layout and instrcution of engineer in charge.
32.1 | Provision of gardens/ lawn area with garden grass in front of the control room building & other areas that can be developed as a garden as per the site Engineer's instruction. This include the all required work including the soil treatment for laying of the lawn grass. | sqm | 400 |  |  | 590 | 53.1 | 53.1 | 696.2 | 278480
32.2 | Motorised fountain at a suitable location as per instrcution of Engineer in charge. | Nos | 1 |  |  | 50000 | 4500 | 4500 | 59000 | 59000
32.3 | Sprinkler arrangement in the lawn to cover all the lawn area and water tap arrangement at different location to all areas of plantation. | Lot | 1 |  |  | 50000 | 4500 | 4500 | 59000 | 59000
32.4 | Flowering plants (Rose, jasmine, hibiscus or as per instruction of Engineer in Charge at least 50 each | Nos | 200 |  |  | 50 | 4.5 | 4.5 | 59 | 11800
32.5 | Fruit bering Non Fruit bearing Plants (Mango, guava, Neem, Acacia) as per instruction of Engineer in Charge. 25 nos of each type of trees to be plantedin the free areas immediately after the substation layout paln is finalised. It must be ensured that the plants survive till hand over. Therefore, proper care shall be taken by the contractor. | Nos | 100 |  |  | 120 | 10.8 | 10.8 | 141.6 | 14160
32.6 | Decorative Plants for Lawn/garden (varieties of Hedge, thuja) as per instruction of Engineer in Charge | Nos | 150 |  |  | 50 | 4.5 | 4.5 | 59 | 8850
32.7 | Decorative plants (foxtail palm of at least 5 ft height) for both side of the 7m road from the main gate as per instruction of the Engineer in charge. | Nos | 100 |  |  | 1030 | 92.7 | 92.7 | 1215.4 | 121540
32.8 | Construction of platform & suitable GI pipe & other attachment for hoisting of National Flags as per the direction of Engineer incharge. | Nos | 1 |  |  | 8402.78 | 756.2502 | 756.2502 | 9915.2804 | 9915.2804
33 | DG Shed: Design, engineering and construction of DG shed for rain/sun protection including the cost of material, supply of labour, T&P, etc. This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth, PCC, RCC, reinforcement steel MS rods (FE-500-TATA/ RINL/ Sail/JINDAL), brick work as per the direction of Enginer In charge. As per approved drawings and specification. The RCC foundation and Plinth to be in the ratio 1:1.5:3. including piling where required. DG shed shall be Steel fame structure type with channels, I beams etc (HDG 610 g/sqm) with top canopy - colour coated corrugated galvalume (TATA blue scope/JSW make). Canopy shall be 2 way - open gable sloped for discharge of rainwater. This incluses all other associated works viz. painting, illumination for DG set etc to complete the work in full shape. The Plinth area of the D.G shed 36 sq mtrs (9mtrsX4 mtrs) | LOT | 1 |  |  | 300000 | 27000 | 27000 | 354000 | 354000
A | TOTAL OF (Civil Work) _SUBSTATION | [8 empty] | 391998122.9344 | 340667348.5346 | 51330774.3998
(FOR 400 KV D/C LILO LINE from 400KV Meramandali-New Duburi D/C line (CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi LINE)
Sl. No. | DESCRIPTION OF ITEMS | UNITS | LINE |  |  | IN INR
| ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) |  | QUANTITY |  |  | UNIT PRICE | GST PER UNIT |  | TOTAL UNIT PER PRICE | TOTAL PRICE
|  |  | Meramundali End | New Duburi End | TOTAL |  | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 | 5 | 6=4+5 | 7 | 8=7x9% | 9=7x9% | 10=7+8+9 | 11=7X10
PART A | CIVIL WORKS
1 | SURVEY OF LINE & PREPARATION LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting
1.1 | Preliminary survey, Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | KM. | 25 | 25 | 50 | 11097.98 | 998.8182 | 998.8182 | 13095.6164 | 654780.82
1.2 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | KM. | 25 | 25 | 50 | 5222.58 | 470.0322 | 470.0322 | 6162.6444 | 308132.22
1.3 | Preparation of land schedule with HAL & SAVIK classification on revenue maps indicating alignment therein duly authenticated by Revenue Inspector & Tahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 400KV line. Final route to be plotted on 1:50000 topo sheet for approval. | KM. | 25 | 25 | 50 | 8486.69 | 763.8021 | 763.8021 | 10014.2942 | 500714.71
1.4 | Soil Testing in complete shape along with submission of report etc. up to the depth of 15 Mtrs. | Per Loc. | 50 | 50 | 100 | 30029.82 | 2702.6838 | 2702.6838 | 35435.1876 | 3543518.76
1.5 | Soil Testing in complete shape along with submission of report etc. upto the depth of 30 mtrs for River bed pile. | Per Loc. | 4 | 4 | 8 | 58754 | 5287.86 | 5287.86 | 69329.72 | 554637.76
2 | EXCAVATION WORKS FOR OPEN CAST/SHALLOW TYPE FOUNDATIONS, PILE CAPPINGS, RIVETMENT WORKS ETC
2.1 | Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge.
2.1.1 | Soft/Loose soil | CUM | 7692.3539 | 7692.3539 | 15384.7078 | 195.85 | 17.6265 | 17.6265 | 231.103 | 3555452.1267
2.1.2 | Dense/Compact soil | CUM | 7692.3539 | 7692.3539 | 15384.7078 | 306.83 | 27.6147 | 27.6147 | 362.0594 | 5570178.0752
2.1.3 | Partial Submerged soil | CUM | 6153.8831 | 6153.8831 | 12307.7662 | 352.53 | 31.7277 | 31.7277 | 415.9854 | 5119851.0625
2.1.4 | Fully submerged soil | CUM | 3076.9416 | 3076.9416 | 6153.8831 | 352.53 | 31.7277 | 31.7277 | 415.9854 | 2559925.5312
2.1.5 | Soft/Disintegrated rock(Not requiring Blasting) | CUM | 3076.9416 | 3076.9416 | 6153.8831 | 587.55 | 52.8795 | 52.8795 | 693.309 | 4266542.552
2.1.6 | Hard Rock(Requiring Blasting/Using breaker machinery) | CUM | 3076.9416 | 3076.9416 | 6153.8831 | 1175.08 | 105.7572 | 105.7572 | 1386.5944 | 8532939.8724
3 | FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge. This includes the open cast foundations, Piles, Pile cappings, risers, chimney, rivetment works etc.
3.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower open foundations, pile cappings and rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 485 | 485 | 970 | 5513.48 | 496.2132 | 496.2132 | 6505.9064 | 6310729.208
3.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1.5:3) of grade M20 for open cast foundation with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement for tower open foundations, 500mm Under-reamed piles, all pile cappings risers, chimey etc. and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, dewatering, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P, head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 5839 | 5839 | 11678 | 8890.43 | 800.1387 | 800.1387 | 10490.7074 | 122510481.0172
3.3 | Supply of all materials like cement, coarse aggregates (Nominal size 12mm to 20mm), fine aggregates and making 1000mm river bed pile foundations (after pile boring as per required depth, basing on design) as per requirement, including supply of all equipment with labours, head loading of all type of Civil materials , proper curing of the foundations and T&P as per specification in the concrete ratio 1:1:2 and disposal of excess earth as per the direction of Engineer In Charge. | CUM | 200 | 200 | 400 | 7870.43 | 708.3387 | 708.3387 | 9287.1074 | 3714842.96
3.4 | Cutting bending hooking, fixing and binding in poisition of MS bars for rainforcement of all foundations (open or pile types) concrete of towers including supply of wire for binding With supply of steel rod(TATA/RINL/SAIL Make) and head loading. No other make of steel shall be allowed. | MT | 512 | 512 | 1024 | 68623.36 | 6176.1024 | 6176.1024 | 80975.5648 | 82918978.3552
4 | PILE FOUNDATION BORING & CONCRETE WORKS
4.1 | 500mm Dia Under reamed Pile foundation as per approved design and drawing
4.2 | Boring for under ream cast-in-Situ piling (500mm dia), with Manual Auger method or by using Motor driven Machinery ,including supply of Bentonite required for as per required procedure depending on the length of the bore stabilization. | Mtrs. | 400 | 400 | 800 | 2643.93 | 237.9537 | 237.9537 | 3119.8374 | 2495869.92
5 | 1000mm Dia Pile Foundation in the River bed as per approved design and drawing
5.1 | Boring of 1000mm dia pile by DMC method or motor driven machinery etc., including supply of all equipments with labours and T&P as per specification with supply of Bentonite required for stabilization of bore. | Mtrs. | 400 | 400 | 800 | 6462.95 | 581.6655 | 581.6655 | 7626.281 | 6101024.8
5.2 | Fixing charges of MS Liner including the supply of materials like MS Sheet of adequate thickness, fabrication, cutting, bending, binding, putting the liner in appropriate position and other related works | MT | 10 | 10 | 20 | 106462.95 | 9581.6655 | 9581.6655 | 125626.281 | 2512525.62
6 | REVETMENT: (including Benching) Supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge.
6.3 | PCC in the ratio 1:2:4 as above Design, Engineering, Providing and laying of plain cement concrete (PCC 1:2:4) with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 10 | 10 | 20 | 10185.56 | 916.7004 | 916.7004 | 12018.9608 | 240379.216
6.4 | RR masonary work in the ratio 1:5 including supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge. | CUM | 30 | 30 | 60 | 30185.56 | 2716.7004 | 2716.7004 | 35618.9608 | 2137137.648
6 | ROW (Right Of Way):- The agency shall pay the compensation @100% of the bench mark value of the land for construction of tower foundation and erection and 15% of bench mark value for acquisition of ROW in the land required for transmission line corridor as per the required width as per the letter no-RDM-LRGEA-POLICY-0003/43341/R&DM Dated 21.12.2022 of Additional Chief Secretary to Govt, R&DM Department, Govt. of Odisha. The agency shall also pay the crops compensation if any during the construction of transmission line in the own cost. The agency is sole responsible for obtaining ROW clearance. The agency shall pay all the cost for obtaining the ROW clearance for construction of Tower foundation, Erection and stringing of said line.
7.1 | Compensation for construction of Tower foudation & erection of transmission line including crops compensation & etc. (100% Bench mark cost plus other compensation) | Per location | 75 | 75 | 150 | 100041.091 | 9003.6982 | 9003.6982 | 118048.4874 | 17707273.1088
7.2 | Compensation for or acquisition of ROW in the land required & trees & crops compensation to owners for transmission line corridor as per the required width (15% Bench mark cost plus other compensation if any) | RKM | 25 | 25 | 50 | 200000 | 18000 | 18000 | 236000 | 11800000
8 | Forest Clearance work including preparation of Land Schedule (as per requirement ), DGPS Survey, authentication by concerned offices, preparation of complete Forest Diversion Proposal, obtaining Stage-I clearance, grant of working premission, submission of Stage-I compliances and obtaining Stahge-II clearance etc. Any other requirement of documents as per the prevailing norms of Forest department from time to time shall also be complied. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 06 months of award of contract. The contractor have to pay the DGPS authnetication & base point fees and all other payments to ORSAC. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | Per Hectare | 45 | 45 | 90 | 150000 | 13500 | 13500 | 177000 | 15930000
B | TOTAL(B) | [8 empty] | 309545915.3433
(FOR 400 KV D/C LILO LINE from 400KV Meramandali-Mendhasal D/C line(CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi LINE)
Sl. No. | DESCRIPTION OF ITEMS |  | LINE |  |  | IN INR
| ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) | UNITS | QUANTITY |  |  | UNIT PRICE | GST PER UNIT |  | TOTAL UNIT PER PRICE | TOTAL PRICE
|  |  | Meramandali End | Mendhasal End | Total |  | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 | 5 | 6=4+5 | 7 | 8=7x9% | 9=7x9% | 10=7+8+9 | 11=7X10
PART A | CIVIL WORKS
1 | SURVEY OF LINE & PREPARATION LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting
1.1 | Preliminary survey, Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | KM. | 23 | 23 | 46 | 11097.98 | 998.8182 | 998.8182 | 13095.6164 | 602398.3544
1.2 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | KM. | 23 | 23 | 46 | 5222.58 | 470.0322 | 470.0322 | 6162.6444 | 283481.6424
1.3 | Preparation of land schedule on revenue (if required)maps indicating alignment therein duly authenticated by Revenue Inspector & Tahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 132 KV line. Final route to be plotted on 1:50000 topo sheet for approval. | KM. | 23 | 23 | 46 | 8486.69 | 763.8021 | 763.8021 | 10014.2942 | 460657.5332
1.4 | Soil Testing in complete shape along with submission of report etc. up to the depth of 15 Mtrs. | Per Loc. | 45 | 45 | 90 | 30029.82 | 2702.6838 | 2702.6838 | 35435.1876 | 3189166.884
1.5 | Soil Testing in complete shape along with submission of report etc. upto the depth of 30 mtrs for River bed pile. | Per Loc. | 2 | 2 | 4 | 58754 | 5287.86 | 5287.86 | 69329.72 | 277318.88
2 | EXCAVATION WORKS FOR OPEN CAST/SHALLOW TYPE FOUNDATIONS, PILE CAPPINGS, RIVETMENT WORKS ETC
2.1 | Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge.
2.1.1 | Soft/Loose soil | CUM | 7186.3539 | 7186.3539 | 14372.7078 | 195.85 | 17.6265 | 17.6265 | 231.103 | 3321575.8907
2.1.2 | Dense/Compact soil | CUM | 7186.3539 | 7186.3539 | 14372.7078 | 306.83 | 27.6147 | 27.6147 | 362.0594 | 5203773.9624
2.1.3 | Partial Submerged soil | CUM | 5749.0831 | 5749.0831 | 11498.1662 | 352.53 | 31.7277 | 31.7277 | 415.9854 | 4783069.2826
2.1.4 | Fully submerged soil | CUM | 2874.5416 | 2874.5416 | 5749.0831 | 352.53 | 31.7277 | 31.7277 | 415.9854 | 2391534.6413
2.1.5 | Soft/Disintegrated rock(Not requiring Blasting) | CUM | 2874.5416 | 2874.5416 | 5749.0831 | 587.55 | 52.8795 | 52.8795 | 693.309 | 3985891.0688
2.1.6 | Hard Rock(Requiring Blasting/Using breaker machinery) | CUM | 2874.5416 | 2874.5416 | 5749.0831 | 1175.08 | 105.7572 | 105.7572 | 1386.5944 | 7971646.4593
3 | FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge. This includes the open cast foundations, Piles, Pile cappings, risers, chimney, rivetment works etc.
3.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower open foundations, pile cappings and rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 440 | 440 | 880 | 5513.48 | 496.2132 | 496.2132 | 6505.9064 | 5725197.632
3.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1.5:3) of grade M20 for open cast foundation with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement for tower open foundations, 500mm Under-reamed piles, all pile cappings risers, chimey etc. and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, dewatering, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P, head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 4600 | 4600 | 9200 | 8890.43 | 800.1387 | 800.1387 | 10490.7074 | 96514508.08
3.3 | Supply of all materials like cement, coarse aggregates (Nominal size 12mm to 20mm), fine aggregates and making 1000mm river bed pile foundations (after pile boring as per required depth, basing on design) as per requirement, including supply of all equipment with labours, head loading of all type of Civil materials , proper curing of the foundations and T&P as per specification in the concrete ratio 1:1:2 and disposal of excess earth as per the direction of Engineer In Charge. | CUM | 200 | 200 | 400 | 7870.43 | 708.3387 | 708.3387 | 9287.1074 | 3714842.96
3.4 | Cutting bending hooking, fixing and binding in poisition of MS bars for rainforcement of all foundations (open or pile types) concrete of towers including supply of wire for binding With supply of steel rod(TATA/RINL/SAIL Make) and head loading. No other make of steel shall be allowed. | MT | 425 | 425 | 850 | 68623.36 | 6176.1024 | 6176.1024 | 80975.5648 | 68829230.08
4 | PILE FOUNDATION BORING & CONCRETE WORKS
4.1 | 500mm Dia Under reamed Pile foundation as per approved design and drawing
4.2 | Boring for under ream cast-in-Situ piling (500mm dia), with Manual Auger method or by using Motor driven Machinery ,including supply of Bentonite required for as per required procedure depending on the length of the bore stabilization. | Mtrs. | 80 | 80 | 160 | 2643.93 | 237.9537 | 237.9537 | 3119.8374 | 499173.984
5 | 1000mm Dia Pile Foundation in the River bed as per approved design and drawing
5.1 | Boring of 1000mm dia pile by DMC method or motor driven machinery etc., including supply of all equipments with labours and T&P as per specification with supply of Bentonite required for stabilization of bore. | Mtrs. | 80 | 80 | 160 | 22952.72 | 2065.7448 | 2065.7448 | 27084.2096 | 4333473.536
5.2 | Fixing charges of MS Liner including the supply of materials like MS Sheet of adequate thickness (6mm/8mm as per approved drawing), fabrication, cutting, bending, binding, putting the liner in appropriate position and other related works | MT | 10 | 10 | 20 | 106462.95 | 9581.6655 | 9581.6655 | 125626.281 | 2512525.62
6 | REVETMENT: (including Benching) Supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge.
6.3 | PCC in the ratio 1:2:4 as above Design, Engineering, Providing and laying of plain cement concrete (PCC 1:2:4) with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 10 | 10 | 20 | 10185.56 | 916.7004 | 916.7004 | 12018.9608 | 240379.216
6.4 | RR masonary work in the ratio 1:5 including supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge. | CUM | 20 | 20 | 40 | 30185.56 | 2716.7004 | 2716.7004 | 35618.9608 | 1424758.432
6 | ROW (Right Of Way):- The agency shall pay the compensation @100% of the bench mark value of the land for construction of tower foundation and erection and 15% of bench mark value for acquisition of ROW in the land required for transmission line corridor as per the required width as per the letter no-RDM-LRGEA-POLICY-0003/43341/R&DM Dated 21.12.2022 of Additional Chief Secretary to Govt, R&DM Department, Govt. of Odisha. The agency shall also pay the crops compensation if any during the construction of transmission line in the own cost. The agency is sole responsible for obtaining ROW clearance. The agency shall pay all the cost for obtaining the ROW clearance for construction of Tower foundation, Erection and stringing of said line.
7.1 | Compensation for construction of Tower foudation & erection of transmission line including crops compensation & etc. (100% Bench mark cost plus other compensation) | Per location | 70 | 70 | 140 | 100041.0923 | 9003.6983 | 9003.6983 | 118048.489 | 16526788.4546
7.2 | Compensation for or acquisition of ROW in the land required & trees & crops compensation to owners for transmission line corridor as per the required width (15% Bench mark cost plus other compensation if any) | RKM | 23 | 23 | 46 | 200000 | 18000 | 18000 | 236000 | 10856000
8 | Forest Clearance work including preparation of Land Schedule (as per requirement ), DGPS Survey, authentication by concerned offices, preparation of complete Forest Diversion Proposal, obtaining Stage-I clearance, grant of working premission, submission of Stage-I compliances and obtaining Stahge-II clearance etc. Any other requirement of documents as per the prevailing norms of Forest department from time to time shall also be complied. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 06 months of award of contract. The contractor have to pay the DGPS authnetication & base point fees and all other payments to ORSAC. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | Per Hectare | 45 | 45 | 90 | 150000 | 13500 | 13500 | 177000 | 15930000
C | TOTAL (C ) | [8 empty] | 259577392.5938 | 259577392.5941 | -0.00033927
| TOTAL ERECTION_CIVIL (SUB_STATION + MRDL-MENDHASAL LILO LILE + MRDL-NEW DUBURI LILO LINE) (A+B+C) | [8 empty] | 961121430.8715 |  | -1.797e-06
Note on D87: OPTCL: Antiweed treatment area x 0.075= PCC Voulme and X 0.1 is Metal spreading volume
Note on D92: OPTCL: Should be 4?
Note on B298: OPTCL: For open foundations and pile cappings etc

## Schedule 2 Elec Erection (hidden)
400/220/33 KV Sub-Station at NEULPOI & Associated 400 KV LILO LINE (ERECTION) |  |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK: Construction of 2X500 MVA,2X63 MVA 400/220/33 KV Sub-Station with SAS at Neulpoi with associated 400 KV D/C LILO LINE from 400KV Meramandali-New Duburi D/C line (CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi and 400 KV D/C LILO LINE from 400KV Meramandali-Mendhasal D/C line(CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi in Dhenkanal District on EPC contract basis
NOTICE INVITING TENDER-NIT NO.
PRICE BID FOR WORKS CONTRACT : SCHEDULE -2 ERECTION COMPONENT OF THE WORKS CONTRACT-
NAME OF BIDDER
400/220 kV Substation Neulpoi: 400 KV Bays-[21 Nos (10 Fdr+2 ICT+7Tie+2Reactor)] In 1 & 1/2 CB System, 220KV Bay-7 Nos.(FDR-2,ICT-2+ TRF -2, B/C-1) 33KV Bay-9 Nos.(FDR-6,TFR-2, B/C -1]
Sl. No. | ERECTION, INSTALLATION, TESTING & COMMISSIONING _SUBSTATION |  |  |  |  | RUPEES IN INR
| DESCRIPTION OF ITEMS(SCHEDULE-2C) ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) | UNIT | Quantity (Neulpoi GSS) |  |  | UNIT PRICE | GST PER UNIT |  | TOTAL PER UNIT PRICE | AMOUNT
[7 empty] | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT) |  |  | Total REVISED Erection Price excluding service tax IN INR
1 | 2 | 3 | 4 |  |  | 5 | 6=5x9% | 7=5x9% | 8=5+6+7 | 9=4X8
A | ELECTRICAL WORKS
1 | 420 KV, 2000-1000-500A, 63 kA, 5 Core Single Phase Current Transformer | Nos | 84 |  |  | 14688.51 | 1321.9659 | 1321.9659 | 17332.4418 | 1455925.1112
2 | 420 KV, 3150A, 63 kA Isolators
2.1 | With One Earth Switch | Nos | 54 |  |  | 28724.18 | 2585.1762 | 2585.1762 | 33894.5324 | 1830304.7496
2.2 | With Two Earth Switch | Nos | 2 |  |  | 20681.4 | 1861.326 | 1861.326 | 24404.052 | 48808.104
3 | 420 KV, 63 kA, 3 Core Single Phase Line Capacitor Voltage Transformer | Nos | 36 |  |  | 14688.51 | 1321.9659 | 1321.9659 | 17332.4418 | 623967.9048
4 | 420 KV, 3150A, 63kA, SF6 Circuit Breaker With Support Structure.
4.1 | Circuit Breaker with CSD. | Nos | 19 |  |  | 102493.09 | 9224.3781 | 9224.3781 | 120941.8462 | 2297895.0778
4 .2 | Circuit Breaker without CSD. | Nos | 2 |  |  | 102493.09 | 9224.3781 | 9224.3781 | 120941.8462 | 241883.6924
5 | Metal oxide polymer housed surge arrrestor for 420 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 42 |  |  | 7181.04 | 646.2936 | 646.2936 | 8473.6272 | 355892.3424
6 | 400 KV Bus Post Insulators | Nos | 288 |  |  | 3387.3 | 304.857 | 304.857 | 3997.014 | 1151140.032
7 | 245 KV, (1200-600-300/1-1-1-1-1-1A), 50kA, 5 CORE SINGLE PHASE CURRENT TRANSFORMER | Nos | 27 |  |  | 10851.36 | 976.6224 | 976.6224 | 12804.6048 | 345724.33 |  | 12804.6048
8 | 245 KV, 2 Core, Voltage Transformer (1 core 3P & 1 core 0.2) | Nos | 12 |  |  | 12207.78 | 1098.7002 | 1098.7002 | 14405.1804 | 172862.1648 |  | 10851.36
9 | 245 KV, 2000A, 50 kA Isolators
9.1 | Without Earth Switch | Nos | 20 |  |  | 23240.47 | 2091.6423 | 2091.6423 | 27423.7546 | 548475.092
9.2 | With Single Earth Switch | Nos | 2 |  |  | 51572.9619 | 4641.5666 | 4641.5666 | 60856.095 | 121712.19 |  | 51572.9619
9.3 | Tandem Isolator without Earth Switch | Nos | 7 |  |  | 10445.1538 | 940.0638 | 940.0638 | 12325.2814 | 86276.97 |  | 10445.1538
10 | 245KV, 3150A, 50kA, SF6 Circuit Breaker with Support Structure | Nos | 7 |  |  | 65133.0085 | 5861.9708 | 5861.9708 | 76856.95 | 537998.65 |  | 65133.0085
11 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 18 |  |  | 4047.5 | 364.275 | 364.275 | 4776.05 | 85968.9
12 | 220 KV Bus Post Insulators | Nos | 54 |  |  | 2219.6 | 199.764 | 199.764 | 2619.128 | 141432.912
13 | 132KV, 2000A, 40 kA Isolators without Earth Switch (1-Pole) For 400KV 125Mvar Reactor | Nos | 2 |  |  | 10934.77 | 984.1293 | 984.1293 | 12903.0286 | 25806.0572
14 | Metal oxide polymer housed surge arrrestor for 132 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 2 |  |  | 3525.24 | 317.2716 | 317.2716 | 4159.7832 | 8319.5664
15 | 36KV, 31.5kA Current Transformers
15.1 | 36 KV,800-400-200,31.5kA,3 core Single phase Current Transformer (2 Nos PS class & 1 No. 0.2s class) | Nos | 6 |  |  | 2023.75 | 182.1375 | 182.1375 | 2388.025 | 14328.15
15.2 | 36 KV, 800-400-200, 31.5kA, 4 core Single phase Current Transformer (3 Nos PS class & 1 No. 0.2s class) | Nos | 21 |  |  | 2023.75 | 182.1375 | 182.1375 | 2388.025 | 50148.525
16 | 36 KV, 1250A, 31.5kA Isolators
16.1 | Single Isolator without Earth Switch | Nos | 20 |  |  | 5222.58 | 470.0322 | 470.0322 | 6162.6444 | 123252.888
16.2 | Single Isolator with Earth Switch | Nos | 6 |  |  | 8356.12 | 752.0508 | 752.0508 | 9860.2216 | 59161.3296
16.3 | Beam Mounted Single Isolator without Earth Switch | Nos | 4 |  |  | 4308.63 | 387.7767 | 387.7767 | 5084.1834 | 20336.7336
17 | Metal oxide polymer housed surge arrrestor for 33 kV system. Station Class Low Duty (SL) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor - As per TS | Nos | 24 |  |  | 1011.87 | 91.0683 | 91.0683 | 1194.0066 | 28656.1584
18 | 36 KV, 2 Core Single Phase IVT (1 core 3P & 1 core 0.2) | Nos | 3 |  |  | 1827.9 | 164.511 | 164.511 | 2156.922 | 6470.766
19 | 36 KV, 1250A, 31.5kA, Vaacuum Circuit Breaker with supporting Structure. Facilities for integration with SAS as per the site requirement. | Nos | 9 |  |  | 18801.28 | 1692.1152 | 1692.1152 | 22185.5104 | 199669.5936
20 | 33 KV Bus Post Insulators | Nos | 30 |  |  | 509.2 | 45.828 | 45.828 | 600.856 | 18025.68
21 | BUS BAR STRINGING: Supply of labour, T&P and other necessary arrangements for stringing of bus bar conductors, hoisting of single or double insulator strings, Single or Double Hard-wares Fittings, Clamp & connectors, as per requirements, Jumpers, connections to Equipments, testing, commissioning etc. as per the instruction of Engineer-in charge.
21.1 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS FOR FOLLOWING ARRANGEMENT: 1. 400KV Bus-A & B and Equipment to Equipment connectionare 120mm IPS Aluminium Pipe Bus 2. Cross Bus shall be with Twin ACSR Moose and Cross bus to equipment shall also be with Twin ACSR Moose. 3. 220KV Main Bus-I & II sahll be with twin ACSR Moose (conductor spacing-300mm) and Transfer bus shall be with Single ACSR Moose. 4. 220KV Equipment connections shall be with single ACSR moose. 5. 33KV Main Bus & Transfer Bus shall be with Twin ACSR Moose (conductor spacing-250mm). 6. 33KV Equipment connections shall be with single ACSR Moose for feeders and Twin ACSR Moose for the Bus coupler & Transformer bays. 7. 33KV Station transformer connections shalll be with Single ACSR Panther conductor. 8. The Single hardware fittings shall be of 160KN & 120KN for 400KV & 220KV system, 120KN and 90KN for 33KV system. The UTS of the twin hardware fittings shall be suitably chosen for twin insulators of the above mentioned UTS. 10. The harware fittings shall be single anchored and without turn buckle. 11. This also includes any other hardware fittings and clamps required to complete the work. 12. The qty of hardware fittings, clamps & connectors, Conductor, IPS Aluminium tube and Insulators shall be as per the approved drawing.
21.1.1 | All suspension & tension hardware fittings for 400KV system for Twin ACSR Moose | Lot | 1 |  |  | 300000 | 27000 | 27000 | 354000 | 354000
21.2.2 | All suspension & tension hardware fittings for 220KV system for Twin ACSR Moose, Single ACSR Moose | Lot | 1 |  |  | 200000 | 18000 | 18000 | 236000 | 236000
21.1.2 | All suspension & tension hardware fittings for 33KV system for Twin ACSR Moose, Single ACSR Moose | Lot | 1 |  |  | 100000 | 9000 | 9000 | 118000 | 118000
21.2.3 | Clamps & Connectors, Spacers etc for Twin ACSR Moose, IPS Aluminium Tube for 400KV system | Lot | 1 |  |  | 300000 | 27000 | 27000 | 354000 | 354000
21.1.3 | Clamps & Connectors, Spacers etc for Twin ACSR Moose, Single ACSR Moose for 220KV system | Lot | 1 |  |  | 200000 | 18000 | 18000 | 236000 | 236000
21.2.4 | Clamps & Connectors, Spacers etc for Twin ACSR Moose, Single ACSR Moose for 33KV system | Lot | 1 |  |  | 100000 | 9000 | 9000 | 118000 | 118000
21.2 | ACSR MOOSE CONDUCTOR | Mtrs | 30000 |  |  | 200 | 18 | 18 | 236 | 7080000
21.3 | IPS 4.5” Aluminium Tube (OD: 120 mm, Thickness: 12 mm)(for 400 KV Bus and connection from equipment to equipment in 400 KV side) including welding sleeves,corona bell etc. The Lot shall be as per the approved drawing. | Lot | 1 |  |  | 350000 | 31500 | 31500 | 413000 | 413000
21.4 | ACSR Panther Conductor | Mtrs | 200 |  |  | 150 | 13.5 | 13.5 | 177 | 35400
21.5 | Antifog type Disc Insulators for 400KV Switchyard (160KN & 120 KN) | Lot | 1 |  |  | 400000 | 36000 | 36000 | 472000 | 472000
21.6 | Antifog type Disc Insulators for 220KV Switchyard (160KN & 120 KN) | Lot | 1 |  |  | 200000 | 18000 | 18000 | 236000 | 236000
21.7 | Antifog type Disc Insulators for 33KV Switchyard (120KN & 90KN) | Lot | 1 |  |  | 100000 | 9000 | 9000 | 118000 | 118000
22 | SUBSTATION EARTHING SYSTEMS: (The qty for the earthing materials shall be as per the approved earthing design calculations based on the soil resistivity of the project area)
22.1 | EARTHING CONDUCTOR FOR BURRIAL :(40MM MS ROD) for laying as main earth mat for the whole (400KV, 220KV & 33KV) switchyards as per design calculation(spacing maximum 5m both way). @1mtr=9.86Kg | Mtrs | 28398 |  |  | 85.77 | 7.7193 | 7.7193 | 101.2086 | 2874121.8228
22.2 | EARTHING CONDUCTOR: 75X10 mm GI Flat for Raiser from the burial earth mat to foundation plint level of equipmentstructure etc.) @1mtr=5.9Kg | Mtrs | 16101.69 |  |  | 67.39 | 6.0651 | 6.0651 | 79.5202 | 1280409.6091
22.3 | EARTHING CONDUCTOR: 50X6 mm GI Flat as riser to structures, equipment, coulmns and up to the bottom of spikes, fencing, cable tray and auxiliary Boards earthing etc.). Each equipment strructure & Columns shall be connected to earth at two separate points. @1mtr=2.4Kg | Mtrs | 12500 |  |  | 67.39 | 6.0651 | 6.0651 | 79.5202 | 994002.5
22.4 | Earthing Device & associated accessories: 50 mm heavy duty GI perforated pipe, 3 mtrs long for treated earth pit | Nos | 350 |  |  | 2327.91 | 209.5119 | 209.5119 | 2746.9338 | 961426.83
22.5 | Earthing Device & associated accessories: 40mm MS rod, 3 mtrs long for treated earth pits | Nos | 500 |  |  | 2327.91 | 209.5119 | 209.5119 | 2746.9338 | 1373466.9
22.6 | Switchyard buildings lightning protection (all materials & accessories like Shielding Wire, PG clamp, Test link, D shackle, other required materials etc) as per IS/National Building code standard and as per approved drawing | Lot | 1 |  |  | 50000 | 4500 | 4500 | 59000 | 59000
22.7 | Supply of UPVC Pipes (2", 1.5", 1" & 1/2" etc), Joints, bends, Valves and all accessories for spreading the water network from the overhead tank to each treated earth pit as per approved drawing. | LOT | 1 |  |  | 100000 | 9000 | 9000 | 118000 | 118000
23 | GI Cable Trays including support GI angle suitable for different sections i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories as per TS and approved drawing. | Lot | 1 |  |  | 200000 | 18000 | 18000 | 236000 | 236000
24 | Switchyard Structures( Including Foundation Bolts And Nuts) Galvanised (Lattice) For All 400 kV & 220 kV
24.1 | Different Types Of Columns with earth spikes and Beams (Lattice Type) as per approved layout design
24.1.1 | 400 KV Columns & beams | Lot | 1
24.1.2 | 220 KV Column & beams | Lot | 1
24.1.3 | 33 KV Column & beams | Lot | 1
24.2 | Total Weight Of Column & Beam | MT | 1082 |  |  | 4533.3 | 407.997 | 407.997 | 5349.294 | 5787936.108
24.3 | Total Weight Of Different Size Of Gi Nuts And Bolts For column & beam structures. | MT | 54 |  |  | 4533.3 | 407.997 | 407.997 | 5349.294 | 288861.876
24.4 | Support Structures (Including Foundation Bolts And Nuts) Galvanised (Pipe Type) For All 400 KV & 220 KV Equipments as per approved layout design
24.4.1 | 400KV Equipment | Lot | 1
24.4.2 | 220KV Equipment | Lot | 1
24.4.3 | 333KV Equipment | Lot | 1
24.5 | Total Weight Of Support Structure For Above Equipment | MT | 180 |  |  | 4533.3 | 407.997 | 407.997 | 5349.294 | 962872.92
24.6 | Total weight of different size of GI Nuts and bolts for equipment structures. | MT | 9 |  |  | 4533.3 | 407.997 | 407.997 | 5349.294 | 48143.646
25 | General Equipment & Substation Accessories
25.1 | Power Cables-1.1KV, FRLSH XLPE & PVC, Armoured Aluminium Conductor (As Per Specification)
25.1.1 | XLPE 3.5 C X 630 mm2 | Mtrs | 3200 |  |  | 1776.57 | 159.8913 | 159.8913 | 2096.3526 | 6708328.32
25.1.2 | XLPE 3.5 C X 185 mm2 | Mtrs | 900 |  |  | 1347.74 | 121.2966 | 121.2966 | 1590.3332 | 1431299.88
25.1.3 | XLPE 3.5 C X 120 mm2 | Mtrs | 500 |  |  | 796.4 | 71.676 | 71.676 | 939.752 | 469876
25.1.4 | PVC 3.5 C X 70 mm2 | Mtrs | 10500 |  |  | 471.7 | 42.453 | 42.453 | 556.606 | 5844363
25.1.5 | PVC 3.5 C X 35 mm2 | Mtrs | 675 |  |  | 404.32 | 36.3888 | 36.3888 | 477.0976 | 322040.88
25.1.6 | PVC 4 C X 16 mm2 | Mtrs | 5050 |  |  | 214.41 | 19.2969 | 19.2969 | 253.0038 | 1277669.19
25.1.7 | PVC 4 C X 6 mm2 | Mtrs | 7000 |  |  | 122.52 | 11.0268 | 11.0268 | 144.5736 | 1012015.2
25.1.8 | PVC 2C X 6 mm2 | Mtrs | 12500 |  |  | 122.52 | 11.0268 | 11.0268 | 144.5736 | 1807170
25.2 | Control Cables- 1.1 KV, FRLSH PVC, Armoured Stranded Copper conductor (As Per Specification)
25.2.1 | 4 C X 2.5 mm2 | Mtrs | 16000 |  |  | 42.88 | 3.8592 | 3.8592 | 50.5984 | 809574.4
25.2.2 | 5 C X 2.5 mm2 | Mtrs | 20000 |  |  | 42.88 | 3.8592 | 3.8592 | 50.5984 | 1011968
25.2.3 | 7C X 2.5 mm2 | Mtrs | 1200 |  |  | 42.88 | 3.8592 | 3.8592 | 50.5984 | 60718.08
25.2.4 | 10 C X 2.5 mm2 | Mtrs | 6000 |  |  | 49 | 4.41 | 4.41 | 57.82 | 346920
25.2.5 | 12 C X 2.5 mm2 | Mtrs | 550 |  |  | 49 | 4.41 | 4.41 | 57.82 | 31801
25.2.6 | 16 C X 2.5 mm2 | Mtrs | 7500 |  |  | 49 | 4.41 | 4.41 | 57.82 | 433650
25.2.7 | 19 C X 2.5 mm2 | Mtrs | 13200 |  |  | 61.27 | 5.5143 | 5.5143 | 72.2986 | 954341.52
25.3 | Single core 1.1KV, PVC Un-armoured copper conductor: for connection from Battery Set to Battery Charger and from Battery Charger to DCDB on cable tray / HDPE pipe/PVC pipe etc
25.3.1 | 1CX 120 mm2 | Mtrs | 300 |  |  | 66 | 5.94 | 5.94 | 77.88 | 23364
25.4 | Supply of screened / Shielded Twisted pair copper cable for Analog Communication for showing winding temp, Oil temp,lighting, fire fighting, DG etc, LT current & LT voltage signals of sub-station auxiliary system in HMI
25.4.1 | 8PX1.5 mm2 screened copper cable | Mtrs | 1500 |  |  | 38.73 | 3.4857 | 3.4857 | 45.7014 | 68552.1
25.4.2 | 2PX1.5 mm2 screened copper cable | Mtrs | 750 |  |  | 38.73 | 3.4857 | 3.4857 | 45.7014 | 34276.05
26 | Supply Of Station Transformer & Other Materials For meeting the Auxiliary Supply
26.1 | Station Transformer 33KV/433V, 1000 KVA (As Per Specification) | Nos | 2 |  |  | 51572.96 | 4641.5664 | 4641.5664 | 60856.0928 | 121712.1856
26.2 | HG fuse set for 33 KV side of the Station transformer including base(each set comprises three single HG fuse) | SETS | 2 |  |  | 5900 | 531 | 531 | 6962 | 13924
27 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area)
27.1 | Substation Switchyard Lighting: Installation of fixtures & lamps (LED) of reputed make (Philips/CGL/Bajaj/Havells/ Osram/ Wipro premium quality) with switch gear, GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved).(150 watt each) | Nos | 250 |  |  | 2219.6 | 199.764 | 199.764 | 2619.128 | 654782
27.2 | STREET LIGHTING: Installation of HDG Octagonal street lighting poles 7 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. Poles shall be installed on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes installation of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/ Havells/ Osram/Wipro), with switch gear, GI junction box, GI Conduit etc. & as per technical specification. | Set | 50 |  |  | 2219.6 | 199.764 | 199.764 | 2619.128 | 130956.4
28 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 16-ANNEXURE - I)
28.1 | FOAM TYPE-9 LTRS | Nos | 5 |  |  | 165 | 14.85 | 14.85 | 194.7 | 973.5
28.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | Nos | 5 |  |  | 336 | 30.24 | 30.24 | 396.48 | 1982.4
28.3 | DRY POWDER TYPE - 5 KGS | Nos | 9 |  |  | 135 | 12.15 | 12.15 | 159.3 | 1433.7
28.4 | CO2 - 4.5 KGS | Nos | 12 |  |  | 156 | 14.04 | 14.04 | 184.08 | 2208.96
28.5 | CO2 - 9 KGS | Nos | 12 |  |  | 155 | 13.95 | 13.95 | 182.9 | 2194.8
28.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | Nos | 6 |  |  | 146 | 13.14 | 13.14 | 172.28 | 1033.68
28.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND | SET | 8 |  |  | 336 | 30.24 | 30.24 | 396.48 | 3171.84
29 | SUBSTATION AUTOMATION SYSTEM FOR 400/220/33 KV SUBSTATION ON PRP MODE: Design , engineering , drawing, supervision, installation , testing & commissioning of Substation Automation system alongwith Supply of the following 400, 220 and 33 kV level of protection panels consisting of Bay control Units & numerical protection relays and other auxiliary relays suitable for SAS as per technical specification. NOTE: All protective relays & BCU shall be numerical type.
29.1 | Gateway Panel: for Sub-Station Automation (in PRP on FO as per the specification & indicative drawing) system (for All 400KV, 220KV & 33 KV side bays) and with other accessories, comprising: 1. HMI servers (Main & Stand By) 2. DR PC for Local 3. Gateway- 2 nos (both in hot mode) 4. Color Laser jet Printer-1Nos 5. Dot Matrix Printer-1Nos 6. Ethernet Fiber Switches (with 20% spares Port) 7. LIU 8. Multimode glass fibre Doublle jacket armoured optical cables 9. Red boxes 10. Inverters(Input shall be both A.C & D.C and output shall be A.C) - 3 KVA (Main & Stand by) 11. Furniture (Operator desk 1 Nos & Chair-6Nos) 12. Full HD or better resolution LED TV 75 inch (Sony, LG, Samsung) or higher for display etc as per TS, including all type of accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system complete in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. | SET | 1 |  |  | 100000 | 9000 | 9000 | 118000 | 118000
29.2 | BCU for Substation Auxilliary System (Station AC, Station DC, Lighting, Fire fighting, Diesel generator etc.) | SET | 1 |  |  | 20000 | 1800 | 1800 | 23600 | 23600
29.3 | GPS System with IRIG-B/SNTP/PTP with VDU (Clock) | Nos | 1 |  |  | 20000 | 1800 | 1800 | 23600 | 23600
30 | 400 KV SIDE PROTECTION & OTHER PANELS as per Technical specification.
30.1 | 400KV feeder Protection Panel: MAIN-I , MAIN-II Distance protection relays of different make & Backup Protection, Bay control unit (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Set | 10 |  |  | 27418.53 | 2467.6677 | 2467.6677 | 32353.8654 | 323538.654
30.2 | 400KV Transformer Protection Panel: Differential Protection Main- I & II of different make , Separate REF- Main- I & II (different make) & BACK-UP PROTECTION for HV & IV side (considering HV, IV & LV side for 500 MVA 400/220/33 KV ICT), Bay control units (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Set | 2 |  |  | 27418.53 | 2467.6677 | 2467.6677 | 32353.8654 | 64707.7308
30.3 | 400KV Tie Bay protection Panel: with Bay control unit (BCU), other protection & aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Set | 7 |  |  | 27418.53 | 2467.6677 | 2467.6677 | 32353.8654 | 226477.0578
30.4 | 400KV BUS-BAR Protection System (Distributed architecture with Main-I & Main-II): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Provision of bus bar modules for at least Four future bays shall be made. The bus bar protection system shall be integrated with the Automation system. | Lot | 1 |  |  | 27418.53 | 2467.6677 | 2467.6677 | 32353.8654 | 32353.8654
30.5 | 400 KV Bus Reactor Panel: With Numerical Backup-Impedance, Differential, Separate REF & Back-up protection, Bay Control Unit (BCU) & aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Set | 2 |  |  | 27418.53 | 2467.6677 | 2467.6677 | 32353.8654 | 64707.7308
31 | 220 KV SIDE PROTECTION & OTHER PANELS
31.1 | 220KV Feeder Protection Panel: MAIN-I , MAIN-II of different make, Backup Protection relays, Bay control unit (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Nos | 2 |  |  | 16973.38 | 1527.6042 | 1527.6042 | 20028.5884 | 40057.1768
31.2 | 220KV, 500MVA ICT Protection Panel: This includes all Relays including LBB trip relays and Bay Control Units (BCU), complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | Nos | 2 |  |  | 16973.38 | 1527.6042 | 1527.6042 | 20028.5884 | 40057.1768
31.3 | 220KV, 63MVA Power Transformer Protection Panel: Differential (Main-I & Main-II of different make), saparate numerical REF, Backup Protection and other aux relays including LBB trip relays & Bay control units (BCU) as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | Nos | 2 |  |  | 16973.38 | 1527.6042 | 1527.6042 | 20028.5884 | 40057.1768
31.4 | 220KV Bus Coupler Protection Panel: Backup Protection Relays and other aux relays including LBB trip relays & BCU as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | Nos | 1 |  |  | 16973.38 | 1527.6042 | 1527.6042 | 20028.5884 | 20028.5884
31.5 | 220KV Transfer Bus Coupler Protection Panel: Backup Protection Relays and other aux relaysincluding LBB trip relays & BCU as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | Nos | 1 |  |  | 16974.38 | 1527.6942 | 1527.6942 | 20029.7684 | 20029.7684
31.6 | 220KV BUS-BAR Protection Sysstem (Distributed architecture): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Provision of bus bar modules for at least Four future bays shall be made. The bus bar protection system shall be integrated with the Automation system. | Lot | 1 |  |  | 16975.38 | 1527.7842 | 1527.7842 | 20030.9484 | 20030.9484
32 | 33 KV SIDE PROTECTION PANELS: Single Panel Twin Bay type ( 2 Bays in One Panel) with IEC:61850-ED2 PRP on FO
32.1 | FEEDER PROTECTION PANEL (WIth BCPU & with other auxiliary relays including LBB trip relays as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) Note: 06 No.s of Line feeder bays to be considered in 03 nos of Panels | Nos | 3 |  |  | 16975.38 | 1527.7842 | 1527.7842 | 20030.9484 | 60092.8452
32.2 | POWER TRANSFORMER PROTECTION PANEL (WIth BCPU & separate numerical REF and other auxiliary relays including LBB trip relays as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) Note: 02 No.s of Transformer feeder bays to be considered. (The Panel shall have 02 Nos. of transformer feeders). | Nos | 1 |  |  | 16975.38 | 1527.7842 | 1527.7842 | 20030.9484 | 20030.9484
32.3 | BUS COUPLER PROTECTION RELAY PANEL WIth BCPU & with other auxiliary relays including LBB trip relays as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) | Nos | 1 |  |  | 16975.38 | 1527.7842 | 1527.7842 | 20030.9484 | 20030.9484
33 | AC & DC SYSTEM
33.1 | AC SYSTEM (Indoor Type with 2 mm CRCA sheet and 3 mm CRCA gland plate & as per TS:)
33.1.1 | MAIN AC DB (Indoor Type): MAIN DB-1, MAIN DB-2 with B/C. The incomer & Bus coupler shall have 800 A, 50KA, drawout type ACB with Numerical SAS compliant Relay (O/C, E/F, U/V, O/V protection). The ACDB shall be suitable for automatic switching OFF & ON during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 |  |  | 7357.07 | 662.1363 | 662.1363 | 8681.3426 | 8681.3426
33.1.2 | ACDB (Indoor Type) WITH BUS 1, BUS 2, BUS 3, Bus Coupler 1 & Bus Coupler 2: HAVING 400A Motorized MCCB for automatic operation in Incomers and Bus couplers with electrical interlock system. With Three Bus sections and Two nos of Bus couplers. Two bus sections shall be connected with two bus sections of the Main ACDB and the 3rd bus section shall be connected to the DG having all emergency loads. The outgoing feeders for the Main ACDB shall be appropriately designed to cater all loads having 20% spares of each rating feeder in each section. The cosntruction of the ACDB shall be as per the TS. The ACDB shall be suitable for automatic switching OFF & ON, auto start of DG set etc during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 |  |  | 7357.07 | 662.1363 | 662.1363 | 8681.3426 | 8681.3426
33.1.3 | Main Lighting Distribution Board (Indoor Type): Having 250A MCCB with source-1, Source-2 & Bus coupler. | SET | 1 |  |  | 6956.21 | 626.0589 | 626.0589 | 8208.3278 | 8208.3278
33.1.4 | Indoor Lighting Distribution Board (Indoor Type) | SET | 1 |  |  | 6956.21 | 626.0589 | 626.0589 | 8208.3278 | 8208.3278
33.1.5 | Emergency Lighting Distribution Board (Outdoor type): The ELDB should be supplying to 20% of switchyard lights, each of 220KV and 33KV Switchyard. | SET | 1 |  |  | 6956.21 | 626.0589 | 626.0589 | 8208.3278 | 8208.3278
33.1.6 | INDOOR RECEPTACLE BOARD | SET | 2 |  |  | 6956.21 | 626.0589 | 626.0589 | 8208.3278 | 16416.6556
33.1.7 | ACDB for Yard Kiosk (Indoor Type): LT supply to Protection panels, Kiosk lighting, AC etc | SET | 6 |  |  | 6601 | 594.09 | 594.09 | 7789.18 | 46735.08
33.2 | AC SYSTEM : Outdoor Type, Sub Station Swithyard Console Boxes, HDG type (86 micron), 3 mm thick CRCA, (BMK,AC CONSOLE & OTHER MB) as per TS.
33.2.1 | Bay Marshalling Kiosk: 1 BMK for 1 no 400KV Dia, 1 no of BMK for 2 nos 220KV bays and 1 BMK for 4 nos 33KV bays | SET | 14 |  |  | 6601 | 594.09 | 594.09 | 7789.18 | 109048.52
33.2.2 | Console box for switchyard lighting | SET | 4 |  |  | 7703.3 | 693.297 | 693.297 | 9089.894 | 36359.576
33.2.3 | Switchyard Receptacle Board for Transformer Oil Filteration | SET | 4 |  |  | 7703.3 | 693.297 | 693.297 | 9089.894 | 36359.576
33.2.4 | Switchyard Receptacle Board for welding and other emergency | SET | 8 |  |  | 7703.3 | 693.297 | 693.297 | 9089.894 | 72719.152
33.2.5 | CT CONSOLE BOXES as per TS | SET | 46 |  |  | 2376.27 | 213.8643 | 213.8643 | 2803.9986 | 128983.9356
33.2.6 | CVT/IVT CONSOLE BOXES as per TS | SET | 17 |  |  | 2376.27 | 213.8643 | 213.8643 | 2803.9986 | 47667.9762
33.2.7 | Console box for street lighting | SET | 4 |  |  | 7703.3 | 693.297 | 693.297 | 9089.894 | 36359.576
33.2.8 | Console box for Transit House/Colony Supply purpose | SET | 1 |  |  | 7703.3 | 693.297 | 693.297 | 9089.894 | 9089.894
33.2.9 | OUT DOOR KIOSK FOR STATION TRANSFORMER With Busbar & SFU of appropriate rating with required sizes of terminal studs for power cable termination & any other accessories required. | SET | 2 |  |  | 8260 | 743.4 | 743.4 | 9746.8 | 19493.6
33.3 | DC SYSTEM
33.3.1 | 220 V DC DISTRIBUTION BOARD (Indoor Type): Having 2 nos 63A DC MCCB for Incomers, Bus Coupler with interlock, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE and shall be SAS compliant & as per TS. Consider separate source (DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered. | SET | 1 |  |  | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 9613.7196
33.3.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD (Indoor Type) | SET | 1 |  |  | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 9613.7196
33.3.3 | BATTERY BANK (350 AH PLANTE TYPE) for 220 V DC System (2V Battery Cells 107 Nos + 3 Nos spare) & its spare as per TS | SET | 2 |  |  | 15276.04 | 1374.8436 | 1374.8436 | 18025.7272 | 36051.4544
33.3.4 | Battery Charger For 350 AH Plante Type Battery, 107 cells, 2 V, Trickle charge volt - 2.25V (Float & Float Cum Boost). Charger ON/OFF status, input/output voltage, output current, associated charger protection signals shall be provided for integration with SAS & its spare as per TS. | SET | 2 |  |  | 4582.81 | 412.4529 | 412.4529 | 5407.7158 | 10815.4316
33.3.5 | DCDB for Yard Kiosk (Indoor Type): DC supply to Protection panels having source-1 & 2 with auto changeover facility. Consider separate source (DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output to be considered. | SET | 6 |  |  | 7703.3 | 693.297 | 693.297 | 9089.894 | 54539.364
34 | AIR CONDITIONING: Installation of 2T capacity Split Air Conditioning Units (Dual Inverter, five star latest model - LG/Samsung/Hitachi/Carrier/Mitsubishi/Voltas/Daikin Make) with copper condensor having remote temperature & operation control facility with voltage stabilizer. Following item description also includes AC Control Panel made of 2mm CR sheet, having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (As per specification) for CRB cum GIS (Control/SAS Room, AC DC Room, Communication room, office room & Conference room), Switchyard Kisok, Transit House. Supply of Logic controller for Auto Switch ON & OFF of AC units depending on requirement. Also includes supply of all other additional accessories such as copper tubes, copper cable, steel brackets for holding outdoor units and other accessories necessary for completion of the AC system. As per approved drawing and direction of engineer-in-charge.
34.1 | AC for CRB: For Control/SAS Room, ACDC Room Communication room, office room & Conference room . | Set | 18 |  |  | 5000 | 450 | 450 | 5900 | 106200
34.2 | AC for Switchyard Kiosk (2 nos per Kiosk) as per T.S. (The ACs shall run in tandem i.e 1 of the ACs at a time for 4 hours each.) | Set | 12 |  |  | 5000 | 450 | 450 | 5900 | 70800
34.3 | AC For Transit House | Set | 4 |  |  | 5000 | 450 | 450 | 5900 | 23600
35 | Accessories For OPGW System As Per Technical Specification
35.1 | 48 fibre optic approach cable along with installation hardware including HDPE pipes | Km | 1 |  |  | 70800 | 6372 | 6372 | 83544 | 83544
35.2 | Optical line terminal equipment (OLTE)-STM16 type SDH equipment with integrated MUX & tributary cards for speech & data ports for interfacing of speech & data which should be compatible with existing OPTCL system. | Nos. | 1 |  |  | 150000 | 13500 | 13500 | 177000 | 177000
35.3 | Supply of FODP (Fibre optic Distribution panel) 96F: Indoor type, rack mounted with FCPC coupling and pigtails (DWSM fibre) | Nos. | 1 |  |  | 7080 | 637.2 | 637.2 | 8354.4 | 8354.4
35.4 | Digital tele-protection coupler with accessories compatible for interfacing with SDHMUX | Nos. | 8 |  |  | 35400 | 3186 | 3186 | 41772 | 334176
35.5 | 48V, 300 AH, maintenance free VRLA battery set | Set | 2 |  |  | 29500 | 2655 | 2655 | 34810 | 69620
35.6 | SMPS based battery charger of 75A suitable for 48V VRLA battery | SET | 2 |  |  | 7800 | 702 | 702 | 9204 | 18408
35.7 | 48 V DCDB (with I/C-I, I/C-II & B/C) | Nos. | 1 |  |  | 7800 | 702 | 702 | 9204 | 9204
35.8 | Earth flat, cable tray, telephone cable, ACDB, DCDB, foundation rail, Junction Box, Cat 5 cable & Misc items | Lot | 1 |  |  | 200000 | 18000 | 18000 | 236000 | 236000
36 | MAINTENANCE & TESTING EQUIPMENT (Demonstration of the following Maintenance & Testing Equipment to | LOT | 1 |  |  | 0 | 0 | 0 | 0 | 0
36.1 | Demonstration of Universal Relay Testing Kit (Omicron CMC 356) | Set | 1
36.2 | Demonstration of Capacitance Tan-Delta Testing Kit (Omicron/Doble make) | Set | 1
36.3 | Demonstration of Contact Resistance Measurement Kit- (Milli volt drop measurement (Contact resistance measurement -200Amp DC) (Omicron/Doble/Sonel make) | Set | 1
36.4 | Demonstration of Automatic 3 ph Transformer Turns Ratio Testing Kit (Omicron/Doble/DV Power make) | Set | 1
36.5 | Demonstration of Winding Resistance Testing Kit (Omicron/Doble make) | Set | 1
36.6 | Demonstration of Third Harmonic Resistive Current Measurement Kit for SA (Omicron/Doble/Megger/Becon Energy Solutn make) | Set | 1
36.7 | Demonstration of 100KV Automatic Transformer Oil Breakdown Voltage test set (Megger- OTS 100AF / Baur- DTA 100C) | Nos | 1
36.8 | Demonstration of 10KV Insulation Tester with 15m test leads (Megger- S1-1068 / Sonel-MIC 10K1) | Nos | 1
36.9 | Demonstration of Digital Earth Tester (Facility for soil resistivity measurement and test leads suitable for connection to the test probe/spikes placed at 20m between each other ) (Megger-DET2/3 / Sonel MRU-120 / Fluke 1625) | Nos | 1
36.1 | Demonstration of Digital Multimeter (Megger / Fluke) | Nos | 2
36.11 | Demonstration of Digital Clamp meter (Megger/Fluke/Motwane) | Nos | 1
36.12 | Demonstration of Leakage current clamp meter AC & DC both (30mA / 300mA / 30A / 300A) (Megger/Fluke/Kyoritsu) | Nos | 1
36.13 | Demonstration of SF6 Gas Leakage Detector (Wika/DILO) | Nos | 1
36.14 | Demonstration of Fibre Glass Discharge / Earth Rod: Grip up to 50mm, Min height-16ft, rubber grip, 35 sq.mm copper cable (1 set- 3 cables, 1 set of rod, carry bag) (Bemico) | Set | 6
38 | Installation and commissioning of the De-Mineralised Plant of 50 L/Hr or more for Making Distilled Water for Battery Banks. (Cation and anion resin bed type) including testing of the quality of the de-mineralised water. | Set | 1 |  |  | 3000 | 270 | 270 | 3540 | 3540
39 | Installation and commissioning of 20 Ltr Storage Water Cooler (Voltas/Bluestar only) | Nos | 1 |  |  | 1590 | 143.1 | 143.1 | 1876.2 | 1876.2
40 | Installation and commissioning of Water Purifier (RO+UV+UF type) and connected with the Storage water cooler including testing of the drinking water for suitability. | Nos | 1 |  |  | 1590 | 143.1 | 143.1 | 1876.2 | 1876.2
41 | Insulating Mat: Placement of insulating mats on front & rear side of various panels in Control room building, switchyard kiosks etc. as per instruction of Engineer Incharge. | Nos | 37 |  |  | 20 | 1.8 | 1.8 | 23.6 | 873.2
42 | CCTV Surveilance system: Installation, Commissioning, Testing for IP Based CCTV Surveillance System (Server Based approach), DVR with 4TB Hard Disk, Day/Night Cameras, PC Monitor (Full HD - 32 inch) including all materials for areas inside & outside Control room building, Entire Switchyard areas covering boundaries, entry/exit points of substation & Other areas etc., suitable for 360 deg movement with all necessary hardware fittings for monitoring and surveillance of the entire substation. The CCTV system shall be able to be integrated with the SAS system. No. of such cameras (different type viz. PTZ, bullet or dome) are to be calculated as per standard practice & its installations at the strategic locations. Tentative Requirement: 1. Fixed type bullet cameras for monitoring of Security shed cum Main gate complex, Main Entrance door of Control Room Building, Main Entrance door of Fire-fighting Pump House, Main Entrance door of store shed, Open stockyard, Main entrance gate of switchyard and all gates of switchyard etc. 2. Dome/Bullet cameras for indoor areas - Relay panel room, AC/DC Room, SAS Room, Corridoor areas etc. 3. PTZ cameras (as per requirement mentioned below): a) Switchyard areas (400/220/33 kV) b) All the Transformers, reactors, station transformers under present scope Note: Any other requirement besides above to be explored & can be finalised during detail Engg. | Lot | 1 |  |  | 45000 | 4050 | 4050 | 53100 | 53100
43 | Installation, Testing and Commissioning of Transformers/Reactors: Installing on the plinth and placing in position, Erection of accessories of the Transformers, erection of NCTs on the Transformers, Earthing as per Standard (Including Supply of Materials), Vacuum Treatment of the tank and winding, Oil Filtration (Including Supply of Vacuum cum Oil Filter Machine), Supply & Laying of all types of Control & Power Cables Pertaining to Transformers, Testing and Commissioning including all tests of the Oil as per stipulation in the Standard Approved Testing Laboratory and as per the instruction of the Engineer in Charge. This include all related works for Erection, Testing and Commissioning of the Power Transformers/Auto Transformers. (Contractor to arrange Power Supply for Filtration And Vacuum Treatment works). It also includes supply of all materials required for erection Including T & P's.
43.1 | Installation, Testing and commissioning of 400/220KV, 500 MVA ICT & all accessories
43.1.1 | 400/220KV, 500 MVA ICT without OLTC. | Nos | 2 |  |  | 2225000 | 200250 | 200250 | 2625500 | 5251000
43.1.2 | NCTs including its mounting arragement as per TS. | Set | 2 |  |  | 2023.75 | 182.1375 | 182.1375 | 2388.025 | 4776.05
43.1.3 | Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) (1 set for each of the ICT). | Set | 2 |  |  | 200000 | 18000 | 18000 | 236000 | 472000
43.1.4 | Online insulating oil drying system(As per Technical Specification) (1 set for each of the ICT) | Set | 2 |  |  | 50000 | 4500 | 4500 | 59000 | 118000
43.1.5 | Online dissolved gas(Multi gas) & moisture analyser(As per Technical Specification) (1 set for each of the ICT) | Set | 2 |  |  | 50000 | 4500 | 4500 | 59000 | 118000
43.2 | Installation, Testing & Commissioning of 400 kV, 125 MVAr BUS Reactor & all accessories
43.2.1 | 400 kV, 125 MVAr BUS Reactor | Nos | 2 |  |  | 2029887.9752 | 182689.9178 | 182689.9178 | 2395267.8107 | 4790535.6214
43.2.2 | NCTs including its mounting arragement as per TS. | Set | 2 |  |  | 2023.75 | 182.1375 | 182.1375 | 2388.025 | 4776.05
43.2.3 | Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) (1 set for each Reactor). | Set | 2 |  |  | 200000 | 18000 | 18000 | 236000 | 472000
43.2.4 | Online insulating oil drying system(As per Technical Specification) (1 set for each Reactor) | Set | 2 |  |  | 50000 | 4500 | 4500 | 59000 | 118000
43.2.5 | Online dissolved gas (Multi gas) & moisture analyser(As per Technical Specification) (1 set for each Reactor) | Set | 2 |  |  | 50000 | 4500 | 4500 | 59000 | 118000
43.3 | Installation, Testing & Commissioning of 220/33 KV, 63 MVA Power & all accessories
| 220/33KV 63 MVA Power transformers | Nos | 2 |  |  | 183051.36 | 16474.6224 | 16474.6224 | 216000.6048 | 432001.2096
43.3.1 | NCTs including its mounting arragement as per TS. | Set | 2 |  |  | 2023.75 | 182.1375 | 182.1375 | 2388.025 | 4776.05
43.3.2 | Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) (1 set for each Reactor). | Set | 2 |  |  | 200000 | 18000 | 18000 | 236000 | 472000
43 | FIRE FIGHTING EQIPMENT: Installation, Testing and commissioning of the fitre fighting equipment (Main Pump, Jockey Pump, DG Set cum Pump, Control Panel, Different sizes of MS pipe (to be painted for rust proof), different type of valves, Fire sensor etc for the Fire Fighting System (HIGH PRESSURE : Hydrant and Mulsifire to take care of 2 Nos 500 MVA ICT, 2 Nos 125 MVAR 400 KV Reactor, 2 Nos 63 MVA Transformer and switcyard equipment and control room building. | LOT | 1 |  |  | 1000000 | 90000 | 90000 | 1180000 | 1180000
44 | Installation, Testing and commissioning of the 250 KVA DG set in complete set (silent/no noise type, suitable for outdoor type, less smoke(as per rule for pollution control) and control AMF panel. | SET | 1 |  |  | 25000 | 2250 | 2250 | 29500 | 29500
A | Total Electrical Works -SUB-STATION- | [8 empty] | 75600179.4649
(FOR 400 KV D/C LILO LINE from 400KV Meramandali-New Duburi D/C line (CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi LINE)
| ERECTION_LINE EQUIPMENT & MATERIALS |  |  |  |  | IN INR
S. No. | ERECTION OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT | QUANTITY |  |  | UNIT PRICE | GST PER UNIT |  | TOTAL UNIT PER PRICE | TOTAL PRICE
|  |  | Meramundali End | New Duburi End | TOTAL |  | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 | 5 | 6=4+5 | 7 | 8=7x9% | 9=7x9% | 10=7+8+9 | 11=7X10
PART B | ELECTRICAL WORKS
1 | ERECTION,TESTING & COMMISSIONING of Following tested Lattice type Galvanized steel tangent / Angle tower without stubs and cleats including different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete with tightening, punching of bolts including step bolts. All other left out portion of the bolts above bottom cross arm shall be riveted by using suitable hammer. Painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping legs & bracing members. All Erection should confirm to the Technical Specification laid there in the Tender Specification.
1.1 | DA TYPE (0 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 11.118 MT) | Nos. | 25 | 25 | 50
1.1.1 | +3 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 1.50MT) | Nos. | 6 | 6 | 12
1.1.2 | +6 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 2.619 MT) | Nos. | 6 | 6 | 12
1.1.2 | +9 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 3.248 MT) | Nos. | 3 | 3 | 6
1.2 | DB TYPE (15 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 20.052 MT) | Nos. | 10 | 10 | 20
1.2.1 | +3 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 3.039 MT) | Nos. | 2 | 2 | 4
1.2.2 | +6 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 4.791 MT) | Nos. | 3 | 3 | 6
1.2.3 | +9 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 6.301 MT) | Nos. | 0 | 0 | 0
1.3 | DC TYPE (30 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 21.491 MT) | Nos. | 20 | 20 | 40
1.3.1 | +3 mtr Body Extension of DC(NOMINAL UNIT WEIGHT 3.498MT) | Nos. | 4 | 4 | 8
1.3.2 | +6 mtr Body Extension of DC (NOMINAL UNIT WEIGHT 6.636 MT) | Nos. | 4 | 4 | 8
1.3.3 | +9 mtr Body Extension of DC(NOMINAL UNIT WEIGHT 6.875 MT) | Nos. | 4 | 4 | 8
1.4 | DD TYPE (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 32.592 MT) | Nos. | 20 | 20 | 40
1.4.1 | +3 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 5.454 MT) | Nos. | 2 | 2 | 4
1.4.2 | +6 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 8.084 MT) | Nos. | 4 | 4 | 8
1.4.3 | +9 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 10.863 MT) | Nos. | 2 | 2 | 4
1.4.2 | +18 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 24.431 MT) | Nos. | 2 | 2 | 4
1.4.1 | +25 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 35.796MT) | Nos. | 2 | 2 | 4
1.5 | TOTAL WEIGHT OF STRUCTURES WITHOUT STUBS INCLUDING MS & HT MATERIALS | MT | 1868.499 | 1868.499 | 3736.998 | 5744.84 | 517.0356 | 517.0356 | 6778.9112 | 25332777.5966
1.6 | STUBS
1.6.1 | DA (Nominal unit weight 0.586 MT) | Nos | 25 | 25 | 50
1.6.2 | DB (Nominal unit weight 1.125 MT) | Nos | 10 | 10 | 20
1.6.3 | DC (Nominal unit weight 1.308 MT) | Nos | 20 | 20 | 40
1.6.4 | DD (Nominal unit weight 2.92 MT) | Nos | 16 | 16 | 32
1.6.5 | DD +18/25 (Nominal unit weight 2.92 MT) | Nos | 4 | 4 | 8
1.6.6 | TOTAL WEIGHT OF STUBS |  | 110.46 | 110.46 | 220.92 | 5744.84 | 517.0356 | 517.0356 | 6778.9112 | 1497597.0623
1.7 | TEMPLATES
1.7.1 | DA (Nominal unit weight 1.524 MT) | Nos | 2 | 2 | 4
1.7.2 | DB (Nominal unit weight 3.441 MT) | Nos | 1 | 1 | 2
1.7.3 | DC (Nominal unit weight 3.693 MT) | Nos | 2 | 2 | 4
1.7.4 | DD (Nominal unit weight 3.889 MT) | Nos | 2 | 2 | 4
1.7.5 | DD +18/25 (Nominal unit weight 3.889 MT) | Nos | 1 | 1 | 2
1.7.6 | WEIGHT OF TEMPLATES FOR DA , DB , DC,DD | MT | 25.542 | 25.542 | 51.084 | 5744.84 | 517.0356 | 517.0356 | 6778.9112 | 346293.8997
1.6 | Weight of different type G.I Nuts and Bolts | MT | 94 | 94 | 188 | 5744.84 | 517.0356 | 517.0356 | 6778.9112 | 1274435.3056
2 | Hoisting and fixing of insulators with required accessories, paying out of conductor, jointing, stringing, sagging & Jumpering etc. of power conductor with G.I. Earth wire & OPGW in the proposed lines with all required accessories including scaffolding/other required arrangements for 33 KV,11 KV, LT , P&T lines, NH/roads, railway line, river etc and using own required T&P and compression jointing machines etc. as per the direction of Engineer in charge.
2.1 | ACSR Double Moose with one Earth Wire and one OPGW | Route(Km) | 25 | 25 | 50 | 214799.1614 | 19331.9245 | 19331.9245 | 253463.0105 | 12673150.5226
3 | Erection of the following tower accessories as per technical specification and as directed by the engineer-in charge.
3.1 | DANGER BOARD | Nos. | 75 | 75 | 150 | 124.03 | 11.1627 | 11.1627 | 146.3554 | 21953.31
3.2 | NUMBER PLATE | Nos. | 75 | 75 | 150 | 124.03 | 11.1627 | 11.1627 | 146.3554 | 21953.31
3.3 | PHASE PLATE | Nos. | 450 | 450 | 900 | 124.03 | 11.1627 | 11.1627 | 146.3554 | 131719.86
3.4 | BIRD GUARD | Nos. | 150 | 150 | 300 | 124.03 | 11.1627 | 11.1627 | 146.3554 | 43906.62
3.5 | ANTICLIMBING DEVICE | Nos. | 75 | 75 | 150 | 2676.58 | 240.8922 | 240.8922 | 3158.3644 | 473754.66
3.6 | CIRCUIT PLATE | Nos. | 150 | 150 | 300 | 124.03 | 11.1627 | 11.1627 | 146.3554 | 43906.62
4 | EARTHING OF TOWER
4.1 | Pipe Type earthing including cost of charcoal,salt/coke and good borrowed earth and Bentonite where necessary in accordance with IS:3043 and with supply of all T&P and Labour. | Nos. | 115 | 115 | 230 | 2389.18 | 215.0262 | 215.0262 | 2819.2324 | 648423.452
4.2 | Counterpoise Earthing as per Indian Standards | Mtr. Length | 100 | 100 | 200 | 73.52 | 6.6168 | 6.6168 | 86.7536 | 17350.72
5 | WELDING OF TOWER BOLTS/NUTS
5.1 | Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods, welding generator machine (diesel engine operator.), application of required zinc rich paints around the welding portion after welding (two coats),fuel,lubricants,T&P and labours and other arrangements etc. | Nos. | 150000 | 150000 | 300000 | 8.57 | 0.7713 | 0.7713 | 10.1126 | 3033780
6 | Dismantaling of Tower Structure
6.1 | Dismantaling of Tower Super Structure including cutting of the welded tower bolts, transportation & delivey with stacking at nearest OPTCL store as per instruction Engineer-in-charge. | MT | 100 | 100 | 200 | 4595.87 | 413.6283 | 413.6283 | 5423.1266 | 1084625.32
6.2 | Dismantaling, transportation & Delivey and Stacking of strung of Twin ACSR MOOSE conducter (With Earth wire/OPGW) at nearest OPTCL store as per instruction Engineer-in-Charge including dismantling of insulators, hardware fittings, conductor accessories, spacers etc. | Route Km | 2 | 2 | 4 | 165490.45 | 14894.1405 | 14894.1405 | 195278.731 | 781114.924
7 | Approval for PTCC, railway crossing, NHAI, Water and other atatutory bodies clearances (except payment of statutory fees) has to be obtained by submitting the required documents to the concerned department through OPTCL. Way-Leave blockade charges and any other charges are to be borne by the bidders. The documents for PTCC clearance & Railway clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | SET | 1 | 1 | 2 | 500000 | 45000 | 45000 | 590000 | 1180000
B | TOTAL OF ELECTRICAL WORKS (PART B) | [8 empty] | 48606743.1828
(FOR 400 KV D/C LILO LINE from 400KV Meramandali-Mendhasal D/C line(CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi LINE)
| ERECTION_LINE EQUIPMENT & MATERIALS |  |  |  |  | IN INR
S. No. | ERECTION OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT | QUANTITY |  |  | UNIT PRICE | GST PER UNIT |  | TOTAL UNIT PER PRICE | TOTAL PRICE
|  |  | Meramandali End | Mendhasal End | Total |  | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 | 5 | 6=4+5 | 7 | 8=7x9% | 9=7x9% | 10=7+8+9 | 11=7X10
PART B | ELECTRICAL WORKS
1 | ERECTION,TESTING & COMMISSIONING of Following tested Lattice type Galvanized steel tangent / Angle tower without stubs and cleats including different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete with tightening, punching of bolts including step bolts. All other left out portion of the bolts above bottom cross arm shall be riveted by using suitable hammer. Painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping legs & bracing members. All Erection should confirm to the Technical Specification laid there in the Tender Specification.
1.1 | DA TYPE (0 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 11.704 MT) | Nos. | 25 | 25 | 50
1.1.1 | +3 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 1.50MT) | Nos. | 3 | 3 | 6
1.1.2 | +6 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 2.619 MT) | Nos. | 3 | 3 | 6
1.1.2 | +9 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 2.248 MT) | Nos. | 3 | 3 | 6
1.2 | DB TYPE (15 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 20.177 MT) | Nos. | 5 | 5 | 10
1.2.1 | +3 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 3.039 MT) | Nos. | 2 | 2 | 4
1.2.2 | +6 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 4.791 MT) | Nos. | 3 | 3 | 6
1.2.3 | +9 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 6.301 MT) | Nos. | 0 | 0 | 0
1.3 | DC TYPE (30 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 22.799 MT) | Nos. | 20 | 20 | 40
1.3.1 | +3 mtr Body Extension of DC(NOMINAL UNIT WEIGHT 3.498MT) | Nos. | 5 | 5 | 10
1.3.2 | +6 mtr Body Extension of DC (NOMINAL UNIT WEIGHT 4.636 MT) | Nos. | 5 | 5 | 10
1.3.3 | +9 mtr Body Extension of DC(NOMINAL UNIT WEIGHT 6.875 MT) | Nos. | 5 | 5 | 10
1.4 | DD TYPE (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 35.512 MT) | Nos. | 20 | 20 | 40
1.4.1 | +3 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 5.454 MT) | Nos. | 2 | 2 | 4
1.4.2 | +6 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 8.084 MT) | Nos. | 3 | 3 | 6
1.4.3 | +9 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 10.863 MT) | Nos. | 3 | 3 | 6
1.4.4 | +18 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 24.431 MT) | Nos. | 2 | 2 | 4
1.4.5 | +25 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 35.796MT) | Nos. | 2 | 2 | 4
1.5 | TOTAL WEIGHT OF STRUCTURES WITHOUT STUBS INCLUDING MS & HT MATERIALS | MT | 1775.67 | 1775.67 | 3551.34 | 5744.84 | 517.0356 | 517.0356 | 6778.9112 | 24074218.501
1.6 | ERECTION OF STUBS
1.6.1 | DA (Nominal unit weight 0.586 MT) | Nos | 25 | 25 | 50
1.6.2 | DB (Nominal unit weight 1.125 MT) | Nos | 5 | 5 | 10
1.6.3 | DC (Nominal unit weight 1.308 MT) | Nos | 20 | 20 | 40
1.6.4 | DD (Nominal unit weight 2.92 MT) | Nos | 16 | 16 | 32
1.6.5 | DD +18/25 (Nominal unit weight 2.92 MT) | Nos | 4 | 4 | 8
1.6.6 | TOTAL WEIGHT OF STUBS | MT | 104.835 | 104.835 | 209.67 | 5744.84 | 517.0356 | 517.0356 | 6778.9112 | 1421334.3113
1.7 | ERECTION OF TEMPLATES
1.7.1 | DA (Nominal unit weight 1.524 MT) | Nos | 2 | 2 | 4
1.7.2 | DB (Nominal unit weight 3.441 MT) | Nos | 1 | 1 | 2
1.7.3 | DC (Nominal unit weight 3.693 MT) | Nos | 2 | 2 | 4
1.7.4 | DD (Nominal unit weight 3.889 MT) | Nos | 2 | 2 | 4
1.7.5 | DD +18/25 (Nominal unit weight 3.889 MT) | Nos | 1 | 1 | 2
1.7.6 | WEIGHT OF TEMPLATES FOR DA , DB , DC,DD | MT | 25.542 | 25.542 | 51.084 | 5744.84 | 517.0356 | 517.0356 | 6778.9112 | 346293.8997
1.6 | Weight of different type G.I Nuts and Bolts | MT | 92 | 92 | 184 | 5744.84 | 517.0356 | 517.0356 | 6778.9112 | 1247319.6608
2 | Hoisting and fixing of insulators with required accessories, paying out of conductor, jointing, stringing, sagging & Jumpering etc. of power conductor with G.I. Earth wire & OPGW in the proposed lines with all required accessories including scaffolding/other required arrangements for 33 KV,11 KV, LT , P&T lines, NH/roads, railway line, river etc and using own required T&P and compression jointing machines etc. as per the direction of Engineer in charge. | [5 empty] | 0 | 0 | 0 | 0
2.1 | ACSR Double Moose with one Earth Wire and one OPGW | Route(Km) | 23 | 23 | 46 | 226392.6814 | 20375.3413 | 20375.3413 | 267143.3641 | 12288594.7464
3 | Erection of the following tower accessories as per technical specification and as directed by the engineer-in charge.
3.1 | DANGER BOARD | Nos. | 70 | 70 | 140 | 124.03 | 11.1627 | 11.1627 | 146.3554 | 20489.756
3.2 | NUMBER PLATE | Nos. | 70 | 70 | 140 | 124.03 | 11.1627 | 11.1627 | 146.3554 | 20489.756
3.3 | PHASE PLATE | Nos. | 420 | 420 | 840 | 124.03 | 11.1627 | 11.1627 | 146.3554 | 122938.536
3.4 | BIRD GUARD | Nos. | 150 | 150 | 300 | 124.03 | 11.1627 | 11.1627 | 146.3554 | 43906.62
3.5 | ANTICLIMBING DEVICE | Nos. | 70 | 70 | 140 | 2676.58 | 240.8922 | 240.8922 | 3158.3644 | 442171.016
3.6 | CIRCUIT PLATE | Nos. | 140 | 140 | 280 | 124.03 | 11.1627 | 11.1627 | 146.3554 | 40979.512
4 | EARTHING OF TOWER
4.1 | Pipe Type earthing including cost of charcoal,salt/coke and good borrowed earth and Bentonite where necessary in accordance with IS:3043 and with supply of all T&P and Labour. | Nos. | 110 | 110 | 220 | 2389.18 | 215.0262 | 215.0262 | 2819.2324 | 620231.128
4.2 | Counterpoise Earthing as per Indian Standards | Mtr. Length | 100 | 100 | 200 | 73.5199 | 6.6168 | 6.6168 | 86.7535 | 17350.7011
5 | WELDING OF TOWER BOLTS/NUTS
5.1 | Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods, welding generator machine (diesel engine operator.), application of required zinc rich paints around the welding portion after welding (two coats),fuel,lubricants,T&P and labours and other arrangements etc. | Nos. | 150000 | 150000 | 300000 | 8.57 | 0.7713 | 0.7713 | 10.1126 | 3033780
6 | Dismantaling of Tower Structure
6.1 | Dismantaling of Tower Super Structure including cutting of the welded tower bolts, transportation & delivey with stacking at nearest OPTCL store as per instruction Engineer-in-charge. | MT | 100 | 100 | 200 | 4595.87 | 413.6283 | 413.6283 | 5423.1266 | 1084625.32
6.2 | Dismantaling, transportation & Delivey and Stacking of strung of Twin ACSR MOOSE conducter (With Earth wire/OPGW) at nearest OPTCL store as per instruction Engineer-in-Charge including dismantling of insulators, hardware fittings, conductor accessories, spacers etc. | Route Km | 2 | 2 | 4 | 165490.45 | 14894.1405 | 14894.1405 | 195278.731 | 781114.924
7 | Approval for PTCC, railway crossing, NHAI, Water and other atatutory bodies clearances (except payment of statutory fees) has to be obtained by submitting the required documents to the concerned department through OPTCL. Way-Leave blockade charges and any other charges are to be borne by the bidders. The documents for PTCC clearance & Railway clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | SET | 1 | 1 | 2 | 500000 | 45000 | 45000 | 590000 | 1180000
C | TOTAL OF ELECTRICAL WORKS (PART C) | [8 empty] | 46785838.3884
| TOTAL ERECTION_ELECTRICAL (SUB_STATION + MRDL-MENDHASAL LILO LILE + MRDL-NEW DUBURI LILO LINE) (A+B+C) | [8 empty] | 170992761.0361

## Schedule 1 Supply (hidden)
400/220/33 KV Sub-Station at NEULPOI & Associated 400 KV LILO LINE (SUPPLY) |  |  | ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK: Construction of 2X500 MVA,2X63 MVA 400/220/33 KV Sub-Station with SAS at Neulpoi with associated 400 KV D/C LILO LINE from 400KV Meramandali-New Duburi D/C line (CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi and 400 KV D/C LILO LINE from 400KV Meramandali-Mendhasal D/C line(CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi in Dhenkanal District on EPC contract basis
NOTICE INVITING TENDER-NIT NO. -
PRICE BID FOR WORKS CONTRACT (SAC CODE - 995423): SCHEDULE -1 SUPPLY COMPONENT OF THE WORKS CONTRACT-
NAME OF BIDDER
400/220 kV Substation Neulpoi: 400 KV Bays-[21 Nos (10 Fdr+2 ICT+7Tie+2Reactor)] In 1 & 1/2 CB System, 220KV Bay-7 Nos.(FDR-2,ICT-2+ TRF -2, B/C-1) 33KV Bay-9 Nos.(FDR-6,TFR-2, B/C -1]
Sl. No. | SUBSTATION EQUIPMENTS / MATERIALS | UNITS | Quantity (Neulpoi GSS) |  |  | RUPEES IN INR
| DESCRIPTION OF ITEMS(SCHEDULE-VIIA-SS) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) |  |  |  |  | UNIT PRICE | GST PER UNIT |  | TOTAL PER UNIT PRICE | TOTAL PRICE
[7 empty] | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT) |  |  | TOTAL FORD Price except Entry Tax IN INR
1 | 2 | 3 | 4 |  |  | 5 | 6=5x9% | 7=5x9% | 8=5+6+7 | 9=4X8 | 16=4X15
1 | 420 KV, 2000-1000-500A, 63 kA, 5 Core Single Phase Current Transformer | Nos | 84 |  |  | 557388.72 | 50164.9848 | 50164.9848 | 657718.6896 | 55248369.9264 | #REF!
2 | 420 KV, 3150A, 63 kA Isolators
2.1 | With One Earth Switch | Nos | 54 |  |  | 1121801.79 | 100962.1611 | 100962.1611 | 1323726.1122 | 71481210.0588 | #REF!
2.2 | With Two Earth Switch | Nos | 2 |  |  | 1121801.79 | 100962.1611 | 100962.1611 | 1323726.1122 | 2647452.2244 | #REF!
3 | 420 KV, 63 kA, 3 Core Single Phase Line Capacitor Voltage Transformer | Nos | 36 |  |  | 228106.29 | 20529.5661 | 20529.5661 | 269165.4222 | 9689955.1992
4 | 420 KV, 3150A, 63kA, SF6 Circuit Breaker With Support Structure. | [9 empty] | #REF!
4.1 | Circuit Breaker with CSD. | Nos | 19 |  |  | 2690839.9 | 242175.591 | 242175.591 | 3175191.082 | 60328630.558 | #REF!
4 .2 | Circuit Breaker without CSD. | Nos | 2 |  |  | 2690839.9 | 242175.591 | 242175.591 | 3175191.082 | 6350382.164 | #REF!
5 | Metal oxide polymer housed surge arrrestor for 420 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 42 |  |  | 160064.98 | 14405.8482 | 14405.8482 | 188876.6764 | 7932820.4088 | #REF!
6 | 400 KV Bus Post Insulators | Nos | 288 |  |  | 45750 | 4117.5 | 4117.5 | 53985 | 15547680 | #REF!
7 | 245 KV, (1200-600-300/1-1-1-1-1-1A), 50kA, 5 CORE SINGLE PHASE CURRENT TRANSFORMER | Nos | 27 |  |  | 323854.32 | 29146.8888 | 29146.8888 | 382148.0976 | 10317998.6352 | #REF!
8 | 245 KV, 2 Core, Voltage Transformer (1 core 3P & 1 core 0.2) | Nos | 12 |  |  | 132637.6 | 11937.384 | 11937.384 | 156512.368 | 1878148.416 | #REF!
9 | 245 KV, 2000A, 50 kA Isolators
9.1 | Without Earth Switch | Nos | 20 |  |  | 329000.84 | 29610.0756 | 29610.0756 | 388220.9912 | 7764419.824
9.2 | With Single Earth Switch | Nos | 2 |  |  | 378121.38 | 34030.9242 | 34030.9242 | 446183.2284 | 892366.4568 | #REF!
9.3 | Tandem Isolator without Earth Switch | Nos | 7 |  |  | 335407.86 | 30186.7074 | 30186.7074 | 395781.2748 | 2770468.9236 | #REF!
10 | 245KV, 3150A, 50kA, SF6 Circuit Breaker with Support Structure | Nos | 7 |  |  | 1348277.99 | 121345.0191 | 121345.0191 | 1590968.0282 | 11136776.1974 | #REF!
11 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 18 |  |  | 70578.02 | 6352.0218 | 6352.0218 | 83282.0636 | 1499077.1448 | #REF!
12 | 220 KV Bus Post Insulators | Nos | 54 |  |  | 22505 | 2025.45 | 2025.45 | 26555.9 | 1434018.6 | #REF!
13 | 132KV, 2000A, 40 kA Isolators without Earth Switch (1-Pole) For 400KV 125Mvar Reactor | Nos | 2 |  |  | 219068.84 | 19716.1956 | 19716.1956 | 258501.2312 | 517002.4624 | #REF!
14 | Metal oxide polymer housed surge arrrestor for 132 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 2 |  |  | 28807.29 | 2592.6561 | 2592.6561 | 33992.6022 | 67985.2044 | #REF!
15 | 36KV, 31.5kA Current Transformers | [9 empty] | #REF!
15.1 | 36 KV,800-400-200,31.5kA,3 core Single phase Current Transformer (2 Nos PS class & 1 No. 0.2s class) | Nos | 6 |  |  | 50825.97 | 4574.3373 | 4574.3373 | 59974.6446 | 359847.8676 | #REF!
15.2 | 36 KV, 800-400-200, 31.5kA, 4 core Single phase Current Transformer (3 Nos PS class & 1 No. 0.2s class) | Nos | 21 |  |  | 50825.97 | 4574.3373 | 4574.3373 | 59974.6446 | 1259467.5366
16 | 36 KV, 1250A, 31.5kA Isolators
16.1 | Single Isolator without Earth Switch | Nos | 20 |  |  | 124595.84 | 11213.6256 | 11213.6256 | 147023.0912 | 2940461.824
16.2 | Single Isolator with Earth Switch | Nos | 6 |  |  | 255041.27 | 22953.7143 | 22953.7143 | 300948.6986 | 1805692.1916
16.3 | Beam Mounted Single Isolator without Earth Switch | Nos | 4 |  |  | 95247.32 | 8572.2588 | 8572.2588 | 112391.8376 | 449567.3504
17 | Metal oxide polymer housed surge arrrestor for 33 kV system. Station Class Low Duty (SL) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor - As per TS | Nos | 24 |  |  | 9296.39 | 836.6751 | 836.6751 | 10969.7402 | 263273.7648
18 | 36 KV, 2 Core Single Phase IVT (1 core 3P & 1 core 0.2) | Nos | 3 |  |  | 19800 | 1782 | 1782 | 23364 | 70092
19 | 36 KV, 1250A, 31.5kA, Vaacuum Circuit Breaker with supporting Structure. Facilities for integration with SAS as per the site requirement. | Nos | 9 |  |  | 219472.75 | 19752.5475 | 19752.5475 | 258977.845 | 2330800.605
20 | 33 KV Bus Post Insulators | Nos | 30 |  |  | 5547 | 499.23 | 499.23 | 6545.46 | 196363.8
21 | BUS BAR & CIRCUIT MATERIALS
21.1 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS FOR FOLLOWING ARRANGEMENT: 1. 400KV Bus-A & B and Equipment to Equipment connectionare 120mm IPS Aluminium Pipe Bus 2. Cross Bus shall be with Twin ACSR Moose and Cross bus to equipment shal also be with Twin ACSR Moose. 3. 220KV Main Bus-I & II shall be with twin ACSR Moose (conductor spacing-300mm) and Transfer bus shall be with Single ACSR Moose. 4. 220KV Equipment connections shall be with single ACSR moose. 5. 33KV Main Bus & Transfer Bus shall be with Twin ACSR Moose (conductor spacing-250mm). 6. 33KV Equipment connections shall be with single ACSR Moose for feeders and Twin ACSR Moose for the Bus coupler & Transformer bays. 7. 33KV Station transformer connections shalll be with Single ACSR Panther conductor. 8. The Single hardware fittings shall be of 160KN & 120KN for 400KV & 220KV system, 120KN and 90KN for 33KV system. The UTS of the twin hardware fittings shall be suitably chosen for twin insulators of the above mentioned UTS. 10. The harware fittings shall be single anchored and without turn buckle. 11. This also includes any other hardware fittings and clamps required to complete the work. 12. The qty of hardware fittings, clamps & connectors, Conductor, IPS Aluminium tube and Insulators shall be as per the approved drawing.
21.1.1 | All suspension & tension hardware fittings for 400KV system for Twin ACSR Moose | Lot | 1 |  |  | 7000000 | 630000 | 630000 | 8260000 | 8260000
21.2.2 | All suspension & tension hardware fittings for 220KV system for Twin ACSR Moose, Single ACSR Moose | Lot | 1 |  |  | 2000000 | 180000 | 180000 | 2360000 | 2360000
21.1.2 | All suspension & tension hardware fittings for 33KV system for Twin ACSR Moose, Single ACSR Moose | Lot | 1 |  |  | 1472775 | 132549.75 | 132549.75 | 1737874.5 | 1737874.5 | #REF!
21.2.3 | Clamps & Connectors, Spacers etc for Twin ACSR Moose, IPS Aluminium Tube for 400KV system | Lot | 1 |  |  | 1892736.76 | 170346.3084 | 170346.3084 | 2233429.3768 | 2233429.3768 | #REF!
21.1.3 | Clamps & Connectors, Spacers etc for Twin ACSR Moose, Single ACSR Moose for 220KV system | Lot | 1 |  |  | 1261824.51 | 113564.2059 | 113564.2059 | 1488952.9218 | 1488952.9218 | #REF!
21.2.4 | Clamps & Connectors, Spacers etc for Twin ACSR Moose, Single ACSR Moose for 33KV system | Lot | 1 |  |  | 598444 | 53859.96 | 53859.96 | 706163.92 | 706163.92 | #REF!
21.2 | ACSR MOOSE CONDUCTOR | KM | 30 |  |  | 409923 | 36893.07 | 36893.07 | 483709.14 | 14511274.2 | #REF!
21.3 | IPS 4.5” Aluminium Tube (OD: 120 mm, Thickness: 12 mm)(for 400 KV Bus and connection from equipment to equipment in 400 KV side) including welding sleeves,corona bell etc. The Lot shall be as per the approved drawing. | Lot | 1 |  |  | 1500000 | 135000 | 135000 | 1770000 | 1770000 | #REF!
21.4 | ACSR Panther Conductor | Mtrs | 200 |  |  | 206 | 18.54 | 18.54 | 243.08 | 48616
21.5 | Antifog type Disc Insulators for 400KV Switchyard (160KN & 120 KN) | Lot | 1 |  |  | 3500000 | 315000 | 315000 | 4130000 | 4130000
21.6 | Antifog type Disc Insulators for 220KV Switchyard (160KN & 120 KN) | Lot | 1 |  |  | 5000000 | 450000 | 450000 | 5900000 | 5900000 | #REF!
21.7 | Antifog type Disc Insulators for 33KV Switchyard (120KN & 90KN) | Lot | 1 |  |  | 2500000 | 225000 | 225000 | 2950000 | 2950000 | #REF!
22 | SUBSTATION EARTHING SYSTEMS: (The qty for the earthing materials shall be as per the approved earthing design calculations based on the soil resistivity of the project area) | [9 empty] | #REF!
22.1 | EARTHING CONDUCTOR FOR BURRIAL :(40MM MS ROD) for laying as main earth mat for the whole (400KV, 220KV & 33KV) switchyards as per design calculation(spacing maximum 5m both way). | MT | 280 |  |  | 70000 | 6300 | 6300 | 82600 | 23128000 | #REF!
22.2 | EARTHING CONDUCTOR: 75X10 mm GI Flat for Raiser from the burial earth mat to foundation plint level of equipmentstructure etc.) | MT | 95 |  |  | 70000 | 6300 | 6300 | 82600 | 7847000
22.3 | EARTHING CONDUCTOR: 50X6 mm GI Flat as riser to structures, equipment, coulmns and up to the bottom of spikes, fencing, cable tray and auxiliary Boards earthing etc.). Each equipment strructure & Columns shall be connected to earth at two separate points. | MT | 30 |  |  | 70000 | 6300 | 6300 | 82600 | 2478000 | #REF!
22.4 | Earthing Device & associated accessories: 50 mm heavy duty GI perforated pipe, 3 mtrs long for treated earth pit | Nos | 350 |  |  | 2251.91 | 202.6719 | 202.6719 | 2657.2538 | 930038.83 | #REF!
22.5 | Earthing Device & associated accessories: 40mm MS rod, 3 mtrs long for treated earth pits | Nos | 500 |  |  | 2251.91 | 202.6719 | 202.6719 | 2657.2538 | 1328626.9 | #REF!
22.6 | Switchyard buildings lightning protection (all materials & accessories like Shielding Wire, PG clamp, Test link, D shackle, other required materials etc) as per IS/National Building code standard and as per approved drawing | Lot | 1 |  |  | 67489.769 | 6074.0792 | 6074.0792 | 79637.9274 | 79637.9274 | #REF!
22.7 | Supply of UPVC Pipes (2", 1.5", 1" & 1/2" etc), Joints, bends, Valves and all accessories for spreading the water network from the overhead tank to each treated earth pit as per approved drawing. | LOT | 1 |  |  | 500000 | 45000 | 45000 | 590000 | 590000 | #REF!
23 | GI Cable Trays including support GI angle suitable for different sections i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories as per TS and approved drawing. | Lot | 1 |  |  | 500000 | 45000 | 45000 | 590000 | 590000 | #REF!
24 | Switchyard Structures( Including Foundation Bolts And Nuts) Galvanised (Lattice) For All 400 kV & 220 kV | [9 empty] | #REF!
24.1 | Different Types Of Columns with earth spikes and Beams (Lattice Type) as per approved layout design | [9 empty] | #REF!
24.1.1 | 400 KV Columns & beams | Lot | 1 | [7 empty] | #REF!
24.1.2 | 220 KV Column & beams | Lot | 1 | [7 empty] | #REF!
24.1.3 | 33 KV Column & beams | Lot | 1
24.2 | Total Weight Of Column & Beam | MT | 1082 |  |  | 92260.97 | 8303.4873 | 8303.4873 | 108867.9446 | 117795116.0572
24.3 | Total Weight Of Different Size Of Gi Nuts And Bolts For column & beam structures. | MT | 54 |  |  | 117049.77 | 10534.4793 | 10534.4793 | 138118.7286 | 7458411.3444 | #REF!
24.4 | Support Structures (Including Foundation Bolts And Nuts) Galvanised (Pipe Type) For All 400 KV & 220 KV Equipments as per approved layout design | [9 empty] | #REF!
24.4.1 | 400KV Equipment | Lot | 1
24.4.2 | 220KV Equipment | Lot | 1
24.4.3 | 333KV Equipment | Lot | 1
24.5 | Total Weight Of Support Structure For Above Equipment | MT | 180 |  |  | 92260.97 | 8303.4873 | 8303.4873 | 108867.9446 | 19596230.028 | #REF!
24.6 | Total weight of different size of GI Nuts and bolts for equipment structures. | MT | 9 |  |  | 117049.77 | 10534.4793 | 10534.4793 | 138118.7286 | 1243068.5574
25 | General Equipment & Substation Accessories | [9 empty] | #REF!
25.1 | Power Cables-1.1KV, FRLSH XLPE & PVC, Armoured Aluminium Conductor (As Per Specification) | [9 empty] | #REF!
25.1.1 | XLPE 3.5 C X 630 mm2 | Mtrs | 3200 |  |  | 1017.85 | 91.6065 | 91.6065 | 1201.063 | 3843401.6
25.1.2 | XLPE 3.5 C X 185 mm2 | Mtrs | 900 |  |  | 759.303 | 68.3373 | 68.3373 | 895.9775 | 806379.786
25.1.3 | XLPE 3.5 C X 120 mm2 | Mtrs | 500 |  |  | 453.26 | 40.7934 | 40.7934 | 534.8468 | 267423.4
25.1.4 | PVC 3.5 C X 70 mm2 | Mtrs | 10500 |  |  | 262.3 | 23.607 | 23.607 | 309.514 | 3249897
25.1.5 | PVC 3.5 C X 35 mm2 | Mtrs | 675 |  |  | 145.62 | 13.1058 | 13.1058 | 171.8316 | 115986.33 | #REF!
25.1.6 | PVC 4 C X 16 mm2 | Mtrs | 5050 |  |  | 114.31 | 10.2879 | 10.2879 | 134.8858 | 681173.29 | #REF!
25.1.7 | PVC 4 C X 6 mm2 | Mtrs | 7000 |  |  | 114.31 | 10.2879 | 10.2879 | 134.8858 | 944200.6
25.1.8 | PVC 2C X 6 mm2 | Mtrs | 12500 |  |  | 114.31 | 10.2879 | 10.2879 | 134.8858 | 1686072.5 | #REF!
25.2 | Control Cables- 1.1 KV, FRLSH PVC, Armoured Stranded Copper conductor (As Per Specification) | [9 empty] | #REF!
25.2.1 | 4 C X 2.5 mm2 | Mtrs | 16000 |  |  | 122.09 | 10.9881 | 10.9881 | 144.0662 | 2305059.2
25.2.2 | 5 C X 2.5 mm2 | Mtrs | 20000 |  |  | 184.82 | 16.6338 | 16.6338 | 218.0876 | 4361752 | #REF!
25.2.3 | 7C X 2.5 mm2 | Mtrs | 1200 |  |  | 184.82 | 16.6338 | 16.6338 | 218.0876 | 261705.12 | #REF!
25.2.4 | 10 C X 2.5 mm2 | Mtrs | 6000 |  |  | 251.171 | 22.6054 | 22.6054 | 296.3818 | 1778290.68
25.2.5 | 12 C X 2.5 mm2 | Mtrs | 550 |  |  | 251.17 | 22.6053 | 22.6053 | 296.3806 | 163009.33 | #REF!
25.2.6 | 16 C X 2.5 mm2 | Mtrs | 7500 |  |  | 382.1 | 34.389 | 34.389 | 450.878 | 3381585
25.2.7 | 19 C X 2.5 mm2 | Mtrs | 13200 |  |  | 443.11 | 39.8799 | 39.8799 | 522.8698 | 6901881.36
25.3 | Single core 1.1KV, PVC Un-armoured copper conductor: for connection from Battery Set to Battery Charger and from Battery Charger to DCDB on cable tray / HDPE pipe/PVC pipe etc | [9 empty] | #REF!
25.3.1 | 1CX 120 mm2 | Mtrs | 300 |  |  | 635 | 57.15 | 57.15 | 749.3 | 224790 | #REF!
25.4 | Supply of screened / Shielded Twisted pair copper cable for Analog Communication for showing winding temp, Oil temp,lighting, fire fighting, DG etc, LT current & LT voltage signals of sub-station auxiliary system in HMI
25.4.1 | 8PX1.5 mm2 screened copper cable | Mtrs | 1500 |  |  | 296 | 26.64 | 26.64 | 349.28 | 523920 | #REF!
25.4.2 | 2PX1.5 mm2 screened copper cable | Mtrs | 750 |  |  | 59.32 | 5.3388 | 5.3388 | 69.9976 | 52498.2 | #REF!
26 | Supply Of Station Transformer & Other Materials For meeting the Auxiliary Supply
26.1 | Station Transformer 33KV/433V, 1000 KVA (As Per Specification) | Nos | 2 |  |  | 2293722.92 | 206435.0628 | 206435.0628 | 2706593.0456 | 5413186.0912 | #REF!
26.2 | HG fuse set for 33 KV side of the Station transformer including base(each set comprises three single HG fuse) | SETS | 2 |  |  | 574704 | 51723.36 | 51723.36 | 678150.72 | 1356301.44 | #REF!
27 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area) | [9 empty] | #REF!
27.1 | Substation Switchyard Lighting: It Includes supply of fixtures & lamps (LED) of reputed make (Philips/CGL/Bajaj/Havells/ Osram/ Wipro premium quality) with switch gear, GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved).(150 watt each) | Nos | 250 |  |  | 12000 | 1080 | 1080 | 14160 | 3540000
27.2 | STREET LIGHTING: HDG Octagonal street lighting poles 7 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. The pole shall be manufactured in a single section with weight of galvanization 610 g/sqm or thickness of galvanization 86 micron. The pole shall be meant for installation in Wind Zone V. Poles should be suitable for installation on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes supply of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/ Havells/ Osram/Wipro), with switch gear, GI Conduit etc. & as per technical specification. The pole shall have separate or inbuilt GI junction box with suitable cover with (water/dust) ingress protection for housing electrical accessories. The JB shall have provision of fuses/MCB, buses, TBs as required for cable in and out. | Set | 50 |  |  | 30000 | 2700 | 2700 | 35400 | 1770000
28 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 16-ANNEXURE - I) | [9 empty] | #REF!
28.1 | FOAM TYPE-9 LTRS | Nos | 5 |  |  | 6430 | 578.7 | 578.7 | 7587.4 | 37937 | #REF!
28.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | Nos | 5 |  |  | 49733 | 4475.97 | 4475.97 | 58684.94 | 293424.7 | #REF!
28.3 | DRY POWDER TYPE - 5 KGS | Nos | 9 |  |  | 10020 | 901.8 | 901.8 | 11823.6 | 106412.4 | #REF!
28.4 | CO2 - 4.5 KGS | Nos | 12 |  |  | 21390 | 1925.1 | 1925.1 | 25240.2 | 302882.4 | #REF!
28.5 | CO2 - 9 KGS | Nos | 12 |  |  | 31620 | 2845.8 | 2845.8 | 37311.6 | 447739.2 | #REF!
28.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | Nos | 6 |  |  | 37241 | 3351.69 | 3351.69 | 43944.38 | 263666.28 | #REF!
28.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND | SET | 8 |  |  | 5415 | 487.35 | 487.35 | 6389.7 | 51117.6 | #REF!
29 | SUBSTATION AUTOMATION SYSTEM FOR 400/220/33 KV SUBSTATION ON PRP MODE: Design , engineering , drawing, supervision, installation , testing & commissioning of Substation Automation system alongwith Supply of the following 400, 220 and 33 kV level of protection panels consisting of Bay control Units & numerical protection relays and other auxiliary relays suitable for SAS as per technical specification. NOTE: All protective relays & BCU shall be numerical type.
29.1 | Gateway Panel: for Sub-Station Automation (in PRP on FO as per the specification & indicative drawing) system (for All 400KV, 220KV & 33 KV side bays) and with other accessories, comprising: 1. HMI servers (Main & Stand By) 2. DR PC for Local 3. Gateway- 2 nos (both in hot mode) 4. Color Laser jet Printer-1Nos 5. Dot Matrix Printer-1Nos 6. Ethernet Fiber Switches (with 20% spares Port) 7. LIU 8. Multimode glass fibre Doublle jacket armoured optical cables 9. Red boxes 10. Inverters(Input shall be both A.C & D.C and output shall be A.C) - 3 KVA (Main & Stand by) 11. Furniture (Operator desk 1 Nos & Chair-6Nos) 12. Full HD or better resolution LED TV 75 inch (Sony, LG, Samsung) or higher for display etc as per TS, including all type of accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system complete in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. | SET | 1 |  |  | 1755416.88 | 157987.5192 | 157987.5192 | 2071391.9184 | 2071391.9184 | #REF!
29.2 | BCU for Substation Auxilliary System (Station AC, Station DC, Lighting, Fire fighting, Diesel generator etc.) | SET | 1 |  |  | 350000 | 31500 | 31500 | 413000 | 413000 | #REF!
29.3 | GPS System with IRIG-B/SNTP/PTP with VDU (Clock) | Nos | 1 |  |  | 500000 | 45000 | 45000 | 590000 | 590000 | #REF!
30 | 400 KV SIDE PROTECTION & OTHER PANELS as per Technical specification suitable for operating the Circuit breakers with CSD. | [9 empty] | #REF!
30.1 | 400KV feeder Protection Panel: MAIN-I , MAIN-II Distance protection relays of different make & Backup Protection, Bay control unit (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Set | 10 |  |  | 2361316 | 212518.44 | 212518.44 | 2786352.88 | 27863528.8 | #REF!
30.2 | 400KV Transformer Protection Panel: Differential Protection Main- I & II of different make , Separate REF- Main- I & II (different make) & BACK-UP PROTECTION for HV & IV side (considering HV, IV & LV side for 500 MVA 400/220/33 KV ICT), Bay control units (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Set | 2 |  |  | 2361316 | 212518.44 | 212518.44 | 2786352.88 | 5572705.76 | #REF!
30.3 | 400KV Tie Bay protection Panel: with Bay control unit (BCU), other protection & aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Set | 7 |  |  | 2361316 | 212518.44 | 212518.44 | 2786352.88 | 19504470.16 | #REF!
30.4 | 400KV BUS-BAR Protection System (Distributed architecture with Main-I & Main-II): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Provision of bus bar modules for at least Four future bays shall be made. The bus bar protection system shall be integrated with the Automation system. | Lot | 1 |  |  | 3758000 | 338220 | 338220 | 4434440 | 4434440 | #REF!
30.5 | 400 KV Bus Reactor Panel: With Numerical Backup-Impedance, Differential, Separate REF & Back-up protection, Bay Control Unit (BCU) & aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Set | 2 |  |  | 2330373 | 209733.57 | 209733.57 | 2749840.14 | 5499680.28
31 | 220 KV SIDE PROTECTION & OTHER PANELS | [9 empty] | #REF!
31.1 | 220KV Feeder Protection Panel: MAIN-I , MAIN-II of different make, Backup Protection relays, Bay control unit (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Nos | 2 |  |  | 2850000 | 256500 | 256500 | 3363000 | 6726000 | #REF!
31.2 | 220KV, 500MVA ICT Protection Panel: This includes all Relays including LBB trip relays and Bay Control Units (BCU), complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | Nos | 2 |  |  | 2850000 | 256500 | 256500 | 3363000 | 6726000 | #REF!
31.3 | 220KV, 63MVA Power Transformer Protection Panel: Differential (Main-I & Main-II of different make), saparate numerical REF, Backup Protection and other aux relays including LBB trip relays & Bay control units (BCU) as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | Nos | 2 |  |  | 2850000 | 256500 | 256500 | 3363000 | 6726000 | #REF!
31.4 | 220KV Bus Coupler Protection Panel: Backup Protection Relays and other aux relays including LBB trip relays & BCU as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | Nos | 1 |  |  | 1200000 | 108000 | 108000 | 1416000 | 1416000 | #REF!
31.5 | 220KV Transfer Bus Coupler Protection Panel: Backup Protection Relays and other aux relaysincluding LBB trip relays & BCU as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | Nos | 1 |  |  | 1200000 | 108000 | 108000 | 1416000 | 1416000 | #REF!
31.6 | 220KV BUS-BAR Protection Sysstem (Distributed architecture): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Provision of bus bar modules for at least Four future bays shall be made. The bus bar protection system shall be integrated with the Automation system. | Lot | 1 |  |  | 3750000 | 337500 | 337500 | 4425000 | 4425000 | #REF!
32 | 33 KV SIDE PROTECTION PANELS: Single Panel Twin Bay type ( 2 Bays in One Panel) with IEC:61850-ED2 PRP on FO | [9 empty] | #REF!
32.1 | FEEDER PROTECTION PANEL (WIth BCPU & with other auxiliary relays including LBB trip relays as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) Note: 06 No.s of Line feeder bays to be considered in 03 nos of Panels | Nos | 3 |  |  | 3000000 | 270000 | 270000 | 3540000 | 10620000
32.2 | POWER TRANSFORMER PROTECTION PANEL (WIth BCPU & separate numerical REF and other auxiliary relays including LBB trip relays as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) Note: 02 No.s of Transformer feeder bays to be considered. (The Panel shall have 02 Nos. of transformer feeders). | Nos | 1 |  |  | 1800000 | 162000 | 162000 | 2124000 | 2124000 | #REF!
32.3 | BUS COUPLER PROTECTION RELAY PANEL WIth BCPU & with other auxiliary relays including LBB trip relays as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) | Nos | 1 |  |  | 700000 | 63000 | 63000 | 826000 | 826000 | #REF!
33 | AC & DC SYSTEM
33.1 | AC SYSTEM (Indoor Type with 2 mm CRCA sheet and 3 mm CRCA gland plate & as per TS:) | [9 empty] | #REF!
33.1.1 | MAIN AC DB (Indoor Type): MAIN DB-1, MAIN DB-2 with B/C. The incomer & Bus coupler shall have 800 A, 50KA, drawout type ACB with Numerical SAS compliant Relay (O/C, E/F, U/V, O/V protection). The ACDB shall be suitable for automatic switching OFF & ON during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 |  |  | 1093219 | 98389.71 | 98389.71 | 1289998.42 | 1289998.42 | #REF!
33.1.2 | ACDB (Indoor Type) WITH BUS 1, BUS 2, BUS 3, Bus Coupler 1 & Bus Coupler 2: HAVING 400A Motorized MCCB for automatic operation in Incomers and Bus couplers with electrical interlock system. With Three Bus sections and Two nos of Bus couplers. Two bus sections shall be connected with two bus sections of the Main ACDB and the 3rd bus section shall be connected to the DG having all emergency loads. The outgoing feeders for the Main ACDB shall be appropriately designed to cater all loads having 20% spares of each rating feeder in each section. The cosntruction of the ACDB shall be as per the TS. The ACDB shall be suitable for automatic switching OFF & ON, auto start of DG set etc during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 |  |  | 771193 | 69407.37 | 69407.37 | 910007.74 | 910007.74 | #REF!
33.1.3 | Main Lighting Distribution Board (Indoor Type): Having 250A MCCB with source-1, Source-2 & Bus coupler. | SET | 1 |  |  | 191442.2344 | 17229.8011 | 17229.8011 | 225901.8366 | 225901.8366
33.1.4 | Indoor Lighting Distribution Board (Indoor Type) | SET | 1 |  |  | 24249.3497 | 2182.4415 | 2182.4415 | 28614.2326 | 28614.2326 | #REF!
33.1.5 | Emergency Lighting Distribution Board (Outdoor type): The ELDB should be supplying to 20% of switchyard lights, each of 220KV and 33KV Switchyard. | SET | 1 |  |  | 21058.6458 | 1895.2781 | 1895.2781 | 24849.202 | 24849.202 | #REF!
33.1.6 | INDOOR RECEPTACLE BOARD | SET | 2 |  |  | 7657.6894 | 689.192 | 689.192 | 9036.0735 | 18072.1469 | #REF!
33.1.7 | ACDB for Yard Kiosk (Indoor Type): LT supply to Protection panels, Kiosk lighting, AC etc | SET | 6 |  |  | 54087.06 | 4867.8354 | 4867.8354 | 63822.7308 | 382936.3848 | #REF!
33.2 | AC SYSTEM : Outdoor Type, Sub Station Swithyard Console Boxes, HDG type (86 micron), 3 mm thick CRCA, (BMK,AC CONSOLE & OTHER MB) as per TS. | [9 empty] | #REF!
33.2.1 | Bay Marshalling Kiosk: 1 BMK for 1 no 400KV Dia, 1 no of BMK for 2 nos 220KV bays and 1 BMK for 4 nos 33KV bays | SET | 14 |  |  | 148445.88 | 13360.1292 | 13360.1292 | 175166.1384 | 2452325.9376 | #REF!
33.2.2 | Console box for switchyard lighting | SET | 4 |  |  | 44533.64 | 4008.0276 | 4008.0276 | 52549.6952 | 210198.7808 | #REF!
33.2.3 | Switchyard Receptacle Board for Transformer Oil Filteration | SET | 4 |  |  | 44533.64 | 4008.0276 | 4008.0276 | 52549.6952 | 210198.7808
33.2.4 | Switchyard Receptacle Board for welding and other emergency | SET | 8 |  |  | 44533.64 | 4008.0276 | 4008.0276 | 52549.6952 | 420397.5616 | #REF!
33.2.5 | CT CONSOLE BOXES as per TS | SET | 46 |  |  | 44533.64 | 4008.0276 | 4008.0276 | 52549.6952 | 2417285.9792 | #REF!
33.2.6 | CVT/IVT CONSOLE BOXES as per TS | SET | 17 |  |  | 44533.64 | 4008.0276 | 4008.0276 | 52549.6952 | 893344.8184 | #REF!
33.2.7 | Console box for street lighting | SET | 4 |  |  | 371115.33 | 33400.3797 | 33400.3797 | 437916.0894 | 1751664.3576 | #REF!
33.2.8 | Console box for Transit House/Colony Supply purpose | SET | 1 |  |  | 371115.33 | 33400.3797 | 33400.3797 | 437916.0894 | 437916.0894 | #REF!
33.2.9 | OUT DOOR KIOSK FOR STATION TRANSFORMER With Busbar & SFU of appropriate rating with required sizes of terminal studs for power cable termination & any other accessories required. | SET | 2 |  |  | 371115.33 | 33400.3797 | 33400.3797 | 437916.0894 | 875832.1788 | #REF!
33.3 | DC SYSTEM | [9 empty] | #REF!
33.3.1 | 220 V DC DISTRIBUTION BOARD (Indoor Type): Having 2 nos 63A DC MCCB for Incomers, Bus Coupler with interlock, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE and shall be SAS compliant & as per TS. Consider separate source (DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered. | SET | 1 |  |  | 371115.33 | 33400.3797 | 33400.3797 | 437916.0894 | 437916.0894 | #REF!
33.3.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD (Indoor Type) | SET | 1 |  |  | 371115.33 | 33400.3797 | 33400.3797 | 437916.0894 | 437916.0894
33.3.3 | BATTERY BANK (350 AH PLANTE TYPE) for 220 V DC System (2V Battery Cells 107 Nos + 3 Nos spare) & its spare as per TS | SET | 2 |  |  | 2025000 | 182250 | 182250 | 2389500 | 4779000 | #REF!
33.3.4 | Battery Charger For 350 AH Plante Type Battery, 107 cells, 2 V, Trickle charge volt - 2.25V (Float & Float Cum Boost). Charger ON/OFF status, input/output voltage, output current, associated charger protection signals shall be provided for integration with SAS & its spare as per TS. | SET | 2 |  |  | 395293.68 | 35576.4312 | 35576.4312 | 466446.5424 | 932893.0848 | #REF!
33.3.5 | DCDB for Yard Kiosk (Indoor Type): DC supply to Protection panels having source-1 & 2 with auto changeover facility. Consider separate source (DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output to be considered. | SET | 6 |  |  | 54087.06 | 4867.8354 | 4867.8354 | 63822.7308 | 382936.3848 | #REF!
34 | AIR CONDITIONING: Supply of 2T capacity Split Air Conditioning Units (Dual Inverter, five star latest model - LG/Samsung/Hitachi/Carrier/Mitsubishi/Voltas/Daikin Make) with copper condensor having remote temperature & operation control facility with voltage stabilizer. Following item description also includes AC Control Panel made of 2mm CR sheet, having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (As per specification) for CRB cum GIS (Control/SAS Room, AC DC Room, Communication room, office room & Conference room), Switchyard Kisok, Transit House. Supply of Logic controller for Auto Switch ON & OFF of AC units depending on requirement. Also includes supply of all other additional accessories such as copper tubes, copper cable, steel brackets for holding outdoor units and other accessories necessary for completion of the AC system. As per approved drawing and direction of engineer-in-charge. | [9 empty] | #REF!
34.1 | AC for CRB: For Control/SAS Room, ACDC Room Communication room, office room & Conference room . | Set | 18 |  |  | 58141 | 5232.69 | 5232.69 | 68606.38 | 1234914.84
34.2 | AC for Switchyard Kiosk (2 nos per Kiosk) as per T.S. (The ACs shall run in tandem i.e 1 of the ACs at a time for 4 hours each.) | Set | 12 |  |  | 58141 | 5232.69 | 5232.69 | 68606.38 | 823276.56
34.3 | AC For Transit House | Set | 4 |  |  | 58141 | 5232.69 | 5232.69 | 68606.38 | 274425.52
35 | Accessories For OPGW System As Per Technical Specification
35.1 | 48 fibre optic approach cable along with installation hardware including HDPE pipes | Km | 1 |  |  | 133002.8 | 11970.252 | 11970.252 | 156943.304 | 156943.304
35.2 | Optical line terminal equipment (OLTE)-STM16 type SDH equipment with integrated MUX & tributary cards for speech & data ports for interfacing of speech & data which should be compatible with existing OPTCL system. | Nos. | 1 |  |  | 22280.49 | 2005.2441 | 2005.2441 | 26290.9782 | 26290.9782
35.3 | Supply of FODP (Fibre optic Distribution panel) 96F: Indoor type, rack mounted with FCPC coupling and pigtails (DWSM fibre) | Nos. | 1 |  |  | 52954.38 | 4765.8942 | 4765.8942 | 62486.1684 | 62486.1684
35.4 | Digital tele-protection coupler with accessories compatible for interfacing with SDHMUX | Nos. | 8 |  |  | 103413.49 | 9307.2141 | 9307.2141 | 122027.9182 | 976223.3456
35.5 | 48V, 300 AH, maintenance free VRLA battery set | Set | 2 |  |  | 117656.93 | 10589.1237 | 10589.1237 | 138835.1774 | 277670.3548
35.6 | SMPS based battery charger of 75A suitable for 48V VRLA battery | SET | 2 |  |  | 109324.96 | 9839.2464 | 9839.2464 | 129003.4528 | 258006.9056
35.7 | 48 V DCDB (with I/C-I, I/C-II & B/C) | Nos. | 1 |  |  | 11988 | 1078.92 | 1078.92 | 14145.84 | 14145.84
35.8 | Earth flat, cable tray, telephone cable, ACDB, DCDB, foundation rail, Junction Box, Cat 5 cable & Misc items | Lot | 1 |  |  | 200000 | 18000 | 18000 | 236000 | 236000
36 | MAINTENANCE & TESTING EQUIPMENT: The equipment shall be the as per the models or newer as mentioned against each item. | LOT | 1 |  |  | 15849817.385 | 1426483.5647 | 1426483.5647 | 18702784.5143 | 18702784.5143 | #REF!
36.1 | Universal Relay Testing Kit (Omicron CMC 356) | Set | 1
36.2 | Capacitance Tan-Delta Testing Kit (Omicron/Doble make) | Set | 1 | [7 empty] | #REF!
36.3 | Contact Resistance Measurement Kit- (Milli volt drop measurement (Contact resistance measurement -200Amp DC) (Omicron/Doble/Sonel make) | Set | 1 | [7 empty] | #REF!
36.4 | Automatic 3 ph Transformer Turns Ratio Testing Kit (Omicron/Doble/DV Power make) | Set | 1 | [7 empty] | #REF!
36.5 | Winding Resistance Testing Kit (Omicron/Doble make) | Set | 1 | [7 empty] | #REF!
36.6 | Third Harmonic Resistive Current Measurement Kit for SA (Omicron/Doble/Megger/Becon Energy Solutn make) | Set | 1 | [7 empty] | #REF!
36.7 | 100KV Automatic Transformer Oil Breakdown Voltage test set (Megger- OTS 100AF / Baur- DTA 100C) | Nos | 1 | [7 empty] | #REF!
36.8 | 10KV Insulation Tester with 15m test leads (Megger- S1-1068 / Sonel-MIC 10K1) | Nos | 1
36.9 | Digital Earth Tester (Facility for soil resistivity measurement and test leads suitable for connection to the test probe/spikes placed at 20m between each other ) (Megger-DET2/3 / Sonel MRU-120 / Fluke 1625) | Nos | 1
36.1 | Digital Multimeter (Megger / Fluke) | Nos | 2
36.11 | Digital Clamp meter (Megger/Fluke/Motwane) | Nos | 1
36.12 | Leakage current clamp meter AC & DC both (30mA / 300mA / 30A / 300A) (Megger/Fluke/Kyoritsu) | Nos | 1
36.13 | SF6 Gas Leakage Detector (Wika/DILO) | Nos | 1
36.14 | Oil sampling Bottle- Stainless Steel, Capacity- 1 Ltr (Make- Tosin) | Nos | 6
36.15 | Fibre Glass Discharge / Earth Rod: Grip up to 50mm, Min height-16ft, rubber grip, 35 sq.mm copper cable (1 set- 3 cables, 1 set of rod, carry bag) (Bemico) | Set | 6
36.16 | Electrical Rubber Hand Gloves | Pairs | 4
36.17 | Portable High Beam Light (with at least 2000mAh rechargeable battery, rated power-15W, Input-230V , 50Hz) (Phillips) | Nos | 2
36.18 | Desktop Computer: (HP/Lenovo/Dell) | Set | 2
Processor-Intel Core i5 10th Gen or better
RAM- 8GB DDR4 or More
ROM- 512GB SSD
Monitor- 21.5" FHD (1920 x 1080) or higher
Graphics- Intel UHD
OS- Genuine Windows 10 or 11 Pro
36.19 | Webcam- 720P Logitech | Nos | 2
36.2 | Speaker- 2 nos Stereo type | Nos | 2
36.21 | UPS 600VA (APC/V Guard) | Nos | 2
36.22 | Laser Printer, Black & White, Duplex printing (print, scan & copy) (HP/Canon/Epson) | Nos | 1
37 | Other Tools And Plants (T&P'S) Requirement (As Per details below). The T & P materials shall be of Taparia/Bosch/Stanley make. | Lot | 1 |  |  | 320000 | 28800 | 28800 | 377600 | 377600
37.1 | D Spanner Set (6mm – 42mm) | Set | 1
37.2 | Ring Spanner Set (6mm – 42mm) | Set | 1
37.3 | Box spanner set | Set | 1
37.4 | Pipe Wrench 24 " | Nos | 1
37.5 | Pipe Wrench 18 " | Nos | 1
37.6 | Adjustable spanner -12”(slide wrench) | Nos | 1
37.7 | Adjustable spanner -18”(slide wrench) | Nos | 1 | [7 empty] | #REF!
37.8 | Insulated cutting plier (standard size) | Nos | 1
37.9 | Nose Plier (standard size) | Nos | 1
37.1 | Screw Driver set
37.10.1 | 12” Plain head | Nos | 2
37.10.2 | 12” star head | Nos | 2
37.10.3 | 8” Plain head | Nos | 2
37.10.4 | 6” plain head | Nos | 2
37.10.5 | 6” star head | Nos | 2
37.11 | Set of screw driver cum line tester | Set | 1
37.12 | Allen Key set | Set | 1
37.13 | Files
37.13.1 | Flat File-12” | Nos | 1
37.13.2 | Flat file-6” | Nos | 1
37.13.3 | Round file- 12” | Nos | 1
37.13.4 | Round file- 6” | Nos | 1
37.14 | Hammer with Handle
37.14.1 | 1 lb | Nos | 2
37.14.2 | 2 lb | Nos | 1
37.14.3 | ½ lb | Nos | 2
37.15 | Steel Tape (Any reputed make)
37.15.1 | 5Mtr | Nos | 1
37.15.2 | 30Mtr | Nos | 1
37.16 | Crow bar (Any reputed make)
37.16.1 | 5ft | Nos | 2
37.16.2 | 3ft | Nos | 2
37.17 | Oil Cane (Any reputed make) | Nos | 2
37.18 | Hand Drill Machine (impact drill) with key (Make-Bosch/Black & Decker) | Nos | 1
37.19 | Vacuum Cleaner (at least 15L) (Make-Eureka Forbes / Black & Decker / Phillips / Karcher) | No | 1
37.2 | Stand Fan (450mm sweep,1400rpm, 240V AC) (Make-Crompton, Bajaj, Havells, Almonard, Usha) | Nos | 2
38 | Self supproted cum extendable Ladder-25ft (FRP) of Adequate Height to be used for Maintenance of Equipment Inside Switchyard. | Nos | 1 |  |  | 60000 | 5400 | 5400 | 70800 | 70800
39 | Self supproted platform Ladder- 12feet (FRP) of Adequate Height to be used for Maintenance of Equipment Inside Switchyard. | Nos | 1 |  |  | 45000 | 4050 | 4050 | 53100 | 53100
40 | De-Mineralised Plant of 50 L/Hr or more for Making Distilled Water for Battery Banks. (Cation and anion resin bed type) | Set | 1 |  |  | 300000 | 27000 | 27000 | 354000 | 354000
41 | 20 Ltr Storage Water Cooler (Voltas/Bluestar only) | Nos | 1 |  |  | 40000 | 3600 | 3600 | 47200 | 47200
42 | Water Purifier (RO+UV+UF type) suitable for connecting to the above water storage cooler (Kent/Aquaguard/Livpure/Pureit/Bluestar/LG)only | Nos | 1 |  |  | 15000 | 1350 | 1350 | 17700 | 17700
43 | Supply & installation of Office Furniture: Godrej make (As per details below). | Lot | 1 |  |  | 500000 | 45000 | 45000 | 590000 | 590000
43.1 | For Control Room, conference room, office rooms, Library, testing room etc
43.1.1 | 5ftX3ft executive table with drawer on both sides | Nos | 4 | [7 empty] | #REF!
43.1.2 | 4.5ft X 2.5ft Table with one side drawer | Nos | 7 | [7 empty] | #REF!
43.1.3 | Computer table suitable keeping monitor, CPU, UPS and printer with two nos revolving arm chair suitable for computer use. | Set | 1 | [7 empty] | #REF!
43.1.4 | Executive revolving, adjustable (height) chairs with arm | Nos | 4
43.1.5 | Cushion fixed “S” type steel chairs with arm | Nos | 16
43.1.6 | 6ftX3ft conference table | Nos | 1
43.1.7 | Cushion arm steel chairs for conference table purpose. | Nos | 6
43.1.8 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 3
43.1.9 | 6ft height steel almirah with glass doors for library purpose | Nos | 2
43.1.10 | 6ft height (having minimum 6 lockers facility) steel cupboard with locking arrangement. | Nos | 2
43.1.11 | 4ft steel rack (minimum three selves) for keeping the files and other items. | Nos | 8
43.2 | For Communication Room
43.2.1 | 5ftX3ft executive table with drawer both sides | Nos | 1 | [7 empty] | #REF!
43.2.2 | Executive revolving, adjustable (height) chairs with arm | Nos | 1
43.2.3 | Cushion fixed “S” type steel chairs with arm | Nos | 2
43.2.4 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 1
44 | Insulating Mat: Best Quality & approved make (Confirming to IS:15652:2006) to be kept infront of all panels, boards etc.(2000X1000X3mm Size) | Nos | 37 |  |  | 2500 | 225 | 225 | 2950 | 109150
45 | CCTV Surveilance system: Supply, Installation, Commissioning, Testing for IP Based CCTV Surveillance System (Server Based approach), DVR with 4TB Hard Disk, Day/Night Cameras, PC Monitor (Full HD - 32 inch) including all materials for areas inside & outside Control room building, Entire Switchyard areas covering boundaries, entry/exit points of substation & Other areas etc., suitable for 360 deg movement with all necessary hardware fittings for monitoring and surveillance of the entire substation. The CCTV system shall be able to be integrated with the SAS system. No. of such cameras (different type viz. PTZ, bullet or dome) are to be calculated as per standard practice & its installations at the strategic locations. Tentative Requirement: 1. Fixed type bullet cameras for monitoring of Security shed cum Main gate complex, Main Entrance door of Control Room Building, Main Entrance door of Fire-fighting Pump House, Main Entrance door of store shed, Open stockyard, Main entrance gate of switchyard and all gates of switchyard etc. 2. Dome/Bullet cameras for indoor areas - Relay panel room, AC/DC Room, SAS Room, Corridoor areas etc. 3. PTZ cameras (as per requirement mentioned below): a) Switchyard areas (400/220/33 kV) b) All the Transformers, reactors, station transformers under present scope Note: Any other requirement besides above to be explored & can be finalised during detail Engg. | Lot | 1 |  |  | 1000000 | 90000 | 90000 | 1180000 | 1180000
46 | 400/220/33 KV, 500 MVA ICT with Nitrogen Injection System for fire protection, online drying out system, Online dissolved gas(Multi gas) & moisture analyser and spare & other accessories etc as per Technical spec.
46.1 | 400/220KV, 500 MVA ICT without OLTC and including all accessories and spares etc as per Technical spec. | NOS | 2 |  |  | 265907075.33 | 23931636.7797 | 23931636.7797 | 313770348.8894 | 627540697.7788
46.2 | Type Test Charges on 400/220/33 KV, 500 MVA ICT (on one unit out of the lot) for the following as per Technical Spec.: - Temperature Rise Test - Measurement of Zero Sequence Impedance - Auxiliary Power Consumption - Vacuum Test - Pressure Test - IP 55 Test on MB | Lot | 1 |  |  | 1000000 | 90000 | 90000 | 1180000 | 1180000 |  | 1090690697.7788 | 0.0012
46.3 | Other requirement of 400/220/33 KV, 500 MVA ICT as indicated below as per Technical Spec: | [10 empty] | 1090690697.78
46.3.1 | NCTs including its mounting arragement as per TS. | Set | 2 |  |  | 41578.98 | 3742.1082 | 3742.1082 | 49063.1964 | 98126.3928
46.3.2 | Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) (1 set for each of the ICT). | Set | 2 |  |  | 9958421.02 | 896257.8918 | 896257.8918 | 11750936.8036 | 23501873.6072
46.3.3 | Online insulating oil drying system(As per Technical Specification) (1 set for each of the ICT) | Set | 2 |  |  | 2000000 | 180000 | 180000 | 2360000 | 4720000
46.3.4 | Online dissolved gas(Multi gas) & moisture analyser(As per Technical Specification) (1 set for each of the ICT) | Set | 2 |  |  | 1000000 | 90000 | 90000 | 1180000 | 2360000
46.3.5 | Oil storage Tank as per Technical Specification (3 Nos) | Set | 3 |  |  | 500000 | 45000 | 45000 | 590000 | 1770000
46.4 | The following type test shall be carried out in presence of Purchaser’s representative on one unit out of the lot at the discretion of the purchaser. (a) Dynamic Short Circuit (DSC)Test charges including post DSC tests | Lot | 1 |  |  | 1500000 | 135000 | 135000 | 1770000 | 1770000
46.5 | Charges for Transportation of Transformer (one unit out of the lot) from the Factory site to the Location for Dynamic Short Circuit (DSC)Test & back to Factory and other incidental charges if any. | Lot | 1 |  |  | 2000000 | 180000 | 180000 | 2360000 | 2360000
47 | 400 kV, 125 MVAr BUS Reactor with Nitrogen Injection System for fire protection,online drying out system,Online dissolved gas(Multi gas) & moisture analyser and spare & other accessories etc as per Technical spec.
47.1 | 400 kV, 125 MVAr BUS Reactor with accessories and spares etc as per Technical spec. | Nos | 2 |  |  | 80000000 | 7200000 | 7200000 | 94400000 | 188800000
47.2 | Type Test Charges on 400 kV 125 MVAr BUS Reactor for the following as per Technical Spec.: - Temperature Rise Test - Top oil and hot spot temperature rise test - Winding temperature rise test - Measurement of Zero Sequence Reactance -IP-55 Test on MB | Lot | 1 |  |  | 1000000 | 90000 | 90000 | 1180000 | 1180000
47.3 | Other requirement of 400 kV 125 MVAr BUS Reactoras indicated below as per Technical Spec.:
47.3.1 | NCTs including its mounting arragement as per TS. | Set | 2 |  |  | 41578.98 | 3742.1082 | 3742.1082 | 49063.1964 | 98126.3928
47.3.2 | Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) (1 set for each Reactor). | Set | 2 |  |  | 9958421.02 | 896257.8918 | 896257.8918 | 11750936.8036 | 23501873.6072
47.3.3 | Online insulating oil drying system(As per Technical Specification) (1 set for each Reactor) | Set | 2 |  |  | 2500000 | 225000 | 225000 | 2950000 | 5900000
47.3.4 | Online dissolved gas(Multi gas) & moisture analyser(As per Technical Specification) (1 set for each Reactor) | Set | 2 |  |  | 1500000 | 135000 | 135000 | 1770000 | 3540000
47.4 | The following type test shall be carried out in presence of Purchaser’s representative on one unit out of the lot at the discretion of the purchaser. (a) Dynamic Short Circuit (DSC)Test charges including post DSC tests | Lot | 1 |  |  | 2000000 | 180000 | 180000 | 2360000 | 2360000
47.5 | Charges for Transportation of Transformer (one unit out of the lot) from the Factory site to the Location for Dynamic Short Circuit (DSC)Test & back to Factory and other incidental charges if any. | Lot | 1 |  |  | 2500000 | 225000 | 225000 | 2950000 | 2950000
48 | Supply of Power Transformer with spares as per technical specification & conducting the type tests as per the TS. (Including NCT as per TS for High Impedance REF protection)
48.1 | 220/33 KV, 63 MVA Yn Yn Power Transformer as per TS | Nos | 2 |  |  | 70000000 | 6300000 | 6300000 | 82600000 | 165200000
48.2 | The following type tests shall be carried out in presence of Purchaser’s representative on one unit out of the lot at the discretion of the purchaser. (a) Temperature Rise Test. (b) Measurement of Zero Sequence Impedance. (c) Auxiliary Power Consumption.. (d) Vacuum Test (e) Pressure Test (f) IP-55 Test on MB) | Lot | 1 |  |  | 500000 | 45000 | 45000 | 590000 | 590000
48.3 | The following type test shall be carried out in presence of Purchaser’s representative on one unit out of the lot at the discretion of the purchaser. (a) Dynamic Short Circuit (DSC)Test charges including post DSC tests | Lot | 1 |  |  | 3000000 | 270000 | 270000 | 3540000 | 3540000
48.4 | Charges for Transportation of Transformer (one unit out of the lot) from the Factory site to the Location for Dynamic Short Circuit (DSC)Test & back to Factory and other incidental charges if any. | Lot | 1 |  |  | 3500000 | 315000 | 315000 | 4130000 | 4130000
48.5 | FIRE FIGHTING (Nitrogen Injection Type Fire Prevention & Extinguishing System): Suitable for 63 MVA, 220/33 KV Power Transformer as per Technical Specification & latest standard. | Set | 2 |  |  | 9958421.02 | 896257.8918 | 896257.8918 | 11750936.8036 | 23501873.6072
48.6 | NCTs including its mounting arragement as per TS. | Set | 2 |  |  | 41578.98 | 3742.1082 | 3742.1082 | 49063.1964 | 98126.3928
49 | FIRE FIGHTING EQIPMENT: As per specification-(Main Pump,Jockey Pump,DG Set cum Pump, Control Panel,Different sizes of MS pipe(to be painted for rust proof),different type of valves,Fire sensor etc for the Fire Fighting System(HIGH PRESSURE : Hydrant and Mulsifire to take care of 2 Nos 500 MVA ICT,2 Nos 125 MVAR 400 KV Reactor, 2 Nos 63 MVA Transformer and switcyard equipment and control room building. | LOT | 1 |  |  | 10000000 | 900000 | 900000 | 11800000 | 11800000
50 | 250 KVA DG set (3Ph, 4 wire, 415V, 50Hz) complete set (silent/no noise type, suitable for outdoor/indoor, less smoke(as per rule for pollution control) and control AMF panel. | LOT | 1 |  |  | 2500000 | 225000 | 225000 | 2950000 | 2950000
A | TOTAL COST OF SUPPLY FOR SUBSTATION | [8 empty] | 1809230301.5381 |  | 865377533.3772
| (FOR 400 KV D/C LILO LINE from 400KV Meramandali-New Duburi D/C line (CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi LINE) | [10 empty] | -943852768.1609
| SUPPLY_LINE EQUIPMENT & MATERIALS |  |  |  |  | IN INR
S. No. | SUPPLY OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT | QUANTITY |  |  | UNIT PRICE | GST PER UNIT |  | TOTAL UNIT PER PRICE | TOTAL PRICE
|  |  | Meramundali End | New Duburi End | TOTAL |  | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 | 5 | 6=4+5 | 7 | 8=7x9% | 9=7x9% | 10=7+8+9 | 11=7X10
1 | SUPPLY of Following type tested Lattice type Galvanized steel tangent / Angle tower(MS and HT) with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification.
1.1 | DA TYPE (0 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 11.118 MT) | Nos. | 25 | 25 | 50
1.1.1 | +3 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 1.50MT) | Nos. | 6 | 6 | 12
1.1.2 | +6 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 2.619 MT) | Nos. | 6 | 6 | 12
1.1.3 | +9 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 3.248 MT) | Nos. | 3 | 3 | 6
1.2 | DB TYPE (15 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 20.052 MT) | Nos. | 10 | 10 | 20
1.2.1 | +3 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 3.039 MT) | Nos. | 2 | 2 | 4
1.2.2 | +6 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 4.791 MT) | Nos. | 3 | 3 | 6
1.2.3 | +9 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 6.301 MT) | Nos. | 0 | 0 | 0
1.3 | DC TYPE (30 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 21.491 MT) | Nos. | 20 | 20 | 40
1.3.1 | +3 mtr Body Extension of DC(NOMINAL UNIT WEIGHT 3.498MT) | Nos. | 4 | 4 | 8
1.3.2 | +6 mtr Body Extension of DC (NOMINAL UNIT WEIGHT 6.636 MT) | Nos. | 4 | 4 | 8
1.3.3 | +9 mtr Body Extension of DC(NOMINAL UNIT WEIGHT 6.875 MT) | Nos. | 4 | 4 | 8
1.4 | DD TYPE (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 32.592 MT) | Nos. | 20 | 20 | 40
1.4.1 | +3 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 5.454 MT) | Nos. | 2 | 2 | 4
1.4.2 | +6 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 8.084 MT) | Nos. | 4 | 4 | 8
1.4.3 | +9 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 10.863 MT) | Nos. | 2 | 2 | 4
1.4.4 | +18 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 24.431 MT) | Nos. | 2 | 2 | 4
1.4.5 | +25 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 35.796MT) | Nos. | 2 | 2 | 4
1.5 | TOTAL WEIGHT OF STRUCTURES WITHOUT STUBS INCLUDING MS & HT MATERIALS | MT | 1868.499 | 1868.499 | 3736.998 | 99357.97 | 8942.2173 | 8942.2173 | 117242.4046 | 438134631.5054
1.6 | STUBS
1.6.1 | DA (Nominal unit weight 0.586 MT) | Nos | 25 | 25 | 50
1.6.2 | DB (Nominal unit weight 1.125 MT) | Nos | 10 | 10 | 20
1.6.3 | DC (Nominal unit weight 1.308 MT) | Nos | 20 | 20 | 40
1.6.4 | DD (Nominal unit weight 2.92 MT) | Nos | 16 | 16 | 32
1.6.5 | DD +18/25 (Nominal unit weight 2.92 MT) | Nos | 4 | 4 | 8
1.6.6 | TOTAL WEIGHT OF STUBS | MT | 110.46 | 110.46 | 220.92 | 99357.97 | 8942.2173 | 8942.2173 | 117242.4046 | 25901192.0242
1.7 | TEMPLATES
1.7.1 | DA (Nominal unit weight 1.524 MT) | Nos | 2 | 2 | 4
1.7.2 | DB (Nominal unit weight 3.441 MT) | Nos | 1 | 1 | 2
1.7.3 | DC (Nominal unit weight 3.693 MT) | Nos | 2 | 2 | 4
1.7.4 | DD (Nominal unit weight 3.889 MT) | Nos | 2 | 2 | 4
1.7.5 | DD +18/25 (Nominal unit weight 3.889 MT) | Nos | 1 | 1 | 2
1.7.6 | WEIGHT OF TEMPLATES FOR DA , DB , DC,DD | MT | 25.542 | 25.542 | 51.084 | 68942.26 | 6204.8034 | 6204.8034 | 81351.8668 | 4155778.7636
1.8 | Weight of different type G.I Nuts and Bolts | MT | 94 | 94 | 188 | 117049.77 | 10534.4793 | 10534.4793 | 138118.7286 | 25966320.9768
2 | Supply of the following tower accessories as per technical specification and as directed by the engineer in charge.
2.1 | EARTHING DEVICE | Nos. | 115 | 115 | 230 | 2251.91 | 202.6719 | 202.6719 | 2657.2538 | 611168.374
2.2 | DANGER BOARD | Nos. | 75 | 75 | 150 | 233.75 | 21.0375 | 21.0375 | 275.825 | 41373.75
2.3 | NUMBER PLATE | Nos. | 75 | 75 | 150 | 127.73 | 11.4957 | 11.4957 | 150.7214 | 22608.21
2.4 | PHASE PLATE | Nos. | 450 | 450 | 900 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 105807.06
2.5 | BIRD GUARD | Nos. | 150 | 150 | 300 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 35269.02
2.6 | ANTICLIMBING DEVICE | Nos. | 75 | 75 | 150 | 4344.16 | 390.9744 | 390.9744 | 5126.1088 | 768916.32
2.7 | CIRCUIT PLATE | Nos. | 150 | 150 | 300 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 35269.02
2.8 | COUNTERPOISE EARTHING | Nos. | 10 | 10 | 20 | 2251.91 | 202.6719 | 202.6719 | 2657.2538 | 53145.076
3 | Supply of following POWER CONDUCTORS in the proposed 400 KV lines as per the technical specification and as per the instruction of the engineer in charge.
3.1 | ACSR Moose (54+7/3.53/3.66 mm) | Kms. | 305 | 305 | 610 | 409923 | 36893.07 | 36893.07 | 483709.14 | 295062575.4
4 | POWER CONDUCTOR ACESSORIES FOR ACSR MOOSE
4.1 | VIBRATION DAMPER | Nos. | 3600 | 3600 | 7200 | 1067.73 | 96.0957 | 96.0957 | 1259.9214 | 9071434.08
4.2 | MID SPAN JOINT | Nos. | 50 | 50 | 100 | 1044.52 | 94.0068 | 94.0068 | 1232.5336 | 123253.36
4.3 | REPAIR SLEEVE | Nos. | 20 | 20 | 40 | 458.17 | 41.2353 | 41.2353 | 540.6406 | 21625.624
4.4 | PG CLAMP FOR ACSR MOOSE | Nos. | 50 | 50 | 100 | 500 | 45 | 45 | 590 | 59000
4.5 | BUNDLE SPACER ACSR MOOSE | Nos. | 2500 | 2500 | 5000 | 1746.85 | 157.2165 | 157.2165 | 2061.283 | 10306415
4.6 | RIGID SPACER ACSR MOOSE | Nos. | 1350 | 1350 | 2700 | 1746.85 | 157.2165 | 157.2165 | 2061.283 | 5565464.1
5 | Supply of the GI earth wire of size 7/3.66 mm as per the technical specification and as per the direction of Engineer in charge. | Kms. | 26 | 26 | 52 | 32346.93 | 2911.2237 | 2911.2237 | 38169.3774 | 1984807.6248
6 | EARTH CONDUCTOR ACESSORIES
6.1 | VIBRATION DAMPER | Nos. | 300 | 300 | 600 | 427 | 38.43 | 38.43 | 503.86 | 302316
6.2 | FLEXIBLE COPPER EARTH BOND | Nos. | 150 | 150 | 300 | 274.62 | 24.7158 | 24.7158 | 324.0516 | 97215.48
6.3 | SUSPENSION CLAMP | Nos. | 25 | 25 | 50 | 459.83 | 41.3847 | 41.3847 | 542.5994 | 27129.97
6.4 | TENSION CLAMP | Nos. | 50 | 50 | 100 | 555.06 | 49.9554 | 49.9554 | 654.9708 | 65497.08
6.5 | MID SPAN COMPRESSION JOINT | Nos. | 10 | 10 | 20 | 37.04 | 3.3336 | 3.3336 | 43.7072 | 874.144
6.6 | REPAIR SLEEVE | Nos. | 5 | 5 | 10 | 37.04 | 3.3336 | 3.3336 | 43.7072 | 437.072
7 | Supply of OPGW Fibre Optic Cable & Hard ware for Speech , data & protection
7.1 | 24 fibre (DWSM) OPGW fibre optic cable. | Km | 26 | 26 | 52 | 133002.8 | 11970.252 | 11970.252 | 156943.304 | 8161051.808
7.2 | OPGW hardware set like suspension Assembly,Tensin Assembly(Dead end assembly, Pass through assembly) ,Vibration Damper,Down Lead Clamp Assemblies for 24/48 Fibre(DWSM) OPGW,Joint Box | LOT | 1 | 1 | 2 | 500000 | 45000 | 45000 | 590000 | 1180000
8 | Supply of the following Anti fog type disc insulators as per the technical specification and as per the instruction of the Engineer in charge.
8.1 | 160KN Antifog Disc Insulator | Nos. | 25987.5 | 25987.5 | 51975 | 797.6 | 71.784 | 71.784 | 941.168 | 48917206.8
8.2 | 120 KN Antifog Disc Insulator | Nos. | 4000 | 4000 | 8000 | 710.86 | 63.9774 | 63.9774 | 838.8148 | 6710518.4
9 | Supply of the following hard ware fittings suitable for ACSR Moose conductors as per the technical specification.
9.1 | For ACSR Moose
9.1.1 | Double suspension Hardware fittings.(AGS type) suitable for 120 KN insulator. | Nos | 150 | 150 | 300 | 5208.46 | 468.7614 | 468.7614 | 6145.9828 | 1843794.84
9.1.2 | Double tension Hardware fittings suitable for 160 KN insulator. | Nos. | 600 | 600 | 1200 | 4992.49 | 449.3241 | 449.3241 | 5891.1382 | 7069365.84
9.1.3 | Single suspension Pilot Insulator Hard wares fittings suitable for 120 KN insulator. | Nos. | 160 | 160 | 320 | 3421.17 | 307.9053 | 307.9053 | 4036.9806 | 1291833.792
9.1.4 | “D” Shackle | Nos. | 200 | 200 | 400 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 47025.36
9.1.5 | Hanger | Nos. | 50 | 50 | 100 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 11756.34
9.1.6 | U'-Bolt. | Nos | 50 | 50 | 100 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 11756.34
10 | High Resolution Binacular(NICON COOLPIX P900) | Nos | 1 | 1 | 2 | 50000 | 4500 | 4500 | 59000 | 118000
B | TOTAL -LINE | [8 empty] | 893881834.5548 |  | 869202360.1988
| (FOR 400 KV D/C LILO LINE from 400KV Meramandali-Mendhasal D/C line(CKT-I & II) to proposed 400/220/33KV Grid Sub-Station at Neulpoi LINE) | [10 empty] | -24679474.356
| SUPPLY_LINE EQUIPMENT & MATERIALS |  |  |  |  | IN INR
S. No. | SUPPLY OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT | QUANTITY |  |  | UNIT PRICE | GST PER UNIT |  | TOTAL UNIT PER PRICE | TOTAL PRICE
|  |  | Meramandali End | Mendhasal End | Total |  | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 | 5 | 6=4+5 | 7 | 8=7x9% | 9=7x9% | 10=7+8+9 | 11=7X10
1 | SUPPLY of Following type tested Lattice type Galvanized steel tangent / Angle tower(MS and HT) with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification.
1.1 | DA TYPE (0 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 11.118 MT) | Nos. | 25 | 25 | 50
1.1.1 | +3 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 1.50MT) | Nos. | 3 | 3 | 6
1.1.2 | +6 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 2.619 MT) | Nos. | 3 | 3 | 6
1.1.3 | +9 mtr Body Extension of DA(NOMINAL UNIT WEIGHT 3.248 MT) | Nos. | 3 | 3 | 6
1.2 | DB TYPE (15 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 20.052 MT) | Nos. | 5 | 5 | 10
1.2.1 | +3 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 3.039 MT) | Nos. | 2 | 2 | 4
1.2.2 | +6 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 4.791 MT) | Nos. | 3 | 3 | 6
1.2.3 | +9 mtr Body Extension of DB(NOMINAL UNIT WEIGHT 6.301 MT) | Nos. | 0 | 0 | 0
1.3 | DC TYPE (30 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 21.491 MT) | Nos. | 20 | 20 | 40
1.3.1 | +3 mtr Body Extension of DC(NOMINAL UNIT WEIGHT 3.498MT) | Nos. | 5 | 5 | 10
1.3.2 | +6 mtr Body Extension of DC (NOMINAL UNIT WEIGHT 6.636 MT) | Nos. | 5 | 5 | 10
1.3.3 | +9 mtr Body Extension of DC(NOMINAL UNIT WEIGHT 6.875 MT) | Nos. | 5 | 5 | 10
1.4 | DD TYPE (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 32.592 MT) | Nos. | 20 | 20 | 40
1.4.1 | +3 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 5.454 MT) | Nos. | 2 | 2 | 4
1.4.2 | +6 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 8.084 MT) | Nos. | 3 | 3 | 6
1.4.3 | +9 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 10.863 MT) | Nos. | 3 | 3 | 6
1.4.4 | +18 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 24.431 MT) | Nos. | 2 | 2 | 4
1.4.5 | +25 mtr Body Extension of DD(NOMINAL UNIT WEIGHT 35.796MT) | Nos. | 2 | 2 | 4
1.4.6 | TOTAL WEIGHT OF STRUCTURES WITHOUT STUBS INCLUDING MS & HT MATERIALS |  | 1775.67 | 1775.67 | 3551.34 | 99357.97 | 8942.2173 | 8942.2173 | 117242.4046 | 416367641.1522
1.5 | STUBS
1.5.1 | DA (Nominal unit weight 0.586 MT) | Nos | 25 | 25 | 50
1.5.2 | DB (Nominal unit weight 1.125 MT) | Nos | 5 | 5 | 10
1.5.3 | DC (Nominal unit weight 1.308 MT) | Nos | 20 | 20 | 40
1.5.4 | DD (Nominal unit weight 2.92 MT) | Nos | 16 | 16 | 32
1.5.5 | DD +18/25 (Nominal unit weight 2.92 MT) | Nos | 4 | 4 | 8
1.5.6 | TOTAL WEIGHT OF STUBS | MT | 104.835 | 104.835 | 209.67 | 99357.97 | 8942.2173 | 8942.2173 | 117242.4046 | 24582214.9725
1.6 | TEMPLATES
1.6.1 | DA (Nominal unit weight 1.524 MT) | Nos | 2 | 2 | 4
1.6.2 | DB (Nominal unit weight 3.441 MT) | Nos | 1 | 1 | 2
1.6.3 | DC (Nominal unit weight 3.693 MT) | Nos | 2 | 2 | 4
1.6.4 | DD (Nominal unit weight 3.889 MT) | Nos | 2 | 2 | 4
1.6.5 | DD +18/25 (Nominal unit weight 3.889 MT) | Nos | 1 | 1 | 2
1.7 | WEIGHT OF TEMPLATES FOR DA , DB , DC,DD | MT | 25.542 | 25.542 | 51.084 | 68942.26 | 6204.8034 | 6204.8034 | 81351.8668 | 4155778.7636
1.8 | Weight of different type G.I Nuts and Bolts | MT | 92 | 92 | 184 | 117049.77 | 10534.4793 | 10534.4793 | 138118.7286 | 25413846.0624
2 | Supply of the following tower accessories as per technical specification and as directed by the engineer in charge.
2.1 | EARTHING DEVICE | Nos. | 110 | 110 | 220 | 2251.91 | 202.6719 | 202.6719 | 2657.2538 | 584595.836
2.2 | DANGER BOARD | Nos. | 70 | 70 | 140 | 233.75 | 21.0375 | 21.0375 | 275.825 | 38615.5
2.3 | NUMBER PLATE | Nos. | 70 | 70 | 140 | 127.73 | 11.4957 | 11.4957 | 150.7214 | 21100.996
2.4 | PHASE PLATE | Nos. | 420 | 420 | 840 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 98753.256
2.5 | BIRD GUARD | Nos. | 150 | 150 | 300 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 35269.02
2.6 | ANTICLIMBING DEVICE | Nos. | 70 | 70 | 140 | 4344.16 | 390.9744 | 390.9744 | 5126.1088 | 717655.232
2.7 | CIRCUIT PLATE | Nos. | 140 | 140 | 280 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 32917.752
2.8 | COUNTERPOISE EARTHING | Nos. | 10 | 10 | 20 | 2251.91 | 202.6719 | 202.6719 | 2657.2538 | 53145.076
3 | Supply of following POWER CONDUCTORS in the proposed 400 KV lines as per the technical specification and as per the instruction of the engineer in charge.
3.1 | ACSR Moose (54+7/3.53/3.66 mm) | Kms. | 280 | 280 | 560 | 409923 | 36893.07 | 36893.07 | 483709.14 | 270877118.4
4 | POWER CONDUCTOR ACESSORIES
4.1 | For ACSR Moose
4.1.1 | VIBRATION DAMPER | Nos. | 3360 | 3360 | 6720 | 1067.73 | 96.0957 | 96.0957 | 1259.9214 | 8466671.808
4.1.2 | MID SPAN JOINT | Nos. | 50 | 50 | 100 | 1044.52 | 94.0068 | 94.0068 | 1232.5336 | 123253.36
4.1.3 | REPAIR SLEEVE | Nos. | 30 | 30 | 60 | 458.17 | 41.2353 | 41.2353 | 540.6406 | 32438.436
4.1.4 | PG CLAMP FOR ACSR MOOSE | Nos. | 50 | 50 | 100 | 500 | 45 | 45 | 590 | 59000
4.1.5 | BUNDLE SPACER ACSR MOOSE | Nos. | 3000 | 3000 | 6000 | 1746.85 | 157.2165 | 157.2165 | 2061.283 | 12367698
4.1.6 | RIGID SPACER ACSR MOOSE | Nos. | 1260 | 1260 | 2520 | 1746.85 | 157.2165 | 157.2165 | 2061.283 | 5194433.16
5 | Supply of the GI earth wire of size 7/3.66 mm as per the technical specification and as per the direction of Engineer in charge. | Kms. | 24 | 24 | 48 | 32346.93 | 2911.2237 | 2911.2237 | 38169.3774 | 1832130.1152
6 | EARTH CONDUCTOR ACESSORIES
6.1 | VIBRATION DAMPER | Nos. | 280 | 280 | 560 | 427 | 38.43 | 38.43 | 503.86 | 282161.6
6.2 | FLEXIBLE COPPER EARTH BOND | Nos. | 140 | 140 | 280 | 274.62 | 24.7158 | 24.7158 | 324.0516 | 90734.448
6.3 | SUSPENSION CLAMP | Nos. | 25 | 25 | 50 | 459.83 | 41.3847 | 41.3847 | 542.5994 | 27129.97
6.4 | TENSION CLAMP | Nos. | 45 | 45 | 90 | 555.06 | 49.9554 | 49.9554 | 654.9708 | 58947.372
6.5 | MID SPAN COMPRESSION JOINT | Nos. | 10 | 10 | 20 | 37.04 | 3.3336 | 3.3336 | 43.7072 | 874.144
6.6 | REPAIR SLEEVE | Nos. | 5 | 5 | 10 | 37.04 | 3.3336 | 3.3336 | 43.7072 | 437.072
7 | Supply of OPGW Fibre Optic Cable & Hard ware for Speech , data & protection
7.1 | 24 fibre (DWSM) OPGW fibre optic cable. | Km | 24 | 24 | 48 | 133002.8 | 11970.252 | 11970.252 | 156943.304 | 7533278.592
7.2 | OPGW hardware set like suspension Assembly,Tensin Assembly(Dead end assembly, Pass through assembly) ,Vibration Damper,Down Lead Clamp Assemblies for 24/48 Fibre(DWSM) OPGW,Joint Box | LOT | 1 | 1 | 2 | 500000 | 45000 | 45000 | 590000 | 1180000
8 | Supply of the following Anti fog type disc insulators as per the technical specification and as per the instruction of the Engineer in charge.
8.1 | 160KN Antifog Disc Insulator | Nos. | 24412.5 | 24412.5 | 48825 | 797.6 | 71.784 | 71.784 | 941.168 | 45952527.6
8.2 | 120 KN Antifog Disc Insulator | Nos. | 4000 | 4000 | 8000 | 710.86 | 63.9774 | 63.9774 | 838.8148 | 6710518.4
9 | Supply of the following hard ware fittings suitable for ACSR Moose conductors as per the technical specification.
9.1 | For ACSR Moose
9.1.1 | Double suspension Hardware fittings.(AGS type) suitable for 160 KN insulator. | Nos | 150 | 150 | 300 | 5208.46 | 468.7614 | 468.7614 | 6145.9828 | 1843794.84
9.1.2 | Double tension Hardware fittings suitable for 160 KN insulator. | Nos. | 540 | 540 | 1080 | 4992.49 | 449.3241 | 449.3241 | 5891.1382 | 6362429.256
9.1.3 | Single suspension Pilot Insulator Hard wares fittings suitable for 120 KN insulator. | Nos. | 160 | 160 | 320 | 3421.17 | 307.9053 | 307.9053 | 4036.9806 | 1291833.792
9.1.4 | “D” Shackle | Nos. | 200 | 200 | 400 | 99.63 | 8.9667 | 8.9667 | 117.5634 | 47025.36
9.1.5 | Hanger | Nos. | 50 | 50 | 100 | 99.6274 | 8.9665 | 8.9665 | 117.5603 | 11756.0332
9.1.6 | U'-Bolt. | Nos | 50 | 50 | 100 | 99.625 | 8.9663 | 8.9663 | 117.5575 | 11755.75
10 | High Resolution Binacular(NICON COOLPIX P900) | Nos | 1 | 1 | 2 | 50000 | 4500 | 4500 | 59000 | 118000
C | TOTAL -LINE | [8 empty] | 842577481.1271
| TOTAL SUPPLY (SUB_STATION + MRDL-MENDHASAL LILO LILE + MRDL-NEW DUBURI LILO LINE) (A+B+C) | [8 empty] | 3545689617.22 |  | 3545689617.22 | -1.7643e-05
-1.4952e-05
-3.4724e-08
1090690697.7788
2454998919.4412
Note on D25: Optcl: WAS 4
Note on B26: Optcl: WAS BEAM ISOLATOR
Note on D26: Optcl: WAS 4
Note on D27: Optcl: WAS 6
Note on D40: Optcl: WAS 6
Note on G131: OPTCL: Rates derived from approved estimate for Chhendipada Project
Note on G132: OPTCL: Rates derived from approved estimate for Chhendipada Project
Note on G267: OPTCL: Cost Data 2023-24
Note on G269: OPTCL: Price derived from Paradeep BoQ with cost escalation @5%
Note on G278: OPTCL: Price derived from Paradeep BoQ with cost escalation @5%
Note on G280: OPTCL: Price derived from Paradeep BoQ with cost escalation @5%

## N to W (hidden)
#REF!
#REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
1 | One
2 | Two
3 | Three
4 | Four
5 | Five
6 | Six
7 | Seven
8 | Eight
9 | Nine
10 | Ten
11 | Eleven
12 | Twelve
13 | Thirteen
14 | Fourteen
15 | Fifteen
16 | Sixteen
17 | Seventeen
18 | Eighteen
19 | Nineteen
20 | Twenty
21 | Twenty One
22 | Twenty Two
23 | Twenty Three
24 | Twenty Four
25 | Twenty Five
26 | Twenty Six
27 | Twenty Seven
28 | Twenty Eight
29 | Twenty Nine
30 | Thirty
31 | Thirty One
32 | Thirty Two
33 | Thirty Three
34 | Thirty Four
35 | Thirty Five
36 | Thirty Six
37 | Thirty Seven
38 | Thirty Eight
39 | Thirty Nine
40 | Forty
41 | Forty One
42 | Forty Two
43 | Forty Three
44 | Forty Four
45 | Forty Five
46 | Forty Six
47 | Forty Seven
48 | Forty Eight
49 | Forty Nine
50 | Fifty
51 | Fifty One
52 | Fifty Two
53 | Fifty Three
54 | Fifty Four
55 | Fifty Five
56 | Fifty Six
57 | Fifty Seven
58 | Fifty Eight
59 | Fifty Nine
60 | Sixty
61 | Sixty One
62 | Sixty Two
63 | Sixty Three
64 | Sixty Four
65 | Sixty Five
66 | Sixty Six
67 | Sixty Seven
68 | Sixty Eight
69 | Sixty Nine
70 | Seventy
71 | Seventy One
72 | Seventy Two
73 | Seventy Three
74 | Seventy Four
75 | Seventy Five
76 | Seventy Six
77 | Seventy Seven
78 | Seventy Eight
79 | Seventy Nine
80 | Eighty
81 | Eighty One
82 | Eighty Two
83 | Eighty Three
84 | Eighty Four
85 | Eighty Five
86 | Eighty Six
87 | Eighty Seven
88 | Eighty Eight
89 | Eighty Nine
90 | Ninety
91 | Ninety One
92 | Ninety Two
93 | Ninety Three
94 | Ninety Four
95 | Ninety Five
96 | Ninety Six
97 | Ninety Seven
98 | Ninety Eight
99 | Ninety Nine
100 | One Hundred

## TOWER-LINE ACCS CALC
Sl No | Description | UOM | Nos req per tower | Nos of Suspension Towers | Nos of AP Towers | Total Nos of Towers | Total Nos |  |  | Sl No | Description | UOM | Nos req per tower | Nos of Towers where CP earthing required | length required per earthing | Total Mtrs
2.1 | EARTHING DEVICE | Nos. | 2 | 57 | 213 | 270 | 540 |  |  | 2.8 | Counterpoise earth wire | mtrs | 2 | 81 | 50 | 8100
2.2 | DANGER BOARD | Nos. | 1 | 57 | 213 | 270 | 270
2.3 | NUMBER PLATE | Nos. | 2 | 57 | 213 | 270 | 540
2.4 | PHASE PLATE | Nos. | 6 | 57 | 213 | 270 | 1620
2.5 | BIRD GUARD | Nos. | 6 | 57 | 213 | 270 | 342
2.6 | ANTICLIMBING DEVICE | Nos. | 1 | 57 | 213 | 270 | 270
2.7 | CIRCUIT PLATE | Nos. | 2 | 57 | 213 | 270 | 540
[13 empty] | ACSR Moose length | Conductor length per drum | Line length/ conductor drum | Multiplying factor | Total
| Conductor Calc | [8 empty] | 4.2 | MID SPAN JOINT | Nos. | 1135.2247 | 1.8 | 630.6804 | 1.5 | 946.0206
| Line Route Length | No of conductor | No of phase per ckt | No of ckt | extra-1.5% | Total ACSR Moose required |  |  |  | 4.3 | REPAIR SLEEVE | Nos. | 1135.2247 | 1.8 | 630.6804 | 1 | 630.6804
| 93.204 | 2 | 3 | 2 | 1.015 | 1135.2247
|  | UOM | Nos req per tower | Nos of Suspension Towers | Nos of AP Towers | Total Nos of Towers | Total Nos
| Double suspension Hardware fittings.(AGS type) (2 x 120kN) | SET | 6 | 57 | 213 | 270 | 342
| Double tension Hardware fittings. (2 x 160kN) | SET | 12 | 57 | 213 | 270 | 2556 | plus 12 for dead end | 2568 | 5136 | 5392.8 |  |  | 160 kn insulators
| Single suspension Pilot Insulator Hardware fittings (1 x 120kN) | Nos. | 3 | 57 | 213 | 270 | 51 | 17 nos more than 45 degree
| “D” Shackle | Nos. | 12 | 57 | 213 | 270 | 2556 | plus 12 for dead end
| Hanger | Nos. | 6 | 57 | 213 | 270 | 342
| U'-Bolt. | Nos. | 12 | 57 | 213 | 270 | 57
| 160KN Silicon Polymer LR Insulator | Nos.(Single) | 24 | 57 | 213 | 270 | 5112
| 120 KN Silicon Polymer LR Insulator | Nos.(Single) | 12 | 57 | 213 | 270 | 684 |  | 684 | 51 | 735 | 771.75 |  | 120 kn insulators
| 120 KN Silicon Polymer LR Insulator for Pilot | Nos.(Single)

## Quad Moose FDN Data
Description |  |  | EXCAVATION (M3) | CONCRETE QTY. IN CUM. |  | TOTAL Reinforcement Steel In KG |  | Total Qty
Type of Tower | Type of Tower | Fdn Clasification
|  |  |  | PCC M10 (1:3:6) in M3 | RCC M20 (1:1.5:3) in M3 |  | Nos of Towers | Excavation | PCC | RCC | STEEL
DA Type | Normal Tower (+0 MTR.) | DRY | 125.16 | 1.45 | 14.35 | 1611.69
|  | WET | 248.14 | 3.06 | 25.16 | 2280.25 | 15 | 3722.1 | 45.9 | 377.4 | 34203.75
|  | PS | 310.58 | 3.89 | 30.73 | 2693.53 | 5 | 1552.9 | 19.45 | 153.65 | 13467.65 | Total Excavation
|  | FS | 368.44 | 4.67 | 35.91 | 3058.86 | [5 empty] | 169543.898
| With Extension (+3 MTR.) | DRY | 125.16 | 1.45 | 14.35 | 1611.69 | [5 empty] | Soft/Loose soil | 40% | 67817.5592
|  | WET | 248.14 | 3.06 | 25.16 | 2280.25 | 6 | 1488.84 | 18.36 | 150.96 | 13681.5 | Dense/Compact soil | 15% | 25431.5847
|  | PS | 310.58 | 3.89 | 30.73 | 2693.53 | 2 | 621.16 | 7.78 | 61.46 | 5387.06 | Partial Submerged soil | 10% | 16954.3898
|  | FS | 368.44 | 4.67 | 35.91 | 3058.86 | [5 empty] | Fully submerged soil | 5% | 8477.1949
| With Extension (+6 MTR.) | DRY | 131.09 | 1.52 | 14.88 | 1743.96 | [5 empty] | Soft/Disintegrated rock(Not requiring Blasting) | 15% | 25431.5847
|  | WET | 267.36 | 3.31 | 26.85 | 2507.7 | 10 | 2673.6 | 33.1 | 268.5 | 25077 | Hard Rock(Requiring Blasting/Using breaker machinery) | 15% | 25431.5847
|  | PS | 333.4 | 4.2 | 32.79 | 2955.58 | 3 | 1000.2 | 12.6 | 98.37 | 8866.74
|  | FS | 393.26 | 5 | 38.16 | 3411.48
| With Extension (+9 MTR.) | DRY | 131.09 | 1.52 | 14.88 | 1743.96
|  | WET | 267.36 | 3.31 | 26.85 | 2507.7 | 15 | 4010.4 | 49.65 | 402.75 | 37615.5
|  | PS | 333.4 | 4.2 | 32.79 | 2955.58 | 1 | 333.4 | 4.2 | 32.79 | 2955.58
|  | FS | 393.26 | 5 | 38.16 | 3411.48
| With Extension (+18,25 MTR.) | DRY
WET
PS
FS
DB Type | Normal Tower (+0 MTR.) | DRY | 302.71 | 3.78 | 46.32 | 3476.38
|  | WET | 562.74 | 7.3 | 70.96 | 6587.4 | 35 | 19695.9 | 255.5 | 2483.6 | 230559
|  | PS | 672.35 | 8.79 | 83.58 | 7648.68 | 5 | 3361.75 | 43.95 | 417.9 | 38243.4
|  | FS | 777.04 | 10.22 | 101.92 | 8184.33
| With Extension (+3 MTR.) | DRY | 302.71 | 3.78 | 46.32 | 3476.38
|  | WET | 562.74 | 7.3 | 70.96 | 6587.4 | 9 | 5064.66 | 65.7 | 638.64 | 59286.6
|  | PS | 672.35 | 8.79 | 83.58 | 7648.68 | 2 | 1344.7 | 17.58 | 167.16 | 15297.36
|  | FS | 777.04 | 10.22 | 101.92 | 8184.33
| With Extension (+6MTR.) | DRY | 302.71 | 3.78 | 46.32 | 3476.38
|  | WET | 562.74 | 7.3 | 70.96 | 6587.4 | 12 | 6752.88 | 87.6 | 851.52 | 79048.8
|  | PS | 672.35 | 8.79 | 83.58 | 7648.68 | 3 | 2017.05 | 26.37 | 250.74 | 22946.04
|  | FS | 777.04 | 10.22 | 101.92 | 8184.33
| With Extension (+9 MTR.) | DRY | 302.71 | 3.78 | 46.32 | 3476.38
|  | WET | 562.74 | 7.3 | 70.96 | 6587.4 | 20 | 11254.8 | 146 | 1419.2 | 131748
|  | PS | 672.35 | 8.79 | 83.58 | 764.68 | 4 | 2689.4 | 35.16 | 334.32 | 3058.72
|  | FS | 672.35 | 8.79 | 83.58 | 7648.68
| With Extension (+18MTR.) | DRY | 777.04 | 10.22 | 101.92 | 8184.33
WET
PS
FS
| With Extension (+25 MTR.) | DRY
WET
PS
FS
DC Type | Normal Tower (+0 MTR.) | DRY | 415.84 | 5.3 | 61.59 | 5770.04
|  | WET | 749.8 | 9.58 | 101.9 | 8959.38 | 20 | 14996 | 191.6 | 2038 | 179187.6
|  | PS | 862.71 | 11.4 | 119.19 | 10361.02 | 5 | 4313.55 | 57 | 595.95 | 51805.1
|  | FS | 994.91 | 13.22 | 136.27 | 11912.95
| With Extension (+3 MTR.) | DRY | 415.84 | 5.3 | 61.59 | 5770.04
|  | WET | 749.8 | 9.58 | 101.9 | 8959.38 | 3 | 2249.4 | 28.74 | 305.7 | 26878.14
|  | PS | 862.71 | 11.4 | 119.19 | 10361.02 | 1 | 862.71 | 11.4 | 119.19 | 10361.02
|  | FS | 994.91 | 13.22 | 136.27 | 11912.95
| With Extension (+6MTR.) | DRY | 415.84 | 5.3 | 61.59 | 5770.04
|  | WET | 749.8 | 9.58 | 101.9 | 8959.38 | 5 | 3749 | 47.9 | 509.5 | 44796.9
|  | PS | 862.71 | 11.4 | 119.19 | 10361.02 | 2 | 1725.42 | 22.8 | 238.38 | 20722.04
|  | FS | 994.91 | 13.22 | 136.27 | 11912.95
| Normal Tower (+9MTR.) | DRY | 415.84 | 5.3 | 61.59 | 5770.04
|  | WET | 749.8 | 9.58 | 101.9 | 8959.38 | 5 | 3749 | 47.9 | 509.5 | 44796.9
|  | PS | 862.71 | 11.4 | 119.19 | 10361.02
|  | FS | 994.91 | 13.22 | 136.27 | 11912.95
| With Extension (+18 MTR.) | DRY
WET
PS
FS
| With Extension (+25 MTR.) | DRY
WET
PS
FS
DD Type | Normal Tower (+0 MTR.) | DRY | 490.65 | 6.32 | 79.88 | 5997.76
|  | WET | 845.22 | 11.16 | 120.83 | 11044.68 | 30 | 25356.6 | 334.8 | 3624.9 | 331340.4
|  | PS | 994.91 | 13.22 | 136.27 | 13148.75 | 7 | 6964.37 | 92.54 | 953.89 | 92041.25
|  | FS | 1141.57 | 15.24 | 160.66 | 14488.45
| With Extension (+3 MTR.) | DRY | 490.65 | 6.32 | 79.88 | 5997.76
|  | WET | 845.22 | 11.16 | 120.83 | 11044.68 | 5 | 4226.1 | 55.8 | 604.15 | 55223.4
|  | PS | 994.91 | 13.22 | 136.27 | 13148.75
|  | FS | 1141.57 | 15.24 | 160.66 | 14488.45
| With Extension (+6 MTR.) | DRY | 490.65 | 6.32 | 79.88 | 5997.76
|  | WET | 845.22 | 11.16 | 120.83 | 11044.68 | 13 | 10987.86 | 145.08 | 1570.79 | 143580.84
|  | PS | 994.91 | 13.22 | 136.27 | 13148.75 | 2 | 1989.82 | 26.44 | 272.54 | 26297.5
|  | FS | 1141.57 | 15.24 | 160.66 | 14488.45
| With Extension (+9 MTR.) | DRY | 490.65 | 6.32 | 79.88 | 5997.76
|  | WET | 845.22 | 11.16 | 120.83 | 11044.68 | 15 | 12678.3 | 167.4 | 1812.45 | 165670.2
|  | PS | 994.91 | 13.22 | 136.27 | 13148.75 | 2 | 1989.82 | 26.44 | 272.54 | 26297.5
|  | FS | 1141.57 | 15.24 | 160.66 | 14488.45
| With Extension (+18 MTR.) | DRY
|  | WET | 765.276 | 11.724 | 113.016 | 10464 | 1 | 765.276 | 11.724 | 113.016 | 10464
PS
FS
| With Extension (+25 MTR.) | DRY
|  | WET | 765.276 | 11.724 | 113.016 | 10464 | 7 | 5356.932 | 82.068 | 791.112 | 73248
PS
FS
[7 empty] | 270 | 169543.898 | 2218.532 | 22440.568 | 2024153.49

## Tower Wt Data Quad Moose 400 kV
[6 empty] | For Supply |  |  |  | For Erection
Description of Tower (w/o N&Bs) | HT | MS | Total Weight | N&Bs | Total Weight | Nos of tower | Total weight of towers | Total Weight of N&Bs |  | Total weight of towers | Total Weight of N&Bs
DA Type Tower Body | 7004.15 | 8844.8 | 15848.95 | 792.4475 | 16641.3975 | 57 | 903390.15 | 45169.5075
+ 0 Extension of DA | 1280.38 | 2110.48 | 3390.86 | 169.543 | 3560.403 | 57 | 193279.02 | 9663.951
+3 Extension to DA | 482.43 | 1901.78 | 2384.21 | 119.2105 | 2503.4205 | 8 | 19073.68 | 953.684
+6 Extension to DA | 894.76 | 3055.4 | 3950.16 | 197.508 | 4147.668 | 13 | 51352.08 | 2567.604
+9 Extension to DA | 1496.48 | 3733.63 | 5230.11 | 261.5055 | 5491.6155 | 16 | 83681.76 | 4184.088
DB Type Tower Body | 15906.547 | 7456.79 | 23363.337 | 1168.1669 | 24531.5039 | 90 | 2102700.33 | 105135.0165
+ 0 Extension of DB | 2422.152 | 2636.86 | 5059.012 | 252.9506 | 5311.9626 | 90 | 455311.08 | 22765.554
+3 Extension to DB | 3177.72 | 3850.604 | 7028.324 | 351.4162 | 7379.7402 | 11 | 77311.564 | 3865.5782
+6 Extension to DB | 2058.48 | 3930.864 | 5989.344 | 299.4672 | 6288.8112 | 15 | 89840.16 | 4492.008
+9 Extension to DB | 2994.024 | 5011.008 | 8005.032 | 400.2516 | 8405.2836 | 24 | 192120.768 | 9606.0384
DC Type Tower Body | 19048.948 | 8920.749 | 27969.697 | 1398.4849 | 29368.1819 | 41 | 1146757.577 | 57337.8789
+ 0 Extension of DC | 3949.34 | 1876.83 | 5826.17 | 291.3085 | 6117.4785 | 41 | 238872.97 | 11943.6485
+3 Extension to DC | 3507.056 | 4890.128 | 8397.184 | 419.8592 | 8817.0432 | 4 | 33588.736 | 1679.4368
+6 Extension to DC | 1974.87 | 5557.34 | 7532.21 | 376.6105 | 7908.8205 | 7 | 52725.47 | 2636.2735
+9 Extension to DC | 3065.79 | 6559.48 | 9625.27 | 481.2635 | 10106.5335 | 5 | 48126.35 | 2406.3175
DD Type Tower Body | 23365.64 | 10550.14 | 33915.78 | 1695.789 | 35611.569 | 82 | 2781093.96 | 139054.698
+ 0 Extension of DD | 3825.01 | 4118.61 | 7943.62 | 397.181 | 8340.801 | 77 | 611658.74 | 30582.937
+3 Extension to DD | 6852.09 | 3663.49 | 10515.58 | 525.779 | 11041.359 | 5 | 52577.9 | 2628.895
+6 Extension to DD | 2906.88 | 6520.7 | 9427.58 | 471.379 | 9898.959 | 15 | 141413.7 | 7070.685
+9 Extension to DD | 4564.38 | 7970.52 | 12534.9 | 626.745 | 13161.645 | 17 | 213093.3 | 10654.665
+18 Extension to DD | 10121.42 | 17921.5 | 28042.92 | 1402.146 | 29445.066 | 1 | 28042.92 | 1402.146
+25 Extension to DD | 13708.98 | 21961.39 | 35670.37 | 1783.5185 | 37453.8885 | 7 | 249692.59 | 12484.6295
[7 empty] | 9765704.805 | 488285.2402 | KGS
[7 empty] | 9765.7048 | 488.2852 | MTs
STUBS
DA Type | 587.272 | 62.92 | 650.192 | 32.5096
DB Type | 1261.408 |  | 1261.408 | 63.0704
DC Type | 1480.256 |  | 1480.256 | 74.0128
DD Type | 1705.936 | 271.392 | 1977.328 | 98.8664
DD +18/25 Type | 1883.744 | 299.072 | 2182.816 | 109.1408
TEMPLATES
DA Type |  | 1649.864 | 1649.864 | 82.4932
DB Type |  | 2178.796 | 2178.796 | 108.9398
DC Type |  | 2189.896 | 2189.896 | 109.4948
DD Type |  | 2335.228 | 2335.228 | 116.7614
DD +18/25 Type |  | 2335.228 | 2335.228 | 116.7614
Note on G22: Admin: For DD + 3 Extension type tower, +0 part is not added.

## Tower schedule
Client :
Contractor :
Project:
Details SurveyTower Schedule
Sl. No. | AP-NO | Type of Tower | Angle of Deviation | Span Length (m) | Section Length (m) | Cumulative chanage (m) | Reduced Level (m) | Wind Span (m) | Weight Span Cold (m) |  |  | Weight Span Hot(m) |  |  | GPS EAST | GPS NORTH | Crossing Details
[9 empty] | Left | Right | Total | Left | Right | Total
1 | GANTRY | GANTRY | 0°00'00" |  | 150 | 0 | 245.1 | 35 | 0 | -10 | -10 | 0 | 10 | 10 | 756188.33 | 2137765.94
70
2 | DE | DD+0 | 0°00'00" |  |  | 70 | 243.62 | 110 | 80 | 57 | 137 | 60 | 68 | 129 | 756400.01 | 2137706.92
150
3 | AP-1 | DD+6 | 58°36'15"RT |  | 409 | 150 | 238.6 | 279.5 | 93 | 164 | 257 | 81 | 175 | 256 | 756400.01 | 2137706.92
409
4 | AP-2 | DD+9 | 43°51'49"RT |  |  | 559 | 243.8 | 405 | 246 | 234 | 480 | 235 | 225 | 460 | 756511.38 | 2137313.78
401
5 | 2/1 | DA+9 |  |  | 394 | 960 | 237.467 | 397.5 | 168 | 179 | 347 | 177 | 185 | 362 | 756322.762 | 2136959.744
394
6 | 2/2 | DA+9 |  |  | 394 | 1354 | 240.858 | 394 | 215 | 251 | 466 | 211 | 237 | 448 | 756137.503 | 2136612.016
394
7 | 2/3 | DA+9 |  |  | 387 | 1748 | 230.627 | 390.5 | 143 | 204 | 347 | 158 | 201 | 359 | 755952.245 | 2136264.287
387
8 | AP-3 | DD+0 | 30°52'37"RT |  | 386 | 2135 | 237.82 | 386.5 | 184 | 193 | 377 | 187 | 193 | 380 | 755770.11 | 2135922.42
386
9 | 3/1 | DA+0 |  |  | 378 | 2521 | 237.86 | 382 | 193 | 135 | 328 | 194 | 151 | 345 | 755439.762 | 2135723.331
378
10 | 3/2 | DA+0 |  |  | #REF! | 2899 | 247.533 | 378 | 243 | 207 | 450 | 228 | 202 | 430 | 755116.011 | 2135528.218
378
11 | 3/3 | DA+0 |  |  |  | 3277 | 244.366 | 375 | 172 | 180 | 352 | 177 | 182 | 359 | 754792.259 | 2135333.105
372
12 | AP-4 | DD+0 | 30°41'53"RT |  |  | 3649 | 245.43 | 376.5 | 192 | 120 | 312 | 191 | 140 | 331 | 754473.4 | 2135140.94
381
13 | AP-5 | DD+18 | 50°54'00"RT |  |  | 4030 | 240.31 | 334.5 | 262 | 47 | 309 | 242 | 86 | 328 | 754092.72 | 2135138.43
288
14 | AP-6 | DD+25 | 4°08'49"RT |  |  | 4318 | 245.63 | 342 | 242 | 186 | 428 | 203 | 190 | 393 | 753909.54 | 2135360.82
396
15 | AP-7 | DD+25 | 0°00'41"RT |  |  | 4714 | 248 | 350.5 | 211 | 336 | 547 | 208 | 267 | 475 | 753680.49 | 2135683.95
305
16 | AP-8 | DD+6 | 31°58'26"LT |  |  | 5019 | 242.08 | 350 | -30 | 153 | 123 | 40 | 166 | 206 | 753504.16 | 2135932.81
395
17 | AP-9 | DD+9 | 41°56'10"LT |  |  | 5414 | 247.55 | 318 | 243 | 57 | 300 | 231 | 88 | 319 | 753139.45 | 2136085.42
241
18 | AP-10 | DD+9 | 5°42'57"RT |  |  | 5655 | 253.87 | 302.5 | 184 | 237 | 421 | 154 | 221 | 375 | 752911.71 | 2136005.98
364
19 | 10/1 | DA+0 |  |  |  | 6019 | 253.468 | 360.5 | 127 | 168 | 295 | 145 | 171 | 316 | 752557.511 | 2135920.853
357
20 | AP-11 | DD+0 | 44°33'52"RT |  |  | 6376 | 255.34 | 355 | 190 | 119 | 309 | 187 | 138 | 325 | 752210.44 | 2135837.44
353
21 | AP-12 | DC+0 | 23°03'39"RT |  |  | 6729 | 264.82 | 370 | 234 | 230 | 464 | 216 | 220 | 436 | 751908.36 | 2136019.31
387
22 | 12/1 | DA+0 |  |  |  | 7116 | 258.117 | 384 | 157 | 192 | 349 | 168 | 192 | 360 | 751681.626 | 2136332.662
381
23 | 12/2 | DA+0 |  |  |  | 7497 | 257.861 | 381 | 189 | 171 | 360 | 190 | 177 | 367 | 751458.163 | 2136641.491
381
24 | AP-12A | DB+0 | 0°38'55"RT |  |  | 7878 | 261.527 | 345.5 | 211 | 166 | 377 | 206 | 162 | 368 | 751234.701 | 2136950.322
310
25 | 12A/0 | DA+3 |  |  |  | 8188 | 256.975 | 308 | 144 | 111 | 255 | 148 | 127 | 275 | 751055.721 | 2137203.666
306
26 | AP-12B | DB+0 | 11°38'03"LT |  |  | 8494 | 265.73 | 355 | 195 | 198 | 393 | 179 | 200 | 379 | 750879.44 | 2137453.19
404
27 | 12B/1 | DA+9 |  |  |  | 8898 | 257.55 | 397 | 207 | 215 | 422 | 206 | 210 | 416 | 750584.454 | 2137729.483
390
28 | 12B/2 | DA+0 |  |  |  | 9288 | 262.886 | 390 | 176 | 166 | 342 | 181 | 175 | 356 | 750299.811 | 2137996.088
390
29 | 12B/3 | DA+6 |  |  |  | 9678 | 262.302 | 383.5 | 224 | 186 | 410 | 216 | 187 | 403 | 750015.168 | 2138262.694
377
30 | AP-12C | DC+6 | 25°41'51"RT |  |  | 10055 | 262.85 | 353 | 192 | 133 | 325 | 191 | 143 | 334 | 749740.24 | 2138520.2
329
31 | 12C/1 | DA+9 |  |  |  | 10384 | 264.794 | 363.5 | 197 | 170 | 367 | 187 | 179 | 366 | 749621.222 | 2138827.417
398
32 | 12C/2 | DA+6 |  |  |  | 10782 | 273.38 | 400.5 | 229 | 196 | 425 | 221 | 198 | 419 | 749477.443 | 2139198.549
403
33 | 12C/3 | DA+3 |  |  |  | 11185 | 277.61 | 387.5 | 208 | 186 | 394 | 207 | 186 | 393 | 749331.704 | 2139574.741
372
34 | 12C/4 | DA+0 |  |  |  | 11557 | 280.647 | 372 | 186 | 203 | 389 | 187 | 198 | 385 | 749197.321 | 2139921.62
372
35 | 12C/5 | DA+0 |  |  |  | 11929 | 277.712 | 372 | 170 | 184 | 354 | 175 | 185 | 360 | 749062.937 | 2140268.499
372
36 | 12C/6 | DA+0 |  |  |  | 12301 | 278.044 | 372 | 188 | 162 | 350 | 188 | 169 | 357 | 748928.554 | 2140615.378
372
37 | 12C/7 | DB+0 |  |  |  | 12673 | 282.32 | 363.5 | 210 | 15 | 225 | 204 | 67 | 271 | 748794.171 | 2140962.257
355
38 | AP-13 | DD+25 | 44°17'37"RT |  |  | 13028 | 284.49 | 299 | 342 | 139 | 481 | 291 | 131 | 422 | 748665.76 | 2141293.72
243
39 | AP-14 | DD+25 | 0°00'02"RT |  |  | 13271 | 282.75 | 224 | 104 | 96 | 200 | 113 | 99 | 212 | 748761.19 | 2141517.27
205
40 | AP-15 | DD+25 | 23°16'31"LT |  |  | 13476 | 283.3 | 335.5 | 109 | 411 | 520 | 106 | 376 | 482 | 748841.63 | 2141705.7
466
41 | 15/1 | DB+9 |  |  |  | 13942 | 255.206 | 415.5 | 58 | 183 | 241 | 94 | 183 | 277 | 748840.347 | 2142171.735
365
42 | 15/2 | DA+9 |  |  |  | 14307 | 255.088 | 366.5 | 182 | 107 | 289 | 182 | 131 | 313 | 748839.343 | 2142536.674
368
43 | AP-16 | DD+9 | 38°39'10"LT |  |  | 14675 | 268.43 | 391 | 261 | 136 | 397 | 238 | 155 | 393 | 748838.33 | 2142904.63
414
44 | AP-17 | DC+6 | 20°32'33"RT |  |  | 15089 | 286 | 402 | 279 | 291 | 570 | 261 | 265 | 526 | 748578.67 | 2143227.46
390
45 | 17/1 | DA+9 |  |  |  | 15479 | 265.149 | 398.5 | 101 | 164 | 265 | 127 | 175 | 302 | 748456.346 | 2143598.03
407
46 | AP-18 | DB+9 | 0°00'17"LT |  |  | 15886 | 273.09 | 407 | 245 | 16 | 261 | 234 | 66 | 300 | 748328.67 | 2143984.81
407
47 | AP-19 | DB+6 | 9°56'36"RT |  |  | 16293 | 313.12 | 394 | 393 | 112 | 505 | 343 | 135 | 478 | 748201.14 | 2144371.04
381
48 | AP-20 | DB+9 | 1°55'44"RT |  |  | 16674 | 324.44 | 366 | 270 | 288 | 558 | 247 | 252 | 499 | 748145.95 | 2144747.99
351
49 | AP-21 | DB+0 | 14°24'12"LT |  |  | 17025 | 315.08 | 355.5 | 63 | 228 | 291 | 100 | 213 | 313 | 748106.87 | 2145096.36
360
50 | 21/1 | DA+0 |  |  |  | 17385 | 307.008 | 355.5 | 132 | 146 | 278 | 148 | 155 | 303 | 747979.001 | 2145432.909
351
51 | 21/2 | DA+9 |  |  |  | 17736 | 302.943 | 346.5 | 206 | 165 | 371 | 196 | 167 | 363 | 747854.335 | 2145761.025
342
52 | AP-22 | DB+6 | 10°20'44"RT |  |  | 18078 | 306.9 | 347.5 | 177 | 283 | 460 | 176 | 249 | 425 | 747732.85 | 2146080.77
353
53 | AP-23 | DD+0 | 52°47'51"LT |  |  | 18431 | 295.48 | 371.5 | 71 | 140 | 211 | 105 | 156 | 261 | 747668.74 | 2146428.08
390
54 | 23/1 | DA+9 |  |  |  | 18821 | 296.92 | 392.5 | 251 | 207 | 458 | 236 | 205 | 441 | 747320.017 | 2146603.806
395
55 | AP-24 | DD+0 | 50°11'22"LT |  |  | 19216 | 304.12 | 381 | 188 | 233 | 421 | 191 | 219 | 410 | 746967.19 | 2146781.6
367
56 | AP-25 | DD+0 | 34°35'56"RT |  |  | 19583 | 295.54 | 368.5 | 134 | 136 | 270 | 150 | 151 | 301 | 746630.12 | 2146635.42
370
57 | AP-26 | DB+0 | 2°16'06"RT |  |  | 19953 | 304.15 | 354.5 | 235 | 77 | 312 | 220 | 108 | 328 | 746266.92 | 2146707.03
339
58 | AP-27 | DB+0 | 5°14'02"RT |  |  | 20292 | 318.59 | 333 | 262 | 134 | 396 | 231 | 145 | 376 | 745937.51 | 2146785.64
327
59 | AP-27A | DB+0 | 8°23'55"RT |  |  | 20619 | 323.05 | 320 | 194 | 182 | 376 | 183 | 173 | 356 | 745627.34 | 2146890.36
313
60 | 27A/1 | DA+0 |  |  |  | 20932 | 319.429 | 312.5 | 131 | 186 | 317 | 140 | 175 | 315 | 745349.023 | 2147032.502
312
61 | AP-27B | DB+0 | 9°29'57"LT |  |  | 21244 | 315.23 | 327 | 126 | 159 | 285 | 137 | 164 | 301 | 745071.4 | 2147174.29
342
62 | AP-28 | DD+3 | 29°31'46"LT |  |  | 21586 | 314.11 | 361.5 | 183 | 131 | 314 | 180 | 148 | 328 | 744745 | 2147277.55
381
63 | AP-29 | DC+6 | 29°31'46"LT |  |  | 21967 | 321.96 | 396 | 250 | 221 | 471 | 233 | 217 | 450 | 744372.74 | 2147198.6
411
64 | 29/1 | DA+0 |  |  |  | 22378 | 324.857 | 393.5 | 190 | 146 | 336 | 194 | 157 | 351 | 743979.544 | 2147316.668
376
65 | 29/2 | DA+6 |  |  |  | 22754 | 326.524 | 394 | 230 | 198 | 428 | 219 | 201 | 420 | 743619.76 | 2147424.703
412
66 | AP-30 | DB+9 | 6°47'16"LT |  |  | 23166 | 325.17 | 392 | 215 | 195 | 410 | 213 | 192 | 405 | 743224.77 | 2147543.31
372
67 | AP-31 | DB+6 | 1°18'45"LT |  |  | 23538 | 326.64 | 384.5 | 177 | 209 | 386 | 180 | 207 | 387 | 742858.82 | 2147607.35
397
68 | 31/1 | DA+3 |  |  |  | 23935 | 327.686 | 393.5 | 189 | 177 | 366 | 192 | 182 | 374 | 742466.019 | 2147666.85
390
69 | 31/2 | DA+3 |  |  |  | 24325 | 331.123 | 386.5 | 214 | 156 | 370 | 209 | 166 | 375 | 742080.418 | 2147725.26
383
70 | AP-32 | DD+3 | 39°05'06"LT |  |  | 24708 | 337.74 | 382 | 228 | 155 | 383 | 218 | 166 | 384 | 741701.75 | 2147782.62
381
71 | 32/1 | DA+3 |  |  |  | 25089 | 344.157 | 372.5 | 227 | 180 | 407 | 216 | 181 | 397 | 741373.086 | 2147589.244
364
72 | 32/2 | DA+3 |  |  |  | 25453 | 344.532 | 356 | 184 | 162 | 346 | 184 | 166 | 350 | 741059.361 | 2147404.657
348
73 | AP-33 | DB+0 | 0°43'00"RT |  |  | 25801 | 349.55 | 364.5 | 186 | 157 | 343 | 183 | 167 | 350 | 740759.76 | 2147228.38
381
74 | AP-34 | DB+0 | 4°13'56"RT |  |  | 26182 | 355.57 | 334 | 224 | 59 | 283 | 215 | 91 | 306 | 740429.16 | 2147039.39
287
75 | 34/1 | DA+0 |  |  |  | 26469 | 366.488 | 303.5 | 228 | 105 | 333 | 197 | 126 | 323 | 740170.294 | 2146915.792
320
76 | 34/2 | DA+0 |  |  |  | 26789 | 374.513 | 319.5 | 216 | 118 | 334 | 196 | 134 | 330 | 739881.149 | 2146777.737
319
77 | 34/3 | DB+0 |  |  |  | 27108 | 380.498 | 299.5 | 201 | -9 | 192 | 186 | 53 | 239 | 739593.091 | 2146640.201
280
78 | AP-35 | DB+0 | 9°17'42"LT |  |  | 27388 | 398.68 | 351 | 290 | 186 | 476 | 228 | 193 | 421 | 739340.67 | 2146519.68
422
79 | 35/1 | DA+9 |  |  |  | 27810 | 394.896 | 393 | 237 | 258 | 495 | 231 | 238 | 469 | 738994.042 | 2146278.61
364
80 | AP-36 | DD+9 | 30°08'13"RT |  |  | 28174 | 381.65 | 348.5 | 107 | 177 | 284 | 128 | 174 | 302 | 738694.82 | 2146070.51
333
81 | 36/1 | DA+0 |  |  |  | 28507 | 389.059 | 334 | 156 | 86 | 242 | 160 | 114 | 274 | 738362.576 | 2146043.309
335
82 | AP-37 | DD+9 | 30°22'57"LT |  |  | 28842 | 392.6 | 369.5 | 249 | 179 | 428 | 222 | 186 | 408 | 738028.9 | 2146015.99
404
83 | 37/1 | DA+6 |  |  |  | 29246 | 400.026 | 394 | 225 | 154 | 379 | 219 | 165 | 384 | 737698.307 | 2145783.964
384
84 | 37/2 | DA+6 |  |  |  | 29630 | 407.015 | 373.5 | 230 | 148 | 378 | 220 | 158 | 378 | 737383.995 | 2145563.365
363
85 | AP-38 | DC+6 | 18°35'14"LT |  |  | 29993 | 412.88 | 385 | 216 | 105 | 321 | 206 | 131 | 337 | 737087.03 | 2145354.94
407
86 | 38/1 | DB+9 |  |  |  | 30400 | 429.487 | 379 | 304 | 42 | 346 | 278 | 85 | 363 | 736845.742 | 2145027.062
351
87 | AP-39 | DB+9 | 9°58'13"RT |  |  | 30751 | 451.42 | 374.5 | 310 | 289 | 599 | 267 | 264 | 531 | 736637.81 | 2144744.51
398
88 | 39/1 | DA+9 |  |  |  | 31149 | 434.346 | 380.5 | 109 | 196 | 305 | 135 | 192 | 327 | 736350.058 | 2144469.718
363
89 | AP-40 | DB+3 | 8°17'53"RT |  |  | 31512 | 438 | 377 | 168 | 201 | 369 | 173 | 200 | 373 | 736087.19 | 2144218.69
391
90 | AP-40A | DB+6 | 12°35'10"LT |  |  | 31903 | 434.06 | 349.5 | 191 | 145 | 336 | 192 | 149 | 341 | 735768.39 | 2143992.28
308
91 | 40A/1 | DA+3 |  |  |  | 32211 | 438.253 | 328.5 | 162 | 104 | 266 | 160 | 129 | 289 | 735562.45 | 2143763.816
349
92 | AP-41 | DD+3 | 46°36'04"RT |  |  | 32560 | 449.48 | 359.5 | 245 | 126 | 371 | 221 | 144 | 365 | 735328.89 | 2143504.71
370
93 | AP-42 | DB+0 | 9°50'35"RT |  |  | 32930 | 462.95 | 353 | 245 | 211 | 456 | 228 | 197 | 425 | 734958.88 | 2143495.88
336
94 | AP-42A | DC+3 | 18°24'36"RT |  |  | 33266 | 453.36 | 370 | 125 | 167 | 292 | 140 | 177 | 317 | 734626.78 | 2143545.37
404
95 | 42A/1 | DA+6 |  |  |  | 33670 | 457.104 | 401 | 237 | 137 | 374 | 228 | 154 | 382 | 734266.782 | 2143727.896
398
96 | 42A/2 | DB+3 |  |  |  | 34068 | 472.026 | 396 | 262 | 40 | 302 | 245 | 84 | 329 | 733911.802 | 2143907.878
394
97 | AP-43 | DC+9 | 15°29'34"LT |  |  | 34462 | 495.78 | 386 | 355 | -46 | 309 | 312 | 24 | 336 | 733560.59 | 2144085.95
378
98 | AP-44 | DD+9 | 2°42'11"LT |  |  | 34840 | 538.28 | 374 | 427 | 130 | 557 | 358 | 147 | 505 | 733189.74 | 2144160.68
370
99 | AP-45 | DB+0 | 10°43'45"RT |  |  | 35210 | 556.91 | 294 | 240 | -80 | 160 | 224 | 17 | 241 | 732824.01 | 2144216.58
218
100 | AP-46 | DB+0 | 0°00'36"LT |  |  | 35428 | 573.53 | 178.5 | 299 | 198 | 497 | 202 | 114 | 316 | 732617.96 | 2144289.22
139
101 | AP-47 | DD+0 | 17°12'32"RT |  |  | 35567 | 567.15 | 267 | -60 | 481 | 421 | 25 | 403 | 428 | 732487.29 | 2144335.26
395
102 | AP-48 | DC+9 | 15°05'28"RT |  |  | 35962 | 504.82 | 358.5 | -82 | 356 | 274 | -4 | 287 | 283 | 732170.17 | 2144570.93
322
103 | AP-49 | DD+9 | 22°36'41"LT |  |  | 36284 | 476.33 | 310.5 | -32 | 25 | -7 | 37 | 73 | 110 | 731970.35 | 2144824.03
299
104 | AP-50 | DC+0 | 16°10'02"RT |  |  | 36583 | 502 | 298 | 275 | -158 | 117 | 227 | -37 | 190 | 731708.77 | 2144969.61
297
105 | AP-51 | DD+0 | 3°17'49"LT |  |  | 36880 | 542.44 | 309 | 458 | -408 | 50 | 337 | -196 | 141 | 731499.95 | 2145180.37
321
106 | AP-52 | DD+9 | 34°08'59"LT |  |  | 37201 | 616.53 | 359 | 741 | -45 | 696 | 529 | 23 | 552 | 731261.01 | 2145395.27
397
107 | AP-53 | DD+9 | 3°38'33"LT |  |  | 37598 | 663.12 | 448.5 | 445 | 301 | 746 | 378 | 293 | 671 | 730867.95 | 2145449.24
500
108 | AP-54 | DC+0 | 19°11'38"LT |  |  | 38098 | 658.2 | 431.5 | 201 | 128 | 329 | 210 | 142 | 352 | 730369.11 | 2145485.66
363
109 | 54/1 | DB+6 |  |  |  | 38461 | 663.163 | 300 | 235 | -95 | 140 | 222 | -2 | 220 | 730018.456 | 2145391.583
237
110 | AP-55 | DB+9 | 1°35'36"RT |  |  | 38698 | 685.22 | 286.5 | 334 | -69 | 265 | 240 | 12 | 252 | 729789.7 | 2145330.21
336
111 | AP-56 | DD+0 | 8°30'59"RT |  |  | 39034 | 730.97 | 368 | 407 | 371 | 778 | 326 | 325 | 651 | 729462.753 | 2145252.171
400
112 | AP-57 | DD+9 | 37°49'19"RT |  |  | 39434 | 689.31 | 304 | 32 | 55 | 87 | 78 | 81 | 159 | 729063.8 | 2145217.91
208
113 | AP-58 | DB+6 | 0°25'45"RT |  |  | 39642 | 696.35 | 273.5 | 153 | 124 | 277 | 127 | 139 | 266 | 728889.59 | 2145330.67
339
114 | AP-59 | DB+6 | 6°46'08"RT |  |  | 39981 | 703.56 | 356.5 | 216 | 137 | 353 | 201 | 152 | 353 | 728606.1 | 2145517.19
374
115 | AP-60 | DB+3 | 8°45'49"RT |  |  | 40355 | 715.44 | 367.5 | 237 | 317 | 554 | 223 | 275 | 498 | 728319.9 | 2145758.29
361
116 | AP-61 | DD+0 | 38°37'22"LT |  |  | 40716 | 695.34 | 290.5 | 45 | 151 | 196 | 87 | 131 | 218 | 728082.62 | 2146030.05
220
117 | 61/1 | DB+0 |  |  |  | 40936 | 691.312 | 251.5 | 69 | 212 | 281 | 89 | 186 | 275 | 727866.233 | 2146069.188
283
118 | AP-62 | DD+0 | 35°22'04"RT |  |  | 41219 | 681.44 | 311 | 71 | 129 | 200 | 98 | 142 | 240 | 727587.9 | 2146119.53
339
119 | 62/1 | DA+9 |  |  |  | 41558 | 678.871 | 350 | 210 | 346 | 556 | 197 | 294 | 491 | 727351.073 | 2146361.539
361
120 | AP-63 | DC+9 | 25°51'05"RT |  |  | 41919 | 651.1 | 360 | 16 | 286 | 302 | 69 | 254 | 323 | 727098.84 | 2146619.29
359
121 | AP-64 | DD+0 | 26°55'03"LT |  |  | 42278 | 642.21 | 364.5 | 74 | 183 | 257 | 107 | 184 | 291 | 726984.6 | 2146960.15
370
122 | AP-65 | DD+0 | 51°18'27"LT |  |  | 42648 | 642.66 | 319 | 188 | 61 | 249 | 188 | 82 | 270 | 726720.65 | 2147220.02
268
123 | 65/1 | DA+0 |  |  |  | 42916 | 652 | 359 | 207 | 150 | 357 | 187 | 172 | 359 | 726454.887 | 2147188.547
450
124 | AP-66 | DB+0 | 5°20'43"LT |  |  | 43366 | 668.18 | 404.5 | 301 | 180 | 481 | 280 | 180 | 460 | 726008.12 | 2147135.64
359
125 | AP-67 | DB+3 | 9°04'54"RT |  |  | 43725 | 665.13 | 349 | 179 | 133 | 312 | 180 | 146 | 326 | 725657.13 | 2147060.4
339
126 | AP-68 | DD+0 | 47°25'26"LT |  |  | 44064 | 673.86 | 320.5 | 206 | 77 | 283 | 195 | 106 | 301 | 725318.11 | 2147042.53
302
127 | AP-69 | DC+0 | 17°49'43"RT |  |  | 44366 | 683.84 | 301 | 225 | -40 | 185 | 197 | 33 | 230 | 725125.48 | 2146809.34
300
128 | AP-70 | DD+0 | 34°02'01"RT |  |  | 44666 | 709.39 | 278 | 342 | 183 | 525 | 269 | 159 | 428 | 724872.43 | 2146647.43
256
129 | 70/1 | DB+3 |  |  |  | 44922 | 700.445 | 299.5 | 73 | 25 | 98 | 98 | 74 | 172 | 724616.185 | 2146653.787
343
130 | AP-71 | DD+0 | 14°19'48"RT |  |  | 45265 | 726.73 | 402 | 319 | -61 | 258 | 270 | 0 | 270 | 724273.42 | 2146662.29
461
131 | 71/1 | DD+6 |  |  |  | 45726 | 792.903 | 379.5 | 529 | -472 | 57 | 469 | -220 | 249 | 723829.76 | 2146787.424
298
132 | AP-72 | DD+0 | 21°26'52"LT |  |  | 46024 | 880.71 | 299.5 | 781 | 384 | 1165 | 529 | 295 | 824 | 723543.37 | 2146868.2
301
133 | AP-73 | DC+6 | 27°47'46"LT |  |  | 46325 | 843.59 | 300 | -80 | 255 | 175 | 9 | 215 | 224 | 723243.43 | 2146838.28
299
134 | AP-74 | DB+0 | 7°44'53"RT |  |  | 46624 | 835.56 | 299.5 | 44 | 170 | 214 | 85 | 163 | 248 | 722994.3 | 2146673.43
300
135 | AP-75 | DC+9 | 19°35'26"RT |  |  | 46924 | 823.86 | 313 | 130 | -19 | 111 | 138 | 46 | 184 | 722724.49 | 2146543.32
326
136 | 75/1 | DB+6 |  |  |  | 47250 | 853.894 | 317.5 | 346 | -17 | 329 | 282 | 48 | 330 | 722400.671 | 2146508.404
309
137 | AP-76 | DB+0 | 1°59'33"RT |  |  | 47559 | 883.73 | 321.5 | 327 | 44 | 371 | 263 | 87 | 350 | 722093.38 | 2146475.27
334
138 | 76/1 | DB+9 |  |  |  | 47893 | 893.561 | 341.5 | 290 | 50 | 340 | 248 | 91 | 339 | 721760.61 | 2146451.057
349
139 | AP-77 | DD+0 | 30°32'24"RT |  |  | 48242 | 922.87 | 297.5 | 300 | 354 | 654 | 260 | 246 | 506 | 721412.52 | 2146425.73
246
140 | AP-78 | DB+3 | 0°10'15"LT |  |  | 48488 | 896.35 | 247.5 | -107 | 383 | 276 | 1 | 264 | 265 | 721192.45 | 2146534.87
249
141 | AP-79 | DD+6 | 45°14'09"LT |  |  | 48737 | 866.54 | 285 | -133 | 168 | 35 | -13 | 166 | 153 | 720969.4 | 2146644.66
321
142 | AP-80 | DC+0 | 24°31'56"LT |  |  | 49058 | 871.48 | 321 | 154 | 202 | 356 | 156 | 187 | 343 | 720665.5 | 2146539.85
321
143 | AP-81 | DB+0 | 11°10'24"LT |  |  | 49379 | 865.52 | 322 | 120 | 186 | 306 | 135 | 178 | 313 | 720432.72 | 2146318.48
323
144 | AP-82 | DC+0 | 22°39'04"LT |  |  | 49702 | 861.9 | 329.5 | 137 | 172 | 309 | 146 | 171 | 317 | 720246.48 | 2146055.11
336
145 | 82/1 | DB+0 |  |  |  | 50038 | 861.351 | 331 | 165 | -10 | 155 | 166 | 51 | 217 | 720173.144 | 2145727.417
326
146 | AP-83 | DD+25 | 5°19'14"RT |  |  | 50364 | 862.11 | 278 | 337 | 145 | 482 | 276 | 131 | 407 | 720101.97 | 2145409.38
230
147 | AP-84 | DD+25 | 7°05'59"RT |  |  | 50594 | 859.27 | 310 | 85 | 197 | 282 | 100 | 196 | 296 | 720031.08 | 2145190.36
390
148 | AP-85 | DD+6 | 41°03'19"RT |  |  | 50984 | 877.98 | 390 | 193 | 339 | 532 | 194 | 299 | 493 | 719866.25 | 2144837.44
390
149 | AP-86 | DB+3 | 2°24'03"LT |  |  | 51374 | 854.16 | 369 | 52 | 129 | 181 | 92 | 144 | 236 | 719510.03 | 2144679.51
348
150 | 86/1 | DB+6 |  |  |  | 51722 | 858.501 | 351 | 219 | 113 | 332 | 205 | 134 | 339 | 719198.435 | 2144525.436
354
151 | AP-87 | DC+0 | 16°12'03"LT |  |  | 52076 | 875.08 | 327 | 241 | 346 | 587 | 221 | 270 | 491 | 718881.09 | 2144368.52
300
152 | AP-88 | DB+6 | 8°48'39"LT |  |  | 52376 | 843.12 | 298.5 | -45 | 145 | 100 | 31 | 146 | 177 | 718660.19 | 2144166.02
297
153 | AP-89 | DD+0 | 36°55'50"LT |  |  | 52673 | 849.61 | 298.5 | 152 | 169 | 321 | 151 | 162 | 313 | 718474.84 | 2143934.48
300
154 | AP-90 | DC+0 | 25°51'35"LT |  |  | 52973 | 847.14 | 299.5 | 132 | 109 | 241 | 139 | 125 | 264 | 718465.7 | 2143634.82
299
155 | AP-91 | DD+0 | 34°42'22"RT |  |  | 53272 | 852.57 | 361 | 191 | 202 | 393 | 175 | 204 | 379 | 718587.95 | 2143361.69
423
156 | AP-92 | DC+0 | 25°37'45"RT |  |  | 53695 | 854.7 | 377.5 | 222 | 276 | 498 | 220 | 239 | 459 | 718510.27 | 2142946.34
332
157 | AP-93 | DD+0 | 49°10'56"RT |  |  | 54027 | 838 | 346 | 57 | 163 | 220 | 95 | 169 | 264 | 718314.05 | 2142678.46
360
158 | AP-94 | DB+0 | 12°19'53"RT |  |  | 54387 | 840.86 | 333 | 197 | 198 | 395 | 192 | 181 | 373 | 717955.1 | 2142649.61
306
159 | AP-95 | DC+0 | 23°45'48"LT |  |  | 54693 | 834.65 | 330.5 | 108 | 193 | 301 | 125 | 189 | 314 | 717652.19 | 2142690.76
355
160 | AP-95A | DD+0 | 39°52'27"RT |  |  | 55048 | 832.03 | 354.5 | 162 | 157 | 319 | 167 | 164 | 331 | 717311.21 | 2142592.81
354
161 | 95A/1 | DA+0 |  |  |  | 55402 | 835.349 | 350 | 198 | 158 | 356 | 191 | 163 | 354 | 716987.018 | 2142736.113
346
162 | AP-95B | DD+0 | 48°32'52"RT |  |  | 55748 | 837.88 | 325.5 | 189 | 198 | 387 | 184 | 181 | 365 | 716670.1 | 2142876.2
305
163 | AP-95C | DD+0 | 38°35'11"LT |  |  | 56053 | 831.73 | 306 | 107 | 207 | 314 | 125 | 187 | 312 | 716578 | 2143166.44
307
164 | AP-96 | DD+0 | 35°22'51"RT |  |  | 56360 | 824.44 | 339.5 | 101 | 117 | 218 | 121 | 138 | 259 | 716323.03 | 2143337.18
372
165 | AP-97 | DC+0 | 18°36'07"RT |  |  | 56732 | 836.66 | 357 | 256 | 145 | 401 | 235 | 154 | 389 | 716190.87 | 2143684.89
342
166 | 97/1 | DA+0 |  |  |  | 57074 | 840.777 | 342 | 197 | 106 | 303 | 189 | 128 | 317 | 716177.698 | 2144026.365
342
167 | AP-98 | DC+0 | 15°43'18"LT |  |  | 57416 | 851.07 | 330.5 | 236 | 59 | 295 | 215 | 96 | 311 | 716164.52 | 2144367.97
319
168 | 98/1 | DB+0 |  |  |  | 57735 | 865.644 | 301.5 | 261 | -31 | 230 | 225 | 40 | 265 | 716066.242 | 2144671.687
284
169 | AP-99 | DD+6 | 39°46'55"LT |  |  | 58019 | 881.18 | 292.5 | 316 | -31 | 285 | 245 | 39 | 284 | 715978.88 | 2144941.67
301
170 | AP-100 | DC+0 | 19°43'12"LT |  |  | 58320 | 911.62 | 350.5 | 333 | 336 | 669 | 264 | 300 | 564 | 715724.22 | 2145102.58
400
171 | AP-101 | DB+9 | 10°04'16"LT |  |  | 58720 | 876.48 | 410 | 65 | 442 | 507 | 102 | 384 | 486 | 715334.14 | 2145189.54
420
172 | 101/1 | DB+9 |  |  |  | 59140 | 829.475 | 409 | -19 | 173 | 154 | 40 | 181 | 221 | 714914.862 | 2145207.819
398
173 | 101/2 | DA+6 |  |  |  | 59538 | 837.507 | 387.5 | 226 | 207 | 433 | 219 | 202 | 421 | 714517.24 | 2145225.154
377
174 | AP-102 | DB+9 | 14°27'52"LT |  |  | 59915 | 831.15 | 355 | 170 | 288 | 458 | 176 | 247 | 423 | 714140.71 | 2145241.57
333
175 | AP-103 | DB+9 | 3°42'15"RT |  |  | 60248 | 812.62 | 340.5 | 45 | 152 | 197 | 87 | 159 | 246 | 713815.25 | 2145172.58
348
176 | AP-104 | DB+0 | 14°23'44"RT |  |  | 60596 | 825.29 | 343.5 | 197 | 328 | 525 | 190 | 275 | 465 | 713470.73 | 2145122.54
339
177 | 104/1 | DB+9 |  |  |  | 60935 | 791.584 | 350 | 12 | 222 | 234 | 65 | 209 | 274 | 713133.641 | 2145158.751
361
178 | AP-105 | DD+9 | 41°34'34"LT |  |  | 61296 | 784.65 | 333 | 140 | 280 | 420 | 153 | 232 | 385 | 712774.42 | 2145197.34
305
179 | 105/1 | DB+9 |  |  |  | 61601 | 767.31 | 360 | 25 | 288 | 313 | 74 | 268 | 342 | 712526.202 | 2145020.649
415
180 | AP-106 | DB+0 | 14°54'55"RT |  |  | 62016 | 760.08 | 392 | 127 | 99 | 226 | 148 | 125 | 273 | 712188.33 | 2144780.14
369
181 | 106/1 | DB+9 |  |  |  | 62385 | 766.153 | 399.5 | 271 | -87 | 184 | 245 | -11 | 234 | 711842.358 | 2144650.584
430
182 | AP-107 | DB+9 | 0°37'08"LT |  |  | 62815 | 830.13 | 375 | 522 | 587 | 1109 | 447 | 433 | 880 | 711439.5 | 2144499.725
320
183 | 107/1 | DB+9 |  |  |  | 63135 | 768.852 | 388 | -262 | 298 | 36 | -106 | 284 | 178 | 711141.23 | 2144384.343
456
184 | AP-108 | DC+0 | 27°46'52"RT |  |  | 63591 | 760.96 | 418 | 159 | 278 | 437 | 174 | 253 | 427 | 710715.98 | 2144219.84
380
185 | AP-109 | DD+0 | 48°27'30"LT |  |  | 63971 | 745.19 | 325 | 103 | -45 | 58 | 129 | 26 | 155 | 710338.71 | 2144263.71
270
186 | 109/1 | DB+0 |  |  |  | 64241 | 769.036 | 259.5 | 316 | -150 | 166 | 245 | -31 | 214 | 710137.786 | 2144083.902
249
187 | AP-110 | DB+0 | 8°14'04"LT |  |  | 64490 | 801.66 | 296 | 401 | 398 | 799 | 283 | 323 | 606 | 709952.39 | 2143917.99
343
188 | AP-111 | DD+9 | 42°36'23"RT |  |  | 64833 | 756.96 | 321.5 | -53 | 412 | 359 | 22 | 311 | 333 | 709732.31 | 2143655.15
300
189 | AP-112 | DD+6 | 35°13'58"RT |  |  | 65133 | 725.3 | 304 | -110 | 182 | 72 | -8 | 172 | 164 | 709435.21 | 2143616.28
308
190 | AP-113 | DC+0 | 16°41'53"RT |  |  | 65441 | 727.43 | 354 | 126 | 249 | 375 | 137 | 236 | 373 | 709163.08 | 2143759.63
400
191 | AP-114 | DD+0 | 33°57'42"LT |  |  | 65841 | 717.94 | 336 | 151 | 111 | 262 | 164 | 122 | 286 | 708877.92 | 2144039.63
272
192 | AP-115 | DC+0 | 22°54'20"RT |  |  | 66113 | 720.94 | 319 | 162 | 179 | 341 | 151 | 181 | 332 | 708610.27 | 2144089.31
366
193 | AP-116 | DB+0 | 3°06'00"RT |  |  | 66479 | 721.63 | 348 | 187 | 186 | 373 | 186 | 179 | 365 | 708304.8 | 2144290.89
330
194 | AP-117 | DB+0 | 11°43'45"LT |  |  | 66809 | 718.52 | 345 | 145 | 137 | 282 | 152 | 151 | 303 | 708039.53 | 2144487.33
360
195 | AP-118 | DC+0 | 17°40'00"LT |  |  | 67169 | 725.8 | 334 | 223 | 63 | 286 | 210 | 98 | 308 | 707712.55 | 2144638.36
308
196 | AP-119 | DD+0 | 48°09'07"RT |  |  | 67477 | 738.38 | 345.5 | 245 | 326 | 571 | 212 | 288 | 500 | 707406.64 | 2144676.6
383
197 | AP-120 | DC+0 | 22°19'33"LT |  |  | 67860 | 714.02 | 292 | 59 | 159 | 218 | 97 | 127 | 224 | 707188.56 | 2144991.28
201
198 | AP-121 | DD+0 | 39°41'02"RT |  |  | 68061 | 709.41 | 200.5 | 42 | 62 | 104 | 74 | 83 | 157 | 707020.11 | 2145100.47
200
199 | AP-121A | DB+0 | 2°41'13"LT |  |  | 68261 | 712.41 | 218 | 138 | 123 | 261 | 118 | 121 | 239 | 706960.44 | 2145291.29
236
200 | 121A/1 | DA+6 |  |  |  | 68497 | 705.86 | 250.5 | 113 | 207 | 320 | 115 | 176 | 291 | 706879.441 | 2145513.21
265
201 | AP-121B | DB+0 | 12°27'11"LT |  |  | 68762 | 702.54 | 271.5 | 59 | 126 | 185 | 90 | 131 | 221 | 706788.5 | 2145762.37
278
202 | 121B/1 | DA+6 |  |  |  | 69040 | 698.425 | 277.5 | 152 | 185 | 337 | 147 | 168 | 315 | 706639.376 | 2145996.407
277
203 | AP-121C | DC+0 | 29°06'48"RT |  |  | 69317 | 697.88 | 265.5 | 92 | 101 | 193 | 110 | 113 | 223 | 706490.56 | 2146229.96
254
204 | AP-122 | DC+3 | 23°03'42"RT |  |  | 69571 | 697.63 | 312 | 153 | 30 | 183 | 141 | 77 | 218 | 706475.53 | 2146483.61
370
205 | AP-123 | DC+6 | 20°55'50"LT |  |  | 69941 | 721.91 | 365.5 | 342 | 137 | 479 | 295 | 151 | 446 | 706600.23 | 2146832.45
361
206 | AP-124 | DB+6 | 1°47'06"LT |  |  | 70302 | 729.3 | 331.5 | 224 | 157 | 381 | 211 | 155 | 366 | 706592.29 | 2147193.43
302
207 | AP-125 | DB+0 | 4°25'42"LT |  |  | 70604 | 734.46 | 404.5 | 145 | 392 | 537 | 147 | 367 | 514 | 706576.26 | 2147494.76
507
208 | 125/1 | DB+3 |  |  |  | 71111 | 695.388 | 399 | 118 | 177 | 295 | 144 | 165 | 309 | 706510.31 | 2147997.502
291
209 | 125/2 | DB+0 |  |  |  | 71402 | 694.309 | 346.5 | 114 | -156 | -42 | 126 | -57 | 69 | 706472.5 | 2148285.733
402
210 | AP-126 | DC+0 | 25°59'52"RT |  |  | 71804 | 764 | 399.5 | 565 | 362 | 927 | 467 | 318 | 785 | 706420.17 | 2148684.65
397
211 | AP-127 | DD+6 | 8°15'23"RT |  |  | 72201 | 726.94 | 478.5 | 37 | 343 | 380 | 82 | 335 | 417 | 706546.44 | 2149061.5
560
212 | AP-128 | DD+6 | 4°16'15"RT |  |  | 72761 | 706.52 | 460 | 220 | 249 | 469 | 228 | 228 | 456 | 706798.57 | 2149561.05
360
213 | AP-129 | DB+6 | 13°50'27"LT |  |  | 73121 | 694.92 | 379 | 112 | 164 | 276 | 133 | 174 | 307 | 706984.38 | 2149869.66
398
214 | AP-130 | DC+6 | 22°15'17"LT |  |  | 73519 | 701.65 | 398 | 235 | 113 | 348 | 225 | 136 | 361 | 707102.18 | 2150249.96
398
215 | AP-131 | DC+9 | 18°24'23"RT |  |  | 73917 | 715.36 | 400.5 | 287 | 31 | 318 | 263 | 77 | 340 | 707067.15 | 2150646.83
403
216 | AP-132 | DC+3 | 18°32'40"LT |  |  | 74320 | 754.57 | 401.5 | 373 | 201 | 574 | 328 | 201 | 529 | 707160.19 | 2151038.52
400
217 | AP-133 | DB+6 | 13°09'17"LT |  |  | 74720 | 751.39 | 391.5 | 199 | 272 | 471 | 200 | 244 | 444 | 707124.06 | 2151436.88
383
218 | 133/1 | DA+9 |  |  |  | 75103 | 734.474 | 343 | 112 | 191 | 303 | 141 | 177 | 318 | 707003.43 | 2151800.838
303
219 | 133/2 | DA+6 |  |  |  | 75406 | 732.017 | 262.5 | 112 | 105 | 217 | 126 | 107 | 233 | 706908.103 | 2152088.453
222
220 | AP-134 | DC+3 | 18°19'32"LT |  |  | 75628 | 735.63 | 246 | 117 | -87 | 30 | 115 | 9 | 124 | 706838.29 | 2152299.09
270
221 | AP-135 | DD+0 | 30°51'51"LT |  |  | 75898 | 764.45 | 335 | 358 | 154 | 512 | 263 | 167 | 430 | 706677.18 | 2152515.53
400
222 | AP-136 | DD+3 | 31°03'41"LT |  |  | 76298 | 770.44 | 390.5 | 247 | 340 | 587 | 235 | 304 | 539 | 706307.12 | 2152668.61
381
223 | 136/1 | DB+9 |  |  |  | 76679 | 733.035 | 279 | 44 | 41 | 85 | 80 | 68 | 148 | 705930.068 | 2152611.664
177
224 | AP-137 | DB+9 | 13°34'34"LT |  |  | 76856 | 736.69 | 262.5 | 136 | 395 | 531 | 110 | 324 | 434 | 705755.04 | 2152585.23
348
225 | 137/1 | DB+9 |  |  |  | 77204 | 701.146 | 391 | -45 | 134 | 89 | 27 | 154 | 181 | 705432.624 | 2152453.888
434
226 | AP-138 | DC+0 | 18°45'07"RT |  |  | 77638 | 728.61 | 385.5 | 301 | 359 | 660 | 282 | 295 | 577 | 705031.05 | 2152290.3
337
227 | 138/1 | DB+9 |  |  |  | 77975 | 690.235 | 319.5 | -20 | 178 | 158 | 44 | 167 | 211 | 704694.498 | 2152270.232
302
228 | 138/2 | DA+9 |  |  |  | 78277 | 686.646 | 282 | 124 | 203 | 327 | 135 | 174 | 309 | 704393.033 | 2152252.257
262
229 | AP-139 | DB+3 | 8°34'35"LT |  |  | 78539 | 684.4 | 306.5 | 59 | 188 | 247 | 88 | 184 | 272 | 704131.97 | 2152236.69
351
230 | 139/1 | DA+0 |  |  |  | 78890 | 685.483 | 334 | 164 | 214 | 378 | 168 | 195 | 363 | 703788.499 | 2152163.753
317
231 | AP-140 | DB+0 | 2°44'46"LT |  |  | 79207 | 677.43 | 339 | 104 | 176 | 280 | 123 | 178 | 301 | 703478.2 | 2152097.86
361
232 | AP-141 | DB+0 | 6°57'25"LT |  |  | 79568 | 678.28 | 358 | 186 | 118 | 304 | 185 | 137 | 322 | 703128.77 | 2152005.96
355
233 | AP-142 | DC+0 | 19°22'12"LT |  |  | 79923 | 688.28 | 362.5 | 238 | 172 | 410 | 219 | 175 | 394 | 702798.87 | 2151874.73
370
234 | 142/1 | DA+3 |  |  |  | 80293 | 687.722 | 387 | 199 | 239 | 438 | 195 | 230 | 425 | 702519.943 | 2151631.732
404
235 | 142/2 | DA+6 |  |  |  | 80697 | 677.466 | 373.5 | 165 | 164 | 329 | 175 | 166 | 341 | 702215.653 | 2151366.638
343
236 | 142/3 | DA+6 |  |  |  | 81040 | 678.817 | 413 | 180 | 127 | 307 | 178 | 157 | 335 | 701957.161 | 2151141.443
483
237 | AP-143 | DB+6 | 9°31'57"RT |  |  | 81523 | 705.89 | 486 | 358 | 238 | 596 | 328 | 239 | 567 | 701593 | 2150824.19
489
238 | 143/1 | DB+9 |  |  |  | 82012 | 704.885 | 463.5 | 253 | 30 | 283 | 252 | 73 | 325 | 701176.37 | 2150568.584
438
239 | AP-144 | DD+9 | 44°20'13"LT |  |  | 82450 | 748 | 393.5 | 412 | 503 | 915 | 369 | 397 | 766 | 700802.97 | 2150339.5
349
240 | 144/1 | DB+9 |  |  |  | 82799 | 695.125 | 386.5 | -149 | 296 | 147 | -43 | 276 | 233 | 700717.638 | 2150000.622
424
241 | AP-145 | DD+6 | 49°51'04"RT |  |  | 83223 | 680.36 | 453.5 | 129 | 155 | 284 | 150 | 171 | 321 | 700614.04 | 2149589.2
483
242 | 145/1 | DB+9 |  |  |  | 83706 | 701.08 | 457 | 330 | -168 | 162 | 315 | -72 | 243 | 700179.945 | 2149377.333
431
243 | AP-146 | DD+6 | 23°39'32"RT |  |  | 84137 | 785.71 | 415.5 | 607 | 143 | 750 | 511 | 159 | 670 | 699792.88 | 2149188.42
400
244 | AP-147 | DD+0 | 16°38'51"LT |  |  | 84537 | 802.83 | 394 | 258 | 442 | 700 | 243 | 372 | 615 | 699392.89 | 2149171.96
388
245 | AP-148 | DB+3 | 10°41'31"LT |  |  | 84925 | 754.17 | 365 | -51 | 330 | 279 | 19 | 277 | 296 | 699026.4 | 2149045.74
342
246 | 148/1 | DB+0 |  |  |  | 85267 | 732.156 | 350 | 13 | 279 | 292 | 66 | 248 | 314 | 698729.731 | 2148876.552
358
247 | 148/2 | DB+0 |  |  |  | 85625 | 715.498 | 339.5 | 80 | 242 | 322 | 111 | 213 | 324 | 698419.046 | 2148699.371
321
248 | AP-149 | DD+0 | 38°23'33"LT |  |  | 85946 | 703.65 | 283.5 | 80 | 393 | 473 | 109 | 267 | 376 | 698139.89 | 2148540.17
246
249 | 149/1 | DB+0 |  |  |  | 86192 | 676.163 | 299 | -145 | 404 | 259 | -19 | 331 | 312 | 698048.194 | 2148312.204
352
250 | AP-150 | DB+6 | 13°27'14"LT |  |  | 86544 | 632.95 | 350 | -50 | 109 | 59 | 23 | 130 | 153 | 697917 | 2147986.04
348
251 | AP-151 | DB+0 | 4°53'04"RT |  |  | 86892 | 649.54 | 361 | 240 | 47 | 287 | 219 | 89 | 308 | 697865.82 | 2147641.85
374
252 | AP-152 | DB+3 | 2°08'15"LT |  |  | 87266 | 671.43 | 340.5 | 328 | 204 | 532 | 287 | 185 | 472 | 697779.56 | 2147278.14
307
253 | 152/1 | DA+6 |  |  |  | 87573 | 661.475 | 328.5 | 103 | 240 | 343 | 122 | 216 | 338 | 697719.98 | 2146977.368
350
254 | 152/2 | DA+9 |  |  |  | 87923 | 648.277 | 297.5 | 111 | 180 | 291 | 135 | 159 | 294 | 697651.918 | 2146633.781
245
255 | AP-153 | DD+0 | 53°11'45"RT |  |  | 88168 | 650.96 | 309.5 | 65 | 138 | 203 | 87 | 153 | 240 | 697604.35 | 2146393.65
374
256 | AP-154 | DC+0 | 26°08'24"RT |  |  | 88542 | 659.72 | 289.5 | 237 | 132 | 369 | 222 | 116 | 338 | 697267.18 | 2146232.11
205
257 | AP-155 | DD+0 | 38°53'18"RT |  |  | 88747 | 657.33 | 203 | 73 | 214 | 287 | 89 | 152 | 241 | 697062.62 | 2146234.04
201
258 | AP-156 | DD+0 | 48°19'37"RT |  |  | 88948 | 648.44 | 251 | -13 | 91 | 78 | 49 | 114 | 163 | 696907.62 | 2146361.49
301
259 | AP-157 | DC+0 | 16°25'40"LT |  |  | 89249 | 656.54 | 306.5 | 211 | 180 | 391 | 188 | 173 | 361 | 696895.82 | 2146662.62
312
260 | 157/1 | DA+9 |  |  |  | 89561 | 644.023 | 340.5 | 132 | 101 | 233 | 140 | 129 | 269 | 696795.947 | 2146958.163
369
261 | AP-158 | DD+9 | 42°56'48"LT |  |  | 89930 | 658.34 | 374 | 269 | 104 | 373 | 241 | 129 | 370 | 696677.8 | 2147307.78
379
262 | AP-159 | DD+9 | 44°07'27"LT |  |  | 90309 | 673.82 | 314 | 276 | 276 | 552 | 251 | 207 | 458 | 696344.79 | 2147487.7
249
263 | AP-160 | DD+9 | 32°47'54"LT |  |  | 90558 | 658.05 | 290 | -26 | -14 | -40 | 44 | 49 | 93 | 696104.73 | 2147420.03
331
264 | AP-161 | DC+0 | 24°54'38"RT |  |  | 90889 | 694.33 | 289 | 346 | 108 | 454 | 284 | 115 | 399 | 695885.66 | 2147172.06
247
265 | AP-162 | DB+0 | 2°28'54"LT |  |  | 91136 | 695.96 | 384.5 | 139 | 209 | 348 | 132 | 218 | 350 | 695659.27 | 2147073.01
522
266 | AP-163 | DD+6 | 55°57'31"RT |  |  | 91658 | 705.78 | 413 | 315 | -409 | -94 | 307 | -187 | 120 | 695190.52 | 2146843.25
304
267 | AP-164 | DD+6 | 34°37'07"RT |  |  | 91962 | 781.83 | 312 | 723 | 1507 | 2230 | 501 | 957 | 1458 | 694926.99 | 2146994.46
320
268 | AP-165 | DD+3 | 0°14'54"LT |  |  | 92282 | 601.12 | 349.5 | -1138 | 851 | -287 | -587 | 650 | 63 | 694789.01 | 2147283.29
379
269 | AP-166 | DD+6 | 14°39'37"RT |  |  | 92661 | 482 | 317 | -454 | 959 | 505 | -253 | 568 | 315 | 694624.26 | 2147624.35
255
270 | AP-167 | DD+6 | 46°06'16"RT |  |  | 92916 | 395 | 197.5 | -690 | 858 | 168 | -299 | 337 | 38 | 694575.16 | 2147874.09
140
271 | AP-168 | DD+0 | 29°14'31"RT |  |  | 93056 | 362 | 131.5 | -713 | 405 | -308 | -192 | 170 | -22 | 694655.23 | 2147988.52
123
272 | GANTRY | GANTRY | 0°00'00" |  |  | 93179 | 354.43 | 61.5 | -280 | 0 | -280 | -45 | 0 | -45 | 694766.41 | 2148042.21
|  |  | More than 45 degree |  | 17
TOWER ABSTRUCT
[5 empty] | TOWER NO. | +0 | +3 | +6 | +9 | +18 | +25 | TOTAL
[5 empty] | DA | 20 | 8 | 13 | 16 | 0 | 0 | 57
[5 empty] | DB | 40 | 11 | 15 | 24 | 0 | 0 | 90
[5 empty] | DC | 25 | 4 | 7 | 5 | 0 | 0 | 41
[5 empty] | DD | 37 | 5 | 15 | 17 | 1 | 7 | 82
[5 empty] | GANTRY | 2 | 0 | 0 | 0 | 0 | 0 | 2
[5 empty] | TOTAL | 124 | 28 | 50 | 62 | 1 | 7 | 272