## ANNEXURE IV
99.9814 |  | TRANSMISSION SYSTEM OUTAGE DATA
PERIOD : 2017-18
Sl. No. | Name of the Transmission Element | OUTAGE |  | RESTORATION |  | OUTAGE PERIOD | DURATION OF OUTAGE ATTRIBUTABLE TO | [5 empty] | Deemed Availability | Reason of Outage | MVA capacity for ICTs / Autos | Ckm and number of Sub-Conductor for lines | Time considered for availability (hrs) (365 X 24) | Element wise availbility (C19 - C7 - C8/60) / C19 | ( OH l x Cktkm l x NSC l ) ( OH t x MVA t x 2.5 ) | (THY x Ckt KM X NSC) (THY X MVA x 2.5)
|  | DATE | TIME | DATE | TIME |  | UTILITY ITSELF |  | OTHERS |  | System Constraints/Natural Calamities
|  | dd/mm/yy | hh:mm | dd/mm/yy | hh:mm | hh:mm | Hrs | Min | Hrs | Min | Hrs | Min
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
400KV LINES
1 | 400 kV Indravati - Indravati PG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.97 | 8760 | 100% | 0 | 69554.4
2 | 400kV Meramundali -New Duburi Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 96.6 | 8760 | 100% | 0 | 1692432
3 | 400kV Meramundali -New Duburi Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 96.6 | 8760 | 100% | 0 | 1692432
4 | 400kV Meramundali -Vedant Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 209 | 8760 | 100% | 0 | 3661680
5 | 400kV Meramundali -Vedant Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 209 | 8760 | 100% | 0 | 3661680
6 | 400kV Meramundali -Mendhasal Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 100.451 | 8760 | 100% | 0 | 1759901.52
7 | 400 kV Meramundali - JSPL Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 37.916 | 8760 | 100% | 0 | 664288.32
8 | 400 kV Meramundali - JSPL Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 37.916 | 8760 | 100% | 0 | 664288.32
9 | 400kV Rengali - Kuchei PG-Kolaghat |  |  |  |  | 0 | 0 | 0 | [7 empty] | 241.5 | 8760 | 100% | 0 | 4231080
1032.953
220KV LINES
10 | 220kV Atri-Pandiabil Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.534 | 8760 | 100% | 0 | 214917.84
11 | 220kV Pandiabil-Samagara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 48.06 | 8760 | 100% | 0 | 421005.6
12 | 220kV Atri-Pandiabil Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.53 | 8760 | 100% | 0 | 214882.8
13 | 220kV Pandiabil-Samagara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 48.06 | 8760 | 100% | 0 | 421005.6
14 | 220kV Balasore- Bhadrak |  |  |  |  | 0.052083 | 1 | 15 | [7 empty] | 67.95 | 8760 | 99.99% | 84.9375 | 595242
|  | 03.05.17 | 17:14 | 03.05.17 | 18:29 | 1:15 | 1 | 15 | [5 empty] | At Balasore-ZMR, PST, PSN At Bhadrak-Did not trip
15 | 220kV Balimela-Jayanagar-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 92.072 | 8760 | 100% | 0 | 806550.72
16 | 220kV Balimela-Jayanagar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 92.072 | 8760 | 100% | 0 | 806550.72
17 | 220kV Balimela-Jayanagar-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 93.46 | 8760 | 100% | 0 | 818709.6
18 | 220kV Balimela-Malkangiri |  |  |  |  | 0 | 0 | 0 | [7 empty] | 22.41 | 8760 | 100% | 0 | 196311.6
19 | 220kV Balimela PH -Balimela |  |  |  |  | 0.020833 | 0 | 30 | [7 empty] | 0.2 | 8760 | 99.99% | 0.1 | 1752
|  | 24.07.17 | 19:42 | 24.07.17 | 20:00 | 0:18 | 0 | 30 | [5 empty] | Balimela PH Tripped
|  | 24.07.17 | 20:28 | 24.07.17 | 20:40 | 0:12
20 | 220kV Balimela PH -Upper Sileru |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.76 | 8760 | 100% | 0 | 216897.6
21 | 220kV Barkote-Bonai |  |  |  |  | 0.061806 | 1 | 29 | [7 empty] | 55.807 | 8760 | 99.98% | 82.7804 | 488869.32
|  | 15.10.17 | 12:30 | 15.10.17 | 12:45 | 0:15 | 0 | 15 | [5 empty] | At Barkote-'B' ph. to E/F
|  | 29.01.18 | 15:40 | 29.01.18 | 16:54 | 1:14 | 1 | 14 | [5 empty] | At Bonai-Tripped
22 | 220kV Bonai-Tarkera |  |  |  |  | 0.050694 | 0 | 13 | [7 empty] | 47.467 | 8760 | 100% | 10.2845 | 415810.92
|  | 15.10.17 | 12:30 | 15.10.17 | 13:43 | 1:13 | 0 | 13 | [5 empty] | At Tarkera-D/P, Dist.-46.87 k.m. 'R' ph. to E/F
23 | 220kV Bhanjanagar-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 134.14 | 8760 | 100% | 0 | 1175066.4
24 | 220kV Bhanjanagar-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 134.14 | 8760 | 100% | 0 | 1175066.4
25 | 220kV Bhanjanagar-Mendhasal ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 136.47 | 8760 | 100% | 0 | 1195477.2
26 | 220kV Bhanjanagar-Nayagarh ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 63 | 8760 | 100% | 0 | 551880
27 | 220kV Bidanasi -Mendhasal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
28 | 220kV Bidanasi -Mendhasal Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
29 | 220kV Bidanasi -Cuttack Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.3 | 8760 | 100% | 0 | 81468
30 | 220kV Bidanasi -Cuttack Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.3 | 8760 | 100% | 0 | 81468
31 | 220kV Bisra-Tarkera-I |  |  |  |  | 0.070833 | 1 | 34 | [7 empty] | 15.335 | 8760 | 99.98% | 24.0248 | 134334.6
|  | 06.06.17 | 16:31 | 06.06.17 | 16:39 | 0:08 |  |  | 0 | 8 |  |  |  | At Bisra PG-O/C, E/F
|  | 31.07.17 | 11:24 | 31.07.17 | 12:58 | 1:34 | 1 | 34 | [5 empty] | At Tarkera-did not trip At Bisra PG-D/P, Zn.-III
32 | 220kV Bisra-Tarkera-II |  |  |  |  | 0.071528 | 1 | 35 | [7 empty] | 15.335 | 8760 | 99.98% | 24.2804 | 134334.6
|  | 06.06.17 | 16:31 | 06.06.17 | 16:39 | 0:08 |  |  | 0 | 8 |  |  |  | At Bisra PG-O/C, E/F
|  | 31.07.17 | 11:24 | 31.07.17 | 12:59 | 1:35 | 1 | 35 | [5 empty] | At Tarkera-Numerical back up At Bisra PG-did not trip
33 | 220kV Budhipadar-Aditya Aluminium Ckt.-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.507 | 8760 | 100% | 0 | 179641.32
34 | 220kV Budhipadar-Aditya Aluminium Ckt.-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | At Budhipadar-LBB |  | 20.507 | 8760 | 100% | 0 | 179641.32
35 | 220kV Budhipadar-Basundhara Ckt-I |  |  |  |  | 0.061806 | 1 | 29 | [7 empty] | 35.29 | 8760 | 99.98% | 52.3468 | 309140.4
|  | 10.12.17 | 5:40 | 10.12.17 | 7:09 | 1:29 | 1 | 29 | [5 empty] | At Budhipadar-D/P, 'R' ph to E/F, Dist.-9 k.m.
36 | 220kV Budhipadar-IbTPS -I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 100% | 0 | 227760
37 | 220kV Budhipadar-IbTPS -II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 100% | 0 | 227760
38 | 220kV Budhipadar-IbTPS -III |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 100% | 0 | 222328.8
39 | 220kV Budhipadar-IbTPS -IV |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 100% | 0 | 222328.8
40 | 220kV Budhipadar-Raigarh-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 60 | 8760 | 100% | 0 | 525600
41 | 220kV Budhipadar-Korba-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 60 | 8760 | 100% | 0 | 525600
42 | 220kV Budhipadar-Lapanga-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20 | 8760 | 100% | 0 | 175200
43 | 220kV Budhipadar-Lapanga-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20 | 8760 | 100% | 0 | 175200
44 | 220kV Budhipadar-SPS Feeder-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.424 | 8760 | 100% | 0 | 117594.24
45 | 220kV Budhipadar-SPS Feeder-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.424 | 8760 | 100% | 0 | 117594.24
46 | 220kV Budhipadar-Bhusan Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.92 | 8760 | 100% | 0 | 130699.2
47 | 220kV Budhipadar-Bhusan Ckt II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.92 | 8760 | 100% | 0 | 130699.2
48 | 220kV Chandaka -Mendhasal Ckt-I |  |  |  |  | 0.0125 | 0 | 26 | [7 empty] | 19 | 8760 | 100% | 8.2333 | 166440
|  | 16.04.17 | 21:10 | 17.04.17 | 14:19 | 17:09 | 0 | 8 | [5 empty] | At Mendhasal-['B' ph, CVT to line jumper snapped at Mendhasal]
|  | 01.06.17 | 14:46 | 01.06.17 | 15:04 | 0:18 | 0 | 18 | [5 empty] | At Chandaka-Master trip
49 | 220kV Chandaka- Mendhasal ckt II |  |  |  |  | 0.19583 | 0 | 45 | [7 empty] | 19.9 | 8760 | 99.99% | 14.925 | 174324
|  | 16.04.17 | 20:39 | 16.04.17 | 21:20 | 0:41 | 0 | 8 | [5 empty] | At Chandaka-'R' ph, 'Y' ph, E/F.The weather was rainy and stormy
|  | 01.06.17 | 14:46 | 01.06.17 | 15:04 | 0:18 | 0 | 18 | [5 empty] | At Chandaka-Master trip
|  | 01.06.17 | 14:46 | 01.06.17 | 18:29 | 3:43 | 0 | 19 | [5 empty] | At Mendhasal-Tripped. After 19 minutes Power flow resumed through Ckt-IV
50 | 220kV Chandaka- Mendhasal ckt III |  |  |  |  | 0 | 0 | 18 | [7 empty] | 19.9 | 8760 | 100% | 5.97 | 174324
|  | 01.06.17 | 14:46 | 01.06.17 | 18:29 | 3:43 | 0 | 18 | [5 empty] | At Chandaka-Tripped. Power Flow resumed through alternate circuits after 18 minutes
51 | 220kV Chandaka- Chandaka-B-Mendhasal ckt IV |  |  |  |  | 0.047222 | 12 | 35 | [7 empty] | 19.958 | 8760 | 99.86% | 251.1382 | 174832.08
|  | 16.04.17 | 20:39 | 16.04.17 | 21:20 | 0:41 | 0 | 8 | [5 empty] | At Chandaka-'Y' ph. to E/F, D/P
|  | 28.05.17 | 19:13 | 28.05.17 | 19:21 | 0:08 | 0 | 8 | [5 empty] | At Chandaka-'R' ph. to 'Y' ph.
|  | 01.06.17 | 14:46 | 01.06.17 | 15:05 | 0:19 | 0 | 19 | [5 empty] | At Chandaka-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
52 | 220kV Duburi-Duburi (New) Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.38 | 8760 | 100% | 0 | 55888.8
53 | 220kV Duburi-Duburi (New) Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.38 | 8760 | 100% | 0 | 55888.8
54 | 220kV Duburi-NINL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6 | 8760 | 100% | 0 | 52560
55 | 220kV Indravati PH-Therubali-I (TVL) |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 100% | 0 | 755112
56 | 220kV Indravati PH-Therubali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 100% | 0 | 755112
57 | 220kV Indravati PH-Therubali-III |  |  |  |  | 0.15694 | 0 | 7 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 91 | 8760 | 100% | 10.6167 | 797160
|  | 16.05.17 | 22:59 | 16.05.17 | 23:33 | 0:34 | 0 | 7 | [5 empty] | At Theruvali-Bus bar protection
|  | 09.01.18 | 11:42 | 09.01.18 | 14:54 | 3:12 | 0 | 0 | [5 empty] | At Indravati-Ýph, Zn.-I, Dist.-36.32 k.m.However Power flow evacuation carried out through ckt-I & II
58 | 220kV Indravati PH-Therubali-IV |  |  |  |  | 0.11806 | 0 | 7 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 91 | 8760 | 100% | 10.6167 | 797160
|  | 16.05.17 | 22:59 | 18.05.17 | 11:38 | 36:39 | 0 | 7 | [5 empty] | ['B' ph. CT burst at Theruvali]Power flow resumed through ckt-I &II
|  | 09.01.18 | 11:42 | 09.01.18 | 14:32 | 2:50 | 0 | 0 | [5 empty] | At Theruvali-Bus bar protection.However Power flow evacuation carried out through ckt-I & II
59 | 220kV Jayanagar-Jeypore PG-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
60 | 220kV Jayanagar-Jeypore PG-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
61 | 220kV Jayanagar-Laxmipur ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65 | 8760 | 100% | 0 | 569400
62 | 220kV Jayanagar-Laxmipur ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65 | 8760 | 100% | 0 | 569400
63 | 220kV Jindal-Jamsedpur DVC |  |  |  |  | 0.09375 | 1 | 7 | [7 empty] | 20.8 | 8760 | #REF! | 23.2267 | 182208
|  | 25.04.17 | 19:09 | 25.04.17 | 20:45 | 1:36 | 0 | 28 | [5 empty] | At Jindal-Tripped
|  | 13.05.17 | 22:09 | 13.05.17 | 22:48 | 0:39 | 0 | 39 | [5 empty] | At Jamshedpur-O/C
64 | 220kV Joda-RCPur PG |  |  |  |  | 0.041667 | 1 | 0 | [7 empty] | 15.5 | 8760 | 99.99% | 15.5 | 135780
|  | 13.05.17 | 22:09 | 13.05.17 | 23:09 | 1:00 | 1 | 0 | [5 empty] | At Ramchandrapur-O/C, E/F
65 | 220kV Joda-Jindal |  |  |  |  | 0.019444 | 0 | 28 | [7 empty] | 21 | 8760 | 99.99% | 9.8 | 183960
|  | 25.04.17 | 19:09 | 25.04.17 | 19:37 | 0:28 | 0 | 28 | [5 empty] | At Joda-Tripped
66 | 220kV Joda-TSIL Ckt. |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.3 | 8760 | 100% | 0 | 63948
67 | 220kV Katapalli- HINDALCO Ckt-I |  |  |  |  | 1900-01-27 11:13 | 0 | 30 | [7 empty] | 10 | 8760 | #REF! | 5 | 87600
|  | 18.05.17 | 23:48 | 19.05.17 | 0:18 | 0:30 | 0 | 30 | [5 empty] | At Katapalli-Tripped
68 | 220kV Katapalli- HINDALCO Ckt-II |  |  |  |  | 0.020833 | 0 | 30 | [7 empty] | 10 | 8760 | 99.99% | 5 | 87600
|  | 18.05.17 | 23:48 | 19.05.17 | 0:18 | 0:30 | 0 | 30 | [5 empty] | At Katapalli-Tripped
69 | 220kV Katapalli- Bargarh New Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 52.035 | 8760 | 100% | 0 | 455826.6
70 | 220kV Bargarh New- New Bolangir Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65.885 | 8760 | 100% | 0 | 577152.6
71 | 220kV Katapalli- Bolangir PG |  |  |  |  | 0.01875 | 0 | 27 | [7 empty] | 118.45 | 8280 | 99.99% | 53.3025 | 980766
|  | 18.05.17 | 23:48 | 19.05.17 | 0:15 | 0:27 | 0 | 27 | [5 empty] | At Bolangir PG-Tripped
72 | 220kV Bolangir PG- Bolangir Ckt-II |  |  |  |  | 0.05 | 1 | 12 | [7 empty] | 3 | 8280 | 99.99% | 3.6 | 24840
|  | 18.05.17 | 23:48 | 19.05.17 | 1:00 | 1:12 | 1 | 12 | [5 empty] | At Bolangir PG-Tripped
73 | 220kV Kuchei PG-Balasore Ckt I |  |  |  |  | 0.060417 | 1 | 0 | [7 empty] | 76.859 | 8760 | 99.99% | 76.859 | 673284.84
|  | 03.05.17 | 17:14 | 03.05.17 | 17:51 | 0:37 | 0 | 10 | [5 empty] | At Baripada PG- 'B' ph, E/F, Zn.-II dist.-108.6 k.m, Fault current-2.993 kA At Balasore-did not trip
|  | 23.02.18 | 8:54 | 23.02.18 | 9:44 | 0:50 | 0 | 50 | [5 empty] | At BaripadaPG-Tripped
74 | 220kV Kuchei PG-Balasore Ckt-II |  |  |  |  | 0.074306 | 1 | 15 | [7 empty] | 76.859 | 8760 | 99.99% | 96.0737 | 673284.84
|  | 03.05.17 | 17:14 | 03.05.17 | 17:56 | 0:42 | 0 | 10 | [5 empty] | At Baripada PG-'B' ph, E/F, Zn.-I, Dist.-50.27 k.m. Fault current-2.993 KA At Balasore-O/C, E/F, Time LBB protection, D/P, 'B' ph to E/F, Dist.-25.057 k.m. Fault current-3074.99 A Broken conductor, Fault duration-0.10 s
|  | 23.02.18 | 8:54 | 23.02.18 | 9:59 | 1:05 | 1 | 5 | [5 empty] | At BaripadaPG-Tripped
75 | 220kV Lapanga-Katapali-I |  |  |  |  | 0 | 0 | 18 | [7 empty] | 49.72 | 8760 | 100% | 14.916 | 435547.2
|  | 18.05.17 | 23:48 | 19.05.17 | 0:37 | 00:49 | 0 | 18 | [5 empty] | At Katapalli-Tripped.Power supply resumed through ckt-II after 18 minutes.
76 | 220kV Lapanga-Katapali-II |  |  |  |  | 0.0125 | 0 | 18 | [7 empty] | 49.72 | 8760 | 100% | 14.916 | 435547.2
|  | 18.05.17 | 23:48 | 19.05.17 | 0:06 | 0:18 | 0 | 18 | [5 empty] | At Katapalli-Tripped
77 | 220kV Laxmipur - Therubali ckt-I |  |  |  |  | 0.025 | 0 | 36 | [7 empty] | 56 | 8760 | 99.99% | 33.6 | 490560
|  | 16.05.17 | 22:59 | 16.05.17 | 23:15 | 0:16 | 0 | 16 | [5 empty] | At Theruvali-Bus bar relay
|  | 09.01.18 | 11:42 | 09.01.18 | 12:02 | 0:20 | 0 | 20 | [5 empty] | At Theruvali-Bus bar protection
78 | 220kV Laxmipur - Therubali ckt-II |  |  |  |  | 0.024306 | 0 | 35 | [7 empty] | 56 | 8760 | 99.99% | 32.6667 | 490560
|  | 16.05.17 | 22:59 | 16.05.17 | 23:19 | 0:20 | 0 | 20 | [5 empty] | At Theruvali-Bus bar relay, Zn.-I
|  | 09.01.18 | 11:42 | 09.01.18 | 11:57 | 0:15 | 0 | 15 | [5 empty] | At Theruvali-Bus bar protection
79 | 220kV Laxmipur - Utkal Alumina ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.04 | 8760 | 100% | 0 | 271910.4
80 | 220kV Laxmipur - Utkal Alumina ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.04 | 8760 | 100% | 0 | 271910.4
81 | 220kV Mendhasala-Godi Sahi-Bidanasi-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 32.991 | 8760 | 100% | 0 | 289001.16
82 | 220kV Meramundali-Godi sahi-Bidanasi-II |  |  |  |  | 0.0076389 | 12 | 46 | [7 empty] | 90.942 | 8760 | 99.85% | 1161.0262 | 796651.92
|  | 16.04.17 | 20:07 | 17.04.17 | 15:37 | 19:30 | 0 | 23 | [5 empty] | At Meramundali-D/P, Dist.-57 k.m. [Insulator puncture at Loc. No.-35(A)]At 20:30 hrs. Bidanasi availed P/S from Mendhasal end
|  | 28.04.17 | 23:07 | 29.04.17 | 0:01 | 54 Min | 0 | 21 | [5 empty] | At Bidanasi-Bus bar At Meramundali-'R' ph, E/F, Dist.-71.3 k.m.At 23:28 hrs. Bidanasi availed P/S from Mendhasal
|  | 01.06.17 | 14:22 | 01.06.17 | 14:33 | 0:11 | 0 | 2 | [5 empty] | At Bidanasi-D/P, Zn.-I, 'B' ph. to E/F, Zn.-I. At 14:24 hrs, Bidanasi availed P/S from Mendhasal
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
83 | 220kV Meramundali-Bhusan Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
84 | 220kV Meramundali-Bhusan Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
85 | 220kV Meramundali-Duburi-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 95.556 | 8760 | 100% | 0 | 837070.56
86 | 220kV Meramundali-Duburi-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 95.556 | 8760 | 100% | 0 | 837070.56
87 | 220kV NALCO-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
88 | 220kV NALCO-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
89 | 220kV Nayagarh-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 68.58 | 8760 | 100% | 0 | 600760.8
90 | 220kV Narendrapur-Atri-Mendhasal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 176.4 | 8760 | 100% | 0 | 1545264
91 | 220kV Narendrapur-Atri-Mendhasal Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 176.4 | 8760 | 100% | 0 | 1545264
92 | 220kV New Duburi -Balasore |  |  |  |  | 0.00625 | 0 | 9 | [7 empty] | 140.97 | 8760 | 100% | 21.1455 | 1234897.2
|  | 03.05.17 | 17:14 | 03.05.17 | 17:23 | 0:09 | 0 | 9 | [5 empty] | At New Duburi-'B' ph. to E/F, Fault current-0.95 KA Dist.-241.8 km. Zn.-I At Balasore-Did not trip
93 | 220kV New Duburi New-Bhadrakh |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.22 | 8760 | 100% | 0 | 667687.2
94 | 220kV New Duburi-Paradeep Ckt-I |  |  |  |  | 0.11528 | 14 | 46 | [7 empty] | 113.433 | 8760 | 99.83% | 1675.0273 | 993673.08
|  | 17.05.17 | 0:02 | 17.05.17 | 0:31 | 0:29 | 0 | 29 | [5 empty] | At New Duburi-'R', 'Y', 'B' ph, E/F, Dist.-101 k.m. Zn.-II At Paradeep-D/P, ['Y' ph. insulator damaged at Loc. No.-420]
|  | 30.05.17 | 16:45 | 30.05.17 | 18:40 | 1:55 | 1 | 55 | [5 empty] | At Paradeep-Tripped
|  | 14.06.17 | 18:40 | 14.06.17 | 18:46 | 0:06 | 0 | 6 | [5 empty] | At New Duburi-D/P
|  | 15.06.17 | 15:53 | 15.06.17 | 16:09 | 0:16 | 0 | 16 | [5 empty] | At New Duburi-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
95 | 220kV New Duburi-Paradeep Ckt-II |  |  |  |  | 0.11944 | 16 | 41 | [7 empty] | 113.433 | 8760 | 99.81% | 1892.4406 | 993673.08
|  | 16.05.17 | 23:41 | 17.05.17 | 12:31 | 12:50 | 2 | 24 | [5 empty] | At New Duburi-'R', 'Y', 'B' ph, E/F, Zn.-II, Dist.-103 k.m. At Paradeep-D/P, Zn.-I, Dist.-1.9 k.m. ['Y' ph. insulator damaged at Loc. No.-420]At 01:07 hrs. Kendrapara, Pattamundai availed restricted P/S from Jajpur end. At 01:52 hrs. Paradeep availed restricted P/S from Kendrapara end. At 01:18 hrs. Jagatsingpur availed P/S from Cuttack end.
|  | 30.05.17 | 16:45 | 30.05.17 | 18:40 | 1:55 | 1 | 55 | [5 empty] | At Paradeep-Tripped
|  | 14.06.17 | 17:59 | 14.06.17 | 18:40 | 0:41 | 0 | 6 | [5 empty] | At New Duburi-D/P, 'B' ph, E/F, Zn.-I, Dist.-44.6 k.m. At Paradeep-'B' ph, O/C, Zn.-I, Dist.-54.6 k.m, [Line patrolling was done but no fault found]. After 6 minutes power flow resumed through Ckt-I
|  | 15.06.17 | 15:53 | 15.06.17 | 16:09 | 0:16 | 0 | 16 | [5 empty] | At New Duburi-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
96 | 220kV Paradeep - IOCL Ckt |  |  |  |  | 0.0048611 | 0 | 7 | [7 empty] | 6 | 8760 | 100% | 0.7 | 52560
|  | 19.10.17 | 20:07 | 19.10.17 | 20:14 | 0:07 | 0 | 7 | [5 empty] | At Paradeep-O/C, 'R' ph, E/F
97 | 220kV Paradeep - ESSAR Steel Ckt -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.868 | 8760 | 100% | 0 | 77683.68
98 | 220kV Paradeep - ESSAR Steel Ckt -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.868 | 8760 | 100% | 0 | 77683.68
99 | 220kV Rengali PH-Nalco-TTPS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 71.337 | 8760 | 100% | 0 | 624912.12
100 | 220kV Rengali GD-Rengali PG -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.4 | 8760 | 100% | 0 | 3504
101 | 220kV Rengali GD-Rengali PG -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.4 | 8760 | 100% | 0 | 3504
102 | 220kV Rengali GD-Chandiposh (T)-Tarkera |  |  |  |  | 0.36944 | 8 | 52 | [7 empty] | 162.08 | 8760 | 99.9% | 1437.1093 | 1419820.8
|  | 22.04.17 | 11:14 | 22.04.17 | 18:47 | 7:33 | 7 | 33 | [5 empty] | At Tarkera-D/P, 11 k.m.
|  | 31.07.17 | 11:24 | 31.07.17 | 12:43 | 1:19 | 1 | 19 | [5 empty] | At Rengali-Tripped
103 | 220kV Rengali GD-Barkote |  |  |  |  | 0.045833 | 14 | 25 | [7 empty] | 55 | 8760 | 99.84% | 792.9167 | 481800
|  | 31.07.17 | 11:24 | 01.08.17 | 20:59 | 33:35 | 1 | 19 | [5 empty] | ['B' ph. drop jumper snapped at Tarkera 'B' ph. jumper snapped at Loc. No.-562]. Power flow resumed through other circuit after 1 Hr 19 minutes
|  | 15.10.17 | 12:30 | 15.10.17 | 12:51 | 0:21 | 0 | 21 | [5 empty] | At Barkote-O/C
|  | 29.01.18 | 15:40 | 29.01.18 | 16:25 | 0:45 | 0 | 45 | [5 empty] | At Barkote-D/P, Dist.-15.6 k.m.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
104 | 220kV Rengali PH-Rengali GD -I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
105 | 220kV Rengali PH-Rengali GD -II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
106 | 220kV Rengali PH -STPS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.5 | 8760 | 100% | 0 | 258420
107 | 220kV STPS (Kaniha)-TTPS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.5 | 8760 | 100% | 0 | 302220
108 | 220kV STPS-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
109 | 220kV STPS-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
110 | 220kV Tarkera-Budhipadar-I |  |  |  |  | 0.10208 | 0 | 49 | [7 empty] | 109 | 8760 | 99.99% | 89.0167 | 954840
|  | 06.06.17 | 16:31 | 06.06.17 | 17:55 | 1:24 | 0 | 13 | [5 empty] | At Budhipadar-'R' ph, E/F, Zn.-I, Dist.-34.6 k.m, ILI-4.55 KA At Tarkera-D/P operated but did not trip.Weather condition was rainy, windy with heavy lightening. Prior to disturbance Auto-IV at Tarkera was under S/D
|  | 31.07.17 | 11:24 | 31.07.17 | 12:27 | 1:03 | 0 | 36 | [5 empty] | At Tarkera-D/P, Dist.-0.2 k.m. Power flow resumed through circuit-II after 36 minutes.
111 | 220kV Tarkera-Budhipadar-II |  |  |  |  | 0.058333 | 0 | 49 | [7 empty] | 109 | 8760 | 99.99% | 89.0167 | 954840
|  | 06.06.17 | 16:31 | 06.06.17 | 17:19 | 0:48 | 0 | 13 | [5 empty] | At Budhipadar-D/P, Zn.-I, 'Y' ph to E/F, Dist.-46.2 k.m, IL2 -4.10 kAAt Tarkera-'Y' ph.Weather condition was rainy, windy with heavy lightening. Prior to disturbance Auto-IV at Tarkera was under S/D
|  | 31.07.17 | 11:24 | 31.07.17 | 12:00 | 0:36 | 0 | 36 | [5 empty] | At Budhipadar-D/P
112 | 220kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
113 | 220kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
114 | 220kV Therubali-Narendrapur-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 196 | 8760 | 100% | 0 | 1716960
115 | 220kV Therubali-Narendrapur-II |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 196 | 8760 | 100% | 68.6 | 1716960
|  | 16.05.17 | 22:59 | 16.05.17 | 23:20 | 0:21 | 0 | 21 | [5 empty] | At Theruvali-'B' ph. to E/F, Bus bar relay
116 | 220kV Therubali-Bhanjanagar-I |  |  |  |  | 0.023611 | 0 | 34 | [7 empty] | 171.46 | 8760 | 99.99% | 97.1607 | 1501989.6
|  | 16.05.17 | 22:59 | 16.05.17 | 23:13 | 0:14 | 0 | 14 | [5 empty] | At Theruvali-Bus bar relay operated with Zn.-I
|  | 09.01.18 | 11:42 | 09.01.18 | 12:02 | 0:20 | 0 | 20 | [5 empty] | At Theruvali-Bus bar protection
117 | 220kV Therubali-Bhanjanagar-II |  |  |  |  | 0.020139 | 0 | 29 | [7 empty] | 171.46 | 8760 | 99.99% | 82.8723 | 1501989.6
|  | 16.05.17 | 22:59 | 16.05.17 | 23:13 | 0:14 | 0 | 14 | [5 empty] | At Theruvali-Bus bar relay
|  | 09.01.18 | 11:42 | 09.01.18 | 11:57 | 0:15 | 0 | 15 | [5 empty] | At Theruvali-Bus bar protection
118 | 220kV TTPS-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
119 | 220kV TTPS-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
120 | 220kV TTPS-Joda-I |  |  |  |  | 0.027083 | 0 | 39 | [7 empty] | 154 | 8760 | 99.99% | 100.1 | 1349040
|  | 13.05.17 | 22:08 | 13.05.17 | 22:47 | 0:39 | 0 | 39 | [5 empty] | At TTPS-D/P, Zn.-I, D/P, Dist.-41.8 k.m, At Joda-D/P, 'R', 'Y' 'B' Zn.-II Dist.-147.8 k.m. 'R' ph. to E/F, ILI-829.85 Amp, IL2-35.42 Amp, IL3-115.17 Amp, IN-960.67 Amp, backup E/F
121 | 220kV TTPS-Joda-II |  |  |  |  | 0.065278 | 0 | 39 | [7 empty] | 154 | 8760 | 99.99% | 100.1 | 1349040
|  | 13.05.17 | 22:08 | 13.05.17 | 23:42 | 1:34 | 0 | 39 | [5 empty] | At TTPS-D/P, Zn.-I, D/P, Dist.-42 k.m.At Joda-D/P, 'R', 'Y', 'B', Zn.-II, Dist.-151.75 k.m, 'R' ph. to E/F, ILI-780.27 Amp, IL2-39.47 Amp, IL3-113.33, Amp, IN-915.1 Amp, backup E/F. After 33 minutes power flow resued through ckt-I
122 | 220kV U. Kolab-Jayanagar-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
123 | 220kV U. Kolab-Jayanagar-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
124 | 220kV U. Kolab-Therubali-Jayanagar Ckt-III |  |  |  |  | 0.034722 | 0 | 20 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 128 | 8760 | 100% | 42.6667 | 1121280
|  | 16.05.17 | 22:59 | 16.05.17 | 23:19 | 0:20 | 0 | 20 | [5 empty] | Àt Theruvali-Bus bar protection |  | 5928.174
|  | 09.01.18 | 11:42 | 09.01.18 | 12:32 | 0:50 | 0 | 0 | [5 empty] | Àt Theruvali-Bus bar protection. However Power flow evacuation resumed through alternate circuit. |  | 6056.174
132 KV
125 | 132kV Akhusing-Mohana |  |  |  |  | 0 | 0 | 0 | [7 empty] | 70 | 8760 | 100% | 0 | 613200
126 | 132kV Akhusing-Parlakhemundi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.9 | 8760 | 100% | 0 | 673644
127 | 132kV Angul-Boinda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 38.5 | 8760 | 100% | 0 | 337260
128 | 132kV Angul-Nandira (MCL)- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.826 | 8760 | 100% | 0 | 94835.76
129 | 132kV Angul-Nandira (MCL)- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.826 | 8760 | 100% | 0 | 94835.76
130 | 132kV Arya Iron - Barbil |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.9 | 8760 | 100% | 0 | 42924
131 | 132kV Arya Iron - BRPL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.008 | 8760 | 100% | 0 | 78910.08
132 | 132 kV Aska-Chatrapur-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 43.85 | 8760 | 100% | 0 | 384126
133 | 132 kV Aska-Purusottampur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.4 | 8760 | 100% | 0 | 248784
134 | 132kV Atri - Argul Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.4 | 8760 | 100% | 0 | 169944
135 | 132kV Atri - Argul Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.4 | 8760 | 100% | 0 | 169944
136 | 132kV Atri - Banki |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.9 | 8760 | 100% | 0 | 183084
137 | 132 kV Badagada-Nimapara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 36.87 | 8760 | 100% | 0 | 322981.2
138 | 132 kV Balasore-Baripada |  |  |  |  | 0 | 0 | 0 | [7 empty] | 57.3 | 8760 | 100% | 0 | 501948
139 | 132 kV Balasore-Balasore (T) |  |  |  |  | 0.013889 | 0 | 20 | [7 empty] | 3.565 | 8760 | 100% | 1.1883 | 31229.4
|  | 01.06.17 | 16:26 | 01.06.17 | 16:46 | 0:20 | 0 | 20 | [5 empty] | At Balasore-O/C, 'R' ph. to E/F
140 | 132 kV Balasore-Basta |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30 | 8760 | 100% | 0 | 262800
141 | 132 kV Balasore-Ispat Alloy |  |  |  |  | 0.22708 | 17 | 27 | [7 empty] | 6.45 | 8760 | 99.8% | 112.5525 | 56502
|  | 29.04.17 | 18:25 | 29.04.17 | 23:20 | 4:55 | 4 | 55 | [5 empty] | At Balasore-O/C, E/F ['Y' ph, insulator at Loc. No.-17, damaged
|  | 29.09.17 | 18:08 | 29.09.17 | 18:16 | 0:08 | 0 | 8 | [5 empty] | At Balasore-O/C
|  | 05.10.17 | 23:24 | 05.10.17 | 23:42 | 0:18 | 0 | 18 | [5 empty] | At Balasore-Over current
|  | 26.11.17 | 1:24 | 26.11.17 | 1:30 | 0:06 | 0 | 6 | [5 empty] | At Balasore-O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
142 | 132 kV Balasore-Birla Tyre |  |  |  |  | 0 | 19 | 34 | [7 empty] | 2.598 | 8760 | 99.78% | 50.8342 | 22758.48
|  | 01.06.17 | 17:44 | 02.06.17 | 13:18 | 19:34 | 19 | 34 | [5 empty] | At Balasore-O/C, E/F ['R' ph. insulator damaged at Loc. No.-1]
143 | 132 kV Balasore-Soro |  |  |  |  | 0.39306 | 14 | 2 | [7 empty] | 29.995 | 8760 | 99.84% | 420.9298 | 262756.2
|  | 22.04.17 | 13:32 | 22.04.17 | 17:34 | 4:02 | 0 | 18 | [5 empty] | At Balasore-'Y' ph, O/C, E/F, d/P, Zn.-I, Dist.-19.53 k.m. [Line patrolling was done but no fault found]At 13:50 hrs. Soro availed P/S from Bhadrak end
|  | 15.08.17 | 14:00 | 15.08.17 | 14:12 | 0:12 | 0 | 12 | [5 empty] | At Balasore-Zn-I, 'B' ph to E/F
|  | 18.09.17 | 7:03 | 18.09.17 | 12:15 | 5:12 | 1 | 32 | [5 empty] | At Balasore-D/P, Zn.-I, 'R'ph. to E/F, Dist.-14.96 k.m.[Line patrolling was done but no fault found]At 08:57 hrs. Soro availed P/S from Bhadrak end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
144 | 132 kV Balasore-Somnathpur-EMAMI |  |  |  |  | 0.12431 | 14 | 59 | [7 empty] | 8.571 | 8760 | 99.83% | 128.4221 | 75081.96
|  | 04.06.17 | 14:12 | 04.06.17 | 14:31 | 0:19 | 0 | 19 | [5 empty] | At Balasore-'R' ph. to E/F, O/C
|  | 29.07.17 | 11:07 | 29.07.17 | 13:26 | 2:19 | 2 | 19 | [5 empty] | At Balasore-L1 to N, Zn.-I, O/C, E/F [Line patrolling was done but no fault found]
|  | 13.12.17 | 0:40 | 13.12.17 | 1:01 | 0:21 | 0 | 21 | [5 empty] | At Balasore-O/C, E/F, D/P, 'B' ph, Zn.-II
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
145 | 132kV Balugaon-Chandpur - Khurda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 73.166 | 8760 | 100% | 0 | 640934.16
146 | 132 kv Balugaon-Solari(T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.5 | 8760 | 100% | 0 | 127020
147 | 132kV Barbil - Nalda(T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.9 | 8760 | 100% | 0 | 104244
148 | 132 kV Bargarh-Barpalli |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20 | 8760 | 100% | 0 | 175200
149 | 132 kV Bargarh-ACC Ckt I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.87 | 8760 | 100% | 0 | 25141.2
150 | 132 kV Bargarh-ACC Ckt II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.87 | 8760 | 100% | 0 | 25141.2
151 | 132 kV Bargarh-Katapalli |  |  |  |  | 0 | 0 | 0 | [7 empty] | 32.32 | 8760 | 100% | 0 | 283123.2
152 | 132kV Baripada-Kuchei PG |  |  |  |  | 0.076389 | 13 | 50 | [7 empty] | 3.1 | 8760 | 99.84% | 42.8833 | 27156
|  | 09.05.17 | 10:25 | 09.05.17 | 10:50 | 0:25 | 0 | 25 | [5 empty] | At Baripada-D/P
|  | 09.05.17 | 16:37 | 09.05.17 | 17:21 | 0:44 | 0 | 44 | [5 empty] | At Baripada-'Y' ph, 5.26 k.m, Fault current-5.61 KA
|  | 02.12.17 | 12:13 | 02.12.17 | 12:37 | 0:24 | 0 | 24 | [5 empty] | At Baripada-E/F. ['Y' ph. LA of 160 MVA Auto on 220 kV side burst at Baripada PG]
|  | 29.12.17 | 15:28 | 29.12.17 | 15:45 | 0:17 | 0 | 17 | [5 empty] | At Baripada-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
153 | 132 kV Barpalli-Bolangir New |  |  |  |  | 0.0090278 | 0 | 13 | [7 empty] | 60 | 8760 | 100% | 13 | 525600
|  | 05.05.17 | 14:07 | 05.05.17 | 14:20 | 0:13 | 0 | 13 | [5 empty] | At New Bolangir-O/C, 'Y' ph.
154 | 132 kV Basta-Jaleswar |  |  |  |  | 0.6125 | 14 | 42 | [7 empty] | 26.844 | 8760 | 99.83% | 394.6068 | 235153.44
|  | 27.07.17 | 9:13 | 27.07.17 | 23:24 | 14:11 | 14 | 11 | [5 empty] | At Basta-D/P, Dist-23.35 km [At Loc. No-188 Insulator puncture and conductor snapped near Loc. No.-3 from Jaleswar]
|  | 16.08.17 | 16:40 | 16.08.17 | 17:11 | 0:31 | 0 | 31 | [5 empty] | At Basta-'Y' ph. To E/F, Zn.-I, Dist.-7.55 k.m.
155 | 132kV BCMohanty-Bamnipal(Tisco) |  |  |  |  | 0.26042 | 6 | 15 | [7 empty] | 10 | 8760 | 99.93% | 62.5 | 87600
|  | 15.01.18 | 7:58 | 15.01.18 | 14:13 | 6:15 | 6 | 15 | [5 empty] | [Earthwire snapped between Loc. No.- 34 to 43]
156 | 132kV BCMohanty-Tomka (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.86 | 8760 | 100% | 0 | 103893.6
157 | 132kV Beekay Stel-Bhalulata |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.4 | 8760 | 100% | 0 | 240024
158 | 132kV Berhampur-Aska |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.98 | 8760 | 100% | 0 | 297664.8
159 | 132kV Berhampur-Digpahandi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.882 | 8760 | 100% | 0 | 279286.32
160 | 132kV Bhadrak-FACOR |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.564 | 8760 | 100% | 0 | 39980.64
161 | 132kV Bhadrak-Damara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 64.7 | 8760 | 100% | 0 | 566772
162 | 132kV Bhadrak-Damara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35.7 | 8760 | 100% | 0 | 312732
163 | 132kV Bhadrak-Bhdrak Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.086 | 8760 | 100% | 0 | 70833.36
164 | 132kV Bhadrak-Jajpur Town |  |  |  |  | 0 | 0 | 20 | [7 empty] | 40.519 | 8760 | 100% | 13.5063 | 354946.44
|  | 15.05.17 | 18:16 | 16.05.17 | 21:17 | 27:01 | 0 | 20 | [5 empty] | ['B' ph. Conductor snapped between Loc. No.- 146 and 147]At 18:36 hrs. Jajpur Town availed P/S from Jajpur Road end
165 | 132kV Bhanjanagar-Aska-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.72 | 8760 | 100% | 0 | 295387.2
166 | 132kV Bhanjanagar-Aska-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.72 | 8760 | 100% | 0 | 295387.2
167 | 132KV Bhanjanagar-Phulabani |  |  |  |  | 0.1 | 14 | 24 | [7 empty] | 86.5 | 8760 | 99.84% | 1245.6 | 757740
|  | 06.05.17 | 16:33 | 06.05.17 | 17:33 | 1:00 | 1 | 0 | [5 empty] | At Bhanjanagar-Tripped
|  | 05.09.17 | 14:02 | 05.09.17 | 14:20 | 0:18 | 0 | 18 | [5 empty] | At Bhanjanagar-'R' ph. to E/F
|  | 02.10.17 | 13:13 | 02.10.17 | 13:45 | 0:32 | 0 | 32 | [5 empty] | At Bhanjanagar-'R'ph to E/F
|  | 02.10.17 | 14:02 | 02.10.17 | 14:36 | 0:34 | 0 | 34 | [5 empty] | At Bhanjanagar-D/P, Zn-I, Dist-56.46 km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
168 | 132kV Bhawanipatna-Junagarh |  |  |  |  | 0.13056 | 3 | 8 | [7 empty] | 25.158 | 8760 | 99.96% | 78.8284 | 220384.08
|  | 25.05.17 | 6:40 | 25.05.17 | 9:48 | 3:08 | 3 | 8 | [5 empty] | ['Y' ph. Jumper snapped at Loc. No.-2 in Bhawanipatna-Junagarh Section]
169 | 132kV Bhubaneswar-Phulnakhara |  |  |  |  | 0.93542 | 0 | 36 | [7 empty] | 23.14 | 8760 | 99.99% | 13.884 | 202706.4
|  | 13.04.17 | 16:35 | 14.04.17 | 8:38 | 16:03 | 0 | 17 | [5 empty] | ['Y' ph. SF6 breaker limt burst at Phulnakhara S/s]At 16:52 hrs. Phulnakhara S/s availed P/S from Cuttack Grid
|  | 14.02.18 | 12:10 | 14.02.18 | 18:34 | 6:24 | 0 | 19 | [5 empty] | At Bhubaneswar-'R' ph, O/C, E/F ['R' ph insulator damaged at Loc. No-16] At 12:29 hrs. Phulnakhara availed P/S from Cuttack S/s
170 | 132kV Bidanasi-Bhubaneswar Power-Chandaka |  |  |  |  | 0.35903 | 8 | 37 | [7 empty] | 35.34 | 8760 | 99.9% | 304.513 | 309578.4
|  | 28.02.18 | 4:20 | 28.02.18 | 12:57 | 8:37 | 8 | 37 | [5 empty] | At Chandaka-H/T ['Y' ph. insulator damaged at Loc. No.-13]
171 | 132kV Boinda-Rairakhol |  |  |  |  | 0 | 0 | 0 | [7 empty] | 60 | 8760 | 100% | 0 | 525600
172 | 132kV Bolangir-Sonepur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 53.845 | 8760 | 100% | 0 | 471682.2
173 | 132 kV Bolangir New - Bolangir Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.78 | 8760 | 100% | 0 | 33112.8
174 | 132 kV Bolangir New - Bolangir Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.008 | 8760 | 100% | 0 | 26350.08
175 | 132kV Bolangir New-Patnagarh |  |  |  |  | 0.0097222 | 0 | 14 | [7 empty] | 39.805 | 8760 | 100% | 9.2878 | 348691.8
|  | 05.01.18 | 8:30 | 05.01.18 | 8:44 | 0:14 | 0 | 14 | [5 empty] | At New Bolangir-Under voltage
176 | 132kVBolani-Arya Iron |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.2 | 8760 | 100% | 0 | 28032
177 | 132kV BRPL-Mesco |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5 | 8760 | 100% | 0 | 43800
178 | 132kV Budhipadar-Jharsuguda |  |  |  |  | 0.010417 | 0 | 15 | [7 empty] | 7 | 8760 | 100% | 1.75 | 61320
|  | 04.08.17 | 11:29 | 04.08.17 | 11:44 | 0:15 | 0 | 15 | [5 empty] | At Budhipadar-E/F
179 | 132kV Budhipadar-Rajgangpur ckt-II |  |  |  |  | 0.10278 | 14 | 25 | [7 empty] | 80 | 8760 | 99.84% | 1153.3333 | 700800
|  | 26.09.17 | 21:46 | 26.09.17 | 22:06 | 0:20 | 0 | 20 | [5 empty] | At Budhipadar-D/P
|  | 07.10.17 | 21:08 | 07.10.17 | 22:20 | 1:12 | 1 | 9 | [5 empty] | At Rajgangpur-TrippedAfter 1 HR 9 mins power flow resumed from Tarketra end.
|  | 31.01.18 | 16:57 | 31.01.18 | 17:53 | 0:56 | 0 | 56 | [5 empty] | At Budhipadar-D/P, Zn.-II
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
180 | 132kV Budhipadar-Sundargarh-I |  |  |  |  | 0.085417 | 2 | 3 | [7 empty] | 31.61 | 8760 | 99.98% | 64.8005 | 276903.6
|  | 12.06.17 | 16:06 | 12.06.17 | 16:15 | 0:09 | 0 | 9 | [5 empty] | At Budhipadar-Tripped
|  | 20.11.17 | 15:07 | 20.11.17 | 17:01 | 1:54 | 1 | 54 | [5 empty] | At Budhipadar-O/C, E/F, 'Y' ph
181 | 132kV Budhipadar-Sundargarh-II |  |  |  |  | 0.0069444 | 2 | 4 | [7 empty] | 31.61 | 8760 | 99.98% | 65.3273 | 276903.6
|  | 12.06.17 | 16:06 | 12.06.17 | 16:16 | 0:10 | 0 | 10 | [5 empty] | At Budhipadar-Tripped
|  | 20.11.17 | 15:07 | 21.11.17 | 12:23 | 21:16 | 1 | 54 | [5 empty] | At Sundergarh-O/C, E/F, 'Y' ph, D/P, Zn-I.['Y' ph. conductor snapped at Loc. No.-91]. After 1 Hr 54 mins power flow resumed through ckt-I
182 | 132kV Budhipadar-MCL(Jorbaga)-I |  |  |  |  | 0.0048611 | 0 | 34 | [7 empty] | 23 | 8760 | 99.99% | 13.0333 | 201480
|  | 24.04.17 | 12:24 | 24.04.17 | 12:31 | 0:07 | 0 | 34 | [5 empty] | At Budhipadar-Back up
|  | 24.04.17 | 12:41 | 25.04.17 | 8:55 | 20:34 | [7 empty] | At Budhipadar-D/P, 'B' ph, E/F [Line patrolling was done but no fault found]
183 | 132kV Budhipadar-MCL(Jorbaga)-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23 | 8760 | 100% | 0 | 201480
184 | 132kV Budhipadar-MSP |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.592 | 8760 | 100% | 0 | 5185.92
185 | 132kV Budhipadar-Brajarajnagar (Remja) |  |  |  |  | 0.013194 | 0 | 19 | [7 empty] | 11.745 | 8760 | 100% | 3.7192 | 102886.2
|  | 02.04.17 | 22:02 | 02.04.17 | 22:21 | 0:19 | 0 | 19 | [5 empty] | At Budhipadar-D/P, E/F, 'B' ph.
186 | 132kV Budhipadar - Kalunga-I |  |  |  |  | 0.015972 | 0 | 8 | [7 empty] | 100 | 8760 | 100% | 13.3333 | 876000
|  | 07.08.17 | 18:35 | 07.08.17 | 18:58 | 0:23 | 0 | 8 | [5 empty] | At Budhipadar-D/P. After 8 minutes power flow resumed through Tarkera end.
187 | 132kV Burla-Chipilima Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.9 | 8760 | 100% | 0 | 174324
188 | 132kV Burla-Hindalco-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9 | 8760 | 100% | 0 | 78840
189 | 132kV Burla-Hindalco-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9 | 8760 | 100% | 0 | 78840
190 | 132kV Burla-Katapali-Chipilima Ckt-II |  |  |  |  | 0.041667 | 1 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 22.66 | 8760 | 99.99% | 22.66 | 198501.6
|  | 18.05.17 | 23:48 | 19.05.17 | 0:48 | 1:00 |  |  | 1 | 0 |  |  |  | At Burla PH-Tripped
191 | 132kV Burla-Katapalli |  |  |  |  | 0.47639 | 1 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 7 | 8760 | 99.99% | 7 | 61320
|  | 18.05.17 | 23:48 | 19.05.17 | 11:14 | 11:26 |  |  | 1 | 0 |  |  |  | At Burla PH-Tripped
192 | 132kV Burla-Lapanga-Budhipadar-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 63.25 | 8760 | 100% | 0 | 554070
193 | 132kV Burla-Lapanga-Budhipadar-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 63.25 | 8760 | 100% | 0 | 554070
194 | 132kV Burla-Sambalpur |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 19.9 | 8760 | 100% | 0 | 174324
195 | 132kV Chainpal-Angul |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.931 | 8760 | 100% | 0 | 130795.56
196 | 132kV Chainpal-FCI-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7 | 8760 | 100% | 0 | 61320
197 | 132kV Chainpal-FCI-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7 | 8760 | 100% | 0 | 61320
198 | 132kV Chainpal-Talcher Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.448 | 2088 | 100% | 0 | 935.424
199 | 132kV Chandaka-Bhubaneswar-I |  |  |  |  | 0.022917 | 0 | 15 | [7 empty] | 5.5 | 8760 | 100% | 1.375 | 48180
|  | 18.08.17 | 15:26 | 18.08.17 | 15:47 | 0:21 | 0 | 3 | [5 empty] | At Both ends-E/F. After 3 minutes power flow resumed through Ckt-II
|  | 05.09.17 | 11:37 | 05.09.17 | 11:41 | 0:04 | 0 | 4 | [5 empty] | At Bhubaneswar-O/C
|  | 14.02.18 | 12:10 | 14.02.18 | 12:18 | 0:08 | 0 | 8 | [5 empty] | At Bhubaneswar-Tripped
200 | 132kV Chandaka-Bhubaneswar-II |  |  |  |  | 0.073611 | 0 | 4 | [7 empty] | 5.5 | 8760 | 100% | 0.36667 | 48180
|  | 05.09.17 | 11:37 | 05.09.17 | 13:04 | 1:27 | 0 | 4 | [5 empty] | At Chandaka-Tripped. After 4 minutes power flow resumed through ckt-I.
|  | 14.02.18 | 12:10 | 14.02.18 | 12:29 | 0:19 | 0 | 8 | [5 empty] | At Bhubaneswar-Tripped
201 | 132kV Chandaka-Mendhasal |  |  |  |  | 0.17014 | 0 | 37 | [7 empty] | 18.5 | 8760 | 99.99% | 11.4083 | 162060
|  | 28.02.18 | 4:20 | 28.02.18 | 8:25 | 4:05 | 0 | 37 | [5 empty] | At Chandaka-O/C
202 | 132kV Chandaka-Nimapara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 62 | 8760 | 100% | 0 | 543120
203 | 132kV Chandaka-Ransingpur |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 28.25 | 8760 | 100% | 3.7667 | 247470
|  | 16.04.17 | 21:06 | 16.04.17 | 21:14 | 0:08 | 0 | 8 | [5 empty] | At Chandaka-'Y' ph. to E/F, Dist.-7.49 k.m., Zn.-I
204 | 132kV Chandikhol-Kendrapada |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.6 | 8760 | 100% | 0 | 276816
205 | 132kV Chatrapur-Balugaon |  |  |  |  | 0 | 0 | 29 | [7 empty] | 54.19 | 8760 | 99.99% | 26.1918 | 474704.4
|  | 01.08.17 | 11:07 | 01.08.17 | 15:21 | 4:14 | 0 | 29 | [5 empty] | At Narendrapur-'R' ph. To E/F, Dist.-47.7 k.m, Zn.-I[Tree fell on line at Loc. No.-283]At 11:36 hrs. Balugon availed P/S from Khurda
206 | 132kV Chatrapur-Ganjam |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.6 | 8760 | 100% | 0 | 110376
207 | 132kV Chatrapur-IRE-I |  |  |  |  | 0.37153 | 0 | 18 | [7 empty] | 5.8 | 8760 | 100% | 1.74 | 50808
|  | 13.08.17 | 11:44 | 13.08.17 | 20:39 | 8:55 | 0 | 18 | [5 empty] | After 18 minuts power flow resumed through ckt-II
208 | 132kV Chatrapur-IRE-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.8 | 8760 | 100% | 0 | 50808
209 | 132kV Chatrapur-Rambha (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.904 | 8760 | 100% | 0 | 253199.04
210 | 132kV Chhend-Adhunik Metalics |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.44 | 8760 | 100% | 0 | 214094.4
211 | 132kV Chhend-Nuagaon(T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35 | 8760 | 100% | 0 | 306600
212 | 132kV Chipilima-Katapalli Ckt-I |  |  |  |  | 0.040278 | 2 | 56 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 99.97% | 37.136 | 110901.6
|  | 18.05.17 | 23:48 | 19.05.17 | 0:46 | 0:58 | 1 | 58
213 | 132kV Chipilima-Katapalli Ckt-II |  |  |  |  | 0.040278 | 2 | 56 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 99.97% | 37.136 | 110901.6
|  | 18.05.17 | 23:48 | 19.05.17 | 0:46 | 0:58 | 1 | 58 | [5 empty] | At Chiplima-Tripped
214 | 132kV Choudwar-Bidanasi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.414 | 8760 | 100% | 0 | 135026.64
215 | 132kV Choudwar-Kendrapara Road Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.6 | 8760 | 100% | 0 | 40296
216 | 132kV Cuttack-Jagatsingpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35.112 | 8760 | 100% | 0 | 307581.12
217 | 132kV Cuttack-Phulnakhara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.256 | 8760 | 100% | 0 | 177442.56
218 | 132kV Dabugaon -Umerkote |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.89 | 8760 | 100% | 0 | 401996.4
219 | 132kV Dhenkanal-Grid Steel -ICCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 37.74 | 8760 | 100% | 0 | 330602.4
220 | 132kV Dhenkanal-Joranda (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.345 | 8760 | 100% | 0 | 169462.2
221 | 132kV Duburi-BC Mohanty |  |  |  |  | 0.37431 | 53 | 47 | [7 empty] | 10.974 | 8760 | 99.39% | 590.2183 | 96132.24
|  | 06.05.17 | 23:07 | 07.05.17 | 2:54 | 03:47 | 3 | 47 | [5 empty] | At Duburi-D/P ['Y' ph. LA burst at B.C. Mohanty end]
|  | 14.05.17 | 9:14 | 14.05.17 | 17:43 | 8:29 | 8 | 29 | [5 empty] | ['Y' ph. LA burst at B.C. Mohanty end]
|  | 28.06.17 | 13:58 | 29.06.17 | 18:39 | 28:41 | 28 | 41 | [5 empty] | ['Y' ph. conductor snapped between Loc. No.-2 and 3]
|  | 03.07.17 | 15:04 | 03.07.17 | 15:34 | 0:30 | 0 | 30 | [5 empty] | At Duburi-E/F, Dist.-1.84 k.m.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
222 | 132kV Duburi-BRPL |  |  |  |  | 0.51319 | 12 | 19 | [7 empty] | 4.43 | 8760 | 99.86% | 54.5628 | 38806.8
|  | 07.11.17 | 14:10 | 07.11.17 | 17:54 | 3:44 | 3 | 44 | [5 empty] | At Duburi-Master trip['B' ph. conductor snapped between Loc. No.-3 and 4 and insulator damaged at Loc. No.-3]
|  | 13.12.17 | 11:22 | 13.12.17 | 19:57 | 8:35 | 8 | 35 | [5 empty] | At Duburi-Tripped ['R' ph. insulator puncture at Loc. No.-3]
223 | 132kV Duburi-Jajpur Road-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.2 | 8760 | 100% | 0 | 115632
224 | 132kV Duburi-Jajpur Road-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.2 | 8760 | 100% | 0 | 115632
225 | 132kV Duburi-Jakhapura (T) |  |  |  |  | 0 | 14 | 35 | [7 empty] | 12.851 | 8760 | 99.83% | 187.4104 | 112574.76
|  | 20.05.17 | 19:11 | 21.05.17 | 9:46 | 14:35 | 14 | 35 | [5 empty] | At Duburi-D/P ['R' ph, insulator damage at Loc. No.-35 and earth wire snapped between Loc. No.-34 and 36]
226 | 132kV Duburi-Mesco |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.65 | 8760 | 100% | 0 | 58254
227 | 132kV ICCL-Choudwar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.5 | 8760 | 100% | 0 | 4380
228 | 132kV ICCL-Mania-OCL |  |  |  |  | 0.14167 | 3 | 24 | [7 empty] | 20.2 | 8760 | 99.96% | 68.68 | 176952
|  | 12.06.17 | 12:46 | 12.06.17 | 16:10 | 3:24 | 3 | 24 | [5 empty] | ['R' ph. insulator damaged at Loc. No.-91]
229 | 132kV Jabamayee FAlloys-Duburi-II |  |  |  |  | 0.011806 | 0 | 17 | [7 empty] | 12 | 8760 | 100% | 3.4 | 105120
|  | 05.09.17 | 13:35 | 05.09.17 | 13:52 | 0:17 | 0 | 17 | [5 empty] | At Jabamayee-D/P
230 | 132kVJagatsinghpur-Gorakhnath (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 16.53 | 8760 | 100% | 0 | 144802.8
231 | 132kVJajpur Road-Anandpur Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30 | 8760 | 100% | 0 | 262800
232 | 132kVJajpur Road-Anandpur Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30 | 8760 | 100% | 0 | 262800
233 | 132kVJajpur Road-Chandikhol |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.71 | 8760 | 100% | 0 | 304059.6
234 | 132kVJajpur Road-Jajpur Town |  |  |  |  | 0 | 0 | 0 | [7 empty] | 25.451 | 8760 | 100% | 0 | 222950.76
235 | 132kVJajpur Road-Kendrapada Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 63.11 | 8760 | 100% | 0 | 552843.6
236 | 132kVJaleswar-Bhogarai |  |  |  |  | 0 | 0 | 0 | [7 empty] | 57.934 | 8760 | 100% | 0 | 507501.84
237 | 132kVJaleswar-Jaleswar (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.34 | 8760 | 100% | 0 | 20498.4
238 | 132kVJaynagar-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.272 | 8760 | 100% | 0 | 396582.72
239 | 132kVJaynagar-Jaynagar(T) |  |  |  |  | 0.0027778 | 0 | 4 | [7 empty] | 40 | 8760 | 100% | 2.6667 | 350400
|  | 19.04.17 | 19:48 | 19.04.17 | 19:52 | 0:04 | 0 | 4 | [5 empty] | At Jayanagar-Zn.-I, 'R' ph, Dist.-1.57 k.m, E/F
240 | 132kVJaynagar-Podagada-Rayagada |  |  |  |  | 0 | 0 | 0 | [7 empty] | 112.236 | 8760 | 100% | 0 | 983187.36
241 | 132kVJaynagar-Sunabeda |  |  |  |  | 0.030556 | 0 | 44 | [7 empty] | 40 | 8760 | 99.99% | 29.3333 | 350400
|  | 13.05.17 | 15:25 | 13.05.17 | 16:09 | 0:44 | 0 | 44 | [5 empty] | At Jayanagar-'Y' ph. E/F
242 | 132kVJaynagar-Tentulikhunti |  |  |  |  | 0 | 0 | 0 | [7 empty] | 56.4 | 8760 | 100% | 0 | 494064
243 | 132kVJharsuguda-Jharsuguda(T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.15 | 8760 | 100% | 0 | 1314
244 | 132kVJharsuguda-L & T |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.56 | 8760 | 100% | 0 | 276465.6
245 | 132kVJoda- Banaspani(T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.99 | 8760 | 100% | 0 | 26192.4
246 | 132kVJoda -Bolani |  |  |  |  | 0 | 0 | 0 | [7 empty] | 18 | 8760 | 100% | 0 | 157680
247 | 132kVJoda-FAP |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.03 | 8760 | 100% | 0 | 9022.8
248 | 132kVJoda-Kenduposi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 49.92 | 8760 | 100% | 0 | 437299.2
249 | 132kVJoda-Palasponga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 42 | 8760 | 100% | 0 | 367920
250 | 132kV Kamakhya Nagar -Kalarangi-Duburi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 74.84 | 8760 | 100% | 0 | 655598.4
251 | 132kV Kantabanji- Kantabanji Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4 | 72 | 100% | 0 | 288
252 | 132kV Karanjia-Palasponga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 84 | 8760 | 100% | 0 | 735840
253 | 132kV Karanjia-Dhenkikote |  |  |  |  | 0 | 0 | 0 | [7 empty] | 41.902 | 168 | 100% | 0 | 7039.536
254 | 132kV Katapalli-Sambalpur-Rairakhol |  |  |  |  | 0 | 0 | 0 | [7 empty] | 58 | 8760 | 100% | 0 | 508080
255 | 132kV Kendrapada-Marshaghai-Paradeep ckt-I |  |  |  |  | 0.12778 | 12 | 23 | [7 empty] | 37.57 | 8760 | 99.86% | 465.2418 | 329113.2
|  | 05.08.17 | 18:35 | 06.08.17 | 8:32 | 13:47 | 0 | 9 | [5 empty] | At Paradeep-D/P, Dist.-10.22 k.m, 'Y' ph. ['Y' ph. jumper snapped at Loc. No.-276]. After 9 minutes power flow resumed through ckt-II
|  | 21.08.17 | 17:21 | 22.08.17 | 15:17 | 21:56 | 0 | 6 | [5 empty] | ['Y' ph. conductor snapped at Loc. No.-257]. After 6 minutes power flow resumed through ckt-I
|  | 22.12.17 | 18:39 | 22.12.17 | 21:43 | 3:04 | 0 | 8 | [5 empty] | At Paradeep-'B' ph. to E/F, Dist.-30.5 k.m.. Afte 8 mins power flow resumed through ckt-II
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
256 | 132kV Kendrapada-Paradeep Ckt-II |  |  |  |  | 0.35833 | 19 | 1 | [7 empty] | 34.774 | 8760 | 99.78% | 661.2856 | 304620.24
|  | 05.08.17 | 18:35 | 05.08.17 | 18:44 | 0:09 | 0 | 9 | [5 empty] | At Paradeep-D/P, Dist.-28.76 k.m, 'Y' ph.
|  | 22.08.17 | 0:54 | 22.08.17 | 9:13 | 8:19 | 6 | 44 | [5 empty] | At Paradeep-D/P, 'B' ph. to E/F Dist.-2.54 k.m. ['Y' ph. jumper snapped at Loc. No.-314] At 07:38 hrs. Kendrapara availed P/S from Jajpur Road end.132 kV Marshaghai-Kendrapara Ckt was under B/D.
|  | 22.12.17 | 18:39 | 22.12.17 | 18:47 | 0:08 | 0 | 8 | [5 empty] | At Paradeep-'Y' ph. to E/F, Dist.-29.26 k.m.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
257 | 132kV Kendrapada-Pattamundai |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.5 | 8760 | 100% | 0 | 170820
258 | 132kV Kesinga-Bhawanipatna |  |  |  |  | 0.48889 | 11 | 44 | [7 empty] | 40.61 | 8760 | 99.87% | 476.4907 | 355743.6
|  | 25.05.17 | 6:40 | 25.05.17 | 9:48 | 3:08 | 3 | 8 | [5 empty] | ['Y' ph. Jumper snapped at Loc. No.-2 in Bhawanipatna-Junagarh Section]
|  | 30.08.17 | 7:54 | 30.08.17 | 16:30 | 8:36 | 8 | 36 | [5 empty] | At Kesinga-D/P, Dist.-19.97 k.m. [Line patrolling was done but no fault found]
259 | 132kV Kesinga-Khariar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 58.5 | 8760 | 100% | 0 | 512460
260 | 132kV Kesinga-Powmex |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.532 | 8760 | 100% | 0 | 127300.32
261 | 132kV Kesinga-Saintala |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.2 | 8760 | 100% | 0 | 290832
262 | 132kV Kharagprasad-Kharagprasad (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.17 | 8760 | 100% | 0 | 10249.2
263 | 132kV Kharagprasad-MGM Ckt |  |  |  |  | 0.01875 | 0 | 27 | [7 empty] | 7.14 | 8760 | 99.99% | 3.213 | 62546.4
|  | 19.04.17 | 17:06 | 19.04.17 | 17:18 | 0:12 | 0 | 12 | [5 empty] | At Kharagprasad-E/F
|  | 20.03.18 | 12:59 | 20.03.18 | 13:14 | 0:15 | 0 | 15 | [5 empty] | At Kharagprasad-O/C, E/F
264 | 132kV Kharagprasad-Nabhabharat Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.577 | 8760 | 100% | 0 | 5054.52
265 | 132kV Kharagprasad-Nabhabharat Ckt-II |  |  |  |  | 0.017361 | 0 | 25 | [7 empty] | 0.577 | 8760 | 100% | 0.24042 | 5054.52
|  | 19.04.17 | 17:06 | 19.04.17 | 17:31 | 0:25 | 0 | 25 | [5 empty] | At Kharagprasad-O/C, E/F
266 | 132kV Kharagprasad-Samal Metallic |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.03 | 8760 | 100% | 0 | 9022.8
267 | 132 kV Khariar - Kantabanji |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33 | 72 | 100% | 0 | 2376
268 | 132 kV Khariar - Nuapara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 77.232 | 8760 | 100% | 0 | 676552.32
269 | 132kV Khurda-Argul-Shamuka |  |  |  |  | 0 | 0 | 0 | [7 empty] | 54.742 | 8760 | 100% | 0 | 479539.92
270 | 132kV Khurda-Kaipadar (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.259 | 8760 | 100% | 0 | 98628.84
271 | 132kV Kuchei PG- Bangiriposhi- Rairangapur |  |  |  |  | 0.25069 | 14 | 42 | [7 empty] | 76.886 | 8760 | 99.83% | 1130.2242 | 673521.36
|  | 22.04.17 | 17:38 | 22.04.17 | 18:15 | 0:37 | 0 | 37 | [5 empty] | At Rairangpur-Dist.-30.776 k.m. IR-105.9 Amp, IY-120.25 Amp, IB-117.21 Amp, 'R' ph to 'Y' ph. At Bangriposi 5.5 k.m, IR-3 kA, IY-2.82 kA, IB-3.26 kA, 'R' ph to 'Y' ph.
|  | 11.05.17 | 15:26 | 11.05.17 | 15:39 | 0:13 | 0 | 13 | [5 empty] | At Bangriposi-O/C, 'B' ph, Zn.-I, Dist.-1.4 k.m.
|  | 02.10.17 | 10:50 | 02.10.17 | 11:21 | 0:31 | 0 | 31 | [5 empty] | At Baripada PG-'R' ph, E/F, Zn.-II, Dist.-15.88 km.
|  | 29.12.17 | 15:28 | 29.12.17 | 20:08 | 4:40 | 1 | 21 | [5 empty] | At Baripada PG-Tripped. ['Y' ph. LA burst at Baripada PG end] At 16:49 hrs. Bangriposi availed P/S from Rairangpur end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
272 | 132kV Kuchei PG- Jaleswar ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 79.282 | 8760 | 100% | 0 | 694510.32
273 | 132kV Kuchei PG- Bhogarai - Jaleswar ckt - II |  |  |  |  | 0.050694 | 1 | 13 | [7 empty] | 132.716 | 5876 | 99.98% | 161.4711 | 779839.216
|  | 23.02.18 | 8:54 | 23.02.18 | 10:07 | 1:13 | 1 | 13 | [5 empty] | At BaripadaPG-Tripped
274 | 132kV Kuchinda-Bamara(T)-Rajgangpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 118.4 | 8760 | 100% | 0 | 1037184
275 | 132kV Lapanga - Rengali RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.308 | 5376 | 100% | 0 | 66167.808
276 | 132kV Machkund PH-Jaynagar |  |  |  |  | 1900-01-01 04:37 | 0 | 0 | [7 empty] | 43 | 8760 | 100% | 0 | 376680
|  | 11.04.17 | 0:10 | 11.04.17 | 0:30 | 0:20 |  |  | 0 | 20 |  |  |  | At Machhkund-Tripped
|  | 08.05.17 | 16:48 | 08.05.17 | 16:57 | 0:09 |  |  | 0 | 9 |  |  |  | At Machhkund-Tripped
|  | 12.05.17 | 15:03 | 12.05.17 | 15:21 | 0:18 |  |  | 0 | 18 |  |  |  | At Machhkund-H/T
|  | 13.05.17 | 14:50 | 13.05.17 | 22:30 | 7:40 |  |  | 0 | 33 |  |  |  | At Machhkund-Tripped.At 15:21 hrs. Akhusing Paralakhemundi availed P/S from Narendrapur. At 15:23 hrs. Jayanagar load changed over to Jayanagar Auto
|  | 18.05.17 | 10:55 | 18.05.17 | 22:02 | 11:07 |  |  | 0 | 8 |  |  |  | At Machhkund-Tripped At 11:03 hrs. all loads changed over
|  | 24.05.17 | 14:45 | 24.05.17 | 15:10 | 0:25 |  |  | 0 | 25 |  |  |  | At Machhkund-E/F
|  | 15.06.17 | 17:25 | 15.06.17 | 20:28 | 3:03 |  |  | 0 | 29 |  |  |  | Failed from Machhkund end.At 17:54 hrs. Jayanagar availed P/S from Jayanagar Auto
|  | 19.06.17 | 15:08 | 19.06.17 | 16:55 | 1:47 |  |  | 0 | 8 |  |  |  | Failed from Machhkund end.At 15:16 hrs. Jayanagar availed P/S from Jayanagar Auto
|  | 26.08.17 | 14:13 | 26.08.17 | 19:30 | 5:17 |  |  | 0 | 15 |  |  |  | At Machhkund-Tripped. At 14:30 hrs all the loads on Machhkund were changed over.
|  | 06.09.17 | 13:25 | 06.09.17 | 17:03 | 3:38 |  |  | 0 | 5 |  |  |  | Failed from Machhkund end. At 13:30 hrs. Rayagada, Paralakhemundi, Akhusing and Mohana changed over to OPTCL system
|  | 07.09.17 | 1:25 | 07.09.17 | 7:59 | 6:34 |  |  | 0 | 6 |  |  |  | At Machhkund-E/F, Zn.-III.At 01:31 hrs. Mohana, Rayagada, Akhusing and Paralakhemundi availed P/S from OPTCL system
|  | 08.09.17 | 9:05 | 08.09.17 | 11:27 | 2:22 |  |  | 0 | 6 |  |  |  | At Machhkund-Tripped. At 09:11 hrs. Rayagada, Paralakhemundi and Mohana load changed over to OPTCL system
|  | 26.09.17 | 18:05 | 26.09.17 | 22:26 | 4:21 |  |  | 0 | 5 |  |  |  | Failed from Machhkund end
|  | 02.10.17 | 3:25 | 02.10.17 | 6:30 | 3:05 |  |  | 3 | 5 |  |  |  | Failed from Machhkund end
|  | 27.12.17 | 17:10 | 27.12.17 | 17:29 | 0:19 |  |  | 0 | 19 |  |  |  | Failed from Machhkund end
|  | 17.03.18 | 7:13 | 17.03.18 | 9:25 | 2:12 |  |  | 1 | 17 |  |  |  | At Machhkund-Tripped. At 08:30 hrs. Akhusing, Paralakhemundi and Mohana availed P/S from Theruvali end.
277 | 132kV Machkund -Jaynagar (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 108 | 8760 | 100% | 0 | 946080
278 | 132kV Mendhasal-Chandpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35 | 8760 | 100% | 0 | 306600
279 | 132kV Mendhasal-Khurda |  |  |  |  | 0.044444 | 1 | 50 | [7 empty] | 18 | 8760 | 99.98% | 33 | 157680
|  | 29.04.17 | 22:31 | 29.04.17 | 23:21 | 0:50 | 0 | 50 | [5 empty] | At Mendhasal-D/P
|  | 29.04.17 | 23:07 | 29.04.17 | 23:21 | 0:14 | 0 | 14
280 | 132kV Meramundali-BRG |  |  |  |  | 0.0090278 | 2 | 13 | [7 empty] | 3.55 | 8760 | 99.97% | 7.8692 | 31098
|  | 28.04.17 | 6:02 | 28.04.17 | 6:15 | 0:13 | 0 | 13 | [5 empty] | At Meramundali-O/C, 'R' At BRG-E/F
|  | 01.08.17 | 13:07 | 01.08.17 | 15:06 | 1:59 | 1 | 59 | [5 empty] | At Meramundali-H/T
281 | 132kV Meramundali-Chainpal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.728 | 8760 | 100% | 0 | 15137.28
282 | 132kV Meramundali-Chainpal Ckt-II |  |  |  |  | 0 | 1 | 22 | [7 empty] | 1.728 | 8760 | 99.98% | 2.3616 | 15137.28
|  | 25.12.17 | 4:13 | 26.12.17 | 17:26 | 37:13 | 0 | 22 | [5 empty] | At Chainpal-E/F. (The line tripped due to fog)After 22 mins power flow resumed through ckt-I
|  | 23.12.17 | 6:23 | 24.12.17 | 17:05 | 34:42 | 0 | 51 | [5 empty] | At Chainpal-E/F [The lines tripped due to fog] After 51 mins power flow resumed through ckt-I
283 | 132kV Meramundali-Dhenkanal S/s |  |  |  |  | 0 | 0 | 0 | [7 empty] | 51.916 | 8760 | 100% | 0 | 454784.16
284 | 132kV Meramundali-Kharagprasad Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.517 | 8760 | 100% | 0 | 48328.92
285 | 132kV Meramundali-Kharagprasad Ckt-II |  |  |  |  | 0.0069444 | 0 | 10 | [7 empty] | 5.517 | 8760 | 100% | 0.9195 | 48328.92
|  | 19.04.17 | 17:06 | 19.04.17 | 17:16 | 0:10 | 0 | 10 | [5 empty] | At Kharagprasad-O/C, E/F
286 | 132kV Meramundali-M.L. Rungta |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.468 | 8760 | 100% | 0 | 65419.68
287 | 132kV Meramundali-Nuapatna-Khajuriakata-Aarati Steel |  |  |  |  | 0.40486 | 21 | 43 | [7 empty] | 142.06 | 8760 | 99.75% | 3085.0697 | 1244445.6
|  | 10.04.17 | 12:40 | 10.04.17 | 12:53 | 0:13 | 0 | 13 | [5 empty] | At Meramundali-'R' ph. to E/F, At Aarti-E/F
|  | 10.04.17 | 12:53 | 10.04.17 | 14:35 | 1:42 | 1 | 42
|  | 11.04.17 | 10:12 | 11.04.17 | 10:20 | 0:08 | 0 | 8 | [5 empty] | At Meramundali-'R' ph, to E/F, At Aarti-E/F
|  | 11.04.17 | 10:41 | 11.04.17 | 11:27 | 0:46 | 0 | 46
|  | 16.04.17 | 19:47 | 17.04.17 | 1:42 | 6:54 | 6 | 54 | [5 empty] | At Meramundali-Dist.-35.261 k.m. 'B' ph, to E/F, IL3-2.9 KA, O/C [Earthwire snapped between Loc. No.-137 and 138]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
288 | 132kV Mohana-Digpahandi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.882 | 8760 | 100% | 0 | 261766.32
289 | 132kV Nalda-Beekay Steel |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.4 | 8760 | 100% | 0 | 47304
290 | 132kV Narendrapur-Berhampur Ckt -I |  |  |  |  | 0.00625 | 0 | 9 | [7 empty] | 10.91 | 8760 | 100% | 1.6365 | 95571.6
|  | 25.04.17 | 10:17 | 25.04.17 | 10:26 | 0:09 | 0 | 9 | [5 empty] | At Narendrapur-D/P, Zn.-II, Dist.-11.0 k.m, 'B' ph, E/F
291 | 132kV Narendrapur-Berhampur Ckt - II |  |  |  |  | 0.00625 | 0 | 9 | [7 empty] | 10.91 | 8760 | 100% | 1.6365 | 95571.6
|  | 25.04.17 | 10:17 | 25.04.17 | 10:26 | 0:09 | 0 | 9 | [5 empty] | At Narendrapur-Backup
292 | 132kV Narendrapur-Chatrapur-I |  |  |  |  | 0.070833 | 12 | 46 | [7 empty] | 13.282 | 8760 | 99.85% | 169.5669 | 116350.32
|  | 19.04.17 | 20:53 | 19.04.17 | 21:31 | 0:38 | 0 | 28 | [5 empty] | At Narendrapur-D/P, Zn.-I, Dist.-19.9 k.m, 'B' ph. to E/F. Power flow resumed through ckt-II after 28 minutes.
|  | 19.04.17 | 21:33 | 19.04.17 | 22:19 | 0:46
|  | 13.08.17 | 11:44 | 13.08.17 | 12:02 | 0:18 | 0 | 18 | [5 empty] | At Narendrapur
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
293 | 132kV Narendrapur-Chatrapur-II |  |  |  |  | 0.19583 | 0 | 28 | [7 empty] | 13.282 | 8760 | 99.99% | 6.1983 | 116350.32
|  | 19.04.17 | 21:00 | 19.04.17 | 21:28 | 0:28 | 0 | 28 | [5 empty] | At Narendrapur-D/P, Zn.-I, 'R' ph. to E/F, Dist.-13.88 k.m.
|  | 01.08.17 | 11:07 | 01.08.17 | 15:21 | 4:14 | 0 | 29 | [5 empty] | At Narendrapur-'R' ph. To E/F, Dist.-47.7 k.m, Zn.-I[Tree fell on line at Loc. No.-283]At 11:36 hrs. Balugon availed P/S from Khurda
294 | 132kV Narendrapur-Narendrapur(T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.51 | 8760 | 100% | 0 | 4467.6
295 | 132kV NBVL-Hind Metals |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1 | 8760 | 100% | 0 | 8760
297 | 132kV Nimapara-Konark |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.31 | 8760 | 100% | 0 | 177915.6
298 | 132kV Nimapara-Puri Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30 | 8760 | 100% | 0 | 262800
299 | 132kV Nimapara-Samagara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.995 | 8760 | 100% | 0 | 245236.2
300 | 132kV OCL-Salipur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 38.81 | 8760 | 100% | 0 | 339975.6
301 | 132kV OPCL-Kamakshyanagar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 55 | 8760 | 100% | 0 | 481800
302 | 132kV Paradeep-Trtol- Jagatsinghpur |  |  |  |  | 0.19028 | 13 | 45 | [7 empty] | 66.91 | 8760 | 99.84% | 920.0125 | 586131.6
|  | 03.04.17 | 2:46 | 03.04.17 | 2:54 | 0:08 | 0 | 8 | [5 empty] | At Paradeep-O/C, 'R' ph, 'Y' ph, 'B' ph, D/P, 'B' ph. to E/F, Dist.2.9 k.m,
|  | 03.04.17 | 16:14 | 03.04.17 | 16:24 | 0:10 | 0 | 10 | [5 empty] | At Paradeep D/P, 'B' ph to E/F, Dist.-3 k.m.
|  | 12.04.17 | 2:37 | 12.04.17 | 2:42 | 0:05 | 0 | 5 | [5 empty] | At Paradeep-D/P, Zn.-I, Dist.-2.7 k.m, O/C, E/F, 'R' ph, 'Y' ph, 'B' ph.
|  | 19.04.17 | 18:48 | 19.04.17 | 19:23 | 0:35 | 0 | 35 | [5 empty] | At Paradeep-O/C, 'R', 'Y', 'B' ph. E/F
|  | 20.04.17 | 0:26 | 20.04.17 | 0:31 | 0:05 | 0 | 5 | [5 empty] | At Paradeep-O/C, E/F, 'B' ph, 'Y' ph, D/P, Zn.-I, Dist.-2.9 k.m.
|  | 19.07.17 | 9:58 | 19.07.17 | 13:15 | 3:17 | 0 | 28 | [5 empty] | [Jumper snapped]At 10:26 hrs. Jagatsinghpur availed P/S from Cuttack end
|  | 30.09.17 | 12:04 | 30.09.17 | 12:07 | 0:03 | 0 | 3 | [5 empty] | At Paradeep-O/C, E/F, Dist.-47.8 k.m.
|  | 22.11.17 | 1:02 | 22.11.17 | 1:09 | 0:07 | 0 | 7 | [5 empty] | At Paradeep-D/P
|  | 22.11.17 | 2:03 | 22.11.17 | 2:07 | 0:04 | 0 | 4 | [5 empty] | At Paradeep-D/P
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
303 | 132kV Paradeep- IFFCO - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.171 | 8760 | 100% | 0 | 62817.96
304 | 132kV Paradeep- IFFCO - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.171 | 8760 | 100% | 0 | 62817.96
305 | 132kV Paradeep-PPL-I |  |  |  |  | 0.0069444 | 0 | 10 | [7 empty] | 6.2 | 8760 | 100% | 1.0333 | 54312
|  | 28.04.17 | 23:06 | 28.04.17 | 23:11 | 0:05 | 0 | 5 | [5 empty] | At Paradeep-O/C, 'R' ph.
|  | 28.04.17 | 23:06 | 28.04.17 | 23:11 | 0:05 | 0 | 5 | [5 empty] | At Paradeep-O/C, 'R' ph,
306 | 132kV Paradeep-PPL-II |  |  |  |  | 0.018056 | 0 | 10 | [7 empty] | 6.2 | 8760 | 100% | 1.0333 | 54312
|  | 28.04.17 | 23:06 | 28.04.17 | 23:19 | 0:13 | 0 | 5 | [5 empty] | At Paradeep-O/C, 'R' ph, 'Y' ph, 'B' ph.Power flow resumed through ckt-I after 5 minutes
|  | 28.04.17 | 23:06 | 28.04.17 | 23:19 | 0:13 | 0 | 5 | [5 empty] | At Paradeep-O/C, 'R' ph. 'Y', 'B' ph.Power flow resumed through ckt-I after 5 minutes
307 | 132kV Paradeep-PPT-I |  |  |  |  | 0.46389 | 0 | 37 | [7 empty] | 7.65 | 8760 | 99.99% | 4.7175 | 67014
|  | 29.04.17 | 20:02 | 30.04.17 | 7:10 | 11:08 | 0 | 10 | [5 empty] | At Paradeep-O/C, 'B' ph [Line patrolling was done but no fault found]Power flow resumed through ckt-II after 10 minutes
|  | 28.08.17 | 22:15 | 30.08.17 | 18:42 | 44:27 | 0 | 27 | [5 empty] | At Paradeep-O/C, 'Y' ph facia display, but breaker did not trip. [Conductor snapped between Loc. No-13 to 18] After 27 minutes
308 | 132kV Paradeep-PPT-II |  |  |  |  | 0.0069444 | 0 | 10 | [7 empty] | 7.65 | 8760 | 100% | 1.275 | 67014
|  | 29.04.17 | 20:02 | 29.04.17 | 20:12 | 0:10 | 0 | 10 | [5 empty] | At Paradeep-O/C, 'B' ph
309 | 132kV Patnagarh-Padampur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 44.636 | 8760 | 100% | 0 | 391011.36
310 | 132kV Pattamundai-Olavar Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.338 | 8760 | 100% | 0 | 213200.88
311 | 132kV Pattamundai-Olavar Ckt -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.338 | 8760 | 100% | 0 | 213200.88
312 | 132kV Polasponga- Keonjhargarh (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.433 | 8760 | 100% | 0 | 170233.08
313 | 132 kV Purusottampur-Chatrapur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.45 | 8760 | 100% | 0 | 135342
314 | 132kV Rairangapur- Karanjia |  |  |  |  | 0 | 0 | 0 | [7 empty] | 71.54 | 8760 | 100% | 0 | 626690.4
315 | 132kV Rajgangapur-OCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.5 | 8760 | 100% | 0 | 4380
316 | 132kV Rajgangapur-Rajgangapur (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.2 | 8760 | 100% | 0 | 36792
317 | 132kV Rajgangpur-Rourkela |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.5 | 8760 | 100% | 0 | 240900
318 | 132kV Ranasinghpur-Badagada |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.63 | 8760 | 100% | 0 | 303358.8
319 | 132kV RAWMET-Choudwar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23 | 8760 | 100% | 0 | 201480
320 | 132kV RAWMET-Arati Steel |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17.678 | 8760 | 100% | 0 | 154859.28
321 | 132kV Rayagada-Akhusingh |  |  |  |  | 0 | 0 | 0 | [7 empty] | 50 | 8760 | 100% | 0 | 438000
322 | 132kV Rayagada-Rayagada Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.646 | 2112 | 100% | 0 | 5588.352
323 | 132kV Rayagada-VBC Ferro |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.3 | 8760 | 100% | 0 | 2628
324 | 132kV Rourkela-Bhalulata |  |  |  |  | 0.30694 | 31 | 9 | [7 empty] | 24.29 | 8760 | 99.64% | 756.6335 | 212780.4
|  | 04.04.17 | 15:25 | 04.04.17 | 22:47 | 7:22 | 0 | 28 | [5 empty] | At Rourkela-O/C[Tree fell on line between Loc. No.- 81 and 82] At 15:53 hrs. Beekay steel availed P/S from Joda end
|  | 16.05.17 | 15:47 | 17.05.17 | 10:18 | 18:31 | 18 | 31 | [5 empty] | At Rourkela-D/P, Dist.-52 k.m. [Tree fault]
|  | 25.02.18 | 22:35 | 26.02.18 | 17:33 | 18:58 | 0 | 10 | [5 empty] | At Rourkela-E/F, 'B' ph, Dist.-49.84 ['B' ph. insulator damaged at Loc. No.-174] At 22:45 hrs. B.K. Steel availed P/S from Joda end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
325 | 132kV Saintala-ACME-Tusura-Bolangir |  |  |  |  | 0 | 0 | 0 | [7 empty] | 68.018 | 8760 | 100% | 0 | 595837.68
326 | 132kV Salipur-Kendrapara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.4 | 5924 | 100% | 0 | 203785.6
327 | 132kV Samagara-Puri |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.99 | 8760 | 100% | 0 | 34952.4
328 | 132kV Sambalpur-Shyam Dri |  |  |  |  | 0 | 0 | 0 | [7 empty] | 26.589 | 8760 | 100% | 0 | 232919.64
329 | 132kV Shamuka-Puri |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17.3 | 8760 | 100% | 0 | 151548
330 | 132kV Shyam DRI-Lapanga-Aryan Ispat |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.98 | 8760 | 100% | 0 | 87424.8
331 | 132kV SMC Power-Aryan Ispat |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.95 | 8760 | 100% | 0 | 69642
332 | 132kV SMC Power-Kuchinda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 53.33 | 8760 | 100% | 0 | 467170.8
333 | 132 kV Sonepur - Boudh |  |  |  |  | 0 | 0 | 0 | [7 empty] | 51.05 | 8760 | 100% | 0 | 447198
334 | 132kV Soro-Bhadrak |  |  |  |  | 0 | 0 | 0 | [7 empty] | 46.215 | 8760 | 100% | 0 | 404843.4
335 | 132kV Sunabeda-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13 | 8760 | 100% | 0 | 113880
336 | 132kV Sunabeda-HAL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.7 | 8760 | 100% | 0 | 6132
337 | 132kV Tarkera-Kalunga |  |  |  |  | 0.011806 | 0 | 17 | [7 empty] | 15.88 | 8760 | 100% | 4.4993 | 139108.8
|  | 27.04.17 | 17:26 | 27.04.17 | 17:36 | 0:10 | 0 | 10 | [5 empty] | At Tarkera-E/F
|  | 07.08.17 | 18:36 | 07.08.17 | 18:43 | 0:07 | 0 | 7 | [5 empty] | At Tarkera-D/P, Zn.-I, Dist.-25.3 k.m, L3 to L1
338 | 132kV Tarkera-Budhipadar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 110 | 8760 | 100% | 0 | 963600
339 | 132kV Tarkera-Chhend-I |  |  |  |  | 0.020139 | 0 | 27 | [7 empty] | 6.165 | 8760 | 99.99% | 2.7742 | 54005.4
|  | 06.11.17 | 10:55 | 06.11.17 | 11:24 | 0:29 | 0 | 27 | [5 empty] | At Tarkera-D/P
340 | 132kV Tarkera-Chhend-II |  |  |  |  | 0.01875 | 0 | 27 | [7 empty] | 6.165 | 8760 | 99.99% | 2.7742 | 54005.4
|  | 06.11.17 | 10:55 | 06.11.17 | 11:22 | 0:27 | 0 | 27 | [5 empty] | At Tarkera-D/P
341 | 132kV Tarkera-Rajgangapur-I |  |  |  |  | 0.11319 | 14 | 34 | [7 empty] | 24.5 | 8760 | 99.83% | 356.8833 | 214620
|  | 27.04.17 | 17:26 | 27.04.17 | 17:34 | 0:08 | 0 | 8 | [5 empty] | At Rajgangpur-E/F.132 kV Budhipadar-Rajgangpur Ckt. was under S/D
|  | 26.09.17 | 21:46 | 26.09.17 | 22:07 | 0:21 | 0 | 21 | [5 empty] | At Rajgangpur-Tripped
|  | 07.10.17 | 21:08 | 07.10.17 | 22:17 | 1:09 | 1 | 9 | [5 empty] | At Tarkera-O/C
|  | 31.01.18 | 16:57 | 31.01.18 | 18:02 | 1:05 | 0 | 56 | [5 empty] | At Tarkera-D/P, 'B' ph. To E/F. After 56 mins power supply resumed to Rajagangpur from Budhipadar.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
342 | 132kV Tarkera-Rajgangapur-II |  |  |  |  | 0.11319 | 14 | 34 | [7 empty] | 24.5 | 8760 | 99.83% | 356.8833 | 214620
|  | 27.04.17 | 17:26 | 27.04.17 | 17:33 | 0:07 | 0 | 7 | [5 empty] | At both end-E/F ['Y' ph. Conductor snapped at Loc. No.-62, 63] At Tarkera-E/F
|  | 26.09.17 | 21:46 | 26.09.17 | 22:07 | 0:21 | 0 | 21 | [5 empty] | At Tarkera-O/C [Earthwire snapped at Rajgangpur 33 kV swotchyard]
|  | 07.10.17 | 21:08 | 07.10.17 | 22:18 | 1:10 | 1 | 10 | [5 empty] | At Tarkera-O/C, E/F
|  | 31.01.18 | 16:57 | 31.01.18 | 18:02 | 1:05 | 0 | 56 | [5 empty] | At Tarkera-D/P, 'B' ph. to E/F. After 56 mins power supply resumed to Rajagangpur from Budhipadar.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
343 | 132kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
344 | 132kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
345 | 132kV Tarkera-Rourkela-I |  |  |  |  | 0.023611 | 0 | 34 | [7 empty] | 3 | 8760 | 99.99% | 1.7 | 26280
|  | 05.07.17 | 11:30 | 05.07.17 | 11:59 | 0:29 | 0 | 29 | [5 empty] | At Tarkera-O/C, 'R' ph. E/F
|  | 18.11.17 | 21:02 | 18.11.17 | 21:07 | 0:05 | 0 | 5 | [5 empty] | At Tarkera-O/C
346 | 132kV Tarkera-Rourkela-II |  |  |  |  | 0.022222 | 0 | 34 | [7 empty] | 3 | 8760 | 99.99% | 1.7 | 26280
|  | 05.07.17 | 11:30 | 06.07.17 | 6:35 | 29:05 | 0 | 29 | [5 empty] | At Tarkera-E/F. ['R' ph. LA burst at Rourkela end]After 29 minutes power flow resumed through ckt-I
|  | 18.11.17 | 21:02 | 18.11.17 | 21:34 | 0:32 | 0 | 5 | [5 empty] | At Tarkera-O/C. After 5 mins power flow resumed through clrcuit-I
347 | 132kV Tarkera-Rourkela-III |  |  |  |  | 0.039583 | 0 | 34 | [7 empty] | 3 | 8760 | 99.99% | 1.7 | 26280
|  | 05.07.17 | 11:30 | 05.07.17 | 12:20 | 0:50 | 0 | 29 | [5 empty] | At Tarkera-Tripped.After 29 minutes power flow resumed through ckt-I
|  | 18.11.17 | 21:02 | 18.11.17 | 21:09 | 0:07 | 0 | 5 | [5 empty] | At Tarkera-O/C. After 5 mins power flow resumed through clrcuit-I
348 | 132kV Tentulikhunti-Dabugaon ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 43.2 | 8760 | 100% | 0 | 378432
349 | 132kV Therubali-IMFAL |  |  |  |  | 0.063194 | 1 | 31 | [7 empty] | 2 | 8760 | 99.98% | 3.0333 | 17520
|  | 03.11.17 | 9:59 | 03.11.17 | 11:30 | 1:31 | 1 | 31 | [5 empty] | At Theruvali-D/P, Zn.-I,['R' ph. CT jumper snapped at Theruvali S/s]
350 | 132kV Therubali-JK Pur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.68 | 8760 | 100% | 0 | 84796.8
351 | 132kV Therubali-Rayagada |  |  |  |  | 0 | 0 | 33 | [7 empty] | 20 | 8760 | 99.99% | 11 | 175200
|  | 25.09.17 | 18:47 | 26.09.17 | 12:08 | 17:21 | 0 | 33 | [5 empty] | At Theruvali-Tripped. [Ý'ph. conductor snapped at Theruvali gantry]. At 19:20 hrs. Rayagada availed Machhkund supply
352 | 132kV Therubali-Muniguda-Vedant Alumina |  |  |  |  | 0.11111 | 14 | 40 | [7 empty] | 76.951 | 8760 | 99.83% | 1128.6147 | 674090.76
|  | 03.04.17 | 18:53 | 03.04.17 | 19:03 | 0:10 | 0 | 10 | [5 empty] | At Theruvali-D/P, Zn.-I, Dist.-422.6 meter
|  | 19.04.17 | 18:05 | 19.04.17 | 18:23 | 0:18 | 0 | 18 | [5 empty] | At Theruvali-D/P, 'B' ph. to E/F, Zn.-II, Dist.-63.87 k.m.
|  | 08.05.17 | 16:10 | 08.05.17 | 16:17 | 0:07 | 0 | 7 | [5 empty] | At Theruvali-'R' ph, 'Y' ph, 'B' ph.
|  | 20.08.17 | 14:39 | 20.08.17 | 16:44 | 2:05 | 2 | 5 | [5 empty] | ['Y' ph CT Jumper snapped at Theruvali
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
353 | 132kV TTPS-Angul |  |  |  |  | 0 | 0 | 0 | [7 empty] | 16 | 8760 | 100% | 0 | 140160
354 | 132kV TTPS-Chainpal-I |  |  |  |  | 0.050694 | 1 | 13 | [7 empty] | 3 | 8760 | 99.99% | 3.65 | 26280
|  | 23.12.17 | 6:23 | 23.12.17 | 7:14 | 0:51 | 0 | 51 | [5 empty] | At Chainpal-O/C, 'R' ph.
|  | 25.12.17 | 4:13 | 25.12.17 | 4:35 | 0:22 | 0 | 22 | [5 empty] | At Chainpal-O/C, 'R' ph.
355 | 132kV TTPS-Chainpal-II |  |  |  |  | 0.073611 | 1 | 13 | [7 empty] | 3 | 8760 | 99.99% | 3.65 | 26280
|  | 23.12.17 | 6:23 | 23.12.17 | 7:45 | 1:22 | 0 | 51 | [5 empty] | At Chainpal-Tripped. After 51 mins power flow reumed through ckt-I
|  | 25.12.17 | 4:13 | 25.12.17 | 4:37 | 0:24 | 0 | 22 | [5 empty] | At Chainpal-O/C, 'R' ph, E/F. After 22 mins power flow resumed through ckt-!.
356 | 132kV TTPS-Chainpal-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
357 | 132kV TTPS-Jabamayee FAlloys |  |  |  |  | 0.011806 | 0 | 17 | [7 empty] | 76.276 | 8760 | 100% | 21.6115 | 668177.76
|  | 05.09.17 | 13:35 | 05.09.17 | 13:52 | 0:17 | 0 | 17 | [5 empty] | At Jabamayee-D/P
358 | 132kV TTPS-OPCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31 | 8760 | 100% | 0 | 271560
359 | 132kV Vedant Alumina-Kesinga |  |  |  |  | 0.11111 | 14 | 40 | [7 empty] | 58.077 | 8760 | 99.83% | 851.796 | 508754.52
|  | 03.04.17 | 18:53 | 03.04.17 | 19:03 | 0:10 | 0 | 10 | [5 empty] | At Theruvali-D/P, Zn.-I, Dist.-422.6 meter
|  | 19.04.17 | 18:05 | 19.04.17 | 18:23 | 0:18 | 0 | 18 | [5 empty] | At Theruvali-D/P, 'B' ph. to E/F, Zn.-II, Dist.-63.87 k.m.
|  | 08.05.17 | 16:10 | 08.05.17 | 16:17 | 0:07 | 0 | 7 | [5 empty] | At Theruvali-'R' ph, 'Y' ph, 'B' ph.
|  | 20.08.17 | 14:39 | 20.08.17 | 16:44 | 2:05 | 2 | 5 | [5 empty] | ['Y' ph CT Jumper snapped at Theruvali
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
(17): 6492.98; (20): 24550.8994; (21): 126745610.336 | 0.0001937 | 99.9806
ICTs / AUTOS
1 | Duburi 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | #REF! | 0 | 6898500
2 | Duburi 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
3 | Meramundali 315MVA ICT – I |  |  |  |  | 0.061111 | 1 | 28 | [6 empty] | 315 |  | 8760 | 99.99% | 787.5 | 6898500
|  | 01.08.17 | 13:07 | 01.08.17 | 14:35 | 1:28 | 1 | 28 | [5 empty] | A Mentally disturbed person climbed on 220 kV S/Y structure so all the 220 kV and 132 kV feeders connected to Meramundali Grid hand tripped.
4 | Meramundali 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
5 | Mendhasal 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
6 | Mendhasal 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
7 | Atri 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
8 | Atri 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
9 | Balasore 160MVA Auto – I |  |  |  |  | 0.066667 | 12 | 28 | [6 empty] | 160 |  | 8760 | 99.86% | 4986.6667 | 3504000
|  | 29.04.17 | 18:25 | 29.04.17 | 18:37 | 0:12 | 0 | 12 | [5 empty] | Tripped
|  | 29.04.17 | 19:22 | 29.04.17 | 19:25 | 0:03 | 0 | 3
|  | 03.05.17 | 17:14 | 03.05.17 | 17:24 | 0:10 | 0 | 10 | [5 empty] | On 132 kV side-E/F
|  | 01.06.17 | 16:26 | 01.06.17 | 16:28 | 0:02 | 0 | 3 | [5 empty] | On 132 kV side-E/F
|  | 01.06.17 | 17:44 | 01.06.17 | 18:53 | 1:09
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
10 | Balasore 160MVA Auto – II |  |  |  |  | 0.0090278 | 12 | 13 | [6 empty] | 160 |  | 8760 | 99.86% | 4886.6667 | 3504000
|  | 03.05.17 | 17:14 | 03.05.17 | 17:24 | 0:10 | 0 | 10 | [5 empty] | On 132 kV side-E/F
|  | 01.06.17 | 16:26 | 01.06.17 | 16:28 | 0:02 | 0 | 3 | [5 empty] | On 132 kV side-E/F
|  | 01.06.17 | 17:44 | 01.06.17 | 17:45 | 0:01
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
11 | Balasore 160MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 4368 | 100% | 0 | 1747200
12 | Baragarh New 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 240 | 100% | 0 | 60000
13 | Bidanasi 100MVA Auto – I |  |  |  |  | 0.0069444 | 0 | 10 | [6 empty] | 100 |  | 8760 | 100% | 41.6667 | 2190000
|  | 28.04.17 | 23:07 | 28.04.17 | 23:17 | 0:10 | 0 | 10 | [5 empty] | Tripped
14 | Bidanasi 100MVA Auto - II |  |  |  |  | 0.0069444 | 0 | 10 | [6 empty] | 100 |  | 8760 | 100% | 41.6667 | 2190000
|  | 28.04.17 | 23:07 | 28.04.17 | 23:17 | 0:10 | 0 | 10 | [5 empty] | Tripped
15 | Bidanasi 160MVA Auto - III |  |  |  |  | 0 | 0 | 10 | [6 empty] | 160 |  | 8760 | 100% | 66.6667 | 3504000
|  | 28.04.17 | 23:07 | 29.04.17 | 19:14 | 20:07 | 0 | 10 | [5 empty] | On 220 kV side-Bus bar protection. Power Flowto Loads continued after 10 minutes through AUTO-I and AUTO-II
16 | Bhadrak 100MVA Auto – I |  |  |  |  | 0 | 4 | 11 | [6 empty] | 100 |  | 8760 | 99.95% | 1045.8333 | 2190000
|  | 31.05.17 | 17:40 | 01.06.17 | 01.06.17 16:10 | 22:30 | 4 | 11 | [5 empty] | Tripped. At 21:51 hrs. Bhadrak availed 132 kV supply from Soro. During charging of Auto-III after maintenance work serious fire hazard occurred pulling out all 132 kV and 220 kV feeder
17 | Bhadrak 100MVA Auto – II |  |  |  |  | 0 | 4 | 11 | [6 empty] | 100 |  | 4248 | 99.9% | 1045.8333 | 1062000
|  | 31.05.17 | 17:40 |  | Yet to be charged |  | 4 | 11 | [5 empty] | Fire Hazard. At 21:51 hrs. Bhadrak availed 132 kV supply from Soro. During charging of Auto-III after maintenance work serious fire hazard occurred pulling out all 132 kV and 220 kV feeder
18 | Bhadrak 160MVA Auto – II |  |  |  |  | 0 | 4 | 11 | [6 empty] | 160 |  | 4512 | 99.91% | 1673.3333 | 1804800
|  | 31.05.17 | 17:40 |  | 24.09.2017 |  | 4 | 11 | [5 empty] | Fire Hazard. At 21:51 hrs. Bhadrak availed 132 kV supply from Soro. During charging of Auto-III after maintenance work serious fire hazard occurred pulling out all 132 kV and 220 kV feeder
19 | Bhadrak 100MVA Auto – III |  |  |  |  | 0 | 4 | 11 | [6 empty] | 100 |  | 8760 | 99.95% | 1045.8333 | 2190000
|  | 31.05.17 | 17:40 |  | 17.08.2018 |  | 4 | 11 | [5 empty] | Fire Hazard. At 21:51 hrs. Bhadrak availed 132 kV supply from Soro. During charging of Auto-III after maintenance work serious fire hazard occurred pulling out all 132 kV and 220 kV feeder
20 | Bolangir 160MVA Auto I |  |  |  |  | 0.0034722 | 0 | 5 | [6 empty] | 160 |  | 8760 | 100% | 33.3333 | 3504000
|  | 01.04.17 | 17:12 | 01.04.17 | 17:17 | 0:05 | 0 | 5 | [5 empty] | On 220 kV side-Buchholz relay
21 | Bolangir 160 MVA Auto II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
22 | Bhanjanagar 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
23 | Bhanjanagar 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
24 | Budhipadar 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
25 | Budhipadar 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
26 | Chandaka 100MVA Auto – I |  |  |  |  | 0.041667 | 12 | 39 | [6 empty] | 100 |  | 8760 | 99.86% | 3162.5 | 2190000
|  | 28.05.17 | 19:13 | 29.05.17 | 1:24 | 06:11 | 0 | 6 | [5 empty] | On 220 kV side-Differential on 132 kV side-Master trip [Flash over occurred on 132 kV side 'R' ph. LA equalizer ring] Power Flow resumed through Auto-II after 6 minutes
|  | 30.05.17 | 15:01 | 30.05.17 | 15:10 | 0:09 | 0 | 11 | [5 empty] | On 220 kV side-O/C , 'R', 'Y', 'B' ph. On 132 kV side-Master trip
|  | 30.05.17 | 15:14 | 30.05.17 | 15:17 | 0:03
|  | 30.05.17 | 15:23 | 30.05.17 | 15:35 | 0:12
|  | 01.06.17 | 14:46 | 01.06.17 | 15:05 | 0:19 | 0 | 19 | [5 empty] | On 220 kV side-Bus bar protection
|  | 18.08.17 | 15:26 | 18.08.17 | 15:43 | 0:17 | 0 | 3 | [5 empty] | At both ends-Master trip. After 3 minutes power flow resumed through Auto-IV
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
27 | Chandaka 160MVA Auto – II |  |  |  |  | 0.065278 | 13 | 17 | [6 empty] | 160 |  | 8760 | 99.85% | 5313.3333 | 3504000
|  | 28.05.17 | 19:13 | 28.05.17 | 19:19 | 0:06 | 0 | 6 | [5 empty] | On 220 kV side-Master trip On 132 kV side-Master trip
|  | 30.05.17 | 15:01 | 30.05.17 | 15:07 | 0:06 | 0 | 12 | [5 empty] | On 220 kV side-O/C , 'R', 'Y', 'B' ph. On 132 kV side-Master trip. Power Flow resumed through Auto-I
|  | 30.05.17 | 15:14 | 30.05.17 | 15:35 | 0:21
|  | 01.06.17 | 14:46 | 01.06.17 | 15:05 | 0:19 | 0 | 19 | [5 empty] | On 220 kV side-Bus bar protection
|  | 18.08.17 | 15:26 | 18.08.17 | 15:31 | 0:05 | 0 | 3 | [5 empty] | At both ends-Master trip.After 3 minutes power flow resumed through Auto-IV
|  | 28.02.18 | 4:20 | 28.02.18 | 4:57 | 0:37 | 0 | 37 | [5 empty] | On 220 kV side-O/C, E/F On 132 kV side-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
28 | Chandaka 100MVA Auto – III |  |  |  |  | 0.27292 | 28 | 27 | [6 empty] | 100 |  | 8760 | 99.98% | 354.1667 | 2190000
|  | 16.04.17 | 20:39 | 16.04.17 | 22:04 | 1:25 | 1 | 25 | [5 empty] | On 220 kV side-REF
|  | 16.04.17 | 22:35 | 17.04.17 | 12:23 | 13:48 | 13 | 48
|  | 28.05.17 | 19:13 | 28.05.17 | 19:35 | 0:22 | 0 | 7 | [5 empty] | On 220 kV side-Master trip On 132 kV side-'Y' ph. to E/F. Power flow resumed through through Auto-II & IV
|  | 30.05.17 | 15:01 | 30.05.17 | 15:17 | 0:16 | 0 | 11 | [5 empty] | On 220 kV side-Master trip On 132 kV side-O/C, 'R' ph, Master trip. Power Flow resumed through Auto-I
|  | 30.05.17 | 15:23 | 30.05.17 | 16:40 | 1:17
|  | 01.06.17 | 14:46 | 01.06.17 | 15:09 | 0:23 | 0 | 19 | [5 empty] | On 220 kV side-Bus bar protection. Power flow resumed through Auto-I&II after 19 minutes.
|  | 28.02.18 | 4:20 | 28.02.18 | 7:10 | 2:50 | 0 | 37 | [5 empty] | On 220 kV side-O/C, E/F On 132 kV side-O/C, E/F After 37 mins power flow resumed through Auto-II.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
29 | Chandaka 160MVA Auto – IV |  |  |  |  | 0.15417 | 13 | 17 | [6 empty] | 160 |  | 8760 | 99.85% | 5313.3333 | 3504000
|  | 28.05.17 | 19:13 | 28.05.17 | 19:20 | 0:07 | 0 | 7
|  | 30.05.17 | 15:01 | 30.05.17 | 15:07 | 0:06 | 0 | 11 | [5 empty] | On 220 kV side-Master trip On 132 kV side-O/C. Power flow resumed through Auto-II
|  | 30.05.17 | 15:30 | 30.05.17 | 17:50 | 2:20
|  | 01.06.17 | 14:46 | 01.06.17 | 15:07 | 0:21 | 0 | 19 | [5 empty] | .Power flow resumed through Auto-I&II after 19 minutes.On 220 kV side-Bus bar protection
|  | 18.08.17 | 15:26 | 18.08.17 | 15:29 | 0:03 | 0 | 3 | [5 empty] | On 132 kV side-Master trip
|  | 28.02.18 | 4:20 | 28.02.18 | 5:05 | 0:45 | 0 | 37 | [5 empty] | On 132 kV side-O/C, E/F On 132 kV side-O/C, E/F. After 37 mins power flow resumed through Auto-II
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
30 | Chandaka-B 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
31 | Chandaka-B 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
32 | Cuttack 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
33 | Duburi 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
34 | Duburi 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
35 | Duburi 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
36 | Jayanagar 160MVA Auto – I |  |  |  |  | 0.13403 | 3 | 7 | [6 empty] | 160 |  | 8760 | 99.96% | 1246.6667 | 3504000
|  | 02.05.17 | 7:25 | 02.05.17 | 10:38 | 3:13 | 3 | 7 | [5 empty] | Tripped [Heavy flash over in 132 kV 'Y' ph. jumper of main bus from PT to isolator] Power flow resumed through Auto-II after 3 Hr 7 Minutes.
37 | Jayanagar 160MVA Auto – II |  |  |  |  | 0.12986 | 3 | 7 | [6 empty] | 160 |  | 8760 | 99.96% | 1246.6667 | 3504000
|  | 02.05.17 | 7:25 | 02.05.17 | 10:32 | 3:07 | 3 | 7 | [5 empty] | Tripped
38 | Joda 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
39 | Joda 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
40 | Joda 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
41 | Katapalli 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
42 | Katapalli 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
43 | Katapalli 160MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
44 | Lapanga 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
45 | Lapanga 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
46 | Mendhasal 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
|  | 29.04.17 | 22:14 | 30.04.17 | 7:50 | 09:36 | 0 | 0 | [5 empty] | Power Flow resumed through Auto-II
47 | Mendhasal 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
48 | Meramundali 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
49 | Meramundali 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
50 | Meramundali 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
51 | Narendrapur 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
52 | Narendrapur 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
53 | Narendrapur 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
54 | Paradeep 100MVA Auto – I |  |  |  |  | 0.041667 | 0 | 27 | [6 empty] | 100 |  | 8760 | 99.99% | 112.5 | 2190000
|  | 28.08.17 | 22:15 | 28.08.17 | 23:15 | 1:00 | 0 | 27 | [5 empty] | Tripped on O/C. Power flow resumed through Auto-II after 27 minutes.
55 | Paradeep 160 MVA Auto – II |  |  |  |  | 0.098611 | 2 | 22 | [6 empty] | 160 |  | 8760 | 99.99% | 180 | 3504000
|  | 30.05.17 | 16:45 | 30.05.17 | 18:40 | 1:55 | 1 | 55 | [5 empty] | [220 kV side 'Y' ph. conductor from breaker to isolator snapped due to puncture of insulator]
|  | 28.08.17 | 22:15 | 28.08.17 | 22:42 | 0:27 | 0 | 27 | [5 empty] | Tripped on O/C
56 | Paradeep 50MVA Auto – III |  |  |  |  | 0.029861 | 0 | 27 | [6 empty] | 50 |  | 8760 | 99.99% | 56.25 | 1095000
|  | 28.08.17 | 22:15 | 28.08.17 | 22:58 | 0:43 | 0 | 27 | [5 empty] | Tripped on O/C.Power flow resumed through Auto-II after 27 minutes.
57 | Samagara 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
58 | Samagara 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
59 | Tarkera 100MVA Auto – I |  |  |  |  | 0.0090278 | 0 | 13 | [6 empty] | 100 |  | 8760 | 100% | 54.1667 | 2190000
|  | 06.06.17 | 16:31 | 06.06.17 | 16:44 | 0:13 | 0 | 13 | [5 empty] | On 220 kV side-O/C, E/F
60 | Tarkera 100MVA Auto – II |  |  |  |  | 0.010417 | 0 | 13 | [6 empty] | 100 |  | 8760 | 100% | 62.5 | 2190000
|  | 06.06.17 | 16:31 | 06.06.17 | 16:46 | 0:15 | 0 | 13 | [5 empty] | On 220 kV side-O/C, E/F
61 | Tarkera 100MVA Auto – III |  |  |  |  | 0.010417 | 0 | 15 | [6 empty] | 100 |  | 8760 | 100% | 62.5 | 2190000
|  | 06.06.17 | 16:31 | 06.06.17 | 16:46 | 0:15 | 0 | 15
62 | Tarkera 100MVA Auto – IV |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
63 | Therubali 100MVA Auto – I |  |  |  |  | 0.010417 | 0 | 15 | [6 empty] | 100 |  | 8760 | 99.99% | 212.5 | 2190000
|  | 16.05.17 | 22:59 | 16.05.17 | 23:14 | 0:15 | 0 | 15 | [5 empty] | Bus bar relay
64 | Therubali 100MVA Auto – II |  |  |  |  | 0.035417 | 0 | 51 | [6 empty] | 100 |  | 8760 | 99.99% | 212.5 | 2190000
|  | 16.05.17 | 22:59 | 16.05.17 | 23:06 | 0:07 | 0 | 7 | [5 empty] | On 220 kV side-O/C
|  | 09.01.18 | 11:42 | 09.01.18 | 11:59 | 0:17 | 0 | 17 | [5 empty] | Bus bar protection
|  | 09.01.18 | 16:23 | 09.01.18 | 16:50 | 0:27 | 0 | 27 | [5 empty] | On 132 kV side-O/C. [132 kV main Bus Section-L 'R' ph. PT burst]
(16): Sub-total (ICTs / Autos); (20): 33244.5833; (21): 183597000 | 0.00018107 | 99.9819
[15 empty] | TOTAL (Lines, ICTs & Autos) |  |  |  | 57795.4827 | 310342610.336
[11 empty] | NAFY |  | [ Σ ( OH l x Cktkm l x NSC l ) + Σ ( OH t x MVA t x 2.5 )] [THY x { Σ (Cktkm l x NSC l ) +Σ (MVA t x 2.5 ) } ] | [5 empty] | 0.00018623
[13 empty] | 100 - (100 X NAFY) | [5 empty] | 99.9814
Note on B50: Newly Added
Note on B53: Newly Added
Note on B68: Added newly
Note on B70: Added newly
Note on B72: Added newly
Note on B74: Added newly
Note on Q101: Confrimed from CP Branch
Note on Q103: Confrimed from CP Branch
Note on B113: Earlier it was Bidanasi- Chandaka
Note on Q123: OPTCL: Chandaka-B LILO charged on 28.03.2017
Note on B193: Part of 400kV Meramundali Mendhasala Ckt - II
Note on Q193: Data confirmed from Sri DPJena
Note on Q214: Atri LILO ckt is added.
Note on Q216: Atri LILO ckt is added.
Note on Q413: Bhubaneswar Power on LILO charged on 17.02.2016
Note on Q451: Kalunga LILO is charged on 07.09.2015
Note on H507: Multified by factor 2
Note on H509: Multified by factor 2
Note on Q521: GRID STEEL on LILO charged on 24.12.2015
Note on R590: commissioned on 28.02.2018
Note on R594: commissioned on 24.02.2018
Note on R631: commissioned on 28.02.2018
Note on Q639: OPTCL: Bangiriposhi LILO charged on 03.10.2016
Note on Q647: commissioned on 30.07.2017
Note on R651: commissioned on 19.08.2017
Note on Q716: distance between Narendrapur-Balugaon and Balugaon- Khurda added.
Note on R760: Line charged on 30.03.2017
Note on Q774: =1.33+17.43+15.87 km
Note on R782: Line Charged on 03.01.2017
Note on R793: commissioned on 28.07.2017
Note on Q801: Lapanga LILO charged on 25.11.2015
Note on Q815: Kalunga LILO is charged on 07.09.2015
Note on R914: Commissioned on 1.10.2017
Note on R916: Commissioned on 21.03.2018
Note on R928: commissioned on 24.09.2017
Note on B1032: Charged on 24.06.2012

## ANNEXURE-III
Transmission Element Data as on 31/03/17 ANNEXURE-III
Name of the Transmission licensee: ODISHA POWER TRANSMISSION CORPORATION LTD
a) Transmission Lines
SL. NO | Name of the Transmission line |  | Voltage Level(in KV) | S/C or D/C | Line Length (in Ckt KM) | Conductor Type & Characteristics | No. of Sub-Conductor (NSC) | Date of Comm. / Comm. Operation
| From | To
1 | Rengali-Kuchei PG | Kolaghat PG | 400 | S/C | 483 | Twin Moose | 2 | 1995
2 | Indravati PH | Indravati PG | 400 | S/C | 7.4 | Twin Moose | 2 | 03/09/09
3 | Meramundal I | Mendhasal I | 400 | D/C | 100.45 | Twin Moose | 2 | 31/01/10
4 | Meramundal I | Mendhasal II | 400 | D/C | 100.45 | Twin Moose | 2 | 31/01/10
3 | Meramundal I | New Duburi | 400 | D/C | 96.8 | Twin Moose | 2 | 19/10/15
4 | Meramundal I | New Duburi | 400 | D/C | 96.8 | Twin Moose | 2 | 19/10/15
5 | Meramundali | JSPL I | 400 | D/C | 75.83 | Twin Moose | 2 | 16/09/2010
6 | Meramundali | JSPL II | 400 | D/C | 75.83 | Twin Moose | 2 | 16/09/2010
7 | Balimela | U. Seluru | 220 | S/C | 24.76 | Single Zebra | 1 | 1982
8 | Balimela | Jayanagar-I | 220 | D/C | 92.072 | Single Zebra | 1 | 1974
9 | Balimela | Jayanagar-II | 220 | D/C | 92.072 | Single Zebra | 1 | 1974
10 | Balimela | Jayanagar-III | 220 | S/C | 93.46 | Single Zebra | 1 | 1982
11 | Balasore | Bhadrak | 220 | S/C | 80 | Single Zebra | 1 | 22.10.08
12 | Barkote | Tarkera | 220 | D/C | 97.48 | Single Zebra | 1 | 1979
13 | Bhanjanagar | Meramundali-I | 220 | D/C | 134.135 | Single Zebra | 1 | 1974
14 | Bhanjanagar | Meramundali-II | 220 | D/C | 134.135 | Single Zebra | 1 | 1974
15 | Bhanjanagar | Mendhasal | 220 | D/C | 156 | Single Zebra | 1 | 1989
16 | Bhanjanagar | Nayagarh | 220 | D/C | 46.47 | Single Zebra | 1 | 1989
17 | Bidanasi | Mendhasal ckt II | 220 | D/C | 15 | Single Zebra | 1 | 2008
18 | Bidanasi | Mendhasal ckt III | 220 | D/C | 15 | Single Zebra | 1 | 2008
19 | Bisra | Tarkera-I | 220 | D/C | 15.335 | Single Zebra | 1 | 1993
20 | Bisra | Tarkera-II | 220 | D/C | 15.335 | Single Zebra | 1 | 1993
21 | Budhipadar | IbTPS -I | 220 | D/C | 26 | Single Zebra | 1 | 1995
22 | Budhipadar | IbTPS -II | 220 | D/C | 26 | Single Zebra | 1 | 1995
23 | Budhipadar | IbTPS -III | 220 | D/C | 25.38 | Single Zebra | 1 | 1995
24 | Budhipadar | IbTPS -IV | 220 | D/C | 25.38 | Single Zebra | 1 | 07/01/08
25 | Budhipadar | Raigarh | 220 | D/C | 60 | Single Zebra | 1 | 1995
26 | Budhipadar | Korba-II | 220 | D/C | 60 | Single Zebra | 1 | 1995
27 | Budhipadar | Katapalli -I | 220 | D/C | 61.679 | Single Zebra | 1 | 20/04/07
28 | Budhipadar | Katapalli -II | 220 | D/C | 61.769 | Single Zebra | 1 | 20/04/07
29 | Budhipadar | SPS I | 220 | D/C | 13.424 | Single Zebra | 1 | 07/11/07
30 | Budhipadar | SPS II | 220 | D/C | 13.424 | Single Zebra | 1 | 07/11/07
31 | Budhipadar | Bhusan Steel-I | 220 | D/C | 14.92 | Single Zebra | 1 | 06/08/05
32 | Budhipadar | Bhusan Steel-II | 220 | D/C | 14.92 | Single Zebra | 1 | 06/08/05
33 | Chandaka | Mendhasal ckt I | 220 | D/C | 19 | Single Zebra | 1 | 2008
34 | Chandaka | Mendhasal ckt II | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
35 | Chandaka | Mendhasal ckt III | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
36 | Chandaka | Mendhasal ckt IV | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
37 | Duburi | Duburi (New) ckt I | 220 | D/C | 11.056 | Single Zebra | 1 | 1996
38 | Duburi | Duburi (New) ckt II | 220 | D/C | 11.056 | Single Zebra | 1 | 1997
39 | Duburi | NINL | 220 | S/C | 6 | Single Zebra | 1 | 01/06/2000
40 | Duburi (New) | Balasore | 220 | D/C | 137.36 | Single Zebra | 1 | 1997
41 | Indravati PH | Therubali-I | 220 | D/C | 86.2 | Single Zebra | 1 | 26/05/01
42 | Indravati PH | Therubali-II | 220 | D/C | 86.2 | Single Zebra | 1 | 26/05/01
43 | Indravati PH | Therubali-III | 220 | D/C | 91 | Single Zebra | 1 | 22/07/05
44 | Indravati PH | Therubali-IV | 220 | D/C | 91 | Single Zebra | 1 | 22/07/05
45 | Jayanagar | Jeyapore PG-I | 220 | D/C | 7.23 | Single Zebra | 1 | 1990
46 | Jayanagar | Jeyapore PG-II | 220 | D/C | 7.23 | Single Zebra | 1 | 1990
47 | Jayanagar | Laxmipur ckt I | 220 | D/C | 65 | Single Zebra | 1 | 1974
48 | Jayanagar | Laxmipur Ckt II | 220 | D/C | 65 | Single Zebra | 1 | 1974
49 | Jindal | Jamsedpur DVC | 220 | S/C | 20.8 | Single Zebra | 1 | 1985
50 | Joda | RCPur PG | 220 | S/C | 15.5 | Single Zebra | 1 | 1985
51 | Joda | Jindal | 220 | S/C | 21 | Single Zebra | 1 | 1985
52 | Joda | TSIL Ckt. | 220 | S/C | 7.3 | Single Zebra | 1 | 23/03/07
53 | Katapali | Bolangir-I | 220 | D/C | 117.85 | Single Zebra | 1 | 2010
54 | Katapali | Bolangir-II | 220 | D/C | 117.85 | Single Zebra | 1 | 2011
55 | Kuchei PG | Balasore Ckt I | 220 | D/C | 76.859 | Single Zebra | 1 | 03/10/07
56 | Kuchei PG | Balasore Ckt II | 220 | D/C | 76.859 | Single Zebra | 1 | 03/10/07
57 | Laxmipur | Therubali Ckt I | 220 | D/C | 56 | Single Zebra | 1 | 1974
58 | Laxmipur | Therubali Ckt II | 220 | D/C | 56 | Single Zebra | 1 | 1974
59 | Laxmipur | Utkal Alu,ina Ckt I | 220 | D/C | 31.04 | Single Zebra | 1 | 2014
60 | Laxmipur | Utkal Alu,ina Ckt II | 220 | D/C | 31.04 | Single Zebra | 1 | 2014
61 | Mendhasal | Bidanasi-II | 220 | D/C | 32.99 | Single Zebra | 1 | 2003
62 | Meramundali | Bidanasi-II | 220 | D/C | 90.94 | Single Zebra | 1 | 2003
63 | Meramundali | Duburi-I | 220 | D/C | 95.556 | Single Zebra | 1 | 1995
64 | Meramundali | Duburi-II | 220 | D/C | 95.556 | Single Zebra | 1 | 1995
65 | Meramundali | BSSL (Bhusan) I | 220 | D/C | 2.4 | Single Zebra | 1 | 22/08/06
66 | Meramundali | BSSL (Bhusan) II | 220 | D/C | 2.4 | Single Zebra | 1 | 22/08/06
67 | NALCO | Meramundali-I | 220 | D/C | 11.465 | Single Zebra | 1 | 27/08/04
68 | NALCO | Meramundali-II | 220 | D/C | 11.465 | Single Zebra | 1 | 27/08/04
69 | NALCO | Rengali PH | 220 | S/C | 71.337 | Single Zebra | 1 | 1984
70 | Nayagarh | Mendhasal | 220 | D/C | 90 | Single Zebra | 1 | 1989
71 | Narendrapur | Mendhasal I | 220 | D/C | 75 | Single Zebra | 1 | 02/07/2010
72 | New Duburi | Paradeep Ckt-I | 220 | D/C | 113.433 | Single Zebra | 1 | 06/05/09
73 | New Duburi | Paradeep Ckt-II | 220 | D/C | 113.433 | Single Zebra | 1 | 06/05/09
74 | Rengali GD | Rengali PG -I | 220 | D/C | 0.4 | Single Zebra | 1 | 1997
75 | Rengali GD | Rengali PG -II | 220 | D/C | 0.4 | Single Zebra | 1 | 1997
76 | Rengali GD | Chandiposh (T) | 220 | D/C | 162.08 | Single Zebra | 1 | 26/03/2000
77 | Rengali GD | Barkote | 220 | D/C | 55 | Single Zebra | 1 | 1979
78 | Rengali PH | Rengali GD -I | 220 | D/C | 5 | Single Zebra | 1 | 1997
79 | Rengali PH | Rengali GD -II | 220 | D/C | 5 | Single Zebra | 1 | 1997
80 | Rengali PH | STPS | 220 | S/C | 29.5 | Single Zebra | 1 | 1984
81 | STPS (Kaniha) | TTPS | 220 | S/C | 34.5 | Single Zebra | 1 | 1984
82 | STPS | Meramundali-I | 220 | D/C | 42.52 | Single Zebra | 1 | 1995
83 | STPS | Meramundali-II | 220 | D/C | 42.52 | Single Zebra | 1 | 1995
84 | Tarkera | Budhipadar-I | 220 | D/C | 109 | Single Zebra | 1 | 1995
85 | Tarkera | Budhipadar-II | 220 | D/C | 109 | Single Zebra | 1 | 1995
86 | Tarkera | RSP I | 220 | D/C | 10 | Single Zebra | 1 | 2008
87 | Tarkera | RSP I | 220 | D/C | 10 | Single Zebra | 1 | 1995
88 | Therubali | Narendrapur-I | 220 | D/C | 196 | Single Zebra | 1 | 2013
89 | Therubali | Narendrapur-II | 220 | D/C | 196 | Single Zebra | 1 | 20/08/2001
90 | Therubali | Bhanjanagar-I | 220 | D/C | 171.46 | Single Zebra | 1 | 1974
91 | Therubali | Bhanjanagar-II | 220 | D/C | 171.46 | Single Zebra | 1 | 1974
92 | TTPS | Meramundali-I | 220 | D/C | 11.155 | Single Zebra | 1 | 1979
93 | TTPS | Meramundali-II | 220 | D/C | 11.155 | Single Zebra | 1 | 1979
94 | TTPS | Joda-I | 220 | D/C | 154 | Single Zebra | 1 | 1967
95 | TTPS | Joda-II | 220 | D/C | 154 | Single Zebra | 1 | 1970
96 | U. Kolab | Jayanagar-I | 220 | D/C | 6 | Single Zebra | 1 | 1987
97 | U. Kolab | Jayanagar-II | 220 | D/C | 6 | Single Zebra | 1 | 1987
98 | U. Kolab | Therubali | 220 | S/C | 128 | Single Zebra | 1 | 1984
Transmission Element Data as on 31/03/17 | [6 empty] | ANNEXURE-III
Name of the Transmission licensee: ODISHA POWER TRANSMISSION CORPORATION LTD
b) Sub Stations
SL. NO | Name of the Sub-Station |  | Voltage Level(in KV) | NO. of ICTs/ AUTOs | MVA Capacity of ICTs / Autos | Date of Commissioning | Date of Comml. Operation
1 | MERAMUNDALI |  | 400/220/132 | 2 | 315 | 02/06/05
|  |  | 220/132 | 2 | 100 | 2002
|  |  |  | 1 | 100 | 2014 | 19.03.2014
2 | MENDHASAL |  | 400/220 | 2 | 315 | 2010
|  |  | 220/132 | 1 | 100 | 2006
|  |  | 220/132 | 1 | 100 | 2010
|  |  | 220/132 | 1 | 100 | 2014
3 | BIDANASI |  | 220/132 | 2 | 100 | 2004
|  |  |  | 1 | 100 | 2013 | 17.07.2013
5 | BHANJANAGAR |  | 220/132 | 2 | 160 | 1984,2014 | 05.01.2014
6 | BHADRAK |  | 220/132 | 2 | 100 | 2008,2009
7 | CHANDAKA |  | 220/132 | 2 | 160 | 2012
|  |  |  | 2 | 100 | 1989
8 | CUTTACK |  | 220/132 | 1 | 160 | 2017
9 | NARENDRAPUR |  | 220/132 | 2 | 160 | 1999
|  |  |  | 1 | 100 | 2012
10 | THERUBALI |  | 220/132 | 2 | 100 | 1981
11 | BALASORE |  | 220/132 | 2 | 160 | 2012
12 | JAYANAGAR |  | 220/132 | 2 | 100 | 1997
13 | DUBURI |  | 220/132 | 3 | 100 | 1989
14 | BUDHIPADAR |  | 220/132 | 2 | 160 | 1995
15 | TARKERA |  | 220/132 | 4 | 100 | 1981
16 | JODA |  | 220/132 | 2 | 100 | 1969
17 | KATAPALLI |  | 220/132 | 2 | 100 | 2007
18 | PARADEEP |  | 220/132 | 2 | 100,160,50 | 2009,2011,2009
19 | BOLANGIR NEW |  | 220/132 | 3 | 100 | 2011,2014 | 05.05.2014
20 | LAPANGA |  | 220/132 | 2 | 160 | 2014
21 | ATRI |  | 220/132 | 2 | 160 | 2016
22 | SAMANGARA |  | 220/132 | 2 | 160 | 2015,2016
Note on E5: Type of tower