## Annexure-A
Annexure-A
RGGVY-I(Scheme Closed)
ABSTRACT OF VILLAGES AS PER SURVEY / CHARGED IN RGGVY ( 10th & 11th Plan) UNDER CESU
Sl No. | Name of the District | Executor CPSUs | No.of Blocks | STATUS OF VILLAGE ELECTRIFICATION AS PER SURVEY & CHARGED |  |  |  | BPL Kit Charged
|  |  |  | TOTAL | UE | DE | PE
1 | Angul | NTPC | 8 | 1546 | 254 | 284 | 1008 | 76544
2 | Nayagarh | NTPC | 8 | 1410 | 290 | 252 | 868 | 87343
3 | Dhenkanal | NTPC | 8 | 1008 | 69 | 160 | 779 | 59619
4 | Puri | NHPC | 11 | 1006 | 28 | 25 | 953 | 36521
5 | Cuttack | PGCIL | 14 | 1795 | 14 | 133 | 1648 | 112034
6 | Kendrapara | PGCIL | 9 | 1350 | 108 | 88 | 1154 | 73053
7 | Jagatsingpur | PGCIL | 8 | 1195 | 63 | 32 | 1100 | 48347
8 | Khurda | PGCIL | 10 | 1322 | 70 | 11 | 1241 | 68311
9 | Jajpur (Portion of Badachana & Dharamsala) | PGCIL | 2 | 169 | 0 | 0 | 169 | 11890
Sub- Total |  |  | 78 | 10801 | 896 | 985 | 8920 | 573662

## Annexure-B
Annexure-B
STATUS OF VILLAGES / BPL'S SANCTIONED UNDER RGGVY-II ( 12th PLAN DPR ) FOR CESU AREA
Sl.no | Name of District | Blocks Covered | STATUS OF VILLAGES |  |  | STATUS OF HABITATIONS |  |  | STATUS OF HOUSEHOLDS |  | Sanctioned cost (in crore)
|  |  | Un-Electrified Village(s) (UEV) | Partially Electrified Village(s) (PEV) | TOTAL ( UE + PE ) | Un-Electrified habitations (UEH) | Partially Electrified habitations (PEH) | TOTAL ( UE + PE ) | Rhhs (incl.BPL Hhs) | BPL Hhs
1 | Angul | 8 | 221 | 1341 | 1562 | 337 | 1945 | 2282 | 88337 | 21943 | 61.41
2 | Nayagarh | 8 | 19 | 1163 | 1182 | 143 | 3004 | 3147 | 116821 | 78366 | 77.04
3 | Dhenkanal | 8 | 16 | 1018 | 1034 | 223 | 1535 | 1758 | 143420 | 35118 | 70.48
4 | Puri | 11 | 4 | 1546 | 1550 | 51 | 5479 | 5530 | 119138 | 66778 | 153.11
5 | Kendrapara | 9 | 1 | 1324 | 1325 | 477 | 5272 | 5749 | 95694 | 37262 | 40.96
6 | Khurda | 10 | 8 | 1272 | 1280 | 200 | 2989 | 3189 | 68637 | 41387 | 104.01
7 | Cuttack | 14 | 0 | 1738 | 1738 | 31 | 7365 | 7396 | 188951 | 68277 | 133.11
8 | Jagatsinghpur | 8 | 20 | 1173 | 1193 | 34 | 4161 | 4195 | 65292 | 29440 | 79.29
9 | Jajpur(Part) | 2 | 0 | 533 | 533 | 8 | 1047 | 1055 | 27390 | 9749 | 14.93
Grand Total |  | 78 | 289 | 11108 | 11397 | 1504 | 32797 | 34301 | 913680 | 388320 | 734.34

## Annexure-C1
Annexure-C1
STATUS OF UE VILLAGES OF RGGVY-II UNDER CESU AREA AS ON 31.10.2019
Sl. No. | District | UE Scope as per DPR | Re-Revised UE as per Survey | STATUS OF VILLAGE
|  |  |  | Completed | Offered for inspection | Inspection Completed | Charged
A | B | C | D | I | J | K | L
1 | Angul | 221 | 27 | 27 | 27 | 27 | 27
2 | Nayagarh | 19 | 19 | 19 | 19 | 19 | 19
3 | Dhenkanal | 16 | 15 | 15 | 15 | 15 | 15
4 | Puri | 4 | 0 | 0 | 0 | 0 | 0
5 | Kendrapara | 1 | 1 | 1 | 1 | 1 | 1
6 | Khurda | 8 | 0 | 0 | 0 | 0 | 0
7 | Cuttack | 0 | 0 | 0 | 0 | 0 | 0
8 | Jagatsinghpur | 20 | 0 | 0 | 0 | 0 | 0
9 | Jajpur ( Part) | 0 | 0 | 0 | 0 | 0 | 0
Sub-Total |  | 289 | 62 | 62 | 62 | 62 | 62

## Annexure-C2
Annexure-C2
STATUS OF PE VILLAGES UNDER RGGVY-II UNDER CESU AREA AS ON 31.10.2019
Sl. No. | District | PE Scope as per DPR | Revised PE as per Survey | STATUS OF VILLAGE |  |  |  | STATUS OF BPL ( in UEV + PEV )
|  |  |  | Village Completed | Offered for Inspection | Inspection Completed | Charged
A | B | C | D | E | F | G | H | N
1 | Angul | 1341 | 701 | 647 | 647 | 647 | 647 | 10000
2 | Nayagarh | 1163 | 1148 | 1150 | 1150 | 1150 | 1150 | 2097
3 | Dhenkanal | 1018 | 761 | 706 | 706 | 706 | 706 | 21302
4 | Puri | 1546 | 1323 | 1110 | 1110 | 1110 | 1110 | 22755
5 | Kendrapara | 1324 | 657 | 657 | 657 | 657 | 657 | 1777
6 | Khurda | 1272 | 817 | 747 | 747 | 747 | 747 | 22091
7 | Cuttack | 1738 | 1154 | 1150 | 1150 | 1150 | 1150 | 3990
8 | Jagatsinghpur | 1173 | 717 | 709 | 709 | 709 | 709 | 35331
9 | Jajpur ( Part) | 533 | 188 | 186 | 186 | 186 | 186 | 14682
Sub-Total |  | 11108 | 7466 | 7062 | 7062 | 7062 | 7062 | 134025

## Annexure-D
Annexure-D
STATUS OF PARAMETERS SANCTIONED UNDER RGGVY-II ( 12th PLAN DPR ) FOR CESU AREA
SL NO | Name of District | New/Augmenting Sub station |  | DTR | [5 empty] | Line |  | Proposed DPR cost (in crore) | Sanctioned cost (in crore)
|  | 33/11 KV Aug s/stn | 33/11 KV New S/S | 100 KVA (Three Phase) | 63 KVA (Three Phase) | 25 KVA (Three Phase) | 16 KVA (Single Phase) | 10 KVA (Single Phase) | TOTAL | 11 Kv line (HT) | LT
1 | Angul | 3 | 0 | 0 | 278 | 372 | 1 | 0 | 651 | 545.28 | 725.04 | 77.4206 | 61.41
2 | Nayagarh | 6 | 0 | 120 | 297 | 653 | 63 | 0 | 1133 | 406.16 | 415.31 | 99.6703 | 77.04
3 | Dhenkanal | 3 | 0 | 0 | 540 | 500 | 0 | 0 | 1040 | 463.81 | 559.88 | 111.1033 | 70.48
4 | Puri | 11 | 0 | 0 | 705 | 1585 | 397 | 0 | 2687 | 1177.73 | 1177.1 | 203.9484 | 153.11
5 | Kendrapara | 0 | 0 | 0 | 413 | 132 | 3 | 0 | 548 | 230.92 | 281.7 | 49.455 | 40.96
6 | Khurda | 6 | 0 | 0 | 627 | 733 | 150 | 0 | 1510 | 655.62 | 853.5 | 140.1853 | 104.01
7 | Cuttack | 6 | 0 | 0 | 46 | 1073 | 1084 | 0 | 2203 | 1046.49 | 1457.63 | 176.787 | 133.11
8 | Jagatsinghpur | 0 | 0 | 0 | 577 | 282 | 34 | 0 | 893 | 728.07 | 893.16 | 85.3535 | 79.29
9 | Jajpur(Part) | 1 | 0 | 0 | 4 | 174 | 10 | 0 | 188 | 94.2 | 166.45 | 18.4554 | 14.93
Sub-Total |  | 36 | 0 | 120 | 3487 | 5504 | 1742 | 0 | 10853 | 5348.28 | 6529.77 | 962.3788 | 734.34

## Annexure-E
Annexure-E
Assessment of Additional DTR requirment in PE villages for charging of left out BPL Households under CESU.
Sl.No | District | No.of PE Villages Pending for BPL Charging | Pending BPL HHs to be charged | Proposed Up-gradation of DTR in KVA | [5 empty] | Proposal New of DTR in KVA |  |  |  | Final additional DTR recuirtment |  |  |  |  | Other Infrastructure
|  |  |  | 16-25 | 16-63 | 16-100 | 25-63 | 25-100 | 63-100 | 16 | 25 | 63 | 100 | 16 | 25 | 63 | 100 | Total | HT(in Kms) | LT(Kms) | DTR Accessories including DP
1 | Puri | 191 | 7999 | 41 |  |  | 36 |  | 14 | 19 | 99 | 36 | 2 | -22 | 104 | 58 | 16 | 178 | 53.5 | 67.2 | 155
2 | Cuttack | 397 | 31239 | 49 | 257 |  | 38 | 104 |  |  | 12 | 9 | 11 | -306 | -81 | 304 | 115 | 338 | 17 | 154.6 | 397
3 | Kendrapara | 1175 | 13145 |  |  |  | 10 |  | 27 |  | 70 | 60 | 18 | 0 | 60 | 43 | 45 | 148 | 58.3 | 60.95 | 296
4 | Jagatsingpur | 69 | 2862 | 10 |  |  | 6 |  | 3 |  | 39 | 12 | 0 | -10 | 43 | 15 | 3 | 61 | 18.9 | 32.45
5 | Angul | 196 | 13771 | 36 |  |  | 59 |  | 68 |  | 61 | 87 | 94 | -36 | 38 | 78 | 162 | 278 | 69.81 | 181.3 | 184
6 | Dhenkanal | 391 | 41352 | 12 |  |  | 40 |  | 100 |  | 79 | 200 | 225 | -12 | 51 | 140 | 325 | 516 | 105 | 220 | 1008
Total |  | 2419 | 110368 | 148 | 257 | 0 | 189 | 104 | 212 | 19 | 360 | 404 | 350 | -386 | 215 | 638 | 666 | 1519 | 322.51 | 716.5 | 2040

## Annexure-F
Annexure-F
Approval Date - 11/09/2015 ( CESU )
DISTRICT WISE STATUS OF DPR APPROVAL IN DDUGJY UNDER CESU AREA
Sl.No. | Name of District | DPR Code | Electrification of UE Villages | Feeder Separation | Connecting / Unconnecting Hhs | Metering | System Strengthening | Sansad Adarsh Gram Yojna | Total DPR Cost (In Cr.)
1 | Angul | DDU:21:384:01 | Nil | 1.69 | 22.33 | Nil | 7.74 | Nil | 31.76
2 | Cuttack | DDU:21:381:01 | Nil | 4.39 | 9.74 | 0.84 | 22.17 | 0.8 | 37.94
3 | Dhenkanal | DDU:21:383:01 | 11.43 | 8.26 | 5.73 | 17.1 | 5.88 | Nil | 48.4
4 | Jagatsinghapur | DDU:21:380:01 | Nil | 7.38 | 12.54 | Nil | 12.66 | 0.84 | 33.42
5 | Kendrapara | DDU:21:379:01 | Nil | 3.2 | 5.72 | 16.52 | 25.91 | 0.19 | 51.54
6 | Khordha | DDU:21:386:01 | Nil | 3.73 | 2.96 | 0.84 | 31.11 | 0.4 | 39.04
7 | Nayagarh | DDU:21:385:01 | 13.11 | Nil | Nil | 0.7 | 8.39 | 0.53 | 22.73
8 | Puri | DDU:21:387:01 | Nil | 2.69 | 19 | Nil | 16.09 | Nil | 37.78
Grand-Total |  |  | 24.54 | 31.34 | 78.02 | 36 | 129.95 | 2.76 | 302.61

## Annexure-G
Annexure-G
BGJY PHYSICAL & FINANCIAL PROGRESS REPORT AS ON 31.10.2019
Sl.no | Name of the District | Total no of habitations taken under the Scheme ( Nos ) | Total no of habitations Electrified ( Nos ) | Balance no of habitations to be Electrified ( Nos ) | Total no.of BPL HHs Charged ( Nos. ) | Fund (Rs) in Crore
[6 empty] | Total Fund released | Expenditure Made | Balance Fund
1 | Angul | 480 | 469 | 11 | 3719 | 13 | 9.7 | 3.3
2 | Nayagarh | 692 | 571 | 121 | 3347 | 14.33 | 13.92 | 0.41
3 | Dhenkanal | 425 | 420 | 5 | 6187 | 16.0057 | 12.93 | 3.0757
4 | Puri | 936 | 936 | 0 | 10692 | 30.3 | 25.65 | 4.65
5 | Kendrapara | 1098 | 1098 | 0 | 5093 | 24.06 | 18.4862 | 5.5738
6 | Khurda | 1124 | 1124 | 0 | 11143 | 28.25 | 27.99 | 0.26
7 | Jagatsinghpur | 641 | 403 | 238 | 2641 | 16.44 | 9.4 | 7.04
8 | Cuttack | 994 | 866 | 128 | 8109 | 24.75 | 15.8 | 8.95
9 | Jajpur ( Part ) | 50 | 44 | 6 | 619 | 1.24 | 1.2 | 0.04
Grand-Total |  | 6440 | 5931 | 509 | 51550 | 168.3757 | 135.0762 | 33.2994

## Annexure-H
Annexure-H
FINANCIAL STATUS OF BGJY AS ON 31.10.2019
Sl No | Name of the District | Fund (Rs) in Crore
|  | Total Fund released | Expenditure Made | Balance Fund
1 | Angul | 13 | 9.7 | 3.3
2 | Nayagarh | 14.33 | 13.92 | 0.41
3 | Dhenkanal | 16.01 | 16.01 | 0
4 | Puri | 30.3 | 25.65 | 4.65
5 | Kendrapara | 24.06 | 18.49 | 5.57
6 | Khurda | 31.9228 | 27.99 | 3.9328
7 | Jagatsinghpur | 16.44 | 9.4 | 7.04
8 | Cuttack | 24.75 | 15.8 | 8.95
9 | Jajpur ( part) | 1.24 | 1.2 | 0.04
TOTAL |  | 172.0528 | 138.16 | 33.8928

## Annexure-I
"Annexure-I"
STATUS OF BSVY UNDER C ESU AREA AS ON 30.09.2019
District | ULBs | Slums Identified | Slums / Wards Programme(Nos.) | Tender Done (Nos.) | Work Order Issued | Village / Habitation Electrified Nos. | Work Order Pending | Dropped | Balance No. of Words/ Slums to be electrified | BPL Families in Habitation / Villages (Nos.) | BPL House holds eleectrified (Nos.)
Dhenkanal | Dhenkanal Muncipalty | 33 | 16 | 16 | 16 | 11 | 0 | 0 | 5 | 500 | 182
| Kamakhyanagar NAC | 17 | 9 | 9 | 9 | 5 | 0 | 0 | 4 | 265 | 215
| Bhuban NAC | 16 | 16 | 16 | 16 | 10 | 0 | 0 | 6 | 935 | 94
| Sub-Total | 66 | 41 | 41 | 41 | 26 | 0 | 0 | 15 | 1700 | 491
Kendrapara | Kendrapara Muncipalty | 107 | 107 | 107 | 107 | 107 | 0 | 0 | 0 | 1000 | 600
| Pattamundai NAC | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 1000 | 984
| Sub-Total | 137 | 137 | 137 | 137 | 137 | 0 | 0 | 0 | 2000 | 1584
Khurda | Khurda Muncipalty | 64 | 63 | 63 | 63 | 63 | 0 | 0 | 0 | 1415 | 287
| Jatani Muncipalty | 62 | 62 | 62 | 62 | 61 | 0 | 0 | 1 | 1521 | 396
| Bhubaneswar Muncipalty | 137 | 127 | 127 | 127 | 123 | 0 | 0 | 4 | 2279 | 607
| Balugaon NAC | 31 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 1068 | 198
| Banpur NAC | 47 | 46 | 46 | 46 | 46 | 0 | 0 | 0 | 1326 | 355
| Sub-Total | 341 | 328 | 328 | 328 | 323 | 0 | 0 | 5 | 7609 | 1843
Cuttack | Cuttack Muncipalty | 152 | 54 | 54 | 54 | 53 | 0 | 0 | 1 | 1745 | 594
| Choudwar Muncipalty | 92 | 80 | 80 | 80 | 69 | 0 | 0 | 11 | 897 | 248
| Athagarh NAC | 26 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 639 | 173
| Banki NAC | 106 | 38 | 38 | 38 | 32 | 0 | 0 | 6 | 766 | 188
| Sub-Total | 376 | 182 | 182 | 182 | 164 | 0 | 0 | 18 | 4047 | 1203
Nayagarh | Nayagarh NAC | 33 | 33 | 13 | 13 | 13 | 20 | 0 | 0 | 114 | 54
| Khandapara NAC | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 308 | 175
| Daspalla NAC | 7 | 7 | 0 | 0 | 0 | 7 | 0 | 0 | 76 | 0
| Ranpur NAC | 10 | 10 | 0 | 0 | 0 | 10 | 0 | 0 | 42 | 0
| Sub-Total | 66 | 66 | 29 | 29 | 29 | 37 | 0 | 0 | 540 | 229
Jagatsinghpur | Jagatsinghpur NAC | 58 | 58 | 22 | 22 | 22 | 36 | 0 | 0 | 1000 | 759
Angul | Angul Muncipalty | 20 | 7 | 7 | 7 | 7 | 0 | 0 | 0 | 500 | 138
| Talcher Muncipalty | 45 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | 1000 | 248
| Athamallik NAC | 23 | 13 | 13 | 13 | 13 | 0 | 0 | 0 | 1000 | 415
| Sub-Total | 88 | 38 | 38 | 38 | 38 | 0 | 0 | 0 | 2500 | 801
Puri | Puri Muncipalty | 209 | 209 | 209 | 209 | 178 | 0 | 0 | 31 | 391 | 314
| Konark NAC | 58 | 57 | 57 | 57 | 36 | 0 | 0 | 21 | 690 | 548
| Nimapara NAC | 88 | 88 | 88 | 88 | 37 | 0 | 0 | 51 | 255 | 137
| Pipili NAC | 45 | 43 | 43 | 43 | 21 | 0 | 0 | 22 | 372 | 186
| Sub-Total | 400 | 397 | 397 | 397 | 272 | 0 | 0 | 125 | 1708 | 1185
328

## Annexure-J1
Annexure-J1
CALCULATION OF POWER TRANSFORMER LOSS IN 33KV/ 11KV PRIMARY DISTRIBUTION S/S
SL. NO. | NAME OF S/S | TFR CAPACITY (MVA) | 33KV I/C CONSUMPTION |  |  | T/F I/P | TOTAL I/P | 11 KV FEEDER NAME | 11KV FDR CONSUMPTION |  |  | T/F O/G | TOTAL CONSUMPTION | LOSS MU | LOSS (%)
|  |  | IR | FR | MF |  |  |  | IR | FR | MF
1 | LAXMISAGAR | 8 | 204276.2 | 208349.1 | 200 | 0.81458 | 4.5678 | KALPANA-I | 2580.6 | 2680.7 | 8000 | 0.8008 | 4.5288 | 0.03904 | 0.8547%
|  | 8 | 342572.8 | 361339.1 | 200 | 3.7533 |  | KALPANA-II | 960.5 | 1005.8 | 40000 | 1.812
[8 empty] | BOMIKHAL | 1028.3 | 1076.2 | 40000 | 1.916
2 | SAHEED NAGAR | 12.5 | 261784.2 | 272610.8 | 400 | 4.3306 | 4.3306 | SAHID NGR FDR I | 634.3 | 664.8 | 40000 | 1.22 | 4.312 | 0.01864 | 0.4304%
[8 empty] | SAHID NGR FDR III | 936.7 | 969.5 | 40000 | 1.312
|  | 12.5 | [5 empty] | SAHID NGR FDR II | 867.6 | 898 | 40000 | 1.216
[8 empty] | SAHID NGR FDR IV | 511.1 | 525.2 | 40000 | 0.564
3 | RANASINGHPUR | 5 | 11929.5 | 13504.5 | 1000 | 1.575 | 1.575 | SIJUA | 1601.6 | 1768.1 | 1000 | 0.1665 | 1.5686 | 0.0064 | 0.4063%
[8 empty] | AIGINIA | 6266.5 | 6901.5 | 1000 | 0.635
|  | 5 | [5 empty] | SARAKANTARA | 3995.4 | 4762.5 | 1000 | 0.7671
4 | AIRPORT | 12.5 | 524.5315 | 548.0495 | 120000 | 2.8222 | 2.8222 | AIRPORT | 1127.377 | 1175.7895 | 20000 | 0.96825 | 2.812 | 0.0102 | 0.3614%
|  | 12.5 | [5 empty] | PALLASHAPALLI | 976.6145 | 1018.9195 | 20000 | 0.8461
[8 empty] | GANGA NAGAR | 1052.461 | 1102.3415 | 20000 | 0.99761
5 | SATYA NAGAR | 8 | 289942.7 | 303751.86 | 200 | 2.7618 | 2.7618 | SATYA NAGAR | 760.536 | 794.5995 | 20000 | 0.68127 | 2.7276 | 0.034282 | 1.241%
[8 empty] | TOSHALI PLAZA | 829.4715 | 871.2265 | 20000 | 0.8351
|  | 8 | [5 empty] | PRESS | 877.03 | 921.0605 | 20000 | 0.88061
[8 empty] | RAHULCO | 448.987 | 465.5155 | 20000 | 0.33057
6 | XAVIER | 12.5 | 123014.8 | 130449.66 | 400 | 2.9739 | 2.9739 | XAVIER NALCO | 4679220 | 5157720 | 1 | 0.4785 | 2.9667 | 0.007244 | 0.2436%
[8 empty] | STPI | 5440420 | 5971490 | 1 | 0.53107
|  | 12.5 | [5 empty] | GOPABANDHU | 10557500 | 11616540 | 1 | 1.059
[8 empty] | SOI | 8020540 | 8918630 | 1 | 0.89809
7 | BHIMATANGI | 8 | 218929 | 228567.7 | 200 | 1.9277 | 3.8763 | LINGARAJ | 15060600 | 16014400 | 2 | 1.9076 | 3.8348 | 0.04156 | 1.072%
|  | 8 | 172726.7 | 182469.6 | 200 | 1.9486 |  | BHIMATANGI | 11925340 | 12888920 | 2 | 1.9272
8 | TANGI RGGVY | 5 | 48365.6 | 49150.1 | 1000 | 0.7845 | 0.7845 | NH5 | 8561.14 | 8787.43 | 1000 | 0.22629 | 0.77355 | 0.01095 | 1.396%
[8 empty] | TANGI | 12231.73 | 12505.36 | 2000 | 0.54726
9 | CHOUDWAR | 8 | 3537548 | 3580419 | 120 | 5.1445 | 5.1445 | CHOUDWAR | 9337.7 | 9564 | 4000 | 0.9052 | 5.0868 | 0.05774 | 1.122%
[8 empty] | CITY BARRAGE | 4398290 | 4447330 | 20 | 0.9808
|  | 8 | [5 empty] | OTM | 25218.75 | 25474.33 | 4000 | 1.0223
[8 empty] | LOCAL | 4672031 | 4717470 | 40 | 1.8176
[8 empty] | ARC | 46493.4 | 46854.3 | 1000 | 0.3609
10 | SANKARPUR | 5 | 21678.6 | 22655.5 | 1000 | 0.9769 | 0.9769 | SANKARPUR | 11872.7 | 12434.9 | 1000 | 0.5622 | 0.9732 | 0.0037 | 0.3787%
|  | 5 | [5 empty] | BERHAMPUR | 5213.8 | 5442.8 | 1000 | 0.229
[8 empty] | MANGARAJPUR | 4557.3 | 4739.3 | 1000 | 0.182
11 | JANKIA | 3.15 | 30800400 | 31608300 | 1 | 0.8079 | 0.8079 | GOLABAI | 2323.3 | 2523.3 | 4000 | 0.8 | 0.8 | 0.0079 | 0.9778%
12 | MATAMATHA | 8 | 557.154 | 581.3415 | 120000 | 2.9025 | 2.9025 | BUXI BAZAR | 958.9265 | 1016.191 | 20000 | 1.1453 | 2.8949 | 0.00757 | 0.2608%
[8 empty] | MUSIUM | 327.0885 | 356.6785 | 20000 | 0.5918
|  | 8 | [5 empty] | CB9 | 1305.475 | 1342.296 | 20000 | 0.73642
[8 empty] | CIRCUIT HOUSE | 638.2895 | 659.3605 | 20000 | 0.42142
13 | MATTAGAJAPUR | 8 | 235.5615 | 246.0355 | 60000 | 0.62844 | 0.62844 | JICA | 41.726 | 53.104 | 20000 | 0.22756 | 0.62083 | 0.00761 | 1.211%
[8 empty] | MATTAGAJAPUR | 208.9 | 214.74 | 20000 | 0.1168
|  | 8 | [5 empty] | PHD | 186.8015 | 188.7225 | 20000 | 0.03842
[8 empty] | POPARADA | 415.227 | 427.1295 | 20000 | 0.23805
14 | CHAINPAL | 5 | 627082 | 643757 | 120 | 2.001 | 2.001 | BHOGABARENI | 16743.56 | 17079.1 | 2000 | 0.67108 | 1.9938 | 0.00718 | 0.3588%
|  | 5 | [5 empty] | BALLAHARA | 28136.82 | 28669.57 | 2000 | 1.0655
[8 empty] | GOTAMARA | 7022.82 | 7151.44 | 2000 | 0.25724
15 | BIJAYCHANDRAPUR | 5 | 16778.9 | 18178.1 | 1000 | 1.3992 | 1.3992 | BIJAYCHANDRAPUR | 15961.6 | 17358.9 | 1000 | 1.3973 | 1.3973 | 0.0019 | 0.1358%
16 | PARADEEPGARH | 7.5 | 68026.1 | 68266.4 | 2000 | 0.4806 | 0.4806 | INDUSTRIAL | 54.61 | 66.59 | 40000 | 0.4792 | 0.4792 | 0.0014 | 0.2913%
|  | 216.65 |  |  |  |  | 38.0333 | AVG. POWER TRANSFORMER LOSS-> |  |  |  |  | 37.77 | 0.26332 | 0.6923%

## Annexure-J2
Annexure-J2
CALCULATION SHEET OF EFFICIENCY OF POWER TRANSFORMER AS PER IE STANDARD | CALCULATION SHEET OF EFFICIENCY OF POWER TRANSFORMER AS PER IE STANDARD | CALCULATION SHEET OF EFFICIENCY OF POWER TRANSFORMER AS PER IE STANDARD | CALCULATION SHEET OF EFFICIENCY OF POWER TRANSFORMER AS PER IE STANDARD | CALCULATION SHEET OF EFFICIENCY OF POWER TRANSFORMER AS PER IE STANDARD | CALCULATION SHEET OF EFFICIENCY OF POWER TRANSFORMER AS PER IE STANDARD | CALCULATION SHEET OF EFFICIENCY OF POWER TRANSFORMER AS PER IE STANDARD
Sl No | Rating Transformer | Full load loss at 75º C in Watts | Calculated loss in KVA at 0.9 pf | No of Power Transformer in CESU | KVA * No of Power Transformer | Calculated Loss* No of TFR in CESU |  |  | A | B | C | E=(1-D/B)*100 | F | G=B*F | H=D*F
A | B | C | D=C/(1000*0.9) | E | F=B*E | G=D*E
1 | 1600 KVA 33/11 KV | 16000 | 17.7778 | 32 | 51200 | 568.8889 |  | 1600
2 | 3000 KVA 33/11 KV | 23000 | 25.5556 | 1 | 3000 | 25.5556 |  | 3000
3 | 3150 KVA 33/11 KV | 23000 | 25.5556 | 109 | 343350 | 2785.5556 |  | 3150
4 | 5000 KVA 33/11 KV | 34000 | 37.7778 | 280 | 1400000 | 10577.7778 |  | 5000
5 | 7500 KVA 33/11 KV | 50000 | 55.5556 | 6 | 45000 | 333.3333 |  | 7500
6 | 8000 KVA 33/11 KV | 50000 | 55.5556 | 151 | 1208000 | 8388.8889 |  | 8000
7 | 12500 KVA 33/11 KV | 57000 | 63.3333 | 48 | 600000 | 3040 |  | 12500
|  | Average Efficiency in %age |  |  | 3650550 | 25720 | 99.3%
[6 empty] | Average Technical Loss of Power Transformer in % age = | 0.7046%

## Annexure-J3
Annexure-J3
AVERAGE T & D LOSS CALCULATION OF 33 KV FEEDERS FOR THE FY 2018-19
SL NO | NAME OF THE GRID | NAME OF THE 33 KV FEEDER | LENGTH (KM) | CONDUCTOR SIZE(SQ MM) | PEAK CURRENT (AMP) | CONNECTED LOAD (KVA) | Total INPUT in MU (A= 33KV Feeder Consumption+Bus Coupler ) | Total (33KV Incomer +33KV consumer+11KV Feeders* ) Consumption in MU (B) | LOSS IN MU (C=A-B) | % LOSS (D=C/A*100) | Total INPUT in MU (A= 33KV Feeder Consumption+Bus Coupler ) | Total (33KV Incomer +33KV consumer+11KV Feeders* ) Consumption in MU (B) | LOSS IN MU (C=A-B) | % LOSS (D=C/A*100) | Total INPUT in MU (A= 33KV Feeder Consumption+Bus Coupler ) | Total (33KV Incomer +33KV consumer+11KV Feeders* ) Consumption in MU (B) | LOSS IN MU (C=A-B) | % LOSS (D=C/A*100) | Total INPUT in MU (A= 33KV Feeder Consumption+Bus Coupler ) | Total (33KV Incomer +33KV consumer+11KV Feeders* ) Consumption in MU (B) | LOSS IN MU (C=A-B) | % LOSS (D=C/A*100) | INPUT MU (A) | OUTPUT MU (B) | LOSS IN MU (C=A-B) | % LOSS (D=(C/A) *100)
1 | MANCHESWAR | BBSR-2 | 10.4 | 232 | 400 | 36500 | 20.8634 | 20.32 | 0.5434 | 2.605% | 14.4984 | 13.718 | 0.7804 | 5.383% | 9.4616 | 8.852 | 0.6096 | 6.443% | 14.854 | 14.388 | 0.466 | 3.137% | 59.6774 | 57.278 | 2.3994 | 4.021%
2 | MANCHESWAR | BBSR-3 | 6.5 | 232 | 280 | 40500 | 25.2727 | 24.8134 | 0.45922 | 1.817% | 23.4696 | 21.9682 | 1.5014 | 6.397% | 17.3322 | 16.4835 | 0.84872 | 4.897% | 16.2894 | 15.2083 | 1.0811 | 6.637% | 82.3639 | 78.4734 | 3.8904 | 4.723%
3 | CHANDAKA | UNIT 8 FDR-1 | 17 | 232 | 400 | 17500 |  |  |  |  | 7.632 | 7.5455 | 0.0865 | 1.133% | 18.648 | 18.5604 | 0.0876 | 0.4698% | 19.776 | 19.5702 | 0.20584 | 1.041% | 46.056 | 45.6761 | 0.37994 | 0.825%
4 | CHANDAKA | UNIT 8 FDR-2 | 17 | 232 | 400 | 62500 |  |  |  |  | 3.576 | 3.5741 | 0.0019 | 0.05313% |  |  |  |  | 4.536 | 4.53 | 0.006 | 0.1323% | 8.112 | 8.1041 | 0.0079 | 0.09739%
| BCDD-01, BBSR | [5 empty] | 55.1661 | 54.24 | 0.9261 | 1.679% | 49.176 | 46.8058 | 2.3702 | 4.82% | 52.2098 | 50.7883 | 1.4215 | 2.723% | 55.4554 | 53.6964 | 1.759 | 3.172% | 196.2093 | 189.5316 | 6.6777 | 3.403%
5 | MANCHESWAR | BBSR-1 | 8.5 | 232 | 545 | - | 33.9904 | 33.7816 | 0.20877 | 0.6142% | 31.5008 | 30.5648 | 0.93602 | 2.971% | 25.008 | 25.6569 | -0.64895 | -2.595% |  |  |  |  | 90.4992 | 90.0034 | 0.49584 | 0.5479%
6 | MANCHESWAR | BBSR-8 | 3 | 100 | 25 | 750 | 1.2458 | 1.2458 | 0 | 0% | 1.0256 | 1.023 | 0.0026 | 0.2535% | 0.87246 | 0.87 | 0 | 0.1% | 0.73584 | 0.73581 | 0 | 0.004077% | 3.8797 | 3.8746 | 0.00509 | 0.1312%
7 | MANCHESWAR | BBSR-9 | 3 | 100 | 25 | 750
8 | RANASINGHPUR | AIIMS NO-I | 0.5 | 300 | 10 | 2500 | 3.922 | 3.9195 | 0.0025 | 0.06374% | [8 empty] | 2.911 | 2.91 | 0.001 | 0.03435% | 6.833 | 6.8295 | 0.0035 | 0.05122%
9 | RANASINGHPUR | AIIMS NO-II | 0.5 | 300 | 5 | 2000
10 | RANASINGHPUR | ASSOTECH | 6 | 100 | 250 | 20500 | 0.4036 | 0.3792 | 0.0244 | 6.046% | [12 empty] | 0.4036 | 0.3792 | 0.0244 | 6.046%
11 | RANASINGHPUR | BIPUL | 8 | 232 | 250 | 20500 |  |  |  |  | 11.7365 | 10.5856 | 1.151 | 9.807% | [8 empty] | 11.7365 | 10.5856 | 1.151 | 9.807%
12 | RANASINGHPUR | RANSINGHPUR | - | - | - | - |  |  |  |  | 1.1184 | 1.1219 | -0.0035 | -0.3129% | [8 empty] | 1.1184 | 1.1219 | -0.0035 | -0.3129%
13 | CHANDAKA | C S PUR-1 | 4.2 | 232 | 340 | 47000 | 12.3594 | 12.4055 | -0.04609 | -0.373% | 34.8725 | 33.2029 | 1.6696 | 4.788% | 44.8222 | 44.6928 | 0.12942 | 0.2887% | 44.4021 | 43.4614 | 0.94075 | 2.119% | 136.4563 | 133.7626 | 2.6937 | 1.974%
14 | CHANDAKA | C S PUR-2 | - | - | - | -
15 | CHANDAKA | INFOCITY | - | - | - | -
16 | CHANDAKA | XAVIER | 9.5 | 232 | 400 | 41000 |  |  |  |  | 32.1117 | 31.2921 | 0.81963 | 2.552% | 26.2306 | 25.8944 | 0.33623 | 1.282% | 23.5466 | 23.5023 | 0.044237 | 0.1879% | 81.8889 | 80.6888 | 1.2001 | 1.466%
17 | CHANDAKA | SJ | 20 | 100 | 40 | 5000
18 | CHANDAKA | NAYAPALLI | 11 | 232 | 500 | 30000 | 24.689 | 23.3905 | 1.2985 | 5.26% | 23.1798 | 21.5983 | 1.5815 | 6.823% | 15.3866 | 15.018 | 0.36864 | 2.396% | 12.13 | 11.5914 | 0.5386 | 4.44% | 75.3855 | 71.5982 | 3.7873 | 5.024%
19 | CHANDAKA | TCS | 3 | 300 | 220 | 1000 | 1.248 | 1.278 | -0.03 | -2.404% | 1.7544 | 1.764 | -0.0096 | -0.5472% | 1.5228 | 1.542 | -0.0192 | -1.261% | 1.5246 | 1.55 | -0.0254 | -1.666% | 6.0498 | 6.134 | -0.0842 | -1.392%
20 | CHANDAKA | KIIT | - | - | - | - | 4.74 | 4.812 | -0.072 | -1.519% | 10.2864 | 10.296 | -0.0096 | -0.09333% |  |  |  |  | 7.5174 | 7.4003 | 0.1171 | 1.558% | 22.5438 | 22.5083 | 0.0355 | 0.1575%
| BCDD-02, BBSR | [5 empty] | 82.5982 | 81.2121 | 1.3861 | 1.678% | 151.6035 | 145.5708 | 6.0327 | 3.979% | 122.6744 | 122.8996 | -0.2252 | -0.1836% | 116.5076 | 115.5922 | 0.91534 | 0.7857% | 436.7947 | 427.486 | 9.3086 | 2.131%
21 | MANCHESWAR | BBSR-4 | 8.5 | 232 | 240 | 48500 | 17.9948 | 17.2521 | 0.7427 | 4.127% | 15.9498 | 15.7591 | 0.19074 | 1.196% | 9.25 | 9.0574 | 0.19264 | 2.083% | 13.31 | 13.0618 | 0.24824 | 1.865% | 56.5046 | 55.1303 | 1.3743 | 2.432%
22 | MANCHESWAR | BBSR-5 | 8.5 | 232 | 240 | 15000 | 23.3552 | 21.9744 | 1.3808 | 5.912% | 22.6776 | 20.8546 | 1.823 | 8.039% | 14.62 | 12.8256 | 1.7944 | 12.27% | 12.83 | 12.5327 | 0.29728 | 2.317% | 73.4828 | 68.1873 | 5.2955 | 7.206%
23 | MANCHESWAR | FDR-7 | 17 | 100 | 160 | 25000 | 17.6336 | 16.8939 | 0.73967 | 4.195% | 17.6014 | 17.1484 | 0.45297 | 2.573% | [8 empty] | 35.235 | 34.0424 | 1.1926 | 3.385%
24 | BADAGADA | UTTARA | 10.5 | 100 | 360 | 29450 | 5.772 | 5.778 | -0.006 | -0.104% | [12 empty] | 5.772 | 5.778 | -0.006 | -0.104%
25 | KESURA | SBI KESURA | 1 | 100 | 32 | 3150 | 2.2708 | 2.2641 | 0.00672 | 0.2959% | 2.3959 | 2.2544 | 0.14152 | 5.907% | 1.16 | 1.15 | 0.01 | 0.8621% | 1.91 | 1.8904 | 0.0196 | 1.026% | 7.7367 | 7.5589 | 0.17784 | 2.299%
26 | RANSINGPUR | BHIMATANGI | 5.5 | 232 | 360 | 29000 |  |  |  |  | 14.0329 | 13.9601 | 0.0728 | 0.5188% | 15.928 | 15.7817 | 0.14631 | 0.9186% | 15.6026 | 15.4031 | 0.19949 | 1.279% | 45.5635 | 45.1449 | 0.4186 | 0.9187%
| BED , BBSR | [5 empty] | 82.1043 | 79.7847 | 2.3196 | 2.825% | 72.6576 | 69.9766 | 2.681 | 3.69% | 40.958 | 38.8146 | 2.1434 | 5.233% | 43.6526 | 42.888 | 0.76461 | 1.752% | 224.2946 | 215.8417 | 8.4529 | 3.769%
27 | NIMAPADA | KONARK | 0.25 | 100 | 92 | 8150 | 16.0115 | 15.8654 | 0.14614 | 0.9127% | 16.3223 | 15.9506 | 0.3717 | 2.277% | [8 empty] | 32.3338 | 31.816 | 0.51784 | 1.602%
28 | NIMAPADA | KAKATPUR | - | - | - | - | [8 empty] | 17.7448 | 15.5136 | 2.2312 | 12.57% | 17.3596 | 15.2296 | 2.13 | 12.27% | 35.1044 | 30.7432 | 4.3612 | 12.42%
29 | NIMAPADA | NIMAPADA | - | - | - | - | [8 empty] | 20.9724 | 19.9049 | 1.0675 | 5.09% | 22.7618 | 20.166 | 2.5958 | 11.4% | 43.7342 | 40.0709 | 3.6633 | 8.376%
30 | KONARK | GOP | 32 | 100 | 115 | 14750 | [8 empty] | 8.2002 | 7.825 | 0.37524 | 4.576% | 9.3489 | 8.2514 | 1.0975 | 11.74% | 17.5491 | 16.0764 | 1.4727 | 8.392%
31 | KONARK | KONARK | - | - | - | - | [8 empty] | 5.8887 | 5.7267 | 0.16205 | 2.752% | 6.3645 | 6.1706 | 0.19391 | 3.047% | 12.2532 | 11.8972 | 0.35596 | 2.905%
32 | KESURA | BALIPATNA | - | - | - | - | 21.0645 | 18.8652 | 2.1992 | 10.44% | 14.4803 | 12.906 | 1.5743 | 10.87% | 18.7314 | 17.4207 | 1.3107 | 6.998% | 18.2359 | 16.984 | 1.2519 | 6.865% | 72.5121 | 66.1759 | 6.3361 | 8.738%
| NED,NIMAPADA | [5 empty] | 37.076 | 34.7306 | 2.3454 | 6.326% | 30.8026 | 28.8566 | 1.946 | 6.318% | 71.5375 | 66.3908 | 5.1467 | 7.194% | 74.0707 | 66.8016 | 7.2691 | 9.814% | 213.4868 | 196.7796 | 16.7072 | 7.826%
CIRCLE-1 | [6 empty] | 256.9445 | 249.9674 | 6.9771 | 2.715% | 304.2398 | 291.2099 | 13.0299 | 4.283% | 287.3797 | 278.8933 | 8.4864 | 2.953% | 289.6863 | 278.9783 | 10.708 | 3.696% | 1070.7854 | 1029.6389 | 41.1464 | 3.843%
33 | KHURDA | BANKI | 51 | 232 | 240 | 29250 | 5.0816 | 4.9181 | 0.16358 | 3.219% | 7.386 | 7.0661 | 0.31986 | 4.331% | 6.991 | 7.3604 | -0.36944 | -5.284% | 7.636 | 7.3385 | 0.29747 | 3.896% | 27.0946 | 26.6832 | 0.41147 | 1.519%
34 | KHURDA | BOLAGARH | 42 | 55 | 320 | 37600 | 16.2453 | 16.087 | 0.15829 | 0.9744% | 23.074 | 22.2601 | 0.8139 | 3.527% | 19.422 | 20.2059 | -0.78389 | -4.036% | 21.307 | 20.7956 | 0.5114 | 2.4% | 80.0483 | 79.3486 | 0.6997 | 0.8741%
35 | KHURDA | JATNI | 21 | 80 | 152 | 26350 | 10.8987 | 10.9629 | -0.064198 | -0.589% | 16.235 | 15.9765 | 0.25847 | 1.592% | 12.408 | 12.2803 | 0.12765 | 1.029% | 10.252 | 9.8921 | 0.3599 | 3.511% | 49.7937 | 49.1119 | 0.68183 | 1.369%
36 | KHURDA | KHURDA | 0.15 | 148 | 180 | 16000 |  |  |  |  | 15.303 | 15.412 | -0.109 | -0.7123% | 12.442 | 12.508 | -0.066 | -0.53% | 12.058 | 12.172 | -0.114 | -0.9454% | 39.803 | 40.092 | -0.289 | -0.7261%
37 | KHURDA | TANGI | 42 | 100 | 224 | 26050 | 16.932 | 16.0736 | 0.85841 | 5.07% | 24.749 | 24.4064 | 0.34262 | 1.384% | 20.283 | 19.988 | 0.29496 | 1.454% | 20.201 | 18.8214 | 1.3796 | 6.829% | 82.165 | 79.2895 | 2.8756 | 3.5%
38 | KHURDA | RAILWAY | 25 | 80 | 364 | 17500 | 20.756 | 20.4098 | 0.3462 | 1.668% | 26.589 | 26.3272 | 0.26178 | 0.9845% | 22.917 | 23.411 | -0.49403 | -2.156% | 27.409 | 25.6965 | 1.7125 | 6.248% | 97.671 | 95.8445 | 1.8265 | 1.87%
39 | ARGUL | NISER-1 | 5 | 400 | 40 | 1500 |  |  |  |  | 4.981 | 4.9755 | 0.005506 | 0.1105% | 4.343 | 4.3574 | -0.014372 | -0.3309% | 4.967 | 4.8686 | 0.098416 | 1.981% | 14.291 | 14.2015 | 0.08955 | 0.6266%
40 | ARGUL | NISER-2 | 5 | 400 | 40 | 1500
41 | ARGUL | IIT-1 & 2 | 0.7 | 100 | 20 | 250
42 | ARGUL | ICFMD | - | - | - | -
43 | RAIPATANA | BINODPADA | - | - | - | - | [8 empty] | 6.636 | 5.8585 | 0.77749 | 11.72% |  |  |  |  | 6.636 | 5.8585 | 0.77749 | 11.72%
44 | MENDHASAL | MENDHASAL | - | - | - | - | [8 empty] | 1.68 | 1.5771 | 0.10285 | 6.122% | 2.502 | 2.3891 | 0.11292 | 4.513% | 4.182 | 3.9662 | 0.21577 | 5.16%
45 | INFOCITY | INFOSYS-JATNI | - | - | - | - | [8 empty] | 14.114 | 12.5438 | 1.5702 | 11.12% |  |  |  |  | 14.114 | 12.5438 | 1.5702 | 11.12%
46 | RANASINGHAPUR | IOCL | 20 | 300 | 25 | 16000 | 0.4533 | 0.453 | 0.0003 | 0.06618% | [12 empty] | 0.4533 | 0.453 | 0.0003 | 0.06618%
| KHD, KHURDA | [5 empty] | 70.3669 | 68.9044 | 1.4626 | 2.079% | 118.317 | 116.4239 | 1.8931 | 1.6% | 121.236 | 120.0906 | 1.1454 | 0.9448% | 106.332 | 101.9738 | 4.3582 | 4.099% | 416.2519 | 407.3926 | 8.8593 | 2.128%
47 | BALUGAON | INS CHILIKA | 1.5 | 55 | 16 | 1000 | 1.2806 | 1.2822 | -0.0016375 | -0.1279% | 1.19 | 1.1914 | 0 | 0% | 0.997 | 1.0002 | -0.0032 | -0.321% | 0.9301 | 0.93 | 0.0001 | 0.01075% | 4.3977 | 4.4038 | -0.0061375 | -0.1396%
48 | BALUGAON | BALUGAON | 8 | 100 | 180 | 21000 | 15.527 | 14.944 | 0.583 | 3.755% | [12 empty] | 15.527 | 14.944 | 0.583 | 3.755%
| BAED, BALUGAON | [5 empty] | 16.8076 | 16.2262 | 0.58136 | 3.459% | 1.19 | 1.1914 | 0 | 0% | 0.997 | 1.0002 | -0.0032 | -0.321% | 0.9301 | 0.93 | 0.0001 | 0.01075% | 19.9247 | 19.3478 | 0.57686 | 2.895%
49 | NAYAGARH | Nayagarh | 8 | 232 | 150 | 13000 | 12.286 | 11.6065 | 0.67954 | 5.531% | 11.5865 | 10.944 | 0.6425 | 5.545% | 8.5406 | 7.843 | 0.69761 | 8.168% | 8.5429 | 7.9962 | 0.54674 | 6.4% | 40.956 | 38.3896 | 2.5664 | 6.266%
| NED,NAYAGARH | [5 empty] | 12.286 | 11.6065 | 0.67954 | 5.531% | 11.5865 | 10.944 | 0.6425 | 5.545% | 8.5406 | 7.843 | 0.69761 | 8.168% | 8.5429 | 7.9962 | 0.54674 | 6.4% | 40.956 | 38.3896 | 2.5664 | 6.266%
50 | PURI | SAKHIGOPAL | 22 | 148 /100 | 320 | - | 24.1829 | 21.694 | 2.4889 | 10.29% | 23.4797 | 22.0392 | 1.4405 | 6.135% | 19.3926 | 17.6352 | 1.7574 | 9.062% | 19.3448 | 17.5785 | 1.7663 | 9.131% | 86.4 | 78.9469 | 7.4531 | 8.626%
51 | SAMUKA | ALARNATH | 22 | - | 180 | 22600 | 13.9926 | 13.4972 | 0.49539 | 3.54% | 15.0858 | 13.6461 | 1.4397 | 9.543% | 13.396 | 11.5237 | 1.8723 | 13.98% | 13.3062 | 11.8613 | 1.4449 | 10.86% | 55.7806 | 50.5282 | 5.2524 | 9.416%
52 | KHURDA | DELANG | 41 | 100 | 304 | 8150 | 10.382 | 9.6529 | 0.72916 | 7.023% | 15.6355 | 14.204 | 1.4315 | 9.155% | 13.3478 | 12.506 | 0.8418 | 6.307% | 15.4818 | 14.236 | 1.2458 | 8.047% | 54.8471 | 50.5988 | 4.2483 | 7.746%
53 | SAMUKA | SAMUKA-I | - | - | - | - |  |  |  |  | 73.743 | 68.6905 | 5.0525 | 6.851% | 57.2006 | 55.0331 | 2.1675 | 3.789% | 53.078 | 50.767 | 2.311 | 4.354% | 184.0216 | 174.4906 | 9.531 | 5.179%
54 | SAMUKA | SAMUKA-II | - | - | - | -
55 | SAMAGHERA | SAMAGHERA-I | - | - | - | -
56 | SAMAGHERA | SAMAGHERA-II | - | - | - | -
57 | PURI | PURI-I | 4.5 | 148 | 390 | 46000
58 | PURI | PURI-II | 3.5 | 148 | 437 | 62600
59 | PURI | SRIRAMNAGAR-I | 1.7 | 148 | 122 | 16000
60 | PURI | SRIRAMNAGAR-2 | 1.7 | 148 | 122 | 16000
| PED, PURI | [5 empty] | 48.5575 | 44.8441 | 3.7135 | 7.648% | 127.944 | 118.5798 | 9.3641 | 7.319% | 103.337 | 96.6979 | 6.6391 | 6.425% | 101.2108 | 94.4427 | 6.7681 | 6.687% | 381.0493 | 354.5645 | 26.4847 | 6.95%
CIRCLE-2 | [6 empty] | 148.0181 | 141.5811 | 6.437 | 4.349% | 259.0374 | 247.1391 | 11.8984 | 4.593% | 234.1106 | 225.6317 | 8.4789 | 3.622% | 217.0158 | 205.3427 | 11.6731 | 5.379% | 858.182 | 819.6946 | 38.4873 | 4.485%
61 | BIDANASI | IOCL(DIRECT CABLE)-2 | - | - | - | - | 1.428 | 1.4436 | -0.0156 | -1.092% |  |  |  |  | 1.8756 | 1.8666 | 0.009 | 0.48% | 1.4424 | 1.441 | 0.0014 | 0.09706% | 4.746 | 4.7512 | -0.0052 | -0.1096%
62 | BIDANASI | IOCL-1 METERING AT KALINGA GRID END | - | - | - | -
| CDD-1, CUTTACK | [5 empty] | 1.428 | 1.4436 | -0.0156 | -1.092% |  |  |  |  | 1.8756 | 1.8666 | 0.009 | 0.4798% | 1.4424 | 1.441 | 0.0014 | 0.09706% | 4.746 | 4.7512 | -0.0052 | -0.1096%
63 | CUTTACK | BENTKAR | 8 | 80 | 64 | 10000 | 5.0874 | 5.205 | -0.11756 | -2.311% | 3.3934 | 3.398 | -0.00458 | -0.135% | 4.2276 | 3.9782 | 0.24938 | 5.899% | 4.248 | 4.2712 | -0.02318 | -0.5457% | 16.9564 | 16.8523 | 0.10406 | 0.6137%
64 | BIDANASI | BADAMBADI | 4.2 | 100 | 404 | 41000 |  |  |  |  | 17.0752 | 15.748 | 1.3272 | 7.773% | 13.9612 | 12.48 | 1.4812 | 10.61% | 11.8908 | 11.84 | 0.0508 | 0.4272% | 42.9272 | 40.068 | 2.8592 | 6.661%
65 | CUTTACK | JS PUR Rural | 12.4 | 100 | 296 | 16300 | 20.502 | 19.764 | 0.738 | 3.6% | 19.2336 | 18.516 | 0.7176 | 3.731% | 15.9624 | 15.612 | 0.3504 | 2.195% | 15.0576 | 14.712 | 0.3456 | 2.295% | 70.7556 | 68.604 | 2.1516 | 3.041%
66 | CUTTACK | CRRI 1 | 4 | 232 | 120 | 16000 | 8.679 | 8.4066 | 0.27248 | 3.14% | 7.4287 | 7.2857 | 0.14293 | 1.924% | 6.202 | 5.818 | 0.38398 | 6.191% | 5.9636 | 5.8983 | 0.06531 | 1.095% | 28.2734 | 27.4087 | 0.8647 | 3.058%
67 | CUTTACK | CRRI 2 | 4 | 232 | 180 | 16000
68 | CUTTACK | CHAULIAGANJ-1 | 7.2 | 100 | 152 | 25000 | 9.8292 | 9.554 | 0.2752 | 2.8% | 24.9625 | 24.242 | 0.72048 | 2.886% | 16.582 | 15.882 | 0.69996 | 4.221% | 10.794 | 9.666 | 1.128 | 10.45% | 62.1676 | 59.344 | 2.8236 | 4.542%
69 | CUTTACK | CHAULIAGANJ-2 | 6.5 | 100 | 112 | 16000
| CDD-2, CUTTACK | [5 empty] | 44.0976 | 42.9295 | 1.1681 | 2.649% | 72.0934 | 69.1897 | 2.9036 | 4.028% | 56.9352 | 53.7703 | 3.1649 | 5.559% | 47.954 | 46.3875 | 1.5665 | 3.267% | 221.0802 | 212.277 | 8.8032 | 3.982%
70 | CHANDIKHOLE | BADACHANA | 17 | 100 | 279 | 24450 | 21.093 | 21.072 | 0.02096 | 0.09937% | 22.9766 | 22.38 | 0.59664 | 2.597% | 21.4522 | 20.028 | 1.4242 | 6.639% | 20.5952 | 21.456 | -0.86076 | -4.179% | 86.117 | 84.936 | 1.181 | 1.371%
71 | CHOUDWAR | CHOUDWAR | 0.7 | 100 | 190 | 16000 | 15.2513 | 15.37 | -0.11872 | -0.7784% | 15.1171 | 15.3248 | -0.20772 | -1.374% | 12.5035 | 12.5407 | -0.0372 | -0.2975% | 11.8722 | 12.1304 | -0.25824 | -2.175% | 54.7441 | 55.366 | -0.62188 | -1.136%
72 | CHOUDWAR | TANGI | 5.5 | 80 | 140 | 21000 | 17.2507 | 16.7582 | 0.49257 | 2.855% | 18.2245 | 17.2992 | 0.92532 | 5.077% | 16.5116 | 15.4994 | 1.0123 | 6.131% | 18.0419 | 17.3152 | 0.7266 | 4.027% | 70.0288 | 66.8719 | 3.1568 | 4.508%
73 | CHOUDWAR | ATHAGARH | 4.7 | 148 | 214 | 18150 | 14.639 | 13.6769 | 0.96212 | 6.572% | 23.052 | 23.349 | -0.297 | -1.288% | 22.669 | 21.7127 | 0.95632 | 4.219% | 23.103 | 23.3394 | -0.2364 | -1.023% | 83.463 | 82.078 | 1.385 | 1.659%
74 | CHOUDWAR | RSB | - | - | - | - | 5.088 | 5.0851 | 0.0029 | 0.057% | 4.708 | 4.6723 | 0.0357 | 0.7583% | 5.502 | 5.4754 | 0.02664 | 0.4842% | 3.342 | 3.042 | 0.29997 | 8.976% | 18.64 | 18.2748 | 0.36521 | 1.959%
75 | CUTTACK | BALIKUDA | 8 | 80 | 180 | 13000 |  |  |  |  | 12.3473 | 12.185 | 0.16224 | 1.314% | 10.2572 | 9.3678 | 0.8894 | 8.671% | 9.6497 | 9.5167 | 0.13296 | 1.378% | 32.2542 | 31.0696 | 1.1846 | 3.673%
| CED, CUTTACK | [5 empty] | 73.322 | 71.9621 | 1.3598 | 1.855% | 96.4256 | 95.2104 | 1.2152 | 1.26% | 88.8956 | 84.624 | 4.2716 | 4.805% | 86.604 | 86.7998 | -0.19582 | -0.2261% | 345.2471 | 338.5963 | 6.6508 | 1.926%
76 | NUAPATNA | BADAMBA & NARSINGHPUR | 20 | 100 | 322 | 38900 | 26.585 | 24.5977 | 1.9873 | 7.475% | 27.697 | 25.4341 | 2.2629 | 8.17% | 22.355 | 20.4533 | 1.9017 | 8.507% | 19.945 | 19.067 | 0.87796 | 4.402% | 96.582 | 89.5522 | 7.0298 | 7.279%
77 | NUAPATNA | ATHAGARH FEEDER | 25 | 100 | 310 | 36000 | 26.5188 | 25.2616 | 1.2572 | 4.741% | 18.739 | 18.3891 | 0.34988 | 1.867% | 23.414 | 21.2809 | 2.1331 | 9.111% | 20.641 | 20.4987 | 0.14228 | 0.6893% | 89.3128 | 85.4303 | 3.8825 | 4.347%
| AED, ATHAGARH | [5 empty] | 53.1038 | 49.8593 | 3.2445 | 6.11% | 46.436 | 43.8232 | 2.6128 | 5.627% | 45.769 | 41.7341 | 4.0349 | 8.816% | 40.586 | 39.5658 | 1.0202 | 2.514% | 185.8948 | 174.9824 | 10.9124 | 5.87%
CUTTACK CIRCLE | [6 empty] | 171.9514 | 166.1946 | 5.7568 | 3.348% | 214.9549 | 208.2233 | 6.7316 | 3.132% | 193.4753 | 181.995 | 11.4804 | 5.934% | 176.5864 | 174.1941 | 2.3923 | 1.355% | 756.9681 | 730.607 | 26.3611 | 3.482%
78 | GUNDICHAPADA | DHENKANAL TOWN | 13 | 100 | 200 | 24150 | 25.0833 | 23.9972 | 1.0861 | 4.33% | 23.3445 | 23.1588 | 0.18568 | 0.7954% | 13.6802 | 13.5272 | 0.15302 | 1.119% | 11.7316 | 11.4868 | 0.2448 | 2.087% | 73.8396 | 72.17 | 1.6696 | 2.261%
79 | GUNDICHAPADA | DAKHINAKALI | 9.1 | 100 | 60 | 16000
80 | GUNDICHAPADA | GUNDICHAPADA-2 | 0.01 | 100 | 260 | 23500 | 7.3963 | 7.229 | 0.16729 | 2.262% | 22.149 | 20.1269 | 2.0221 | 9.13% | 13.6963 | 12.227 | 1.4693 | 10.73% | 18.4018 | 17.5893 | 0.81245 | 4.415% | 61.6434 | 57.1723 | 4.4712 | 7.253%
81 | GUNDICHAPADA | Hindol Road | 63 | 80 | 220 | 27350 | 8.3531 | 7.865 | 0.4881 | 5.843% | 7.7598 | 7.6907 | 0.06908 | 0.8902% | 5.2098 | 5.0689 | 0.14088 | 2.704% | 4.9899 | 4.8543 | 0.13564 | 2.718% | 26.3126 | 25.4789 | 0.8337 | 3.168%
82 | GUNDICHAPADA | OPL | 14 | 80 | 60 | 3400 | 0.1176 | 0.1288 | -0.011196 | -9.52% | 0.103 | 0.11125 | -0.008248 | -8.008% | 0.0404 | 0.045236 | -0.004836 | -11.97% |  |  |  |  | 0.261 | 0.28528 | -0.02428 | -9.303%
83 | KALARANGI | TISCO | 4.5 | 80 | 42 | 5500 | 5.6114 | 5.6342 | -0.022863 | -0.4074% | 4.0526 | 4.0827 | -0.0301 | -0.7427% | 2.3535 | 2.3703 | -0.016779 | -0.7129% | 4.6672 | 4.5414 | 0.12575 | 2.694% | 16.6847 | 16.6287 | 0.056009 | 0.3357%
84 | KALARANGI | SOVA METAL | 1 | 80 | 70 | 6000 |  |  |  |  | 6.1224 | 6.1548 | -0.03238 | -0.5289% | 2.3114 | 2.3066 | 0.00478 | 0.2068% | 4.9626 | 4.9753 | -0.01272 | -0.2563% | 13.3964 | 13.4367 | -0.04032 | -0.301%
85 | KALARANGI | 33KV OTHER MINES | - | - | - | - |  |  |  |  | 5.2153 | 5.0826 | 0.13274 | 2.545% | 3.5386 | 3.448 | 0.090574 | 2.56% | 5.3317 | 5.1514 | 0.18031 | 3.382% | 14.0856 | 13.682 | 0.40362 | 2.865%
86 | KALARANGI | OMC | 14 | 55 | 35 | 7350 | 1.7607 | 1.6271 | 0.13362 | 7.589% | 1.7312 | 1.806 | -0.0748 | -4.321% | 1.0898 | 1.0989 | -0.009088 | -0.8339% | 1.6526 | 1.6328 | 0.019794 | 1.198% | 6.2344 | 6.1648 | 0.069521 | 1.115%
87 | KHAJURIAKATA | HINDOL | - | - | - | - | 3.34 | 3.247 | 0.093 | 2.784% | 4.8282 | 4.729 | 0.0992 | 2.055% | 2.8678 | 2.8085 | 0.05926 | 2.066% | 4.6526 | 4.0065 | 0.64612 | 13.89% | 15.6886 | 14.791 | 0.89758 | 5.721%
88 | KAMAKHYANAGAR | KAMAKHYANAGAR | 2 | 80 | 200 | 21300 | 12.624 | 11.7725 | 0.85148 | 6.745% | [12 empty] | 12.624 | 11.7725 | 0.85148 | 6.745%
| DED, DHENKANAL | [5 empty] | 64.2864 | 61.5009 | 2.7856 | 4.333% | 75.306 | 72.9427 | 2.3633 | 3.138% | 44.7878 | 42.9007 | 1.8871 | 4.213% | 56.39 | 54.2379 | 2.1521 | 3.817% | 240.7702 | 231.5821 | 9.1881 | 3.816%
89 | ANGUL | ANGUL-1 | 5 | 100 | 270 | 41650 | 39.276 | 36.7175 | 2.5585 | 6.514% | 35.804 | 33.59 | 2.214 | 6.184% | 31.725 | 30.564 | 1.161 | 3.66% | 30.205 | 29.209 | 0.996 | 3.297% | 137.01 | 130.0805 | 6.9295 | 5.058%
90 | ANGUL | ANGUL-2 | 5 | 100 | 230 | 6350
91 | ANGUL | HEMSURPADA | 0.5 | 100 | 70 | 3150 | 14.326 | 13.5781 | 0.7479 | 5.221% | 13.39 | 12.235 | 1.155 | 8.626% | 9.765 | 9.828 | -0.063 | -0.6452% | 11.116 | 10.563 | 0.553 | 4.975% | 48.597 | 46.2041 | 2.3929 | 4.924%
92 | ANGUL | RAILWAY | 5 | 148 | 10 | 500 | 0.362 | 0.3618 | 0.0002 | 0.05525% | 0.371 | 0.371 | 0 | 0% | 0.308 | 0.308 | 0 | 0% | 0.283 | 0.28 | 0 | 0% | 1.324 | 1.3208 | 0.0032 | 0.2417%
93 | ANGUL | GANESH SPONGE | 1.2 | 100 | 30 | 5000 | 1.36 | 1.3534 | 0.00656 | 0.4824% | 1.212 | 1.212 | 0 | 0% | 1.597 | 1.597 | 0 | 0% | 1.448 | 1.44 | 0 | 0% | 5.617 | 5.6024 | 0.01456 | 0.2592%
94 | BOINDA | BOINDA | - | - | - | - | 5.756 | 5.5616 | 0.19438 | 3.377% | 6.046 | 5.837 | 0.209 | 3.457% | 5.906 | 5.689 | 0.217 | 3.674% | 5.916 | 5.826 | 0.09 | 1.521% | 23.624 | 22.9136 | 0.71038 | 3.007%
95 | BOINDA | JARPADA | 14 | 80 | 180 | 22900 | 13.08 | 12.8931 | 0.18689 | 1.429% | 13.362 | 12.771 | 0.591 | 4.423% | [8 empty] | 26.442 | 25.6641 | 0.77789 | 2.942%
96 | BOINDA | ATHAMALLIK | 45 | 55 | 120 | 12650 | 8.471 | 8.2007 | 0.27027 | 3.19% | [12 empty] | 8.471 | 8.2007 | 0.27027 | 3.19%
97 | RAIRAKHOL | BAMUR | - | - | - | 4750 | 5.219 | 4.9327 | 0.28631 | 5.486% | 5.465 | 5.166 | 0.299 | 5.471% |  |  |  |  | 5.223 | 4.677 | 0.546 | 10.45% | 15.907 | 14.7757 | 1.1313 | 7.112%
| ANED, ANGUL | [5 empty] | 87.85 | 83.599 | 4.251 | 4.839% | 75.65 | 71.182 | 4.468 | 5.906% | 49.301 | 47.986 | 1.315 | 2.667% | 54.191 | 51.995 | 2.196 | 4.052% | 266.992 | 254.762 | 12.23 | 4.581%
98 | CHAINPAL | CHAINPAL | 0.8 | 300 | 70 | 10000 | 6.0279 | 5.9965 | 0.03136 | 0.5202% | 5.88 | 5.8601 | 0.01982 | 0.3371% | 5.0242 | 4.9836 | 0.04058 | 0.8077% | 4.7318 | 4.6535 | 0.0783 | 1.655% | 21.6638 | 21.4938 | 0.17006 | 0.785%
99 | CHAINPAL | INDUSTRIAL | 10 | 100 | 120 | 8150 | 17.1175 | 16.3068 | 0.81069 | 4.736% | 15.8468 | 15.6388 | 0.20796 | 1.312% | 15.6061 | 15.242 | 0.36413 | 2.333% | 14.7981 | 14.3225 | 0.47558 | 3.214% | 63.3685 | 61.5101 | 1.8584 | 2.933%
100 | CHAINPAL | PARJANGA | 33 | 100 | 240 | 16600 | 16.4881 | 15.3112 | 1.1769 | 7.138% |  |  |  |  | 15.5601 | 14.3748 | 1.1853 | 7.618% | 16.7879 | 15.1619 | 1.626 | 9.686% | 48.8361 | 44.8478 | 3.9883 | 8.167%
101 | CHAINPAL | BANARAPAL | 6 | 100 | 300 | 24000 | 17.9203 | 17.6275 | 0.29278 | 1.634% | 17.3687 | 17.2802 | 0.08854 | 0.5098% | 14.5459 | 13.8922 | 0.6537 | 4.494% | 13.6795 | 13.3334 | 0.3461 | 2.53% | 63.5143 | 62.1332 | 1.3811 | 2.175%
102 | CHAINPAL | TALCHER | - | - | - | - | [8 empty] | 30.6527 | 28.4982 | 2.1545 | 7.029% | 28.7624 | 26.6213 | 2.1411 | 7.444% | 59.4151 | 55.1195 | 4.2956 | 7.23%
103 | RENGALI | RENGALI | 4 | 80 | 190 | 33500 |  |  |  |  | 7.4088 | 6.8234 | 0.58533 | 7.9% | [8 empty] | 7.4088 | 6.8234 | 0.58533 | 7.9%
104 | RENGALI | KANIHA | - | - | - | - |  |  |  |  | 13.8462 | 12.4452 | 1.401 | 10.12% | [8 empty] | 13.8462 | 12.4452 | 1.401 | 10.12%
105 | RENGALI | KHAMAR | 25 | 100 | 190 | 11050 |  |  |  |  | 11.5851 | 11.2173 | 0.36777 | 3.175% | 10.5934 | 10.259 | 0.33433 | 3.156% | 10.6317 | 9.8057 | 0.82599 | 7.769% | 32.8101 | 31.282 | 1.5281 | 4.657%
106 | BARKOTE | PALLAHARA | 30 | 100 | 60 | 8150
| TED,CHAINPAL | [5 empty] | 57.5537 | 55.2419 | 2.3117 | 4.017% | 71.9355 | 69.265 | 2.6705 | 3.712% | 91.9823 | 87.2497 | 4.7326 | 5.145% | 89.3915 | 83.8984 | 5.4931 | 6.145% | 310.8629 | 295.655 | 15.2079 | 4.892%
DHENKANAL CIRCLE | [6 empty] | 209.6901 | 200.3418 | 9.3483 | 4.458% | 222.8915 | 213.3897 | 9.5018 | 4.263% | 186.0711 | 178.1364 | 7.9347 | 4.264% | 199.9725 | 190.1312 | 9.8413 | 4.921% | 818.6251 | 781.9991 | 36.6261 | 4.474%
107 | KENDRAPRA | KENDRAPRA | 6.5 | 100 | 220 | 29150 | 18.1779 | 18.3324 | -0.15448 | -0.8498% | 18.4358 | 18.089 | 0.34681 | 1.881% | 13.8114 | 13.2973 | 0.51408 | 3.722% | 12.8648 | 12.3857 | 0.47912 | 3.724% | 63.29 | 62.1045 | 1.1855 | 1.873%
108 | KENDRAPRA | AUL-PATTAMUNDAI | 6 | 55 | 60 | 5000 | 1.1928 | 1.1873 | 0.00546 | 0.4577% | 1.2016 | 1.252 | -0.05044 | -4.198% | 0.814 | 0.80386 | 0.01014 | 1.246% | 0.8138 | 0.80354 | 0.01026 | 1.261% | 4.0222 | 4.0468 | -0.02458 | -0.6111%
109 | KENDRAPRA | INDUPUR | 18 | 80 | 70 | 6300 | 7.8894 | 7.8619 | 0.02751 | 0.3487% | 7.8068 | 7.8498 | -0.04295 | -0.5502% | 6.1414 | 6.1858 | -0.04444 | -0.7236% | 5.5508 | 5.5872 | -0.0364 | -0.6558% | 27.3885 | 27.4847 | -0.09628 | -0.3515%
110 | KENDRAPRA | LUNA | 18 | 100 | 230 | 21300 | 3.4543 | 3.4122 | 0.04212 | 1.219% | 3.4484 | 3.4661 | -0.01777 | -0.5153% | 2.6192 | 2.5726 | 0.04664 | 1.781% | 2.7738 | 2.8582 | -0.0844 | -3.043% | 12.2957 | 12.3092 | -0.01341 | -0.1091%
111 | KENDRAPRA | DANPUR | 18 | 100 | 230 | 21300 | 17.1276 | 16.1296 | 0.998 | 5.827% | 17.2128 | 16.3826 | 0.8302 | 4.823% | 13.506 | 13.0009 | 0.50508 | 3.74% | 12.9392 | 12.1796 | 0.7596 | 5.871% | 60.7856 | 57.6927 | 3.0929 | 5.088%
112 | KENDRAPRA | PATTAMUNDAI | - | - | - | - | [8 empty] | 5.3011 | 4.6443 | 0.65682 | 12.39% | 4.9473 | 4.8534 | 0.09387 | 1.897% | 10.2484 | 9.4977 | 0.75069 | 7.325%
113 | KENDRAPRA | AUL | 2.3 | 100 | 100 | 10000 | 10.1214 | 9.0635 | 1.0579 | 10.45% |  |  |  |  | 7.9355 | 7.1704 | 0.7651 | 9.641% | 7.08 | 6.5815 | 0.49852 | 7.041% | 25.1369 | 22.8154 | 2.3215 | 9.235%
114 | KENDRAPRA | RAJNAGAR | 22 | 100 | 130 | 23150 | 13.716 | 11.979 | 1.737 | 12.66% | 15.096 | 13.5852 | 1.5108 | 10.01% | 10.92 | 10.0533 | 0.86669 | 7.937% | 9.78 | 9.1708 | 0.60919 | 6.229% | 49.512 | 44.7882 | 4.7238 | 9.541%
115 | KENDRAPRA | GOGUA | 13 | 100 | 80 | 11300 | 7.1834 | 6.9543 | 0.22903 | 3.188% | 7.8253 | 7.7629 | 0.06242 | 0.7977% | 5.9166 | 5.6535 | 0.26305 | 4.446% | 5.7208 | 5.5038 | 0.21701 | 3.793% | 26.6461 | 25.8746 | 0.77151 | 2.895%
| KED-01, KENDRAPARA | [5 empty] | 78.8628 | 74.9203 | 3.9426 | 4.999% | 71.0267 | 68.3876 | 2.6391 | 3.716% | 66.9652 | 63.382 | 3.5832 | 5.351% | 62.4706 | 59.9238 | 2.5468 | 4.077% | 279.3254 | 266.6138 | 12.7116 | 4.551%
116 | MARSHAGHAI | LUNA-GARADPUR | 43.5 | 100 | 320 | 39200 | 12.1752 | 11.8003 | 0.37492 | 3.079% | 12.4824 | 11.9449 | 0.53754 | 4.306% | 4 | 3.6527 | 0.34734 | 8.683% | 8.9906 | 8.9114 | 0.07918 | 0.8807% | 37.6482 | 36.3092 | 1.339 | 3.557%
117 | MARSHAGHAI | MAHAKALPADA | 25 | 148 | 280 | 44200 | 11.4576 | 10.6091 | 0.84845 | 7.405% | 12.0084 | 11.0661 | 0.94233 | 7.847% | 8.9076 | 8.1458 | 0.7618 | 8.552% | 8.0196 | 7.4851 | 0.53446 | 6.664% | 40.3932 | 37.3062 | 3.087 | 7.642%
| KED-02, MARSAGHAI | [5 empty] | 23.6328 | 22.4094 | 1.2234 | 5.177% | 24.4908 | 23.0109 | 1.4799 | 6.043% | 12.9076 | 11.7985 | 1.1091 | 8.593% | 17.0102 | 16.3966 | 0.61364 | 3.607% | 78.0414 | 73.6154 | 4.426 | 5.671%
118 | JAGATSINGHPUR | TIRTOL | 22 | 100 | 180 | 15000 | 16.0736 | 15.737 | 0.33664 | 2.094% | 15.3902 | 15.046 | 0.3442 | 2.236% | 11.7883 | 11.682 | 0.10632 | 0.9019% | 11.3936 | 11.1812 | 0.21244 | 1.865% | 54.6458 | 53.6462 | 0.9996 | 1.829%
119 | JAGATSINGHPUR | JAGATSINHPUR | 5 | 80 | 240 | 23650 | 12.972 | 12.5797 | 0.39226 | 3.024% | 11.79 | 11.7987 | -0.00872 | -0.07396% | 9.4488 | 9.564 | -0.1152 | -1.219% | 8.92 | 8.9528 | -0.0328 | -0.3677% | 43.1308 | 42.8953 | 0.23554 | 0.5461%
120 | JAGATSINGHPUR | BALIKUDA | - | - | - | - | [8 empty] | 8.996 | 8.658 | 0.338 | 3.757% | 11.7 | 11.538 | 0.162 | 1.385% | 20.696 | 20.196 | 0.5 | 2.416%
121 | JAGATSINGHPUR | NAUGAON | - | - | - | - | [8 empty] | 3.8325 | 3.6865 | 0.146 | 3.81% | 5.1755 | 4.85 | 0.3255 | 6.289% | 9.008 | 8.5365 | 0.4715 | 5.234%
| JED, JAGATSINGHAPUR | [5 empty] | 29.0456 | 28.3167 | 0.7289 | 2.509% | 27.1802 | 26.8447 | 0.33548 | 1.234% | 34.0656 | 33.5905 | 0.47512 | 1.395% | 37.1891 | 36.522 | 0.66714 | 1.794% | 127.4806 | 125.274 | 2.2066 | 1.731%
122 | PARADEEP | INDUSTRIAL | 1.2 | 100 | 185 | 21000 | 17.754 | 17.6109 | 0.14305 | 0.8057% | 12.7449 | 12.7065 | 0.03837 | 0.3011% | 15.1822 | 15.0417 | 0.14051 | 0.9255% | 14.2549 | 13.5792 | 0.67575 | 4.74% | 59.936 | 58.9383 | 0.99768 | 1.665%
123 | PARADEEP | TIRTOL | 32 | 100 | 380 | 36300 | 29.117 | 26.7376 | 2.3794 | 8.172% | 18.72 | 17.5609 | 1.1591 | 6.192% | 17.0359 | 15.7791 | 1.2568 | 7.377% | 16.728 | 16.4636 | 0.26443 | 1.581% | 81.6009 | 76.5412 | 5.0597 | 6.201%
124 | PARADEEP | HPCL | 10 | 100 | 30 | 4880 | 0.0864 | 0.08529 | 0.00111 | 1.285% | 0.3376 | 0.3309 | 0.0067 | 1.985% | 0.7581 | 0.69228 | 0.06582 | 8.682% | 0.9606 | 1.0042 | -0.04362 | -4.541% | 2.1427 | 2.1127 | 0.03001 | 1.401%
125 | BODHEI | BODHEI | - | - | - | - | [8 empty] | 5.8844 | 5.9533 | -0.06886 | -1.17% | 5.841 | 5.672 | 0.16896 | 2.893% | 11.7254 | 11.6253 | 0.1001 | 0.8537%
| PDP, PARADEEP | [5 empty] | 46.9574 | 44.4338 | 2.5236 | 5.374% | 31.8025 | 30.5984 | 1.2041 | 3.786% | 38.8606 | 37.4663 | 1.3943 | 3.588% | 37.7845 | 36.719 | 1.0655 | 2.82% | 155.405 | 149.2175 | 6.1875 | 3.982%
PARADEEP CIRCLE | [6 empty] | 178.4987 | 170.0803 | 8.4184 | 4.716% | 154.5002 | 148.8416 | 5.6586 | 3.663% | 152.799 | 146.2373 | 6.5617 | 4.294% | 154.4544 | 149.5613 | 4.8931 | 3.168% | 640.2524 | 614.7206 | 25.5318 | 3.98%
CESU | [6 empty] | 965.1028 | 928.1651 | 36.9377 | 3.827% | 1155.6238 | 1108.8036 | 46.8202 | 4.052% | 1053.8358 | 1010.8937 | 42.9421 | 4.075% | 1037.7154 | 998.2076 | 39.5078 | 3.807% | 3566.958 | 3426.2432 | 140.7148 | 3.945%
Note on A63: Author: 8 GRID INCOMER
Note on C64: Author: 8 GRID INCOMER

## Annexure-J4
Annexure-J4
33 KV FEEDER AUDITED WITH MAIN INCOMER AT 33KV/11 KV PRIMARY DISTRIBUTION S/S- FY 18-19
SL NO | NAME OF THE GRID | NAME OF THE 33 KV FEEDER | LENGTH (KM) | CONDUCTOR SIZE(SQ MM) | PEAK CURRENT (AMP) | CONNECTED LOAD (KVA) | Total INPUT in MU (A= 33KV Feeder Consumption+Bus Coupler ) | Total (33KV Incomer +33KV consumer+11KV Feeders* ) Consumption in MU (B) | LOSS IN MU (C=A-B) | % LOSS (D=C/A*100) | Total INPUT in MU (A= 33KV Feeder Consumption+Bus Coupler ) | Total (33KV Incomer +33KV consumer+11KV Feeders* ) Consumption in MU (B) | LOSS IN MU (C=A-B) | % LOSS (D=C/A*100) | Total INPUT in MU (A= 33KV Feeder Consumption+Bus Coupler ) | Total (33KV Incomer +33KV consumer+11KV Feeders* ) Consumption in MU (B) | LOSS IN MU (C=A-B) | % LOSS (D=C/A*100) | Total INPUT in MU (A= 33KV Feeder Consumption+Bus Coupler ) | Total (33KV Incomer +33KV consumer+11KV Feeders* ) Consumption in MU (B) | LOSS IN MU (C=A-B) | % LOSS (D=C/A*100) | INPUT MU (A) | OUTPUT MU (B) | LOSS IN MU (C=A-B) | % LOSS (D=(C/A) *100)
1 | MANCHESWAR | BBSR-3 | 6.5 | 232 | 280 | 40500 | 25.2727 | 24.8134 | 0.45922 | 1.817% | 23.4696 | 21.9682 | 1.5014 | 6.397% | 17.3322 | 16.4835 | 0.84872 | 4.897% | 16.2894 | 15.2083 | 1.0811 | 6.637% | 82.3639 | 78.4734 | 3.8904 | 4.723%
2 | CHANDAKA | UNIT 8 FDR-1 | 17 | 232 | 400 | 17500 |  |  |  |  | 7.632 | 7.5455 | 0.0865 | 1.133% | 18.648 | 18.5604 | 0.0876 | 0.4698% | 19.776 | 19.5702 | 0.20584 | 1.041% | 46.056 | 45.6761 | 0.37994 | 0.825%
3 | CHANDAKA | UNIT 8 FDR-2 | 17 | 232 | 400 | 62500 |  |  |  |  | 3.576 | 3.5741 | 0.0019 | 0.05313% |  |  |  |  | 4.536 | 4.53 | 0.006 | 0.1323% | 8.112 | 8.1041 | 0.0079 | 0.09739%
4 | MANCHESWAR | BBSR-1 | 8.5 | 232 | 545 | - | 33.9904 | 33.7816 | 0.20877 | 0.6142% | 31.5008 | 30.5648 | 0.93602 | 2.971% | 25.008 | 25.6569 | -0.64895 | -2.595% |  |  |  |  | 90.4992 | 90.0034 | 0.49584 | 0.5479%
5 | RANASINGHPUR | ASSOTECH | 6 | 100 | 250 | 20500 | 0.4036 | 0.3792 | 0.0244 | 6.046% | [12 empty] | 0.4036 | 0.3792 | 0.0244 | 6.046%
6 | RANASINGHPUR | BIPUL | 8 | 232 | 250 | 20500 |  |  |  |  | 11.7365 | 10.5856 | 1.151 | 9.807% | [8 empty] | 11.7365 | 10.5856 | 1.151 | 9.807%
7 | RANASINGHPUR | RANSINGHPUR | - | - | - | - |  |  |  |  | 1.1184 | 1.1219 | -0.0035 | -0.3129% | [8 empty] | 1.1184 | 1.1219 | -0.0035 | -0.3129%
8 | CHANDAKA | XAVIER | 9.5 | 232 | 400 | 41000 |  |  |  |  | 32.1117 | 31.2921 | 0.81963 | 2.552% | 26.2306 | 25.8944 | 0.33623 | 1.282% | 23.5466 | 23.5023 | 0.044237 | 0.1879% | 81.8889 | 80.6888 | 1.2001 | 1.466%
9 | CHANDAKA | SJ | 20 | 100 | 40 | 5000
10 | CHANDAKA | NAYAPALLI | 11 | 232 | 500 | 30000 | 24.689 | 23.3905 | 1.2985 | 5.26% | 23.1798 | 21.5983 | 1.5815 | 6.823% | 15.3866 | 15.018 | 0.36864 | 2.396% | 12.13 | 11.5914 | 0.5386 | 4.44% | 75.3855 | 71.5982 | 3.7873 | 5.024%
11 | CHANDAKA | TCS | 3 | 300 | 220 | 1000 | 1.248 | 1.278 | -0.03 | -2.404% | 1.7544 | 1.764 | -0.0096 | -0.5472% | 1.5228 | 1.542 | -0.0192 | -1.261% | 1.5246 | 1.55 | -0.0254 | -1.666% | 6.0498 | 6.134 | -0.0842 | -1.392%
12 | CHANDAKA | KIIT | - | - | - | - | 4.74 | 4.812 | -0.072 | -1.519% | 10.2864 | 10.296 | -0.0096 | -0.09333% |  |  |  |  | 7.5174 | 7.4003 | 0.1171 | 1.558% | 22.5438 | 22.5083 | 0.0355 | 0.1575%
13 | KHURDA | KHURDA | 0.15 | 148 | 180 | 16000 |  |  |  |  | 15.303 | 15.412 | -0.109 | -0.7123% | 12.442 | 12.508 | -0.066 | -0.53% | 12.058 | 12.172 | -0.114 | -0.9454% | 39.803 | 40.092 | -0.289 | -0.7261%
14 | KHURDA | TANGI | 42 | 100 | 224 | 26050 | 16.932 | 16.0736 | 0.85841 | 5.07% | 24.749 | 24.4064 | 0.34262 | 1.384% | 20.283 | 19.988 | 0.29496 | 1.454% | 20.201 | 18.8214 | 1.3796 | 6.829% | 82.165 | 79.2895 | 2.8756 | 3.5%
15 | ARGUL | NISER-1 | 5 | 400 | 40 | 1500 |  |  |  |  | 4.981 | 4.9755 | 0.005506 | 0.1105% | 4.343 | 4.3574 | -0.014372 | -0.3309% | 4.967 | 4.8686 | 0.098416 | 1.981% | 14.291 | 14.2015 | 0.08955 | 0.6266%
16 | ARGUL | NISER-2 | 5 | 400 | 40 | 1500
17 | ARGUL | IIT-1 & 2 | 0.7 | 100 | 20 | 250
18 | ARGUL | ICFMD | - | - | - | -
19 | CUTTACK | JS PUR Rural | 12.4 | 100 | 296 | 16300 | 20.502 | 19.764 | 0.738 | 3.6% | 19.2336 | 18.516 | 0.7176 | 3.731% | 15.9624 | 15.612 | 0.3504 | 2.195% | 15.0576 | 14.712 | 0.3456 | 2.295% | 70.7556 | 68.604 | 2.1516 | 3.041%
20 | CUTTACK | CHAULIAGANJ-1 | 7.2 | 100 | 152 | 25000 | 9.8292 | 9.554 | 0.2752 | 2.8% | 24.9625 | 24.242 | 0.72048 | 2.886% | 16.582 | 15.882 | 0.69996 | 4.221% | 10.794 | 9.666 | 1.128 | 10.45% | 62.1676 | 59.344 | 2.8236 | 4.542%
21 | CUTTACK | CHAULIAGANJ-2 | 6.5 | 100 | 112 | 16000
22 | CHANDIKHOLE | BADACHANA | 17 | 100 | 279 | 24450 | 21.093 | 21.072 | 0.02096 | 0.09937% | 22.9766 | 22.38 | 0.59664 | 2.597% | 21.4522 | 20.028 | 1.4242 | 6.639% | 20.5952 | 21.456 | -0.86076 | -4.179% | 86.117 | 84.936 | 1.181 | 1.371%
23 | CHOUDWAR | CHOUDWAR | 0.7 | 100 | 190 | 16000 | 15.2513 | 15.37 | -0.11872 | -0.7784% | 15.1171 | 15.3248 | -0.20772 | -1.374% | 12.5035 | 12.5407 | -0.0372 | -0.2975% | 11.8722 | 12.1304 | -0.25824 | -2.175% | 54.7441 | 55.366 | -0.62188 | -1.136%
24 | CHOUDWAR | TANGI | 5.5 | 80 | 140 | 21000 | 17.2507 | 16.7582 | 0.49257 | 2.855% | 18.2245 | 17.2992 | 0.92532 | 5.077% | 16.5116 | 15.4994 | 1.0123 | 6.131% | 18.0419 | 17.3152 | 0.7266 | 4.027% | 70.0288 | 66.8719 | 3.1568 | 4.508%
25 | CHOUDWAR | ATHAGARH | 4.7 | 148 | 214 | 18150 | 14.639 | 13.6769 | 0.96212 | 6.572% | 23.052 | 23.349 | -0.297 | -1.288% | 22.669 | 21.7127 | 0.95632 | 4.219% | 23.103 | 23.3394 | -0.2364 | -1.023% | 83.463 | 82.078 | 1.385 | 1.659%
26 | GUNDICHAPADA | DHENKANAL TOWN | 13 | 100 | 200 | 24150 | 25.0833 | 23.9972 | 1.0861 | 4.33% | 23.3445 | 23.1588 | 0.18568 | 0.7954% | 13.6802 | 13.5272 | 0.15302 | 1.119% | 11.7316 | 11.4868 | 0.2448 | 2.087% | 73.8396 | 72.17 | 1.6696 | 2.261%
27 | BOINDA | BOINDA | - | - | - | - | 5.756 | 5.5616 | 0.19438 | 3.377% | 6.046 | 5.837 | 0.209 | 3.457% | 5.906 | 5.689 | 0.217 | 3.674% | 5.916 | 5.826 | 0.09 | 1.521% | 23.624 | 22.9136 | 0.71038 | 3.007%
28 | KENDRAPRA | KENDRAPRA | 6.5 | 100 | 220 | 29150 | 18.1779 | 18.3324 | -0.15448 | -0.8498% | 18.4358 | 18.089 | 0.34681 | 1.881% | 13.8114 | 13.2973 | 0.51408 | 3.722% | 12.8648 | 12.3857 | 0.47912 | 3.724% | 63.29 | 62.1045 | 1.1855 | 1.873%
29 | KENDRAPRA | LUNA | 18 | 100 | 230 | 21300 | 3.4543 | 3.4122 | 0.04212 | 1.219% | 3.4484 | 3.4661 | -0.01777 | -0.5153% | 2.6192 | 2.5726 | 0.04664 | 1.781% | 2.7738 | 2.8582 | -0.0844 | -3.043% | 12.2957 | 12.3092 | -0.01341 | -0.1091%
30 | JAGATSINGHPUR | TIRTOL | 22 | 100 | 180 | 15000 | 16.0736 | 15.737 | 0.33664 | 2.094% | 15.3902 | 15.046 | 0.3442 | 2.236% | 11.7883 | 11.682 | 0.10632 | 0.9019% | 11.3936 | 11.1812 | 0.21244 | 1.865% | 54.6458 | 53.6462 | 0.9996 | 1.829%
31 | JAGATSINGHPUR | JAGATSINHPUR | 5 | 80 | 240 | 23650 | 12.972 | 12.5797 | 0.39226 | 3.024% | 11.79 | 11.7987 | -0.00872 | -0.07396% | 9.4488 | 9.564 | -0.1152 | -1.219% | 8.92 | 8.9528 | -0.0328 | -0.3677% | 43.1308 | 42.8953 | 0.23554 | 0.5461%
32 | JAGATSINGHPUR | BALIKUDA | - | - | - | - | [8 empty] | 8.996 | 8.658 | 0.338 | 3.757% | 11.7 | 11.538 | 0.162 | 1.385% | 20.696 | 20.196 | 0.5 | 2.416%
33 KV FEEDER AUDITED WITH MAIN INCOMER (A) | [6 empty] | 965.1028 | 928.1651 | 36.9377 | 3.827% | 1155.6238 | 1108.8036 | 46.8202 | 4.052% | 1053.8358 | 1010.8937 | 42.9421 | 4.075% | 1037.7154 | 998.2076 | 39.5078 | 3.807% | 1281.2147 | 1252.2904 | 28.9243 | 2.258%
TOTAL FEEDER AUDITED RESULTS (B) | [22 empty] | 3566.958 | 3426.2432 | 140.7148 | 3.945%
FEEDER AUDITED INCLUDING THE TRF LOSS (C=B-A) | [22 empty] | 2285.7433 | 2173.9528 | 111.7905 | 4.891%

## Annexure-J5
Annexure-J5

## Annexure-J6
Annexure-J6
TECHNICAL LOSS CALCULATION OF 33 KV FEEDERS IN CESU
SL NO. | DIVISION NAME | NAME OF THE GRID | GRID CODE | 33KV FEEDER | 33KV FDR CODE | LENGTH OF FEEDER (KM) | CONDUCTOR SIZE (MM2) | PEAK CURRENT (AMP) | CONNECTED LOAD (KVA) | RESISTANCE | UNIT ADVANCE IN MU | DF | LF | LLF | TECHNICAL LOSS (Formula-1) in MU | %AGE LOSS | TECHNICAL LOSS ( Formula-2) in MU | %AGE LOSS
1 | BCDD-02, BBSR | MANCHESWAR | 17001 | FDR-1 | 17001401 | 8.5 | 232 | 545 | 26000 | 0.1683 | 11.6576 | 0.83467 | 0.6115 | 0.42145 | 0.38681 | 3.318% | 0.39216 | 3.364%
2 | BCDD-01, BBSR | MANCHESWAR | 17001 | FDR-2 | 17001402 | 10.6 | 232 | 400 | 36.5 | 0.1683 | 6.8008 | 0.0015965 | 0.48606 | 0.28621 | 0.17646 | 2.595% | 0.1789 | 2.631%
3 | BCDD-01, BBSR | MANCHESWAR | 17001 | FDR-3 | 17001403 | 6.5 | 232 | 470 | 40.5 | 0.1683 | 8.7891 | 0.0015076 | 0.53461 | 0.33556 | 0.17515 | 1.993% | 0.17758 | 2.02%
4 | BED, BBSR | MANCHESWAR | 17001 | FDR-4 | 17001404 | 8.5 | 232 | 240 | 48500 | 0.1683 | 7.17 | 3.5356 | 0.85407 | 0.75437 | 0.13426 | 1.873% | 0.13612 | 1.898%
5 | BED, BBSR | MANCHESWAR | 17001 | FDR-5 | 17001405 | 8.5 | 232 | 240 | 15000 | 0.1683 | 6.44 | 1.0935 | 0.76712 | 0.6242 | 0.1111 | 1.725% | 0.11263 | 1.749%
6 | BED, BBSR | MANCHESWAR | 17001 | FDR-6 | 17001406 | 8.5 | 232 | 240 | 19500 | 0.1683 | 6.6294 | 1.4215 | 0.78968 | 0.65681 | 0.1169 | 1.763% | 0.11852 | 1.788%
7 | BED, BBSR | MANCHESWAR | 17001 | FDR-7 | 17001407 | 17 | 100 | 160 | 25000 | 0.3878 | 3.34 | 2.7337 | 0.59678 | 0.40427 | 0.14737 | 4.412% | 0.14941 | 4.473%
8 | BCDD-02, BBSR | MANCHESWAR | 17001 | FDR-8(RAILWAY) | 17001408 | 3 | 100 | 25 | 750 | 0.3878 | 0.45747 | 0.52488 | 0.52313 | 0.32356 | 0.00050818 | 0.1111% | 0.00051521 | 0.1126%
9 | BCDD-02, BBSR | MANCHESWAR | 17001 | FDR-9(RAILWAY) | 17001409 | 3 | 100 | 25 | 750 | 0.3878 | 0.45747 | 0.52488 | 0.52313 | 0.32356 | 0.00050818 | 0.1111% | 0.00051521 | 0.1126%
10 | BCDD-01, BBSR | CHANDAKA | 17002 | UNIT-8 FDR-1 | 17002401 | 17 | 232 | 400 | 30 | 0.1683 | 7.46 | 0.0013122 | 0.53317 | 0.33405 | 0.33031 | 4.428% | 0.33488 | 4.489%
11 | BCDD-01, BBSR | CHANDAKA | 17002 | UNIT-8 FDR-2 (RAJBHABAN) | 17002402 | 17 | 232 | 320 | 25 | 0.1683 | 4.68 | 0.0013669 | 0.4181 | 0.22347 | 0.14142 | 3.022% | 0.14337 | 3.064%
12 | BCDD-02, BBSR | CHANDAKA | 17002 | CHANDRASEKHARPUR-1 | 17002403 | 5.5 | 232 | 360 | 21000 | 0.1683 | 7.905 | 1.0206 | 0.62775 | 0.44081 | 0.11422 | 1.445% | 0.1158 | 1.465%
13 | BCDD-02, BBSR | CHANDAKA | 17002 | CHANDRASEKHARPUR-2 | 17002404 | 4.2 | 232 | 340 | 47000 | 0.1683 | 5.8756 | 2.4186 | 0.49404 | 0.29407 | 0.051903 | 0.8834% | 0.052621 | 0.8956%
14 | BCDD-02, BBSR | CHANDAKA | 17002 | NAYAPALLI | 17002405 | 11 | 232 | 500 | 30000 | 0.1683 | 6.2394 | 1.0498 | 0.35675 | 0.17316 | 0.17311 | 2.775% | 0.17551 | 2.813%
15 | BCDD-02, BBSR | CHANDAKA | 17002 | XAVIER | 17002406 | 9.5 | 232 | 400 | 41000 | 0.1683 | 8.598 | 1.7933 | 0.6145 | 0.42499 | 0.23483 | 2.731% | 0.23808 | 2.769%
16 | BCDD-02, BBSR | CHANDAKA | 17002 | BARANGA | 17002407 | 10 | 80 | 170 | 15000 | 0.4862 | 4.185 | 1.5438 | 0.70377 | 0.53699 | 0.16298 | 3.894% | 0.16523 | 3.948%
17 | BCDD-02, BBSR | CHANDAKA | 17002 | NARAJ | 17002408 | 20 | 100 | 40 | 5000 | 0.3878 | 1.7372 | 2.187 | 1.2416 | 1.4815 | 0.039712 | 2.286% | 0.040261 | 2.318%
18 | BCDD-02, BBSR | CHANDAKA | 17002 | TCS | 17002409 | 3 | 300 | 220 | 1000 | 0.1299 | 0.7074 | 0.079527 | 0.091924 | 0.025145 | 0.0010244 | 0.1448% | 0.0010386 | 0.1468%
19 | BCDD-02, BBSR | CHANDAKA | 17002 | SJ DEVELOPER | 17002411 | 20 | 100 | 40 | 5000 | 0.3878 | 3.6606 | 2.187 | 2.6162 | 5.9991 | 0.1608 | 4.393% | 0.16303 | 4.454%
20 | BCDD-02, BBSR | RANASINGHPUR | 17003 | NAYAPALLI | 17003401 | 14 | 232 | 163 | 16000 | 0.1683 | 7.85 | 1.7174 | 1.3768 | 1.7918 | 0.24229 | 3.086% | 0.24564 | 3.129%
21 | BCDD-02, BBSR | RANASINGHPUR | 17003 | BARAMUNDA | 17003402 | 10 | 232 | 200 | 16000 | 0.1683 | 10.9288 | 1.3997 | 1.5622 | 2.2647 | 0.32932 | 3.013% | 0.33387 | 3.055%
22 | BED, BBSR | RANASINGHPUR | 17003 | BHIMATANGI - I | 17003403 | 5.5 | 232 | 360 | 29000 | 0.1683 | 7.9308 | 1.4094 | 0.6298 | 0.44328 | 0.11486 | 1.448% | 0.11645 | 1.468%
23 | BED, BBSR | RANASINGHPUR | 17003 | BHIMATANGI - II / BARAGARH | 17003404 | 12.5 | 232 | 410 | 45500 | 0.1683 | 6.379 | 1.9416 | 0.44479 | 0.24723 | 0.18885 | 2.96% | 0.19146 | 3.001%
24 | BCDD-02, BBSR | RANASINGHPUR | 17003 | AIIMS NO-I | 17003405 | 0.5 | 300 | 10 | 2500 | 0.1299 | 0.064 | 4.374 | 0.18296 | 0.063374 | 8.8908e-07 | 0.001389% | 9.0138e-07 | 0.001408%
25 | BCDD-02, BBSR | RANASINGHPUR | 17003 | VIPUL | 17003409 | 8 | 232 | 250 | 20500 | 0.1683 | 5.483 | 1.4347 | 0.627 | 0.4399 | 0.079958 | 1.458% | 0.081064 | 1.478%
26 | NED, NIMAPARA | KESURA | 17004 | UTTARA | 17004401 | 10.5 | 100 | 360 | 29450 | 0.3878 | 7.279 | 1.4313 | 0.57803 | 0.38291 | 0.43646 | 5.996% | 0.4425 | 6.079%
27 | BED, BBSR | KESURA | 17004 | KESURA | 17004402 | 1 | 100 | 32 | 3150 | 0.3878 | 0.91 | 1.7223 | 0.81298 | 0.69134 | 0.000593 | 0.06516% | 0.0006012 | 0.06607%
28 | BED, BBSR | KESURA | 17004 | LAXMISAGAR (FDR-I) | 17004403 | 5 | 148 | 265 | 28500 | 0.262 | 0.01644 | 1.8816 | 0.0017735 | 0.00035723 | 7.0984e-05 | 0.4318% | 7.1966e-05 | 0.4377%
29 | BED, BBSR | KESURA | 17004 | RASULGARH(FDR-II) | 17004404 | 5 | 148 | 320 | 20000 | 0.262 | 0.96468 | 1.0935 | 0.086183 | 0.023179 | 0.006716 | 0.6962% | 0.0068089 | 0.7058%
30 | NED, NIMAPARA | NIMAPADA / DIGHAL | 17005 | NIMAPADA | 17005401 | 5 | 100 | 260 | 31150 | 0.3878 | 4.0056 | 2.0962 | 0.44043 | 0.24327 | 0.068877 | 1.72% | 0.069829 | 1.743%
31 | NED, NIMAPARA | NIMAPADA / DIGHAL | 17005 | KAKATPUR | 17005402 | 30 | 100 | 200 | 22900 | 0.3878 | 4.5196 | 2.0033 | 0.64604 | 0.4631 | 0.4655 | 10.3% | 0.47193 | 10.44%
32 | NED, NIMAPARA | NIMAPADA / DIGHAL | 17005 | KONARK | 17005403 | 25 | 100 | 240 | 11350 | 0.3878 | 0.17028 | 0.82741 | 0.020283 | 0.0043858 | 0.0052902 | 3.107% | 0.0053634 | 3.15%
33 | NED, NIMAPARA | KONARK | 17006 | KONARK | 17006401 | 0.25 | 100 | 92 | 8150 | 0.3878 | 2.4209 | 1.5499 | 0.75227 | 0.60319 | 0.0010691 | 0.04416% | 0.0010839 | 0.04477%
34 | NED, NIMAPARA | KONARK | 17006 | GOP | 17006402 | 32 | 100 | 115 | 14750 | 0.3878 | 3.5433 | 2.244 | 0.88084 | 0.79687 | 0.28248 | 7.972% | 0.28639 | 8.083%
35 | KHD,KHURDA | KHURDA | 17007 | BANKI | 17007401 | 18 | 232 | 110 | 19850 | 0.1683 | 2.3257 | 3.1572 | 0.60442 | 0.41315 | 0.032712 | 1.407% | 0.033164 | 1.426%
36 | KHD,KHURDA | KHURDA | 17007 | KHURDA | 17007404 | 0.12 | 100 | 170 | 20.5 | 0.3878 | 5.1833 | 0.0021098 | 0.87166 | 0.78216 | 0.0022722 | 0.04384% | 0.0023036 | 0.04444%
37 | KHD,KHURDA | KHURDA | 17007 | RAILWAY | 17007406 | 17.66 | 148 | 360 | 58100 | 0.262 | 7.8903 | 2.8237 | 0.62658 | 0.4394 | 0.56913 | 7.213% | 0.57701 | 7.313%
38 | KHD,KHURDA | KHURDA | 17007 | JATANI | 17007407 | 22.5 | 100 | 124 | 22900 | 0.3878 | 3.289 | 3.2311 | 0.75828 | 0.61165 | 0.17725 | 5.389% | 0.1797 | 5.464%
39 | KHD,KHURDA | MEDHASALA | 17008 | JATANI-MENDHASAL | 17008401 | 17 | 100 | 40 | 13300 | 0.3878 | 0.94 | 5.8174 | 0.67182 | 0.49544 | 0.011288 | 1.201% | 0.011444 | 1.217%
40 | KHD,KHURDA | ARGUL | 17009 | NISER 1 | 17009402 | 4.131 | 400 | 22 | 10000 | 0.0736 | 3.1125 | 7.9527 | 4.0446 | 13.8958 | 0.0044169 | 0.1419% | 0.004478 | 0.1439%
41 | KHD,KHURDA | ARGUL | 17009 | NISER 2 | 17009403 | 4.131 | 400 | 13 | 5000 | 0.0736 | 3.1125 | 6.7292 | 6.8447 | 38.8486 | 0.0043117 | 0.1385% | 0.0043713 | 0.1404%
42 | NYD, NAYAGARH | NAYAGARH | 17011 | RANAPUR | 17011401 | 34 | 55 | 116 | 23150 | 0.7104 | 1.9116 | 3.4917 | 0.47111 | 0.27178 | 0.1908 | 9.981% | 0.19344 | 10.12%
43 | NYD, NAYAGARH | NAYAGARH | 17011 | NAYAGARH | 17011404 | 8 | 232 | 200 | 28195 | 0.1683 | 4.6842 | 2.4665 | 0.66956 | 0.49256 | 0.057299 | 1.223% | 0.058092 | 1.24%
44 | NYD, NAYAGARH | NAYAGARH | 17011 | DASPALLA | 17011405 | 51.3 | 232 | 140 | 51845 | 0.1683 | 1.8598 | 6.4791 | 0.37977 | 0.19133 | 0.069935 | 3.76% | 0.070903 | 3.812%
45 | NYD, NAYAGARH | NAYAGARH | 17011 | ODAGAON | 17011406 | 30 | 80 | 235 | 54542 | 0.4862 | 2.9856 | 4.0607 | 0.3632 | 0.17817 | 0.31001 | 10.38% | 0.31429 | 10.53%
46 | PED, PURI | PURI | 17012 | SAKHIGOPAL | 17012401 | 22 | 148 | 320 | 28150 | 0.262 | 8.219 | 1.5391 | 0.73427 | 0.57818 | 0.73712 | 8.968% | 0.74732 | 9.093%
47 | PED, PURI | PURI | 17012 | SRIRAMNAGAR-I | 17012403 | 1.7 | 148 | 122 | 16000 | 0.262 | 0.2532 | 2.2946 | 0.059332 | 0.014683 | 0.00021025 | 0.08304% | 0.00021315 | 0.08418%
48 | PED, PURI | PURI | 17012 | SRIRAMNAGAR-II | 17012404 | 1.7 | 148 | 122 | 16000 | 0.262 | 0.4128 | 2.2946 | 0.096731 | 0.026832 | 0.00038421 | 0.09308% | 0.00038953 | 0.09436%
49 | PED, PURI | PURI | 17012 | PURI-I | 17012405 | 4.5 | 148 | 390 | 46000 | 0.262 | 4.17 | 2.0636 | 0.30567 | 0.13588 | 0.052634 | 1.262% | 0.053362 | 1.28%
50 | PED, PURI | PURI | 17012 | PURI-II | 17012406 | 3.5 | 148 | 437 | 62600 | 0.262 | 4.878 | 2.5063 | 0.31911 | 0.14529 | 0.054957 | 1.127% | 0.055717 | 1.142%
51 | BAED,BALUGAON | BALUGAON | 17015 | BALUGAON | 17015401 | 8 | 100 | 180 | 21000 | 0.3878 | 4.664 | 2.0412 | 0.74075 | 0.58712 | 0.12747 | 2.733% | 0.12924 | 2.771%
52 | BAED,BALUGAON | BALUGAON | 17015 | TANGI | 17015402 | 30 | 100 | 360 | 28150 | 0.3878 | 1.9949 | 1.3681 | 0.15842 | 0.05176 | 0.16857 | 8.45% | 0.1709 | 8.567%
53 | BAED,BALUGAON | BALUGAON | 17015 | CHILIKA (DEDICATED) | 17015403 | 1.5 | 55 | 16 | 1000 | 0.7104 | 0.41333 | 1.0935 | 0.73853 | 0.58405 | 0.00034414 | 0.08326% | 0.0003489 | 0.08441%
54 | BAED,BALUGAON | CHANDAPUR | 17016 | CHANDPUR | 17016401 | 1.8 | 100 | 25 | 5000 | 0.3878 | 0.4732 | 3.4992 | 0.54112 | 0.34247 | 0.00032273 | 0.0682% | 0.00032719 | 0.06914%
55 | BAED,BALUGAON | CHANDAPUR | 17016 | TANGI-CHANDPUR | 17016402 | 5.5 | 80 | 140 | 21000 | 0.4862 | 2.8624 | 2.6244 | 0.58451 | 0.39022 | 0.044177 | 1.543% | 0.044788 | 1.565%
56 | CED, CUTTACK | CHANDIKHOLE | 17017 | BADACHANA | 17017401 | 15 | 100 | 290 | 31805 | 0.3878 | 7.7389 | 1.9188 | 0.7629 | 0.61819 | 0.65324 | 8.441% | 0.66228 | 8.558%
57 | CED, CUTTACK | CHOUDWAR | 17018 | BAJRANG BALLY/CDR | 17018401 | 0.7 | 100 | 200 | 24948 | 0.3878 | 4.9892 | 2.1824 | 0.71316 | 0.5495 | 0.012888 | 0.2583% | 0.013066 | 0.2619%
58 | CED, CUTTACK | CHOUDWAR | 17018 | ATHAGARH | 17018403 | 4.7 | 148 | 230 | 14615 | 0.262 | 7.2023 | 1.1118 | 0.89522 | 0.82019 | 0.1154 | 1.602% | 0.117 | 1.624%
59 | CDD-2, CUTTACK | CHOUDWAR | 17018 | JAGATPUR | 17018405 | 6.6 | 100 | 350 | 69000 | 0.3878 | 7.4231 | 3.4492 | 0.60632 | 0.41536 | 0.2813 | 3.79% | 0.28519 | 3.842%
60 | CED, CUTTACK | CHOUDWAR | 17018 | IDCO | 17018406 | 16 | 80 | 0.5 | 160 | 0.4862 | 0.1596 | 5.5987 | 9.1254 | 68.4427 | 0.00028751 | 0.1801% | 0.00029149 | 0.1826%
61 | CDD-1, CUTTACK | BIDANASI | 17019 | TULASIPUR 1 | 17019401 | 18 | 232 | 650 | 60800 | 0.1683 | 8.0878 | 1.6365 | 0.35571 | 0.17237 | 0.47654 | 5.892% | 0.48313 | 5.974%
62 | CDD-1, CUTTACK | BIDANASI | 17019 | TULASIPUR 2 | 17019402 | 18 | 232 | 550 | 55800 | 0.1683 | 6.156 | 1.775 | 0.31998 | 0.14591 | 0.28881 | 4.691% | 0.2928 | 4.756%
63 | CDD-1, CUTTACK | BIDANASI | 17019 | SECTOR 6 | 17019403 | 7 | 100 | 320 | 26000 | 0.3878 | 3.2786 | 1.4215 | 0.2929 | 0.12721 | 0.076382 | 2.33% | 0.077439 | 2.362%
64 | CDD-2, CUTTACK | BIDANASI | 17019 | BADAMBADI | 17019404 | 4.2 | 100 | 320 | 26000 | 0.3878 | 5.4912 | 1.4215 | 0.49057 | 0.29064 | 0.10471 | 1.907% | 0.10615 | 1.933%
65 | CDD-1, CUTTACK | BIDANASI | 17019 | SISHUBHABAN | 17019405 | 7 | 100 | 320 | 51300 | 0.3878 | 7.4968 | 2.8048 | 0.66975 | 0.4928 | 0.29589 | 3.947% | 0.29998 | 4.001%
66 | CDD-1, CUTTACK | BIDANASI | 17019 | IOCL-I | 17019406 | 9 | 400 | 40 | 2500 | 0.0736 | 0.584 | 1.0935 | 0.41739 | 0.22285 | 0.00051015 | 0.08736% | 0.00051721 | 0.08856%
67 | CDD-1, CUTTACK | BIDANASI | 17019 | IOCL-II | 17019407 | 9 | 400 | 40 | 2500 | 0.0736 | 0.584 | 1.0935 | 0.41739 | 0.22285 | 0.00051015 | 0.08736% | 0.00051721 | 0.08856%
68 | CED, CUTTACK | CUTTACK | 17020 | BALIKUDA | 17020401 | 6 | 55 | 140 | 24430.4 | 0.7104 | 3.8023 | 3.0531 | 0.77643 | 0.63756 | 0.11505 | 3.026% | 0.11664 | 3.068%
69 | CDD-2, CUTTACK | CUTTACK | 17020 | BENTKAR | 17020402 | 8 | 80 | 80 | 8500 | 0.4862 | 1.3063 | 1.8589 | 0.46681 | 0.26769 | 0.014394 | 1.102% | 0.014593 | 1.117%
70 | CDD-2, CUTTACK | CUTTACK | 17020 | JSPUR RURAL | 17020403 | 12.4 | 100 | 350 | 19000 | 0.3878 | 4.3652 | 0.94978 | 0.35655 | 0.17301 | 0.22014 | 5.043% | 0.22319 | 5.113%
71 | CDD-2, CUTTACK | CUTTACK | 17020 | CRRI-1 | 17020404 | 4 | 232 | 190 | 9500 | 0.1683 | 1.1712 | 0.8748 | 0.17622 | 0.060088 | 0.0031542 | 0.2693% | 0.0031978 | 0.273%
72 | CDD-2, CUTTACK | CUTTACK | 17020 | CRRI-2 | 17020405 | 4 | 232 | 30 | 1700 | 0.1683 | 1.9567 | 0.99144 | 1.8646 | 3.1543 | 0.004128 | 0.211% | 0.0041851 | 0.2139%
73 | CDD-2, CUTTACK | CUTTACK | 17020 | CHAULIAGANJ I | 17020406 | 7.2 | 100 | 300 | 28500 | 0.3878 | 4.9976 | 1.6621 | 0.47624 | 0.27669 | 0.15019 | 3.005% | 0.15227 | 3.047%
74 | CDD-2, CUTTACK | CUTTACK | 17020 | CHAULIAGANJ II | 17020407 | 6.5 | 400 | 150 | 13000 | 0.0736 | 4.1227 | 1.5163 | 0.78574 | 0.65106 | 0.015137 | 0.3672% | 0.015347 | 0.3722%
75 | AED, ATHAGARH | NUAPATNA | 17023 | NARSINGHPUR | 17023401 | 41 | 80 | 220 | 35206 | 0.4862 | 0.2652 | 2.7998 | 0.034462 | 0.0078424 | 0.016344 | 6.163% | 0.01657 | 6.248%
76 | DED, DHENKANAL | GUNDICHAPADA, DKL | 17024 | DKL TOWN | 17024401 | 13 | 100 | 240 | 36718 | 0.3878 | 6.3851 | 2.6767 | 0.76057 | 0.61489 | 0.38568 | 6.04% | 0.39101 | 6.124%
77 | DED, DHENKANAL | GUNDICHAPADA, DKL | 17024 | HINDOL ROAD | 17024403 | 24 | 100 | 132 | 32151 | 0.3878 | 2.9708 | 4.2615 | 0.6434 | 0.45985 | 0.16108 | 5.422% | 0.16331 | 5.497%
78 | DED, DHENKANAL | GUNDICHAPADA, DKL | 17024 | OPL | 17024404 | 6 | 100 | 10 | 1350 | 0.3878 | 0.016467 | 2.362 | 0.047075 | 0.011188 | 5.6229e-06 | 0.03415% | 5.7007e-06 | 0.03462%
79 | DED, DHENKANAL | GUNDICHAPADA, DKL | 17024 | GUNDICHAPADA-2 | 17024405 | 0.1 | 100 | 240 | 24000 | 0.3878 | 7.6053 | 1.7496 | 0.90592 | 0.83774 | 0.004042 | 0.05315% | 0.0040979 | 0.05388%
80 | DED, DHENKANAL | GUNDICHAPADA, DKL | 17024 | DAKHINAKALI | 17024408 | 9 | 100 | 80 | 10644 | 0.3878 | 2.3149 | 2.3278 | 0.82725 | 0.71293 | 0.034398 | 1.486% | 0.034873 | 1.506%
81 | DED, DHENKANAL | KAMAKHYANAGAR | 17025 | KAMAKHYANAGAR | 17025401 | 3 | 55 | 80 | 19668 | 0.7104 | 4.0272 | 4.3014 | 1.4391 | 1.9447 | 0.057294 | 1.423% | 0.058087 | 1.442%
82 | DED, DHENKANAL | KAMAKHYANAGAR | 17025 | KANKADAHADA | 17025402 | 22.5 | 100 | 40 | 5898 | 0.3878 | 0.4374 | 2.5798 | 0.31261 | 0.1407 | 0.004243 | 0.97% | 0.0043016 | 0.9835%
83 | DED, DHENKANAL | KAMAKHYANAGAR | 17025 | SOVAMETAL | 17025403 | 2 | 100 | 145 | 5200 | 0.3878 | 2.0838 | 0.62744 | 0.41085 | 0.21721 | 0.0076507 | 0.3671% | 0.0077565 | 0.3722%
84 | DED, DHENKANAL | KAMAKHYANAGAR | 17025 | MATHAKARGOLA | 17025404 | 19 | 80 | 61 | 16438 | 0.4862 | 2.8434 | 4.7147 | 1.3326 | 1.6871 | 0.12527 | 4.406% | 0.127 | 4.466%
85 | DED, DHENKANAL | KALARANGI | 17026 | TISCO | 17026401 | 5 | 80 | 65 | 5000 | 0.4862 | 1.6519 | 1.3458 | 0.72652 | 0.56757 | 0.012592 | 0.7623% | 0.012766 | 0.7728%
86 | DED, DHENKANAL | KALARANGI | 17026 | OMC | 17026402 | 15 | 80 | 20 | 2346.28 | 0.4862 | 0.55457 | 2.0525 | 0.7927 | 0.66124 | 0.0041666 | 0.7513% | 0.0042242 | 0.7617%
87 | TED,CHAINPAL | CHAINPAL | 17027 | BANARPAL | 17027401 | 6 | 100 | 260 | 24100 | 0.3878 | 6.1306 | 1.6217 | 0.67409 | 0.49834 | 0.16931 | 2.762% | 0.17165 | 2.8%
88 | TED,CHAINPAL | CHAINPAL | 17027 | PARJANG | 17027402 | 19.5 | 100 | 240 | 14500 | 0.3878 | 6.0747 | 1.057 | 0.7236 | 0.5636 | 0.53026 | 8.729% | 0.53759 | 8.85%
89 | TED,CHAINPAL | CHAINPAL | 17027 | RENGALI | 17027403 | 10.07 | 100 | 250 | 30750 | 0.3878 | 2.0213 | 2.152 | 0.23114 | 0.088968 | 0.046903 | 2.32% | 0.047552 | 2.353%
90 | TED,CHAINPAL | CHAINPAL | 17027 | CHAINPAL | 17027406 | 0.8 | 300 | 77 | 12731 | 0.1299 | 2.1157 | 2.8927 | 0.78551 | 0.65073 | 0.00086603 | 0.04093% | 0.00087801 | 0.0415%
91 | TED,CHAINPAL | BARKOTE | 17029 | BARKOTE | 17029401 | 34 | 55 | 50 | 17568 | 0.7104 | 1.3004 | 6.1474 | 0.74352 | 0.59096 | 0.077079 | 5.927% | 0.078145 | 6.009%
92 | ANED, ANGUL | ANGUL | 17030 | RAILWAY | 17030401 | 4.5 | 148 | 4 | 180 | 0.262 | 0.135 | 0.78732 | 0.96485 | 0.93772 | 3.8209e-05 | 0.0283% | 3.8737e-05 | 0.02869%
93 | ANED, ANGUL | ANGUL | 17030 | ANGUL-I | 17030402 | 5 | 232 | 250 | 12600 | 0.1683 | 5.6303 | 0.8818 | 0.64384 | 0.4604 | 0.052302 | 0.9289% | 0.053026 | 0.9418%
94 | ANED, ANGUL | ANGUL | 17030 | M/S GANESH SPONGE | 17030404 | 10.3 | 148 | 15 | 720 | 0.262 | 0.45 | 0.83981 | 0.85765 | 0.75997 | 0.00099672 | 0.2215% | 0.0010105 | 0.2246%
95 | ANED, ANGUL | ANGUL | 17030 | HEMASERPADA | 17030405 | 0.5 | 100 | 160 | 8100 | 0.3878 | 4.984 | 0.88573 | 0.89052 | 0.81253 | 0.0087118 | 0.1748% | 0.0088323 | 0.1772%
96 | ANED, ANGUL | BOINDA | 17031 | BOINDA | 17031402 | 2.5 | 100 | 90 | 4500 | 0.3878 | 1.7893 | 0.8748 | 0.56838 | 0.37212 | 0.006312 | 0.3528% | 0.0063993 | 0.3576%
97 | ANED, ANGUL | RAIRAKHOL | 17032 | BAMUR | 17032401 | 28 | 100 | 90 | 4500 | 0.3878 | 1.7837 | 0.8748 | 0.56658 | 0.37012 | 0.070315 | 3.942% | 0.071288 | 3.997%
98 | KED-01, KENDRAPARA | PATTAMUNDAI | 17033 | AUL | 17033402 | 2.3 | 100 | 100 | 10000 | 0.3878 | 2.0833 | 1.7496 | 0.59558 | 0.40289 | 0.0077621 | 0.3726% | 0.0078695 | 0.3777%
99 | KED-01, KENDRAPARA | PATTAMUNDAI | 17033 | RAJANAGAR | 17033403 | 22 | 100 | 130 | 23150 | 0.3878 | 2.952 | 3.1156 | 0.64917 | 0.46697 | 0.14543 | 4.927% | 0.14744 | 4.995%
100 | KED-01, KENDRAPARA | PATTAMUNDAI | 17033 | GOGUA | 17033404 | 13 | 100 | 80 | 11300 | 0.3878 | 1.733 | 2.4713 | 0.61931 | 0.43069 | 0.030016 | 1.732% | 0.030431 | 1.756%
101 | KED-01, KENDRAPARA | KENDRAPADA | 17034 | KENDRAPARA | 17034401 | 6.5 | 100 | 220 | 29150 | 0.3878 | 3.866 | 2.3182 | 0.50238 | 0.30238 | 0.079685 | 2.061% | 0.080787 | 2.09%
102 | KED-01, KENDRAPARA | KENDRAPADA | 17034 | DANPUR | 17034402 | 18 | 100 | 230 | 21300 | 0.3878 | 3.5784 | 1.6203 | 0.44478 | 0.24722 | 0.19719 | 5.51% | 0.19991 | 5.587%
103 | KED-01, KENDRAPARA | KENDRAPADA | 17034 | INDUPUR | 17034403 | 18 | 80 | 70 | 6300 | 0.4862 | 1.6557 | 1.5746 | 0.6762 | 0.50104 | 0.04641 | 2.803% | 0.047052 | 2.842%
104 | KED-01, KENDRAPARA | KENDRAPADA | 17034 | LUNA | 17034404 | 43.5 | 100 | 320 | 39200 | 0.3878 | 0.7134 | 2.1433 | 0.063734 | 0.015996 | 0.059686 | 8.366% | 0.060512 | 8.482%
105 | KED-01, KENDRAPARA | KENDRAPADA | 17034 | AUL-PATTAMUNDAI | 17034405 | 6 | 55 | 60 | 5000 | 0.7104 | 0.2287 | 1.458 | 0.10897 | 0.031293 | 0.0010372 | 0.4535% | 0.0010515 | 0.4598%
106 | KED-02, MARSAGHAI | MARSHAGHAI | 17035 | LUNA | 17035401 | 26 | 80 | 180 | 32300 | 0.4862 | 4.0784 | 3.1396 | 0.64774 | 0.46521 | 0.41156 | 10.09% | 0.41725 | 10.23%
107 | PDP, PARADEEP | PARADEEP | 17036 | INDUSTRIAL | 17036401 | 5.5 | 100 | 202 | 11545.512 | 0.3878 | 5.9388 | 1 | 0.84049 | 0.73324 | 0.13784 | 2.321% | 0.13975 | 2.353%
108 | PDP, PARADEEP | PARADEEP | 17036 | HPCL | 17036405 | 7.5 | 148 | 40 | 2286.24 | 0.262 | 0.18787 | 1 | 0.13427 | 0.041276 | 0.00028031 | 0.1492% | 0.00028419 | 0.1513%
109 | JED, JAGATSINGHAPUR | JAGATSINGHPUR | 17037 | JAGATSINHPUR | 17037401 | 5 | 80 | 240 | 23650 | 0.4862 | 3.8871 | 1.7241 | 0.46302 | 0.26411 | 0.079882 | 2.055% | 0.080987 | 2.084%
110 | JED, JAGATSINGHAPUR | JAGATSINGHPUR | 17037 | TIRTOL | 17037402 | 22 | 100 | 180 | 15000 | 0.3878 | 4.649 | 1.458 | 0.73838 | 0.58383 | 0.34859 | 7.498% | 0.35342 | 7.602%
111 | JED, JAGATSINGHAPUR | JAGATSINGHPUR | 17037 | NABAPATANA ( MAIN) | 17037403 | 23 | 100 | 85 | 10000 | 0.3878 | 1.449 | 2.0584 | 0.48734 | 0.28747 | 0.040015 | 2.762% | 0.040569 | 2.8%
112 | JED, JAGATSINGHAPUR | JAGATSINGHPUR | 17037 | BALIKUDA ( NEW) | 17037404 | 24 | 148 | 280 | 28150 | 0.262 | 4.5048 | 1.759 | 0.45994 | 0.26123 | 0.27816 | 6.175% | 0.28201 | 6.26%
113 | JED, JAGATSINGHAPUR | JAGATSINGHPUR | 17037 | NAUGAON ( MAIN) | 17037405 | 18.5 | 100 | 75 | 10000 | 0.3878 | 1.8433 | 2.3328 | 0.70263 | 0.53548 | 0.046677 | 2.532% | 0.047322 | 2.567%
114 | AED, ATHAGARH | MANIA | 17038 | RSB | 17038401 | 17 | 80 | 100 | 9800 | 0.4862 | 1.32 | 1.7146 | 0.37736 | 0.1894 | 0.033813 | 2.562% | 0.034281 | 2.597%
115 | DED, DHENKANAL | KHAJURIAKATA | 17040 | HINDOL | 17040402 | 14.8 | 100 | 85 | 13947 | 0.3878 | 1.6151 | 2.8708 | 0.54322 | 0.34471 | 0.030876 | 1.912% | 0.031303 | 1.938%
[10 empty] | SUM= | 421.6591 |  |  |  | 14.0768 | 3.338% | 14.2715 | 3.385%
[8 empty] | 100 | 3.38 | 96.62 | 0.9662
[8 empty] | 100 | 0.69 | 99.31 | 0.9931
[11 empty] | 0.95953 | 4.047%

## Annexure-J7
Annexure-J7
CALCULATION SHEET OF EFFICIENCY OF DISTRIBUTION TRANSFORMER (DTs) AS PER IE STANDARD (IS)
Sl No | Rating of Distribution Transformer | Full load loss at 75º C in Watts | Calculated Loss in KVA at 0.85 pf | % age Efficiency | No of DTs in CESU | KVA * No of DTs in CESU | Calculated Loss in KVA* no of DTs in KVA |  | 96.51%
A | B | C | D=C/(1000*0.85) | E=(1-D/B)*100 | F | G=B*F | H=D*F
1 | 16 KVA 11/0.4 KV | 475 | 0.55882 | 96.51% | 1386 | 22176 | 774.5294 |  | 16
2 | 25 KVA 11/0.4 KV | 685 | 0.80588 | 96.78% | 18428 | 460700 | 14850.8 |  | 25
3 | 50 KVA 11/0.4 KV | 1235 | 1.4529 | 97.09% | 13 | 650 | 18.8882 |  | 50
4 | 63 KVA 11/0.4 KV | 1235 | 1.4529 | 97.69% | 11950 | 752850 | 17362.6471 |  | 63
5 | 100 KVA 11/0.4 KV | 1760 | 2.0706 | 97.93% | 11257 | 1125700 | 23308.6118 |  | 100
6 | 150 KVA 11/0.4 KV | 3000 | 3.5294 | 97.65% | 150 | 22500 | 529.4118 |  | 150
7 | 200 KVA 11/0.4 KV | 3300 | 3.8824 | 98.06% | 262 | 52400 | 1017.1765 |  | 200
8 | 250 KVA 11/0.4 KV | 3700 | 4.3529 | 98.26% | 3665 | 916250 | 15953.5294 |  | 250
9 | 315 KVA 11/0.4 KV | 4600 | 5.4118 | 98.28% | 54 | 17010 | 292.2353 |  | 315
10 | 500 KVA 11/0.4 KV | 6500 | 7.6471 | 98.47% | 1389 | 694500 | 10621.7647 |  | 500
11 | 750 KVA 11/0.4 KV | 7500 | 8.8235 | 98.82% | 59 | 44250 | 520.5882 |  | 750
12 | 1000 KVA 11/0.4 KV | 11000 | 12.9412 | 98.71% | 42 | 42000 | 543.5294 |  | 1000
|  | Average Efficiency in %age |  | 97.93% |  | 4150986 | 85793.7118 | 2.067%
LOSS %

## Annexure-J8
AVERAGE T & D LOSS CALCULATION OF 11KV FEEDERS FOR THE FY 2018-19
SL NO | DIVISION NAME | SL. NO. | 33/11 KV PRIMARY DISTRIBUTION S/S | 33KV/11 KV S/S CODE | 11KV FEEDER NAME | 11KV FEEDER CODE | LENGTH OF FEEDER IN KM |  | CONDUCTOR SIZE IN MM2 | PEAK LOAD CURRENT (AMP) | NO. OF DT | TOTAL DTR CAPACITY (IN KVA) | NO. OF CONSUMERS | AVERAGE T & D LOSS % (FY 18-19) | RESISTANCE AT 60 C (Ω/Km) | AVERAGE UNITS ADVANCED IN FY 18-19 | LF | DF | LLF | TECHNICAL LOSS (MU) | TECHNICAL LOSS (%AGE)
1 | BCDD-01, BBSR | 1 | UNIT-8 | 14011 | CBI | 14011206 | 4.56 | 80 | 80/100 | 250 | 31 | 7138 | 3255 | 9.54% | 0.4862 | 0.794 | 0.032729 | 1.4986 | 0.0074027 | 0.00081448 | 0.8537%
2 | BCDD-01, BBSR | 2 | UNIT-8 | 14011 | RAJ BHAWAN | 14011207 | 2.8 | 80 | 80/100 | 10 | 3 | 1100 | 2 | 0.3846% | 0.4862 | 0.026 | 0.032986 | 5.7737 | 0.0074678 | 8.0722e-07 | 0.02099%
3 | BCDD-01, BBSR | 3 | UNIT-8 | 14011 | MEDICAL( UNIT - V ) | 14011208 | 4.23 | 80 | 80/100 | 180 | 32 | 9725 | 242 | 3.644% | 0.4862 | 0.47333 | 0.017364 | 2.8358 | 0.0037141 | 0.00019651 | 0.5392%
4 | BCDD-01, BBSR | 4 | UNIT-8 | 14011 | OERC | 14011209 | 0.4 | 80 | 80/100 | 200 | 2 | 750 | 147 | 10.98% | 0.4862 | 0.856 | 0.04709 | 0.19683 | 0.011192 | 6.9131e-05 | 0.06295%
5 | BCDD-01, BBSR | 6 | UNIT-8 | 14011 | OUAT | 14011201 | 5.6 | 80 | 80/100 | 220 | 20 | 3368 | 1481 | 7.498% | 0.4862 | 0.758 | 0.029229 | 0.80354 | 0.0065294 | 0.0006832 | 0.9112%
6 | BCDD-01, BBSR | 8 | UNIT-8 | 14011 | G.B.NAGAR | 14011203 | 8.28 | 80 | 80/100 | 185 | 42 | 6373 | 2663 | 9.635% | 0.4862 | 1.0044 | 0.044667 | 1.8081 | 0.010529 | 0.0011519 | 1.196%
7 | BCDD-01, BBSR | 9 | UNIT-8 | 14011 | TEL.BHAWAN | 14011204 | 3 | 80 | 80/100 | 135 | 9 | 975 | 732 | 8.257% | 0.4862 | 0.25533 | 0.052457 | 0.37908 | 0.012693 | 0.00026791 | 0.3245%
8 | BCDD-01, BBSR | 10 | UNIT-8 | 14011 | ASSEMBLY | 14011205 | 2.3 | 80 | 80/100 | 60 | 13 | 5565 | 82 | 2.708% | 0.4862 | 0.18433 | 0.038708 | 4.8683 | 0.0089402 | 2.8577e-05 | 0.1055%
9 | BCDD-01, BBSR | 11 | UNIT-6 | 14012 | UNIT-1 | 14012203 | 4.6 | 80 | 80/100 | 85 | 28 | 4362 | 1388 | 11.71% | 0.4862 | 0.488 | 0.1182 | 2.6936 | 0.034816 | 0.00044671 | 0.3813%
10 | BCDD-01, BBSR | 12 | UNIT-6 | 14012 | MEDICAL | 14012201 | 1.8 | 80 | 80/100 | 20 | 8 | 1850 | 1 | 0.4573% | 0.4862 | 0.08485 | 0.019609 | 4.8551 | 0.0042294 | 1.1756e-06 | 0.02571%
11 | BCDD-01, BBSR | 13 | UNIT-6 | 14012 | FOREST PARK | 14012202 | 7 | 80 | 80/100 | 55 | 35 | 8346 | 950 | 10.82% | 0.4862 | 0.55 | 0.16869 | 7.9648 | 0.056505 | 0.00046191 | 0.427%
12 | BCDD-01, BBSR | 14 | UNIT-6 | 14012 | SPRING TANK | 14012204 | 3.7 | 80 | 80/100 | 60 | 10 | 3150 | 524 | 10.7% | 0.4862 | 0.20867 | 0.15299 | 2.7556 | 0.049322 | 0.00025362 | 0.237%
13 | BCDD-01, BBSR | 16 | UNIT-6 | 14012 | UNIT-6 | 14012206 | 3.55 | 80 | 80/100 | 70 | 19 | 5500 | 599 | 10.55% | 0.4862 | 0.25825 | 0.12928 | 4.1241 | 0.039227 | 0.00026342 | 0.2496%
14 | BCDD-01, BBSR | 17 | AIR PORT | 14215 | PALLASHAPALLI | 14215201 | 4.8 | 80 | 80/100 | 85 | 26 | 3529 | 1202 | 9.766% | 0.4862 | 0.512 | 0.098535 | 2.1792 | 0.027474 | 0.00036783 | 0.3767%
15 | BCDD-01, BBSR | 18 | AIR PORT | 14215 | AIRPORT | 14215202 | 0.5 | 80 | 80/100 | 100 | 2 | 2000 | 1 | 1.008% | 0.4862 | 0.496 | 0.0086456 | 1.0498 | 0.0017889 | 3.4531e-06 | 0.03425%
16 | BCDD-01, BBSR | 19 | AIR PORT | 14215 | GANGANAGAR | 14215203 | 5.1 | 80 | 80/100 | 110 | 25 | 4315 | 1256 | 13.25% | 0.4862 | 0.906 | 0.10327 | 2.059 | 0.029185 | 0.00069529 | 0.5249%
17 | BCDD-01, BBSR | 20 | UNIT-4 | 14013 | SASTRI NAGAR | 14013202 | 8.9 | 80 | 80/100 | 160 | 50 | 8630 | 2501 | 11.22% | 0.4862 | 0.704 | 0.060151 | 2.8311 | 0.014925 | 0.0013127 | 1.17%
18 | BCDD-01, BBSR | 21 | UNIT-4 | 14013 | MADHUSUDHAN NAGAR | 14013201 | 4.9 | 80 | 80/100 | 160 | 29 | 6480 | 588 | 10.67% | 0.4862 | 0.534 | 0.057217 | 2.1258 | 0.014062 | 0.00068098 | 0.638%
19 | BCDD-01, BBSR | 22 | UNIT-3 | 14015 | RAM MANDIR | 14015201 | 8.92 | 80 | 80/100 | 250 | 55 | 11094 | 1334 | 9.961% | 0.4862 | 0.676 | 0.034171 | 2.3292 | 0.0077682 | 0.0016719 | 1.679%
20 | BCDD-01, BBSR | 26 | SATYA NAGAR | 14014 | SATYA NAGAR | 14014201 | 4.5 | 80 | 80/100 | 100 | 27 | 5350 | 1359 | 8.703% | 0.4862 | 0.58217 | 0.074642 | 2.8081 | 0.019386 | 0.00033677 | 0.387%
21 | BCDD-01, BBSR | 27 | SATYA NAGAR | 14014 | PRESS FDR | 14014202 | 8.5 | 80 | 80/100 | 180 | 44 | 7953 | 918 | 9.92% | 0.4862 | 0.70483 | 0.047264 | 2.3191 | 0.01124 | 0.001195 | 1.205%
22 | BCDD-01, BBSR | 28 | SATYA NAGAR | 14014 | TOSHALI PLAZA | 14014203 | 10 | 80 | 80/100 | 155 | 31 | 5976 | 1847 | 8.827% | 0.4862 | 0.709 | 0.048841 | 2.0237 | 0.011677 | 0.001083 | 1.227%
23 | BCDD-01, BBSR | 29 | SATYA NAGAR | 14014 | RAHUL CO. | 14014204 | 3 | 80 | 80/100 | 70 | 4 | 2500 | 60 | 7.499% | 0.4862 | 0.31117 | 0.091874 | 1.8746 | 0.025128 | 0.0001426 | 0.1902%
24 | BCDD-01, BBSR | 30 | SAHID NAGAR | 14016 | SAHEED NAGAR-1 | 14016201 | 6 | 80 | 80/100 | 234 | 60 | 8215 | 2440 | 10.39% | 0.4862 | 1.0647 | 0.038097 | 1.8427 | 0.0087806 | 0.0011137 | 1.071%
25 | BCDD-01, BBSR | 31 | SAHID NAGAR | 14016 | SAHEED NAGAR-2 | 14016202 | 3.3 | 80 | 80/100 | 232 | 39 | 8838 | 899 | 6.461% | 0.4862 | 1.0563 | 0.023885 | 1.9995 | 0.0052333 | 0.00035885 | 0.5554%
26 | BCDD-01, BBSR | 32 | SAHID NAGAR | 14016 | SAHEED NAGAR-3 | 14016203 | 5 | 80 | 80/100 | 258 | 47 | 9640 | 1655 | 8.981% | 0.4862 | 1.1413 | 0.029854 | 1.9612 | 0.0066838 | 0.00085877 | 0.9562%
27 | BCDD-01, BBSR | 33 | SAHID NAGAR | 14016 | SAHEED NAGAR-4 | 14016204 | 2.2 | 80 | 80/100 | 112 | 21 | 5388 | 211 | 7.114% | 0.4862 | 0.53767 | 0.054476 | 2.525 | 0.013269 | 0.00014137 | 0.1987%
28 | BCDD-01, BBSR | 34 | BOARD COLONY | 14017 | FLAT | 14017201 | 8.6 | 100 | 100 | 250 | 26 | 6892 | 1602 | 12.2% | 0.3878 | 0.91267 | 0.041849 | 1.447 | 0.0097708 | 0.0016171 | 1.326%
29 | BCDD-01, BBSR | 35 | BOARD COLONY | 14017 | BOARD COLONY | 14017202 | 7.23 | 100 | 100 | 120 | 25 | 5266 | 1023 | 11.73% | 0.3878 | 0.54 | 0.083823 | 2.3033 | 0.022386 | 0.00071765 | 0.6119%
30 | BCDD-01, BBSR | 36 | BOARD COLONY | 14017 | AG COLONY | 14017203 | 8.9 | 100 | 100 | 200 | 26 | 6892 | 2445 | 12.69% | 0.3878 | 0.67 | 0.054403 | 1.8087 | 0.013248 | 0.0014523 | 1.145%
31 | BCDD-01, BBSR | 37 | BOARD COLONY | 14017 | ACHARYA VIHAR | 14017204 | 6.35 | 100 | 100 | 145 | 48 | 7211 | 996 | 12.33% | 0.3878 | 0.61367 | 0.072931 | 2.6103 | 0.018841 | 0.00077457 | 0.6282%
32 | BCDD-01, BBSR | 39 | DELTA | 14221 | SATABDI NAGAR | 14221202 | 7.3 | 100 | 80/100 | 140 | 31 | 4101 | 1501 | 11.9% | 0.3878 | 0.706 | 0.072888 | 1.5375 | 0.018828 | 0.00082949 | 0.6972%
33 | BCDD-02, BBSR | 3 | BARAMUNDA | 14005 | CRPF | 14005204 | 6.08 | 55 | 55/34 | 105 | 46 | 4639 | 1725 | 14.34% | 0.7104 | 0.57858 | 0.11712 | 2.319 | 0.034399 | 0.0013006 | 0.9071%
34 | BCDD-02, BBSR | 4 | BARAMUNDA | 14005 | BARAMUNDA HB | 14005201 | 5.3 | 55 | 55/34 | 200 | 32 | 4888 | 2561 | 12.1% | 0.7104 | 0.82583 | 0.051901 | 1.2828 | 0.012535 | 0.001499 | 1.239%
35 | BCDD-02, BBSR | 5 | BARAMUNDA | 14005 | BARAMUNDA BDA | 14005202 | 3.28 | 55 | 55/34 | 85 | 24 | 3850 | 1057 | 9.309% | 0.7104 | 0.39849 | 0.093931 | 2.3774 | 0.025845 | 0.00034548 | 0.3711%
36 | BCDD-02, BBSR | 7 | NAYAPALLI | 14008 | RENTAL | 14008205 | 8.82 | 55 | 55 | 186 | 68 | 8195 | 1663 | 16.36% | 0.7104 | 0.78273 | 0.075455 | 2.3126 | 0.019646 | 0.0033814 | 2.066%
37 | BCDD-02, BBSR | 9 | NAYAPALLI | 14008 | IRC-2 | 14008202 | 4.6 | 80 | 100/80/55 | 150 | 36 | 5739 | 2465 | 19.01% | 0.4862 | 0.82858 | 0.10871 | 2.0082 | 0.031198 | 0.0012465 | 0.6556%
38 | BCDD-02, BBSR | 13 | XAVIER | 14009 | XAVIER NALCO | 14009201 | 4.1 | 80 | 80/55 | 230 | 39 | 10459 | 457 | 16.79% | 0.4862 | 0.54629 | 0.062619 | 2.3868 | 0.015661 | 0.0013113 | 0.7809%
39 | BCDD-02, BBSR | 14 | XAVIER | 14009 | STPI | 14009202 | 0.8 | 80 | 80 | 130 | 6 | 4863 | 124 | 10.09% | 0.4862 | 0.54225 | 0.06659 | 1.9635 | 0.016865 | 8.8027e-05 | 0.08721%
40 | BCDD-02, BBSR | 16 | XAVIER | 14009 | SOI | 14009203 | 5.2 | 80 | 80/55 | 115 | 20 | 3715 | 3796 | 11.67% | 0.4862 | 0.94858 | 0.087021 | 1.6956 | 0.023462 | 0.00062289 | 0.5338%
41 | BCDD-02, BBSR | 18 | SAINIK SCHOOL | 14010 | GAJAPATINAGAR | 14010202 | 5.2 | 80 | 80/55 | 90 | 29 | 5316 | 719 | 15.21% | 0.4862 | 0.53412 | 0.14498 | 3.1003 | 0.045809 | 0.00074488 | 0.4896%
42 | BCDD-02, BBSR | 20 | SAINIK SCHOOL | 14010 | VANIVIHAR | 14010204 | 11.5 | 80 | 80/55 | 150 | 20 | 4553 | 179 | 8.467% | 0.4862 | 0.438 | 0.048409 | 1.5932 | 0.011557 | 0.0011544 | 1.363%
43 | BCDD-02, BBSR | 21 | SAINIK SCHOOL | 14010 | VSS NAGAR | 14010201 | 12.3 | 80 | 100/80/55 | 240 | 75 | 12674 | 4235 | 16.66% | 0.4862 | 0.71846 | 0.059519 | 2.7718 | 0.014738 | 0.004031 | 2.42%
44 | BCDD-02, BBSR | 22 | SAINIK SCHOOL | 14010 | SAINIK SCHOOL | 14010205 | 13.2 | 80 | 80/55 | 120 | 48 | 6543 | 2061 | 21.39% | 0.4862 | 0.78338 | 0.1529 | 2.8619 | 0.049284 | 0.0036165 | 1.69%
45 | BCDD-02, BBSR | 25 | CS PUR-1 | 14001 | BDA | 14001203 | 13 | 55 | 80/55 | 260 | 74 | 14470 | 3670 | 16.23% | 0.7104 | 1.5445 | 0.053532 | 2.9212 | 0.012999 | 0.0064436 | 3.971%
46 | BCDD-02, BBSR | 29 | CS PUR-2 | 14002 | HOUSING BOARD-1 | 14002205 | 3 | 55 | 80/55 | 150 | 22 | 5894 | 1243 | 15.86% | 0.7104 | 0.79261 | 0.090683 | 2.0624 | 0.024715 | 0.00094103 | 0.5933%
47 | BCDD-02, BBSR | 36 | INFOCITY | 14003 | INFOCITY | 14003201 | 1.5 | 80 | 80 | 160 | 8 | 2648 | 9 | 16.01% | 0.4862 | 0.75317 | 0.085822 | 0.86868 | 0.023057 | 0.0003418 | 0.2135%
48 | BCDD-02, BBSR | 37 | INFOCITY | 14003 | BANK | 14003202 | 2 | 80 | 80 | 100 | 35 | 9452 | 99 | 16.5% | 0.4862 | 0.24167 | 0.14155 | 4.9612 | 0.044338 | 0.00034234 | 0.2074%
49 | BCDD-02, BBSR | 42 | NEW BARANGA | 14216 | TRISULIA | 14216201 | 35 | 55 | 55/34 | 170 | 187 | 14696 | 3206 | 29.5% | 0.7104 | 0.5705 | 0.14884 | 4.5374 | 0.047489 | 0.027095 | 9.184%
50 | BCDD-02, BBSR | 44 | KALINGA NAGAR | 14007 | K-9 | 14007201 | 6.7 | 55 | 80/55 | 240 | 96 | 11911 | - | 17.84% | 0.7104 | 1.2405 | 0.063755 | 2.6049 | 0.016003 | 0.0034835 | 1.953%
51 | BCDD-02, BBSR | 45 | KALINGA NAGAR | 14007 | DUMDUMA | 14007205 | 6.3 | 55 | 80/55 | 310 | 81 | 10490 | - | 17.76% | 0.7104 | 0.78919 | 0.049121 | 1.7761 | 0.011755 | 0.0040142 | 2.261%
52 | BCDD-02, BBSR | 48 | KALINGA NAGAR | 14007 | K-5 | 14007202 | 18.5 | 80 | 100/80/55 | 162 | 63 | 8587 | - | 18.44% | 0.4862 | 1.0049 | 0.097622 | 2.7822 | 0.027148 | 0.0050885 | 2.76%
53 | BCDD-02, BBSR | 50 | KALINGA NAGAR | 14007 | VIPUL GARDEN | 14007207 | 4.5 | 100 | 100 | 35 | 12 | 5525 | 335 | 18.79% | 0.3878 | 0.15844 | 0.46046 | 8.2856 | 0.26171 | 0.00044423 | 0.2364%
54 | BCDD-02, BBSR | 54 | BHARATPUR | 14006 | PHD | 14006203 | 6 | 80 | 100/80/55 | 80 | 63 | 8697 | - | 18.13% | 0.4862 | 0.50106 | 0.19438 | 5.7061 | 0.069104 | 0.0010244 | 0.565%
55 | BCDD-02, BBSR | 59 | KANAN BIHAR | 14217 | KALARAHANGA | 14217202 | 8.5 | 80 | 80/55 | 50 | 85 | 7541 | 872 | 23.69% | 0.4862 | 0.85933 | 0.40631 | 7.9162 | 0.21333 | 0.0017501 | 0.7388%
56 | BCDD-02, BBSR | 61 | KANAN BIHAR | 14217 | PKB | 14217204 | 10 | 80 | 80/55 | 270 | 126 | 19147 | 3439 | 18.1% | 0.4862 | 0.28367 | 0.057499 | 3.7222 | 0.014145 | 0.0039808 | 2.199%
57 | BED, BBSR | 2 | MANCHESWAR | 14022 | MANCHESWAR-2 | 14022202 | 6.81 | 100 | 100/55 | 168 | 71 | 10985.8 | 677 | 5.495% | 0.3878 | 0.95937 | 0.028053 | 3.4323 | 0.0062402 | 0.00036932 | 0.6721%
58 | BED, BBSR | 3 | MANCHESWAR | 14022 | MANCHESWAR-3 | 14022203 | 1.12 | 100 | 100 | 145 | 7 | 2625 | 2931 | 9.816% | 0.3878 | 1.0623 | 0.058057 | 0.95021 | 0.014308 | 0.00010374 | 0.1057%
59 | BED, BBSR | 22 | BADAGADA | 14019 | BADAGADA LINGARAJ | 14019202 | 4.7 | 100 | 100/55 | 288 | 42 | 5212.2 | 2200 | 14.85% | 0.3878 | 0.93233 | 0.044211 | 0.94992 | 0.010406 | 0.0012491 | 0.8414%
60 | BED, BBSR | 24 | BADAGADA | 14019 | BRAHMESWAR | 14019201 | 7.5 | 100 | 100/80/55 | 324 | 62 | 6778.8 | 4296 | 13.56% | 0.3878 | 0.877 | 0.035899 | 1.0982 | 0.0082109 | 0.0019906 | 1.468%
61 | BED, BBSR | 25 | BADAGADA | 14019 | MAUSIMA | 14019203 | 7 | 55 | 55 | 296 | 73 | 8762.6 | 3009 | 14.76% | 0.7104 | 1.0913 | 0.042756 | 1.5538 | 0.010014 | 0.0034642 | 2.348%
62 | BED, BBSR | 26 | BADAGADA | 14019 | B.J.B NAGAR | 14019206 | 5.6 | 148 | 148/100 | 296 | 59 | 5331.9 | 3351 | 15.37% | 0.262 | 0.8068 | 0.044543 | 0.94547 | 0.010496 | 0.0010713 | 0.6969%
63 | BED, BBSR | 27 | BADAGADA | 14019 | BADAGADA | 14019205 | 8.18 | 100 | 100/80/55 | 128 | 83 | 5717.6 | 3538 | 16.41% | 0.3878 | 0.48517 | 0.10997 | 2.3446 | 0.03167 | 0.0013069 | 0.7963%
64 | BED, BBSR | 28 | BADAGADA | 14019 | SAI | 14019207 | 12 | 100 | 100/80/55 | 182 | 25 | 1705.9 | 1351 | 15.8% | 0.3878 | 0.75467 | 0.074473 | 0.49197 | 0.019332 | 0.0023661 | 1.497%
65 | BED, BBSR | 29 | BADAGADA | 14019 | RAJARANI | 14019208 | 5 | 100 | 100 | 78 | 16 | 1795.5 | 1581 | 15.32% | 0.3878 | 0.51467 | 0.1685 | 1.2082 | 0.056412 | 0.00052841 | 0.3448%
66 | BED, BBSR | 32 | BHIMATANGI | 14018 | POKHARIPUT | 14018201 | 9.32 | 100 | 100/55/34 | 400 | 86 | 8103.9 | 3536 | 15.79% | 0.3878 | 1.2334 | 0.033861 | 1.0634 | 0.0076895 | 0.0035308 | 2.236%
67 | BED, BBSR | 40 | BHINGARPUR | 14224 | GANGESWAR | 14224201 | 32 | 55 | 34/55 | 90 |  | 2106 | 1920 | 55.68% | 0.7104 | 0.906 | 0.53061 | 1.2282 | 0.33136 | 0.048447 | 8.701%
68 | NED, NIMAPARA | 9 | BALAKATI | 14025 | SATYABANPUR | 14025202 | 56 | 55 | 55/34 | 75 | 93 | 4190 | 2369 | 44.7% | 0.7104 | 0.69267 | 0.51113 | 2.9323 | 0.31123 | 0.0553 | 12.37%
69 | NED, NIMAPARA | 10 | BALAKATI | 14025 | BALAKATI | 14025201 | 27 | 55 | 55/34 | 120 | 57 | 3100 | 2911 | 24.57% | 0.7104 | 0.71684 | 0.17561 | 1.3559 | 0.059791 | 0.013113 | 5.337%
70 | NED, NIMAPARA | 12 | NIMAPARA | 14027 | NIMAPARA GOP | 14027205 | 85 | 55 | 55/34 | 85 | 130 | 7175 | 4982 | 47.48% | 0.7104 | 1.3207 | 0.4791 | 4.4306 | 0.27945 | 0.096803 | 20.39%
71 | NED, NIMAPARA | 16 | NIMAPARA | 14027 | DANDIPUR | 14027203 | 29 | 55 | 55/34 | 255 | 206 | 8460 | 6582 | 40.5% | 0.7104 | 0.66176 | 0.13622 | 1.7414 | 0.042088 | 0.044768 | 11.05%
72 | NED, NIMAPARA | 17 | ASTARANGA | 14029 | JUINTY | 14029202 | 46 | 55 | 55/34 | 105 | 108 | 3360 | 3708 | 69.41% | 0.7104 | 0.784 | 0.56691 | 1.6796 | 0.37049 | 0.10599 | 15.27%
73 | NED, NIMAPARA | 21 | KAKATPUR | 14030 | KAKATPUR-2 | 14030205 | 31 | 55 | 55/34 | 120 | 110 | 5080 | 8889 | 37.39% | 0.7104 | 0.92057 | 0.26723 | 2.222 | 0.11058 | 0.027843 | 7.447%
74 | NED, NIMAPARA | 23 | KAKATPUR | 14030 | NUAHAT-1 | 14030202 | 15 | 55 | 55/34 | 200 | 160 | 4900 | 8161 | 54.71% | 0.7104 | 1.2524 | 0.23459 | 1.286 | 0.090944 | 0.030779 | 5.626%
75 | NED, NIMAPARA | 24 | KAKATPUR | 14030 | NUAHAT-2 | 14030204 | 60 | 55 | 55/34 | 120 | 63 | 1653 | 5223 | 31.99% | 0.7104 | 0.61033 | 0.22865 | 0.72302 | 0.087552 | 0.042669 | 13.34%
76 | NED, NIMAPARA | 25 | CHHAITANA | 14032 | CHARISHREE | 14032201 | 10 | 55 | 55/34 | 55 | 57 | 2040 | 2479 | 38.3% | 0.7104 | 0.37599 | 0.59724 | 1.9468 | 0.4048 | 0.0069072 | 1.803%
77 | NED, NIMAPARA | 29 | GOP | 14051 | BEGUNAI | 14051203 | 59 | 55 | 55/34 | 80 | 90 | 2727 | 3039 | 53.19% | 0.7104 | 0.40807 | 0.57023 | 1.7892 | 0.37418 | 0.079697 | 14.98%
78 | NED, NIMAPARA | 33 | KONARK | 14031 | BALI DOKAN | 14031202 | 50 | 55 | 55/34 | 80 | 122 | 3620 | 3797 | 46.49% | 0.7104 | 0.34388 | 0.49839 | 2.3751 | 0.29839 | 0.05386 | 11.59%
79 | KHD,KHURDA | 1 | KALAPATHAR | 14048 | BAIDESWAR | 14048201 | 49.444 | 55 | 34 & 55 | 60 | 104 | 4575 | 3209 | 33.83% | 0.7104 | 0.4212 | 0.48361 | 4.0022 | 0.28382 | 0.028497 | 8.423%
80 | KHD,KHURDA | 2 | KALAPATHAR | 14048 | KALAPATHAR | 14048203 | 35.268 | 55 | 34 & 55 | 60 | 68 | 4441 | 2951 | 39.89% | 0.7104 | 0.84915 | 0.57013 | 3.885 | 0.37407 | 0.026789 | 6.717%
81 | KHD,KHURDA | 3 | KALAPATHAR | 14048 | GEDIAPALLI | 14048202 | 89.229 | 55 | 34 & 55 | 120 | 210 | 8042 | 6990 | 34.7% | 0.7104 | 0.79289 | 0.24799 | 3.5176 | 0.098797 | 0.071605 | 20.64%
82 | KHD,KHURDA | 4 | BAGHAMARI | 14040 | ATRI | 14040203 | 42.141 | 55 | 22, 34 & 55 | 50 | 79 | 3875 | 3547 | 45.83% | 0.7104 | 0.392 | 0.78605 | 4.0678 | 0.6515 | 0.038716 | 8.449%
83 | KHD,KHURDA | 5 | BAGHAMARI | 14040 | SARUA | 14040201 | 38.79 | 55 | 34, 55 & 100 | 50 | 81 | 4873 | 1876 | 20.87% | 0.7104 | 0.24134 | 0.35804 | 5.1155 | 0.17416 | 0.0095268 | 4.564%
84 | KHD,KHURDA | 6 | BAGHAMARI | 14040 | PODADIHA | 14040202 | 43.98 | 55 | 34 & 55 | 60 | 91 | 3895 | 3808 | 45.56% | 0.7104 | 0.58902 | 0.65123 | 3.4073 | 0.46952 | 0.041932 | 9.204%
85 | KHD,KHURDA | 8 | PARICHHAL | 14041 | ROUTPADA | 14041205 | 15.5 | 55 | 34 & 55 | 35 | 38 | 1320 | 910 | 30.39% | 0.7104 | 0.32012 | 0.74465 | 1.9795 | 0.59254 | 0.0063462 | 2.088%
86 | KHD,KHURDA | 9 | PARICHHAL | 14041 | GUDDUM | 14041202 | 14.9 | 55 | 34 & 55 | 39 | 38 | 1432 | 705 | 25.22% | 0.7104 | 0.12077 | 0.55472 | 1.9272 | 0.35711 | 0.0045651 | 1.81%
87 | KHD,KHURDA | 11 | PARICHHAL | 14041 | GADAMANITRI | 14041201 | 14.978 | 55 | 34 & 55 | 38 | 39 | 1330 | 1042 | 22.82% | 0.7104 | 0.12452 | 0.51497 | 1.8371 | 0.31515 | 0.0038448 | 1.685%
88 | KHD,KHURDA | 12 | BEGUNIA | 14182 | BEGUNIA | 14182201 | 9.15 | 55 | 34 & 55 | 45 | 33 | 2124 | 1727 | 21.49% | 0.7104 | 0.19333 | 0.40965 | 2.4774 | 0.21618 | 0.0022594 | 1.051%
89 | KHD,KHURDA | 13 | BEGUNIA | 14182 | DINGAR | 14182202 | 59.948 | 55 | 34 & 55 | 68 | 139 | 4920 | 3687 | 28.82% | 0.7104 | 0.36967 | 0.36351 | 3.7977 | 0.17841 | 0.027897 | 9.679%
90 | KHD,KHURDA | 14 | JANLA | 14034 | MENDHASAL | 14034201 | 7 | 55 | 80, 55 & 34 | 30 | 41 | 3127 | 350 | 37.07% | 0.7104 | 0.54467 | 1.0599 | 5.471 | 1.1106 | 0.0039467 | 1.065%
91 | KHD,KHURDA | 15 | JANLA | 14034 | OIL MILL-1 | 14034202 | 36 | 55 | 34 & 55 | 70 | 99 | 6794 | 1836 | 45.31% | 0.7104 | 0.70344 | 0.55513 | 5.0943 | 0.35756 | 0.035578 | 7.852%
92 | KHD,KHURDA | 17 | JANLA | 14034 | MADANPUR | 14034204 | 28 | 80 | 100, 80, 55 & 34 | 85 | 129 | 11393 | 2053 | 26.16% | 0.4862 | 0.68012 | 0.26396 | 7.0352 | 0.10853 | 0.0084761 | 3.24%
93 | KHD,KHURDA | 18 | GURUJANGA | 14036 | HALADIA | 14036201 | 72.5 | 55 | 80, 55 & 34 | 170 | 218 | 9698 | 6855 | 43.79% | 0.7104 | 1.4013 | 0.22093 | 2.9943 | 0.083232 | 0.098369 | 22.46%
94 | KHD,KHURDA | 21 | 10-POLE | 14044 | TARATUA | 14044206 | 19.86 | 55 | 55 & 34 | 60 | 68 | 4623 | 2123 | 45.42% | 0.7104 | 0.528 | 0.64922 | 4.0442 | 0.46703 | 0.018835 | 4.147%
95 | KHD,KHURDA | 23 | 10-POLE | 14044 | PANABARAJ | 14044203 | 58.5 | 55 | 80, 55 & 34 | 96 | 112 | 5838 | 3487 | 45.95% | 0.7104 | 0.19268 | 0.4105 | 3.1919 | 0.21691 | 0.065965 | 14.36%
96 | KHD,KHURDA | 25 | TIRIMAL | 14050 | IDCO | 14050204 | 11.1 | 55 | 55 & 34 | 30 | 27 | 1569 | 415 | 29.38% | 0.7104 | 0.18995 | 0.83985 | 2.7451 | 0.73225 | 0.0041263 | 1.405%
97 | KHD,KHURDA | 26 | TIRIMAL | 14050 | TIRIMAL | 14050201 | 5.9 | 55 | 55 & 34 | 20 | 16 | 928 | 560 | 34.14% | 0.7104 | 0.094663 | 1.4638 | 2.4354 | 2.0069 | 0.0026716 | 0.7827%
98 | KHD,KHURDA | 28 | TIRIMAL | 14050 | TARABOI | 14050202 | 41.95 | 55 | 55 & 34 | 130 | 101 | 5616 | 3150 | 38.05% | 0.7104 | 0.47515 | 0.25103 | 2.2675 | 0.10062 | 0.040238 | 10.57%
99 | KHD,KHURDA | 29 | TIRIMAL | 14050 | PHD | 14050203 | 0.5 | 34 | 34 | 15 | 1 | 250 | 1 | 15.77% | 1.1325 | 0.063455 | 0.90161 | 0.8748 | 0.83065 | 8.4031e-05 | 0.05329%
100 | KHD,KHURDA | 30 | JATANI | 14033 | RAJA BAZAR | 14033202 | 3.5 | 55 | 100 & 55 | 130 | 20 | 4065 | 2312 | 43.56% | 0.7104 | 0.73855 | 0.28737 | 1.6413 | 0.12354 | 0.0041218 | 0.9463%
101 | KHD,KHURDA | 31 | JATANI | 14033 | KUSUMATI | 14033203 | 11 | 100 | 100 & 55 | 160 | 46 | 5041 | 3200 | 39.73% | 0.3878 | 0.9559 | 0.21295 | 1.6537 | 0.078867 | 0.0068386 | 1.721%
102 | KHD,KHURDA | 32 | JATANI | 14033 | JATNI TOWN | 14033204 | 5.9 | 80 | 80 & 55 | 60 | 26 | 3178 | 1415 | 44.87% | 0.4862 | 0.50617 | 0.64137 | 2.7801 | 0.45736 | 0.0037502 | 0.8358%
103 | KHD,KHURDA | 33 | JATANI | 14033 | BACHHARA | 14033201 | 13.76 | 80 | 80, 55 & 34 | 120 | 47 | 4480 | 3242 | 32.75% | 0.4862 | 0.80203 | 0.23409 | 1.9595 | 0.090657 | 0.0069347 | 2.117%
104 | KHD,KHURDA | 34 | JATANI | 14033 | JATNI RURAL | 14033205 | 45.88 | 80 | 100, 80, 55 & 34 | 160 | 81 | 6787 | 2502 | 31.16% | 0.4862 | 1.38 | 0.16703 | 2.2265 | 0.055724 | 0.025267 | 8.109%
105 | KHD,KHURDA | 35 | HARIRAJPUR | 14035 | KUDIARY | 14035203 | 10.9 | 55 | 80,55 & 34 | 165 | 43 | 6003 | 1785 | 43.26% | 0.7104 | 0.6232 | 0.22485 | 1.9096 | 0.085416 | 0.014298 | 3.305%
106 | KHD,KHURDA | 36 | HARIRAJPUR | 14035 | GOLAPADA | 14035204 | 6.9 | 55 | 80,55 & 34 | 32 | 12 | 699 | 672 | 32.62% | 0.7104 | 0.47733 | 0.87436 | 1.1465 | 0.78648 | 0.0031345 | 0.9608%
107 | KHD,KHURDA | 37 | HARIRAJPUR | 14035 | KAKUDIA | 14035202 | 16.5 | 55 | 55 & 34 | 95 | 48 | 3767 | 1650 | 34.37% | 0.7104 | 0.63958 | 0.31025 | 2.0813 | 0.13906 | 0.01168 | 3.399%
108 | KHD,KHURDA | 40 | DADHIMACHAGADIA | 14203 | KAIPADAR | 14203201 | 35.45 | 55 | 55 & 34 | 80 | 86 | 7066 | 1727 | 37.93% | 0.7104 | 0.3585 | 0.4066 | 4.636 | 0.21358 | 0.027333 | 7.207%
109 | KHD,KHURDA | 41 | DADHIMACHAGADIA | 14203 | DADHIMACHHAGADIA | 14203202 | 10.9 | 80 | 80 & 55 | 61 | 37 | 3809 | 80 | 46.13% | 0.4862 | 0.11975 | 0.64852 | 3.2775 | 0.46617 | 0.0072992 | 1.582%
110 | KHD,KHURDA | 42 | DADHIMACHAGADIA | 14203 | BAJAPUR | 14203203 | 34.84 | 80 | 80, 55 & 34 | 110 | 116 | 7827 | 2327 | 19% | 0.4862 | 0.63371 | 0.14814 | 3.7348 | 0.047186 | 0.0076793 | 4.042%
111 | KHD,KHURDA | 43 | MALIPADA | 14038 | NARANGARH-1 | 14038201 | 21.3 | 80 | 80, 55 & 34 | 152 | 48 | 4424 | 1721 | 39.22% | 0.4862 | 0.55233 | 0.22132 | 1.5277 | 0.08345 | 0.015854 | 4.042%
112 | KHD,KHURDA | 44 | MALIPADA | 14038 | NARANGARH-2 | 14038203 | 3 | 55 | 55 | 14 | 6 | 380 | 53 | 25.27% | 0.7104 | 0.0322 | 1.5482 | 1.4247 | 2.2271 | 0.00073865 | 0.2923%
113 | KHD,KHURDA | 45 | MALIPADA | 14038 | MALIPADA TAPANGA | 14038202 | 41.26 | 80 | 80, 55 & 34 | 159 | 156 | 13637 | 1278 | 23.18% | 0.4862 | 0.656 | 0.12503 | 4.5017 | 0.037511 | 0.015105 | 6.517%
114 | KHD,KHURDA | 46 | NARANGARH | 14039 | KAIMATIA | 14039203 | 5.07 | 55 | 55 | 15 | 17 | 934 | 472 | 32.27% | 0.7104 | 0.08 | 1.8448 | 3.2682 | 3.0917 | 0.0019894 | 0.6166%
115 | KHD,KHURDA | 47 | NARANGARH | 14039 | MANDARBASTA | 14039202 | 33.11 | 55 | 55 & 34 | 70 | 63 | 3015 | 576 | 33.74% | 0.7104 | 0.17227 | 0.41333 | 2.2607 | 0.21934 | 0.020073 | 5.95%
116 | KHD,KHURDA | 48 | NARANGARH | 14039 | NIRAKARPUR-1 | 14039201 | 73.1 | 80 | 80, 55 & 34 | 127 | 173 | 7787 | 6276 | 37.68% | 0.4862 | 0.7591 | 0.25443 | 3.2183 | 0.10267 | 0.046732 | 12.4%
117 | KHD,KHURDA | 49 | NARANGARH | 14039 | MANPUR | 14039204 | 31.15 | 55 | 80, 55 & 34 | 65 | 59 | 2743 | 2509 | 46.61% | 0.7104 | 0.34282 | 0.61506 | 2.215 | 0.42565 | 0.031598 | 6.779%
118 | KHD,KHURDA | 50 | JANKIA | 14037 | SIKO | 14037201 | 100.25 | 55 | 80, 55 & 34 | 140 | 233 | 10485 | 7374 | 28.61% | 0.7104 | 0.81364 | 0.17526 | 3.931 | 0.059623 | 0.066082 | 23.1%
119 | KHD,KHURDA | 51 | JANKIA | 14037 | NIRAKARPUR-2 | 14037203 | 43 | 55 | 55 & 34 & 150mm2 XLPE UG Cable | 92 | 125 | 5949 | 3800 | 32.9% | 0.7104 | 0.72867 | 0.30674 | 3.394 | 0.13662 | 0.028047 | 8.524%
120 | KHD,KHURDA | 52 | JANKIA | 14037 | GOLABAI | 14037202 | 51.23 | 55 | 55 & 34 | 105 | 149 | 7146 | 4278 | 33.34% | 0.7104 | 0.76382 | 0.27233 | 3.5722 | 0.1138 | 0.036254 | 10.87%
121 | KHD,KHURDA | 53 | RAJSUNAKHALA | 14042 | BAIAPALLI | 14042201 | 48.96 | 55 | 55 & 34 | 40 | 77 | 3192 | 2008 | 35.3% | 0.7104 | 0.26543 | 0.75681 | 4.1885 | 0.60957 | 0.026935 | 7.631%
122 | KHD,KHURDA | 55 | RAJSUNAKHALA | 14042 | SUNAKHALA | 14042203 | 18.1 | 55 | 55 & 34 | 80 | 50 | 3993 | 2383 | 38.25% | 0.7104 | 0.53818 | 0.41004 | 2.6198 | 0.21652 | 0.014148 | 3.699%
123 | KHD,KHURDA | 57 | OIL MILL | 14043 | TAPANG | 14043205 | 31.3 | 80 | 80, 55 & 34 | 51 | 111 | 6495 | 907 | 40.77% | 0.4862 | 0.35098 | 0.68567 | 6.6845 | 0.51325 | 0.016131 | 3.956%
124 | KHD,KHURDA | 58 | OIL MILL | 14043 | BPCL | 14043201 | 0.2 | 148 | 185mm2 XLPE Cable | 40 | 1 | 500 | 1 | 0.2259% | 0.262 | 0.086159 | 0.0048438 | 0.6561 | 0.00098753 | 6.574e-08 | 0.00291%
125 | KHD,KHURDA | 59 | OIL MILL | 14043 | INDUSTRIAL | 14043204 | 16.42 | 100 | 100, 80 & 55 | 148 | 88 | 11689 | 203 | 35.88% | 0.3878 | 0.76726 | 0.20791 | 4.1455 | 0.076164 | 0.008435 | 2.351%
126 | KHD,KHURDA | 60 | OIL MILL | 14043 | MUKUNDAPRASAD | 14043202 | 18.83 | 55 | 55 & 34 | 174 | 63 | 7842 | 2479 | 43.47% | 0.7104 | 1.0999 | 0.21426 | 2.3656 | 0.079579 | 0.025591 | 5.887%
127 | KHD,KHURDA | 61 | SUNADEIMUNDIA | 14047 | BANKI TOWN | 14047201 | 43.4 | 80 | 80 & 55 | 135 | 120 | 9491 | 6863 | 35.87% | 0.4862 | 1.158 | 0.22791 | 3.6901 | 0.087137 | 0.026607 | 7.417%
128 | KHD,KHURDA | 62 | SUNADEIMUNDIA | 14047 | RAJIB | 14047202 | 61.373 | 55 | 55 & 34 | 65 | 138 | 5902 | 5498 | 44.36% | 0.7104 | 0.82223 | 0.5853 | 4.7659 | 0.39112 | 0.057207 | 12.9%
129 | KHD,KHURDA | 64 | TULASIPUR | 14045 | TULASIPUR | 14045201 | 14.21 | 34 | 34 | 60 | 44 | 2441 | 2564 | 34.65% | 1.1325 | 0.268 | 0.49524 | 2.1354 | 0.29526 | 0.013582 | 3.92%
130 | KHD,KHURDA | 66 | JATAMUNDIA | 14049 | TALABASTA | 14049201 | 47.77 | 55 | 55 & 34 | 105 | 153 | 6255 | 3200 | 45.29% | 0.7104 | 0.2452 | 0.3699 | 3.1268 | 0.18344 | 0.054495 | 12.03%
131 | KHD,KHURDA | 67 | JATAMUNDIA | 14049 | RAMACHANDI | 14049203 | 60.3 | 55 | 55 & 34 | 145 | 100 | 7215 | 2800 | 44.14% | 0.7104 | 0.44962 | 0.26108 | 2.6117 | 0.10675 | 0.076337 | 17.29%
132 | KHD,KHURDA | 68 | JATAMUNDIA | 14049 | TARAPUR | 14049204 | 26.6 | 55 | 55 & 34 | 45 | 72 | 3284 | 425 | 37.61% | 0.7104 | 0.090036 | 0.71684 | 3.8305 | 0.55446 | 0.016846 | 4.479%
133 | KHD,KHURDA | 69 | JATAMUNDIA | 14049 | JATAMUNDIA (GHASIPUT/PHD) | 14049202 | 0.03 | 34 | 34 | 6 | 2 | 200 | 275 | 32.55% | 1.1325 | 0.16395 | 4.653 | 1.7496 | 18.2507 | 1.7724e-05 | 0.005445%
134 | NYD, NAYAGARH | 1 | NAYAGARH | 14058 | NAYAGARH | 14058201 | 27.65 | 100 | 80 & 100 mm2 | 340 | 124 | 16203 | 5440 | 20.63% | 0.3878 | 0.76001 | 0.05203 | 2.5014 | 0.012572 | 0.012373 | 5.999%
135 | NYD, NAYAGARH | 2 | NAYAGARH | 14058 | SIMILISAHI | 14058202 | 32.45 | 55 | 55 mm2 | 70 | 113 | 4912 | 3222 | 25.6% | 0.7104 | 0.80156 | 0.31364 | 3.6832 | 0.14142 | 0.012684 | 4.955%
136 | NYD, NAYAGARH | 3 | NAYAGARH | 14058 | SINDURIA | 14058203 | 13.45 | 100 | 55 & 100 mm2 | 160 | 82 | 6330 | 3184 | 46.2% | 0.3878 | 0.62769 | 0.24763 | 2.0766 | 0.098582 | 0.010452 | 2.262%
137 | NYD, NAYAGARH | 6 | SARANKUL | 14062 | DARAPADA | 14062204 | 21.75 | 55 | 55 mm2 | 40 | 46 | 2859 | 1372 | 27.78% | 0.7104 | 0.19113 | 0.59564 | 3.7516 | 0.40296 | 0.00791 | 2.847%
138 | NYD, NAYAGARH | 8 | SARANKUL | 14062 | SARANKUL | 14062201 | 5.25 | 55 | 55 mm2 | 65 | 63 | 5102 | 3257 | 37.65% | 0.7104 | 0.3712 | 0.4968 | 4.1199 | 0.29681 | 0.0037136 | 0.9863%
139 | NYD, NAYAGARH | 9 | SARANKUL | 14062 | PANCHARIDA | 14062205 | 78.4 | 55 | 55 mm2 | 55 | 70 | 3146 | 4622 | 40.99% | 0.7104 | 0.035333 | 0.63914 | 3.0023 | 0.45463 | 0.060818 | 14.84%
140 | NYD, NAYAGARH | 12 | ODOGAON | 14063 | KOMANDA | 14063202 | 87 | 55 | 34,55 & 80 2 | 72 | 260 | 10550 | 4622 | 30.44% | 0.7104 | 0.33523 | 0.36262 | 7.6909 | 0.17772 | 0.045211 | 14.85%
141 | NYD, NAYAGARH | 13 | ODOGAON | 14063 | NADIGHARA | 14063206 | 96.6 | 34 | 34 mm2 | 47 | 111 | 4295 | 3894 | 24% | 1.1325 | 0.3747 | 0.43792 | 4.7965 | 0.24101 | 0.046245 | 19.27%
142 | NYD, NAYAGARH | 14 | ODOGAON | 14063 | ODAGAON-1 | 14063203 | 0.9 | 80 | 80 mm2 | 12 | 7 | 1538 | 2307 | 31.58% | 0.4862 | 0.13403 | 2.2573 | 6.7272 | 4.5277 | 0.00022653 | 0.07172%
143 | NYD, NAYAGARH | 15 | ODOGAON | 14063 | ODAGAON-2 | 14063204 | 4.2 | 80 | 80 mm2 | 53 | 21 | 2831 | 3300 | 19.09% | 0.4862 | 0.19888 | 0.30887 | 2.8036 | 0.13809 | 0.00062894 | 0.3295%
144 | NYD, NAYAGARH | 16 | ODOGAON | 14063 | AMBARAPUR | 14063205 | 25.9 | 34 | 34 mm2 | 25 | 50 | 1272 | 2870 | 37.97% | 1.1325 | 0.13497 | 1.3027 | 2.6706 | 1.6181 | 0.023554 | 6.203%
145 | NYD, NAYAGARH | 17 | ITAMATI | 14053 | CHAMPATIPUR | 14053204 | 54.1 | 55 | 34&55 | 100 | 134 | 6028 | 5178 | 36.66% | 0.7104 | 0.52258 | 0.3144 | 3.164 | 0.14196 | 0.043321 | 11.82%
146 | NYD, NAYAGARH | 18 | ITAMATI | 14053 | BADAPANDUSAR | 14053203 | 58.8 | 55 | 34&55 | 65 | 163 | 6754 | 4966 | 44.13% | 0.7104 | 0.45113 | 0.5823 | 5.4539 | 0.38772 | 0.054332 | 12.31%
147 | NYD, NAYAGARH | 19 | ITAMATI | 14053 | ITAMATI | 14053201 | 14.989 | 55 | 34&55 | 60 | 52 | 3724 | 3482 | 44.47% | 0.7104 | 0.36968 | 0.63564 | 3.2578 | 0.45036 | 0.013708 | 3.083%
148 | NYD, NAYAGARH | 20 | ITAMATI | 14053 | LATHIPADA-1 | 14053202 | 37.386 | 55 | 34&55 | 65 | 121 | 4523 | 3394 | 15.82% | 0.7104 | 0.32043 | 0.20875 | 3.6524 | 0.07661 | 0.0068258 | 4.314%
149 | NYD, NAYAGARH | 21 | ITAMATI | 14053 | LATHIPADA-2 | 14053205 | 70.349 | 55 | 34&55 | 90 | 189 | 7043 | 5973 | 34.42% | 0.7104 | 0.35046 | 0.32803 | 4.1075 | 0.15169 | 0.048756 | 14.16%
150 | NYD, NAYAGARH | 22 | BOLAGARH | 14052 | KHANGURIA | 14052204 | 30.712 | 55 | 34&55 | 55 | 63 | 3171 | 2334 | 16.98% | 0.7104 | 0.15794 | 0.26477 | 3.0262 | 0.10903 | 0.0057138 | 3.365%
151 | NYD, NAYAGARH | 25 | BOLAGARH | 14052 | BOLAGARH | 14052201 | 11.31 | 55 | 34&55 | 50 | 27 | 1872 | 1927 | 40.25% | 0.7104 | 0.2805 | 0.69037 | 1.9651 | 0.51937 | 0.0082834 | 2.058%
152 | NYD, NAYAGARH | 26 | MAHIPUR | 14061 | MAHIPUR | 14061201 | 47.13 | 34 | 34 mm2 | 36 | 132 | 4049 | 3985 | 23.11% | 1.1325 | 0.23945 | 0.55059 | 5.9034 | 0.35264 | 0.019368 | 8.381%
153 | NYD, NAYAGARH | 27 | MAHIPUR | 14061 | BIRUDA | 14061202 | 74.26 | 34 | 34 mm2 | 32 | 133 | 4025 | 3086 | 41.74% | 1.1325 | 0.4753 | 1.1188 | 6.602 | 1.2252 | 0.083775 | 20.07%
154 | NYD, NAYAGARH | 28 | MAHIPUR | 14061 | SINGARPALLI-1 | 14061203 | 71.21 | 34 | 34 mm2 | 38 | 129 | 3696 | 2717 | 27% | 1.1325 | 0.13816 | 0.60934 | 5.1051 | 0.41891 | 0.038734 | 14.35%
155 | NYD, NAYAGARH | 29 | MAHIPUR | 14061 | SINGARPALLI-2 | 14061204 | 77.68 | 34 | 34 mm2 | 21 | 95 | 2532 | 1347 | 27% | 1.1325 | 0.13816 | 1.1026 | 6.3285 | 1.1931 | 0.036754 | 13.61%
156 | NYD, NAYAGARH | 31 | NUAGAON | 14060 | SAMAPADA | 14060202 | 17.59 | 34 | 34 & 55 mm2 | 17 | 55 | 1600 | 2205 | 29.68% | 1.1325 | 0.050133 | 1.4971 | 4.94 | 2.0925 | 0.0095654 | 3.223%
157 | NYD, NAYAGARH | 33 | DASPALLA | 14059 | MADHYAKHANDA | 14059202 | 71.2 | 100 | 55 & 100 mm2 | 80 | 121 | 3724 | 3676 | 29.36% | 0.3878 | 0.080746 | 0.31476 | 2.4433 | 0.14221 | 0.019954 | 6.796%
158 | NYD, NAYAGARH | 35 | KHANDAPADA | 14054 | KHANDAPADA | 14054201 | 34.59 | 100 | 34,55,80 & 100 mm2 | 75 | 95 | 4813 | 3293 | 25.23% | 0.3878 | 0.26177 | 0.28849 | 3.3683 | 0.12428 | 0.0074457 | 2.951%
159 | NYD, NAYAGARH | 36 | KHANDAPADA | 14054 | BAIGUNIA | 14054202 | 101.898 | 55 | 34, 55 mm2 | 95 | 180 | 5849 | 5257 | 27.14% | 0.7104 | 0.47531 | 0.24506 | 3.2316 | 0.097053 | 0.050345 | 18.55%
160 | NYD, NAYAGARH | 37 | KHANDAPADA | 14054 | PANIPOILA | 14054203 | 58.734 | 55 | 34, 55 mm2 | 40 | 105 | 3374 | 2891 | 35.47% | 0.7104 | 0.1526 | 0.76059 | 4.4274 | 0.61492 | 0.032595 | 9.189%
161 | NYD, NAYAGARH | 38 | FATEGARH | 14056 | BIJIPUR | 14056201 | 99.3 | 55 | 34, 55 mm2 | 105 | 207 | 7677 | 7308 | 17.17% | 0.7104 | 0.30338 | 0.14027 | 3.8376 | 0.043795 | 0.027045 | 15.75%
162 | NYD, NAYAGARH | 39 | FATEGARH | 14056 | BHAPUR | 14056202 | 72.43 | 55 | 34, 55 mm2 | 100 | 145 | 3897 | 7280 | 36.92% | 0.7104 | 0.31942 | 0.31668 | 2.0455 | 0.14357 | 0.058655 | 15.89%
163 | NYD, NAYAGARH | 40 | FATEGARH | 14056 | GOLAPAKHARI | 14056203 | 67.42 | 55 | 34, 55 mm2 | 85 | 121 | 7677 | 5724 | 41.25% | 0.7104 | 0.26729 | 0.41617 | 4.7406 | 0.22179 | 0.06094 | 14.77%
164 | NYD, NAYAGARH | 41 | KANTILO | 14055 | KANTILO | 14055201 | 29.83 | 55 | 34, 55 mm2 | 75 | 86 | 3941 | 5312 | 46.53% | 0.7104 | 0.43912 | 0.53206 | 2.7581 | 0.33289 | 0.031507 | 6.772%
165 | NYD, NAYAGARH | 42 | KANTILO | 14055 | BANAPUR | 14055202 | 15.94 | 34 | 34 mm2 | 20 | 27 | 1208 | 2481 | 15.35% | 1.1325 | 0.09134 | 0.65838 | 3.1703 | 0.47845 | 0.0027432 | 1.787%
166 | NYD, NAYAGARH | 43 | KANTILO | 14055 | BENAGADIA | 14055203 | 11.29 | 55 | 34, 55 mm2 | 80 | 203 | 6130 | 6948 | 31.23% | 0.7104 | 0.34343 | 0.33475 | 4.0219 | 0.1566 | 0.0063825 | 2.044%
167 | NYD, NAYAGARH | 44 | GANIA | 14057 | GANIA | 14057201 | 81 | 55 | 34, 55 mm2 | 85 | 156 | 4397 | 5169 | 32.38% | 0.7104 | 0.27797 | 0.32674 | 2.7152 | 0.15075 | 0.049765 | 15.37%
168 | NYD, NAYAGARH | 45 | GANIA | 14057 | KOSKA | 14057202 | 74 | 55 | 34, 55 mm2 | 43 | 128 | 3151 | 4379 | 29.64% | 0.7104 | 0.13796 | 0.59123 | 3.8463 | 0.39788 | 0.030708 | 10.36%
169 | NYD, NAYAGARH | 46 | GANIA | 14057 | BALARAMPRASAD | 14057203 | 25 | 55 | 34, 55 mm2 | 52 | 70 | 2785 | 3519 | 46.01% | 0.7104 | 0.23311 | 0.7589 | 2.8111 | 0.61253 | 0.023356 | 5.076%
170 | BAED,BALUGAON | 3 | BALUGAON | 14075 | BANAPUR-2 | 14075203 | 21.51 | 55 | 55/34 | 120 | 153 | 6091 | 6365 | 26.39% | 0.7104 | 1.1548 | 0.18862 | 2.6642 | 0.066186 | 0.011564 | 4.382%
171 | BAED,BALUGAON | 4 | NACHUNI | 14078 | GAMBHARIMUNDA | 14078202 | 51.92 | 55 | 55/34 | 99 | 199 | 6609 | 6037 | 44.64% | 0.7104 | 1.0033 | 0.3867 | 3.504 | 0.19697 | 0.056536 | 12.67%
172 | BAED,BALUGAON | 5 | NACHUNI | 14078 | NAIRI | 14078203 | 35.34 | 55 | 55/34 | 100 | 158 | 5248 | 4106 | 29.99% | 0.7104 | 0.85206 | 0.25724 | 2.7546 | 0.10439 | 0.020809 | 6.938%
173 | BAED,BALUGAON | 6 | NACHUNI | 14078 | KAITHAPALLA | 14078201 | 14.16 | 55 | 55/34 | 25 | 47 | 1798 | 632 | 38.41% | 0.7104 | 0.20376 | 1.3176 | 3.7749 | 1.6523 | 0.0082485 | 2.148%
174 | BAED,BALUGAON | 7 | TANGI | 14076 | BADAPARI | 14076201 | 76 | 80 | 80/34 | 65 | 122 | 3498 | 1046 | 47.88% | 0.4862 | 0.42614 | 0.63171 | 2.8247 | 0.44558 | 0.055235 | 11.54%
175 | BAED,BALUGAON | 8 | TANGI | 14076 | TANGI CHANDAPUR | 14076202 | 15.11 | 55 | 55/34 | 78 | 205 | 8068 | 7877 | 31.21% | 0.7104 | 0.54727 | 0.34317 | 5.4291 | 0.16285 | 0.0084445 | 2.706%
176 | BAED,BALUGAON | 12 | CHANDPUR | 14185 | KAMAGURU | 14185201 | 35.28 | 34 | 34 | 78 | 92 | 2099 | 3464 | 25.46% | 1.1325 | 0.40683 | 0.27992 | 1.4125 | 0.11867 | 0.022905 | 8.997%
177 | BAED,BALUGAON | 13 | CHANDPUR | 14185 | CHANDAPUR | 14185202 | 22 | 34 | 34 | 78 | 22 | 801 | 1911 | 57.49% | 1.1325 | 0.5313 | 0.63213 | 0.53901 | 0.4461 | 0.053692 | 9.339%
178 | BAED,BALUGAON | 20 | DARPANARANPUR | 14205 | GOURANGAPUR | 14205201 | 70 | 34 | 34 | 30 | 120 | 2973 | 2157 | 36.57% | 1.1325 | 0.2359 | 1.0453 | 5.2016 | 1.0833 | 0.061368 | 16.78%
179 | BAED,BALUGAON | 21 | DARPANARANPUR | 14205 | DARPANARANPUR | 14205202 | 60 | 34 | 34 | 25 | 75 | 2025 | 2067 | 36.08% | 1.1325 | 0.12692 | 1.2379 | 4.2515 | 1.4734 | 0.049684 | 13.77%
180 | BAED,BALUGAON | 22 | RANAPUR | 14077 | RANAPUR | 14077202 | 13.73 | 55 | 55/34 | 63 | 65 | 2738 | 1798 | 43.02% | 0.7104 | 0.52965 | 0.58558 | 2.2811 | 0.39144 | 0.012032 | 2.797%
181 | BAED,BALUGAON | 25 | BHUSANDAPUR | 14206 | BHUSANDAPUR | 14206201 | 27 | 34 | 34 | 90 | 60 | 2350 | 1982 | 44.41% | 1.1325 | 0.57837 | 0.42319 | 1.3705 | 0.22791 | 0.044822 | 10.09%
182 | BAED,BALUGAON | 26 | BHUSANDAPUR | 14206 | HARIPUR | 14206202 | 10 | 34 | 34 | 20 | 30 | 1100 | 830 | 47.63% | 1.1325 | 0.16363 | 2.0426 | 2.8868 | 3.7463 | 0.013475 | 2.829%
183 | PED, PURI | 1 | TALABANIA | 14064 | SRI MANDIRA | 14064201 | 6.66 | 55 | 55/34 | 130 | 10 | 2325 | 6123 | 32.3% | 0.7104 | 0.49446 | 0.21306 | 0.93873 | 0.078929 | 0.0050111 | 1.552%
184 | PED, PURI | 2 | TALABANIA | 14064 | MAUSIMAA | 14064203 | 5 | 55 | 55/34 | 175 | 21 | 7825 | 3739 | 36.36% | 0.7104 | 0.47608 | 0.17819 | 2.347 | 0.061042 | 0.0052724 | 1.45%
185 | PED, PURI | 3 | TALABANIA | 14064 | SHREE GUNDICHA | 14064202 | 8 | 55 | 55/34 | 195 | 27 | 5288 | 4230 | 35.48% | 0.7104 | 0.36865 | 0.15603 | 1.4234 | 0.050682 | 0.0086964 | 2.451%
186 | PED, PURI | 4 | TALABANIA | 14064 | KACHERI | 14064205 | 4.32 | 55 | 55 | 55 | 30 | 4324 | 2287 | 18.52% | 0.7104 | 0.70515 | 0.28874 | 4.1265 | 0.12445 | 0.00091732 | 0.4954%
187 | PED, PURI | 5 | TALABANIA | 14064 | RAJBHABAN | 14064204 | 7 | 55 | 55/34 | 160 | 72 | 11502 | 3000 | 30.47% | 0.7104 | 0.78348 | 0.16332 | 3.7732 | 0.054003 | 0.0054587 | 1.792%
188 | PED, PURI | 10 | KACHERI | 14065 | SWARGADWAR-1 | 14065201 | 3 | 80 | 80 | 80 | 38 | 4328 | 1204 | 26.98% | 0.4862 | 0.5522 | 0.28929 | 2.8396 | 0.12481 | 0.00092513 | 0.3428%
189 | PED, PURI | 11 | KACHERI | 14065 | SWARGADWAR-2 | 14065202 | 4.1 | 34 | 21 / 44 | 190 | 34 | 7611 | 2548 | 38.54% | 1.1325 | 1.3378 | 0.17395 | 2.1026 | 0.058998 | 0.0078522 | 2.038%
190 | PED, PURI | 12 | KACHERI | 14065 | DOLAMANDAP | 14065203 | 1.163 | 55 | 55 | 60 | 9 | 2150 | 813 | 56.15% | 0.7104 | 0.4943 | 0.80258 | 1.8808 | 0.67583 | 0.0015961 | 0.2843%
191 | PED, PURI | 13 | KACHERI | 14065 | DUTTATOTA | 14065204 | 7.5 | 55 | 55/34 | 120 | 39 | 4841 | 2551 | 48.26% | 0.7104 | 1.1488 | 0.34495 | 2.1175 | 0.16418 | 0.010002 | 2.072%
192 | PED, PURI | 15 | KACHERI | 14065 | SEABEACH U/G | 14065206 | 6 | 400 | 400 / 95 | 160 | 22 | 6413 | 256 | 29.56% | 0.00736 | 0.38481 | 0.15846 | 2.1038 | 0.051781 | 4.648e-05 | 0.01572%
193 | PED, PURI | 16 | BALIAPANDA | 14066 | PRACHI | 14066204 | 16.5 | 100 | 100/55 | 80 | 62 | 10255 | 1261 | 44.88% | 0.3878 | 0.88528 | 0.48115 | 6.7283 | 0.28144 | 0.0091513 | 2.039%
194 | PED, PURI | 17 | BALIAPANDA | 14066 | LOKANATHA | 14066201 | 18 | 55 | 55 | 170 | 25 | 2140 | 2299 | 43.78% | 0.7104 | 0.80015 | 0.22086 | 0.66073 | 0.083194 | 0.024411 | 5.576%
195 | PED, PURI | 18 | BALIAPANDA | 14066 | PHD | 14066203 | 0.24 | 34 | 34 | 20 | 2 | 500 | 365 | 53.4% | 1.1325 | 0.13538 | 2.29 | 1.3122 | 4.6533 | 0.0004017 | 0.07522%
196 | PED, PURI | 19 | BALIAPANDA | 14066 | BALIAPANDA KACHERI | 14066202 | 4.32 | 55 | 55 | 55 | 44 | 4742 | 2369 | 26.48% | 0.7104 | 0.91048 | 0.41297 | 4.5254 | 0.21903 | 0.0016145 | 0.6096%
197 | PED, PURI | 21 | BALIAPANDA | 14066 | PRACHI U/G | 14066206 | 6.3 | 400 | 400/95 | 40 | 25 | 4325 | 26 | 20.92% | 0.00736 | 0.38668 | 0.44861 | 5.6753 | 0.25072 | 1.4769e-05 | 0.007059%
198 | PED, PURI | 22 | SRI RAM NAGAR | 14070 | BALIGUALI | 14070202 | 20 | 55 | 55/34 | 100 | 43 | 2662 | 1985 | 34.76% | 0.7104 | 0.39077 | 0.29811 | 1.3972 | 0.13072 | 0.014747 | 4.243%
199 | PED, PURI | 24 | SRI RAM NAGAR | 14070 | PKRIT | 14070201 | 15 | 55 | 55/34 | 120 | 39 | 3489 | 3450 | 44.51% | 0.7104 | 1.0058 | 0.31815 | 1.5261 | 0.1446 | 0.017618 | 3.958%
200 | PED, PURI | 25 | SRI RAM NAGAR | 14070 | TOSHALI | 14070204 | 40 | 55 | 55/34 | 40 | 56 | 2992 | 470 | 37.24% | 0.7104 | 0.31289 | 0.79844 | 3.9261 | 0.66969 | 0.024176 | 6.492%
201 | PED, PURI | 26 | CHARINALA | 14067 | CHARINALA KHANDIABANDHA | 14067202 | 21 | 55 | 55/34 | 150 | 42 | 2732 | 3217 | 37.33% | 0.7104 | 0.24053 | 0.21344 | 0.95598 | 0.079135 | 0.021091 | 5.65%
202 | PED, PURI | 27 | CHARINALA | 14067 | CHARINALA HAREKRUSHNAPUR | 14067203 | 26 | 55 | 55/34 | 80 | 94 | 4005 | 3310 | 49.61% | 0.7104 | 1.2634 | 0.53187 | 2.6277 | 0.33268 | 0.031226 | 6.294%
203 | PED, PURI | 30 | BRAHMAGIRI | 14068 | BASUDEIPUR | 14068204 | 18.3 | 55 | 55/34 | 70 | 129 | 4361 | 3364 | 46.32% | 0.7104 | 0.57948 | 0.56747 | 3.27 | 0.37111 | 0.018771 | 4.053%
204 | PED, PURI | 31 | BRAHMAGIRI | 14068 | ALARNATH | 14068202 | 20 | 55 | 55 | 66 | 27 | 1800 | 471 | 51.75% | 0.7104 | 0.35129 | 0.67251 | 1.4315 | 0.49632 | 0.02439 | 4.713%
205 | PED, PURI | 33 | BRAHMAGIRI | 14068 | PALANKA | 14068203 | 42.64 | 55 | 55/34 | 40 | 32 | 1386 | 989 | 54.76% | 0.7104 | 0.34667 | 1.1741 | 1.8187 | 1.3377 | 0.051479 | 9.401%
206 | PED, PURI | 36 | KANASA | 14074 | KARAMALA | 14074202 | 35 | 55 | 55/34 | 82 | 164 | 6027 | 332 | 53% | 0.7104 | 1.0283 | 0.55428 | 3.8579 | 0.35664 | 0.047343 | 8.933%
207 | PED, PURI | 38 | KANASA | 14074 | KANASA | 14074201 | 25 | 55 | 55/34 | 95 | 55 | 2551 | 2065 | 54.01% | 0.7104 | 0.62867 | 0.48759 | 1.4094 | 0.28771 | 0.036616 | 6.78%
208 | PED, PURI | 46 | CHANDANPUR | 14071 | CHANDANPUR | 14071201 | 40 | 55 | 55/34 | 91 | 111 | 4645 | 3020 | 44.04% | 0.7104 | 0.81333 | 0.41503 | 2.6792 | 0.2208 | 0.041255 | 9.369%
209 | PED, PURI | 48 | CHANDANPUR | 14071 | BIRABALABHADRAPUR | 14071203 | 7 | 55 | 55 | 15 | 18 | 1975 | 2842 | 52.53% | 0.7104 | 1.041 | 3.0035 | 6.9109 | 7.8175 | 0.0069451 | 1.322%
210 | PED, PURI | 49 | SAKHIGOPAL | 14072 | BAZAR | 14072204 | 22 | 55 | 55/34 | 91 | 83 | 3905 | 3091 | 37.1% | 0.7104 | 0.71009 | 0.3497 | 2.2524 | 0.16777 | 0.017241 | 4.647%
211 | PED, PURI | 51 | SAKHIGOPAL | 14072 | SATASANKHA | 14072202 | 36 | 55 | 55/34 | 61 | 122 | 4804 | 4154 | 47.43% | 0.7104 | 0.85067 | 0.6668 | 4.1336 | 0.48905 | 0.036953 | 7.792%
212 | PED, PURI | 53 | KUMARESWAR | 14208 | BALANGA | 14208201 | 40.8 | 55 | 55/34 | 122 | 94 | 4586 | 3636 | 35.55% | 0.7104 | 0.79239 | 0.24993 | 1.973 | 0.099957 | 0.034239 | 9.631%
213 | PED, PURI | 54 | KHAJURIA | 14225 | KHAJURIA | 14225201 | 15 | 55 | 55 | 25 | 52 | 2500 | 41 | 48.74% | 0.7104 | 0.24069 | 1.6719 | 5.2488 | 2.5707 | 0.013594 | 2.789%
214 | CDD-1, CUTTACK | 2 | KALINGA | 14084 | CANTONMENT 2 | 14084203 | 0.8 | 55 | 55 | 32 | 5 | 1200 | 218 | 14.97% | 0.7104 | 0.20177 | 0.40112 | 1.9683 | 0.20894 | 9.6548e-05 | 0.06451%
215 | CDD-1, CUTTACK | 3 | KALINGA | 14084 | GORAKABAR | 14084204 | 3 | 100 | 100/55 | 45 | 19 | 2963 | 1409 | 15.52% | 0.3878 | 0.55932 | 0.29588 | 3.456 | 0.12921 | 0.0002417 | 0.1557%
216 | CDD-1, CUTTACK | 4 | KALINGA | 14084 | JNI | 14084205 | 0.4 | 55 | 55 | 35 | 5 | 2100 | 6 | 4.724% | 0.7104 | 0.024897 | 0.11575 | 3.1493 | 0.033869 | 9.3611e-06 | 0.01982%
217 | CDD-1, CUTTACK | 5 | KALINGA | 14084 | CANTENMENT 1 | 14084206 | 6.2 | 80 | 100/80/55 | 200 | 43 | 9264 | 3528 | 16.55% | 0.4862 | 1.0582 | 0.070987 | 2.4312 | 0.018229 | 0.0017452 | 1.054%
218 | CDD-1, CUTTACK | 8 | KALINGA | 14084 | DD UG | 14084207 | 2.5 | 100 | 95 UG | 8 | 2 | 500 | 3 | 5.895% | 0.3878 | 0.42256 | 0.63197 | 3.2805 | 0.4459 | 2.1968e-05 | 0.03727%
219 | CDD-1, CUTTACK | 9 | KALINGA | 14084 | DD OH | 14084209 | 2 | 80 | 80/55 | 156 | 13 | 2188 | 729 | 5.895% | 0.4862 | 0.42256 | 0.032409 | 0.73618 | 0.007322 | 0.00013758 | 0.2334%
220 | CDD-1, CUTTACK | 10 | KALINGA | 14084 | SRI VIHAR | 14084210 | 0.2 | 100 | 95 UG | 27 | 2 | 1000 | 643 | 15.17% | 0.3878 | 0.14563 | 0.48175 | 1.944 | 0.28202 | 1.2661e-05 | 0.008348%
221 | CDD-1, CUTTACK | 11 | MATAMATHA | 14209 | CIRCUIT HOUSE | 14209201 | 0.7 | 100 | 100/55 | 43 | 7 | 2350 | 310 | 13.63% | 0.3878 | 0.35633 | 0.2718 | 2.8685 | 0.11346 | 4.5217e-05 | 0.03318%
222 | CDD-1, CUTTACK | 12 | MATAMATHA | 14209 | CB9 | 14209202 | 2.8 | 80 | 80/55 | 10 | 40 | 7381 | 529 | 11.56% | 0.4862 | 0.69367 | 0.99134 | 38.7413 | 0.98447 | 0.00010642 | 0.09206%
223 | CDD-1, CUTTACK | 13 | MATAMATHA | 14209 | MUSIUM | 14209203 | 2.6 | 80 | 80/100 | 19 | 7 | 1765 | 244 | 15.72% | 0.4862 | 0.12683 | 0.70953 | 4.8759 | 0.54465 | 0.00019735 | 0.1256%
224 | CDD-1, CUTTACK | 16 | MEDICAL | 14083 | RANIHAT | 14083202 | 3.5 | 80 | 80/55 | 140 | 35 | 6224 | 1354 | 14.56% | 0.4862 | 0.87626 | 0.089213 | 2.3335 | 0.02421 | 0.00064114 | 0.4403%
225 | CDD-1, CUTTACK | 19 | MEDICAL | 14083 | MEDICAL-1 | 14083204 | 1.5 | 80 | 80/55 | 95 | 29 | 9555 | 42 | 10.63% | 0.4862 | 0.87447 | 0.096011 | 5.2792 | 0.026577 | 0.00013889 | 0.1306%
226 | CDD-1, CUTTACK | 20 | JOBRA | 14082 | ENGG SCHOOL | 14082201 | 4.5 | 80 | 80/55 | 109 | 37 | 4885 | 1405 | 15.63% | 0.4862 | 0.34433 | 0.12296 | 2.3523 | 0.036686 | 0.0007572 | 0.4846%
227 | CDD-1, CUTTACK | 21 | JOBRA | 14082 | JOBRA BARRAGE | 14082204 | 5.5 | 100 | 80/100 | 188 | 34 | 4664 | 1864 | 13.93% | 0.3878 | 0.92467 | 0.063545 | 1.3021 | 0.015939 | 0.00095408 | 0.6849%
228 | CDD-1, CUTTACK | 22 | JOBRA | 14082 | RAVENSHAW | 14082203 | 3.5 | 80 | 80/55 | 122 | 24 | 4312 | 754 | 14.13% | 0.4862 | 0.69767 | 0.099339 | 1.8551 | 0.027763 | 0.00055833 | 0.3951%
229 | CDD-1, CUTTACK | 23 | JOBRA | 14082 | MATAMATHA | 14082205 | 1.5 | 80 | 80 | 9 | 3 | 450 | 1429 | 13.5% | 0.4862 | 0.65767 | 1.2862 | 2.6244 | 1.5808 | 7.4146e-05 | 0.05493%
230 | CDD-1, CUTTACK | 27 | CDA | 14080 | SATICHOURA | 14080201 | 10 | 80 | 80/55 | 191 | 39 | 8825 | 3019 | 13.49% | 0.4862 | 1.2621 | 0.060594 | 2.4252 | 0.015056 | 0.0021204 | 1.571%
231 | CDD-1, CUTTACK | 28 | BIDANASI | 14085 | BIDANASI | 14085202 | 8 | 80 | 80/55 | 124 | 86 | 3879 | 2800 | 13.43% | 0.4862 | 0.24068 | 0.092885 | 1.6419 | 0.025479 | 0.0012099 | 0.901%
232 | CDD-1, CUTTACK | 29 | BIDANASI | 14085 | CDA | 14085201 | 13 | 80 | 80/55 | 185 | 30 | 6276 | 1892 | 10.96% | 0.4862 | 0.397 | 0.050797 | 1.7806 | 0.012224 | 0.0020996 | 1.916%
233 | CDD-1, CUTTACK | 30 | BIDANASI | 14085 | NARAJ | 14085203 | 8 | 80 | 80/55 | 25 | 7 | 2225 | 118 | 11.42% | 0.4862 | 0.3051 | 0.39162 | 4.6714 | 0.20102 | 0.00038802 | 0.3399%
234 | CDD-1, CUTTACK | 32 | SISHUBHABAN | 14081 | CHANDINICHOWK | 14081203 | 2 | 100 | 100 | 162 | 15 | 4027 | 652 | 21.51% | 0.3878 | 0.616 | 0.11387 | 1.3047 | 0.033149 | 0.00053576 | 0.2491%
235 | CDD-1, CUTTACK | 34 | SISHUBHABAN | 14081 | TOWNHALL | 14081202 | 1 | 100 | 100 | 236 | 40 | 9102 | 2489 | 12.79% | 0.3878 | 0.348 | 0.04647 | 2.0243 | 0.011022 | 0.00018902 | 0.1478%
236 | CDD-2, CUTTACK | 2 | JAGATPUR | 14088 | NADIKULA | 14088203 | 1.8 | 100 | 100/80/55 | 225 | 58 | 17750 | 163 | 6.831% | 0.3878 | 0.8632 | 0.026039 | 4.1407 | 0.0057503 | 0.00016135 | 0.2362%
237 | CDD-2, CUTTACK | 4 | JAGATPUR | 14088 | BARRAGE | 14088202 | 15.8 | 100 | 100/80/55 | 120 | 75 | 8064 | 1985 | 12.13% | 0.3878 | 0.5276 | 0.086696 | 3.5272 | 0.023352 | 0.001636 | 1.349%
238 | CDD-2, CUTTACK | 5 | KALYANI NAGAR | 14089 | CHAULIAGANJ-1 | 14089205 | 20.5 | 100 | 100/80/55 | 140 | 36 | 4759 | 2944 | 14.77% | 0.3878 | 0.959 | 0.090471 | 1.7842 | 0.024642 | 0.0030488 | 2.064%
239 | CDD-2, CUTTACK | 6 | KALYANI NAGAR | 14089 | RING-2 | 14089204 | 3.41 | 100 | 100/80/55 | 120 | 23 | 5275 | 1349 | 14.03% | 0.3878 | 0.7205 | 0.10024 | 2.3073 | 0.028088 | 0.00042469 | 0.3028%
240 | CDD-2, CUTTACK | 7 | KALYANI NAGAR | 14089 | RING-1 | 14089203 | 4.047 | 80 | 80/55 | 210 | 36 | 6578 | 2615 | 15.82% | 0.4862 | 0.54267 | 0.064607 | 1.6441 | 0.016261 | 0.0011204 | 0.7082%
241 | CDD-2, CUTTACK | 8 | KALYANI NAGAR | 14089 | KALYANINAGAR | 14089201 | 4.1 | 80 | 100/80/55 | 150 | 20 | 4175 | 1700 | 16.56% | 0.4862 | 0.48633 | 0.094673 | 1.4609 | 0.026105 | 0.00092968 | 0.5615%
242 | CDD-2, CUTTACK | 9 | KALYANI NAGAR | 14089 | CHAULIAGANJ-2 | 14089206 | 5.9 | 100 | 100/80/55 | 65 | 31 | 5626 | 3031 | 17.16% | 0.3878 | 0.33633 | 0.22646 | 4.543 | 0.086322 | 0.00066258 | 0.386%
243 | CDD-2, CUTTACK | 10 | KALYANI NAGAR | 14089 | MAHANADI | 14089202 | 5 | 80 | 80 | 60 | 13 | 2089 | 679 | 10.97% | 0.4862 | 0.19344 | 0.15683 | 1.8275 | 0.051041 | 0.00035468 | 0.3233%
244 | CDD-2, CUTTACK | 13 | BADAMBADI | 14087 | BADAMBADI-1 | 14087201 | 2 | 100 | 100/80/55 | 140 | 41 | 6439 | 2476 | 13.45% | 0.3878 | 1.0503 | 0.082394 | 2.4141 | 0.02191 | 0.00026446 | 0.1966%
245 | CDD-2, CUTTACK | 15 | OGP | 14090 | OGP | 14090203 | 0.92 | 80 | 80 | 20 | 2 | 500 | 5 | 5.533% | 0.4862 | 0.25867 | 0.23728 | 1.3122 | 0.092497 | 1.3141e-05 | 0.02375%
246 | CDD-2, CUTTACK | 17 | OGP | 14090 | INDUSTRIAL2 | 14090202 | 15.6 | 100 | 100/80/55 | 75 | 20 | 2146 | 1688 | 14.76% | 0.3878 | 0.389 | 0.1688 | 1.5019 | 0.056555 | 0.0015281 | 1.035%
247 | CDD-2, CUTTACK | 18 | OGP | 14090 | KATHAJODI | 14090204 | 2.7 | 100 | 100/80/55 | 80 | 7 | 1400 | 167 | 14.03% | 0.3878 | 0.7205 | 0.15037 | 0.91854 | 0.048162 | 0.00025626 | 0.1827%
248 | CDD-2, CUTTACK | 19 | 42 MAUZA | 14092 | BENTKAR | 14092202 | 38.7 | 55 | 55/34 | 55 | 49 | 2816 | 2850 | 25.79% | 0.7104 | 0.58096 | 0.40223 | 2.6874 | 0.20988 | 0.013859 | 5.373%
249 | CDD-2, CUTTACK | 20 | 42 MAUZA | 14092 | CHANDULI | 14092201 | 30.5 | 55 | 55/34 | 40 | 47 | 2420 | 1940 | 27.41% | 0.7104 | 0.40539 | 0.58765 | 3.1755 | 0.39379 | 0.01084 | 3.955%
250 | CDD-2, CUTTACK | 21 | 42 MAUZA | 14092 | KALAPADA | 14092204 | 23.6 | 55 | 55/34 | 25 | 34 | 1894 | 1263 | 25.6% | 0.7104 | 0.23798 | 0.87828 | 3.9765 | 0.79276 | 0.0065958 | 2.576%
251 | CDD-2, CUTTACK | 22 | 42 MAUZA | 14092 | JHINKIRIA | 14092203 | 19.8 | 55 | 55/34 | 30 | 21 | 1502 | 1458 | 28.44% | 0.7104 | 0.27662 | 0.81314 | 2.6279 | 0.69158 | 0.0069516 | 2.444%
252 | CDD-2, CUTTACK | 23 | KANDARPUR | 14093 | KANDARPUR | 14093202 | 8.2 | 55 | 55/34 | 80 | 70 | 2961 | 2183 | 27.26% | 0.7104 | 0.4311 | 0.29223 | 1.9427 | 0.12677 | 0.0037526 | 1.377%
253 | CDD-2, CUTTACK | 24 | KANDARPUR | 14093 | ALL INDIA RADIO | 14093201 | 14.8 | 55 | 55/34 | 85 | 65 | 4443 | 1807 | 24.98% | 0.7104 | 0.8579 | 0.25201 | 2.7436 | 0.10121 | 0.0061046 | 2.444%
254 | CDD-2, CUTTACK | 25 | KANDARPUR | 14093 | PARAMAHANSA | 14093203 | 42.9 | 55 | 55/34 | 80 | 80 | 3093 | 3201 | 37.48% | 0.7104 | 0.32787 | 0.40181 | 2.0293 | 0.20952 | 0.032449 | 8.658%
255 | CDD-2, CUTTACK | 26 | KANDARPUR | 14093 | AYATPUR | 14093204 | 14.6 | 55 | 55/34 | 60 | 59 | 2406 | 1732 | 27.52% | 0.7104 | 0.4488 | 0.39336 | 2.1048 | 0.20246 | 0.0060023 | 2.181%
256 | CDD-2, CUTTACK | 27 | KISHAN NAGAR | 14094 | KISHANNAGAR | 14094201 | 12.4 | 55 | 55/34 | 90 | 19 | 602 | 368 | 27.56% | 0.7104 | 0.067 | 0.26265 | 0.35109 | 0.10772 | 0.0061029 | 2.214%
257 | CDD-2, CUTTACK | 28 | KISHAN NAGAR | 14094 | MALIPUR | 14094202 | 17.55 | 55 | 55/34 | 80 | 31 | 1349 | 1287 | 28.86% | 0.7104 | 0.21007 | 0.30942 | 0.88508 | 0.13847 | 0.0087732 | 3.04%
258 | CDD-2, CUTTACK | 29 | KISHAN NAGAR | 14094 | SOMPUR | 14094203 | 30.35 | 55 | 55/34 | 75 | 48 | 2254 | 2075 | 32.09% | 0.7104 | 0.13319 | 0.36694 | 1.5774 | 0.1811 | 0.01744 | 5.435%
259 | CDD-2, CUTTACK | 30 | KISHAN NAGAR | 14094 | RAMCHANDRAPUR | 14094204 | 17.7 | 55 | 55/34 | 60 | 17 | 954 | 738 | 27.03% | 0.7104 | 0.021813 | 0.38631 | 0.83456 | 0.19665 | 0.0070681 | 2.615%
260 | CDD-2, CUTTACK | 31 | CRRI | 14091 | MAHANADI VIHAR | 14091202 | 4 | 100 | 100/80/55/34 | 30 | 7 | 663 | 750 | 12.38% | 0.3878 | 0.36281 | 0.354 | 1.16 | 0.17105 | 0.00018961 | 0.1531%
261 | CDD-2, CUTTACK | 33 | CRRI | 14091 | CRRI | 14091203 | 2.4 | 100 | 100/80/55/34 | 70 | 9 | 2013 | 35 | 5.483% | 0.3878 | 0.18419 | 0.067176 | 1.5094 | 0.017045 | 6.1723e-05 | 0.1126%
262 | CDD-2, CUTTACK | 34 | CRRI | 14091 | NAYABAZAR | 14091204 | 7.7 | 100 | 100/80/55/34 | 200 | 50 | 6838 | 3429 | 17.79% | 0.3878 | 1.1222 | 0.076275 | 1.7946 | 0.019909 | 0.0018882 | 1.062%
263 | CDD-2, CUTTACK | 35 | MATTAGAJAPUR | 14211 | POPARADA | 14211201 | 2.8 | 55 | 55/80 | 40 | 13 | 1299 | 700 | 20.97% | 0.7104 | 0.22967 | 0.44956 | 1.7045 | 0.25159 | 0.00063578 | 0.3032%
264 | CDD-2, CUTTACK | 36 | MATTAGAJAPUR | 14211 | MATTAGAJA PUR | 14211202 | 5.2 | 55 | 55/80 | 30 | 9 | 400 | 367 | 22.43% | 0.7104 | 0.11733 | 0.64131 | 0.69984 | 0.45728 | 0.0012071 | 0.5381%
265 | CDD-2, CUTTACK | 42 | MAHANADI VIHAR ODSSP | 14242 | MAHANADI BIHAR-2 | 14242202 | 5 | 100 | 100/80/55 | 110 | 29 | 4488 | 1580 | 12.83% | 0.3878 | 0.8223 | 0.10001 | 2.1415 | 0.028005 | 0.00052171 | 0.4067%
266 | CDD-2, CUTTACK | 43 | MAHANADI VIHAR ODSSP | 14242 | SIKHARPUR | 14242203 | 2.6 | 100 | 100/80/55/34 | 80 | 21 | 2701 | 1621 | 12.08% | 0.3878 | 0.87098 | 0.12945 | 1.7721 | 0.039298 | 0.00020135 | 0.1667%
267 | CDD-2, CUTTACK | 44 | MAHANADI VIHAR ODSSP | 14242 | GANDARPUR | 14242204 | 2.5 | 100 | 100/80/55/34 | 65 | 12 | 1652 | 1435 | 12.17% | 0.3878 | 0.35373 | 0.16055 | 1.334 | 0.052729 | 0.00017149 | 0.1409%
268 | CED, CUTTACK | 3 | CHHATISIA | 14103 | KUSPANGI | 14103203 | 32.3 | 34 | 34 | 50 | 74 | 6744 | 990 | 34.36% | 1.1325 | 0.71443 | 0.5894 | 7.0796 | 0.39579 | 0.028739 | 8.364%
269 | CED, CUTTACK | 4 | BADACHANA | 14105 | CHANDIKHOL | 14105204 | 23 | 34 | 34/55 | 140 | 80 | 5759 | 2763 | 68.16% | 1.1325 | 0.98636 | 0.41756 | 2.1591 | 0.223 | 0.090396 | 13.26%
270 | CED, CUTTACK | 7 | BADACHANA | 14105 | BADACHANA | 14105202 | 25 | 55 | 34/55/80 | 70 | 102 | 5310 | 3500 | 22.53% | 0.7104 | 0.74994 | 0.276 | 3.9816 | 0.11614 | 0.0080252 | 3.562%
271 | CED, CUTTACK | 8 | BADACHANA | 14105 | SAKUNTALAPUR | 14105203 | 40 | 55 | 34/55/80 | 115 | 40 | 2061 | 2490 | 22.53% | 0.7104 | 0.74994 | 0.168 | 0.94067 | 0.056179 | 0.016764 | 7.442%
272 | CED, CUTTACK | 10 | CHHATIA | 14108 | BAIREE | 14108202 | 60 | 55 | 34/55 | 176 | 182 | 6900 | 6525 | 49.87% | 0.7104 | 1.335 | 0.24302 | 2.0578 | 0.09585 | 0.10048 | 20.15%
273 | CED, CUTTACK | 14 | CHOUDWAR | 14184 | CHOUDWAR | 14184202 | 4.8 | 80 | 80/100 | 100 | 18 | 3464 | 2267 | 52.41% | 0.4862 | 0.8795 | 0.44951 | 1.8182 | 0.25155 | 0.0046613 | 0.8894%
274 | CED, CUTTACK | 15 | CHOUDWAR | 14184 | CITY BARRAGE | 14184201 | 20.8 | 55 | 34/55 | 110 | 54 | 5536 | 3703 | 54.31% | 0.7104 | 0.97244 | 0.42344 | 2.6416 | 0.22813 | 0.032387 | 5.963%
275 | CED, CUTTACK | 16 | CHOUDWAR | 14184 | OTM | 14184204 | 56.15 | 55 | 34/55/80 | 125 | 73 | 7469 | 2989 | 46.22% | 0.7104 | 1.3514 | 0.31711 | 3.1363 | 0.14387 | 0.071197 | 15.4%
276 | CED, CUTTACK | 17 | CHOUDWAR | 14184 | LOCAL | 14184205 | 16.3 | 55 | 34/55/80 | 200 | 64 | 6775 | 5832 | 53.83% | 0.7104 | 1.5435 | 0.23085 | 1.778 | 0.088804 | 0.03266 | 6.067%
277 | CED, CUTTACK | 18 | CHOUDWAR | 14184 | ARC | 14184203 | 16.8 | 55 | 34/55 | 40 | 51 | 7941 | 1267 | 57.32% | 0.7104 | 0.77494 | 1.229 | 10.4202 | 1.4542 | 0.022049 | 3.847%
278 | CED, CUTTACK | 19 | TANGI | 14107 | BHATIMUNDA | 14107202 | 56.65 | 55 | 34/55/80 | 125 | 66 | 3733 | 3451 | 57.91% | 0.7104 | 1.2227 | 0.39735 | 1.5675 | 0.20578 | 0.10274 | 17.74%
279 | CED, CUTTACK | 21 | TANGI | 14107 | MANGULI | 14107203 | 56.57 | 55 | 34/55/80 | 180 | 57 | 3624 | 2907 | 28.07% | 0.7104 | 1.1814 | 0.13374 | 1.0568 | 0.041059 | 0.042449 | 15.12%
280 | CED, CUTTACK | 22 | TANGI | 14107 | NH5 | 14107204 | 22 | 80 | 34/55/80 | 45 | 14 | 743 | 794 | 55.4% | 0.4862 | 0.43962 | 1.0558 | 0.86663 | 1.1029 | 0.018969 | 3.424%
281 | CED, CUTTACK | 23 | TANGI | 14107 | TANGI | 14107205 | 26 | 80 | 34/55/80 | 85 | 25 | 2138 | 2493 | 38.49% | 0.4862 | 0.4943 | 0.38834 | 1.3202 | 0.19831 | 0.014381 | 3.737%
282 | CED, CUTTACK | 24 | DAMODARPUR | 14101 | SUNDARGAON | 14101202 | 59 | 80 | 34/55/80 | 124 | 101 | 4652 | 2362 | 35.54% | 0.4862 | 0.72307 | 0.24583 | 1.9691 | 0.097511 | 0.03415 | 9.608%
283 | CED, CUTTACK | 25 | DAMODARPUR | 14101 | NIRTAR | 14101203 | 4.5 | 55 | 55 | 12 | 5 | 1450 | 1 | 2.021% | 0.7104 | 0.0553 | 0.14443 | 6.3423 | 0.045573 | 1.6658e-05 | 0.08243%
284 | CED, CUTTACK | 26 | DAMODARPUR | 14101 | GOBINDPUR | 14101201 | 35 | 55 | 34/55 | 55 | 70 | 4502 | 3151 | 48.72% | 0.7104 | 0.84036 | 0.75967 | 4.2964 | 0.61361 | 0.036645 | 7.522%
285 | CED, CUTTACK | 27 | ADASPUR | 14104 | NODA DIMIRI/SITHALO | 14104202 | 4 | 80 | 80 | 15 | 9 | 211 | 72 | 45.38% | 0.4862 | 0.58604 | 2.5947 | 0.73833 | 5.9048 | 0.0020516 | 0.4521%
286 | CED, CUTTACK | 28 | ADASPUR | 14104 | UTARANA/ERANCHA | 14104203 | 62 | 55 | 55 | 60 | 43 | 2455 | 3363 | 62.45% | 0.7104 | 0.08924 | 0.89266 | 2.1476 | 0.81601 | 0.10274 | 16.45%
287 | CED, CUTTACK | 29 | ADASPUR | 14104 | ADASPUR & UN COLL | 14104201 | 74 | 55 | 34/55 | 190 | 167 | 9809 | 5726 | 42.26% | 0.7104 | 0.19419 | 0.19075 | 2.7098 | 0.067257 | 0.10135 | 23.98%
288 | CED, CUTTACK | 30 | NIALI | 14106 | KAPASI | 14106203 | 95 | 80 | 34/55/80 | 160 | 161 | 7425 | 5680 | 62.49% | 0.4862 | 1.0492 | 0.33499 | 2.4358 | 0.15677 | 0.14719 | 23.55%
289 | CED, CUTTACK | 31 | NIALI | 14106 | TOLA | 14106204 | 52 | 80 | 34/55/80 | 110 | 101 | 5788 | 4574 | 59.87% | 0.4862 | 0.88014 | 0.46677 | 2.7618 | 0.26765 | 0.065013 | 10.86%
290 | CED, CUTTACK | 32 | NIALI | 14106 | NIALI TOWN | 14106202 | 68 | 80 | 34/55/80 | 110 | 138 | 10129 | 6113 | 57.64% | 0.4862 | 1.6251 | 0.44941 | 4.8332 | 0.25145 | 0.079872 | 13.86%
291 | CED, CUTTACK | 33 | NIALI | 14106 | KALIAGHAI | 14106201 | 57 | 80 | 34/55/80 | 230 | 94 | 4879 | 4266 | 56.03% | 0.4862 | 0.81238 | 0.20894 | 1.1134 | 0.076713 | 0.089299 | 15.94%
292 | CED, CUTTACK | 34 | BALICHANDRAPUR | 14109 | CHARINANGALA | 14109202 | 42 | 80 | 34/55/80 | 125 | 114 | 5235 | 3644 | 69.31% | 0.4862 | 0.66004 | 0.47555 | 2.1982 | 0.27603 | 0.06993 | 10.09%
293 | CED, CUTTACK | 35 | BALICHANDRAPUR | 14109 | RUKUTIPATA | 14109203 | 14 | 55 | 34/55 | 48 | 55 | 2857 | 1920 | 68.42% | 0.7104 | 0.39289 | 1.2225 | 3.1241 | 1.4401 | 0.026202 | 3.83%
294 | CED, CUTTACK | 36 | BALICHANDRAPUR | 14109 | BALICHADRAPUR | 14109201 | 10 | 80 | 80 | 70 | 72 | 3663 | 4376 | 46.23% | 0.4862 | 0.72974 | 0.56641 | 2.7466 | 0.36994 | 0.006998 | 1.514%
295 | CED, CUTTACK | 37 | BALICHANDRAPUR | 14109 | MANITRI | 14109204 | 18 | 55 | 34/55 | 55 | 29 | 1622 | 1323 | 70.47% | 0.7104 | 0.24089 | 1.0989 | 1.5479 | 1.1857 | 0.036419 | 5.168%
296 | CED, CUTTACK | 38 | BALICHANDRAPUR | 14109 | BANDARESWARA | 14109205 | 40 | 55 | 55/80 | 130 | 100 | 4977 | 4050 | 40.12% | 0.7104 | 0.68972 | 0.2647 | 2.0095 | 0.109 | 0.041561 | 10.36%
297 | CED, CUTTACK | 40 | BALIKUDA | 14102 | 42 MOUZA | 14102201 | 45 | 55 | 55/80 | 280 | 91 | 6922 | 5968 | 40.29% | 0.7104 | 1.4824 | 0.1234 | 1.2976 | 0.036862 | 0.073358 | 18.21%
298 | CED, CUTTACK | 42 | KASARDA | 14220 | ERANCHA | 14220201 | 73 | 55 | 55 | 74 | 107 | 4630 | 2662 | 66.13% | 0.7104 | 0.21375 | 0.76639 | 3.284 | 0.62317 | 0.14052 | 21.25%
299 | CED, CUTTACK | 43 | KASARDA | 14220 | KASARDA | 14220202 | 124 | 55 | 55 | 82 | 62 | 2620 | 1810 | 47.04% | 0.7104 | 0.29088 | 0.49198 | 1.6771 | 0.29203 | 0.13734 | 29.2%
300 | CED, CUTTACK | 46 | SANKARPUR | 14233 | SANKARPUR | 14233201 | 13.4 | 55 | 34/55 | 70 | 48 | 2895 | 1435 | 40.66% | 0.7104 | 0.4914 | 0.49816 | 2.1708 | 0.29816 | 0.011043 | 2.716%
301 | CED, CUTTACK | 47 | SANKARPUR | 14233 | BERHAMPUR | 14233202 | 25.8 | 55 | 34/55 | 35 | 40 | 1709 | 1136 | 51.17% | 0.7104 | 0.1925 | 1.2538 | 2.5629 | 1.5085 | 0.026892 | 5.256%
302 | CED, CUTTACK | 48 | SANKARPUR | 14233 | MANGARAJPUR | 14233203 | 32.6 | 55 | 34/55 | 30 | 49 | 2261 | 1220 | 55.6% | 0.7104 | 0.17373 | 1.5896 | 3.9558 | 2.3393 | 0.038715 | 6.963%
303 | AED, ATHAGARH | 1 | NARANGABASTA | 14113 | MEGHA | 14113201 | 59.1 | 55 | 55/34 | 155 | 126 | 6983 | 4814 | 73.67% | 0.7104 | 1.5141 | 0.40766 | 2.3647 | 0.21448 | 0.17178 | 23.32%
304 | AED, ATHAGARH | 2 | NARANGABASTA | 14113 | MANCHESWAR | 14113202 | 49.52 | 34 | 34 | 40 | 24 | 1579 | 760 | 66.53% | 1.1325 | 0.13885 | 1.4266 | 2.072 | 1.9134 | 0.13633 | 20.49%
305 | AED, ATHAGARH | 3 | GURUDIJHATIA | 14213 | GURUDIJHATIA | 14213201 | 25.9 | 80 | 80 | 50 | 55 | 4455 | 766 | 66.55% | 0.4862 | 0.9696 | 1.1415 | 4.6767 | 1.2706 | 0.031762 | 4.773%
306 | AED, ATHAGARH | 4 | GURUDIJHATIA | 14213 | KUMARPUR | 14213202 | 58.5 | 80 | 80/34 | 80 | 100 | 3588 | 2346 | 69.97% | 0.4862 | 0.5946 | 0.7501 | 2.3541 | 0.60014 | 0.086742 | 12.4%
307 | AED, ATHAGARH | 5 | KHUNTUNI | 14117 | KHUNTUNI GURUDIJHATIA | 14117201 | 15 | 80 | 80 | 75 | 61 | 2685 | 1884 | 40.97% | 0.4862 | 0.33498 | 0.46853 | 1.8791 | 0.26932 | 0.0087727 | 2.141%
308 | AED, ATHAGARH | 10 | BADAMBA | 14110 | GOPINATHPUR | 14110205 | 48.4 | 55 | 80/55/34 | 90 | 85 | 3550 | 4476 | 70.08% | 0.7104 | 0.65464 | 0.66785 | 2.0704 | 0.49039 | 0.10844 | 15.47%
309 | AED, ATHAGARH | 11 | BADAMBA | 14110 | GOPMATHURA | 14110201 | 15.84 | 55 | 55/34 | 30 | 37 | 1814 | 713 | 54.05% | 0.7104 | 0.32496 | 1.5452 | 3.1738 | 2.2191 | 0.017845 | 3.302%
310 | AED, ATHAGARH | 12 | BADAMBA | 14110 | BADAMBA TOWN | 14110202 | 14.98 | 80 | 10/80/55/34 | 70 | 61 | 2207 | 1332 | 59.57% | 0.4862 | 0.34922 | 0.72984 | 1.6549 | 0.5721 | 0.016212 | 2.721%
311 | AED, ATHAGARH | 13 | BADAMBA | 14110 | RAGADIPADA | 14110204 | 55.77 | 55 | 55/34 | 95 | 97 | 3589 | 3182 | 49.88% | 0.7104 | 0.4237 | 0.45031 | 1.9829 | 0.25229 | 0.071627 | 14.36%
312 | AED, ATHAGARH | 14 | KANPUR | 14111 | GODIBANDHA | 14111204 | 58.477 | 55 | 55/34 | 38 | 72 | 2218 | 1614 | 37.99% | 0.7104 | 0.14537 | 0.85744 | 3.0636 | 0.75966 | 0.036183 | 9.524%
313 | AED, ATHAGARH | 16 | KANPUR | 14111 | BALIJHARIA | 14111203 | 27.358 | 55 | 55/34 | 66 | 57 | 2810 | 2146 | 68.46% | 0.7104 | 0.38055 | 0.88959 | 2.2347 | 0.81101 | 0.054517 | 7.964%
314 | AED, ATHAGARH | 17 | KANPUR | 14111 | KANPUR | 14111202 | 29.076 | 55 | 55/34 | 64 | 61 | 3052 | 3098 | 43.8% | 0.7104 | 0.36623 | 0.587 | 2.503 | 0.39305 | 0.026404 | 6.028%
315 | AED, ATHAGARH | 18 | KANPUR | 14111 | BAGDHARIA | 14111201 | 18.875 | 55 | 55/34 | 30 | 43 | 1530 | 1182 | 37.61% | 0.7104 | 0.45741 | 1.0753 | 2.6769 | 1.1401 | 0.010924 | 2.904%
316 | AED, ATHAGARH | 20 | NARSINGHPUR | 14112 | JAIPUR | 14112205 | 33.753 | 55 | 55/34 | 13 | 40 | 1160 | 548 | 34.63% | 0.7104 | 0.16542 | 2.2847 | 4.6835 | 4.6327 | 0.014906 | 4.304%
317 | AED, ATHAGARH | 22 | NARSINGHPUR | 14112 | NARSINGHPUR | 14112203 | 30.52 | 80 | 80/34 | 100 | 60 | 4152 | 2859 | 48.05% | 0.4862 | 0.55468 | 0.41206 | 2.1793 | 0.21825 | 0.025714 | 5.352%
318 | AED, ATHAGARH | 23 | NARSINGHPUR | 14112 | KAKUDIA | 14112202 | 40.706 | 34 | 34 | 30 | 72 | 2451 | 2614 | 59.98% | 1.1325 | 0.3228 | 1.7148 | 4.2883 | 2.6955 | 0.088798 | 14.8%
319 | AED, ATHAGARH | 25 | KHUNTAKATA | 14214 | KHUNTUKATA | 14214201 | 82.2 | 80 | 80/55/34 | 150 | 136 | 6689 | 5052 | 72.08% | 0.4862 | 0.96012 | 0.41211 | 2.3406 | 0.21829 | 0.15586 | 21.62%
320 | AED, ATHAGARH | 26 | KHUNTAKATA | 14214 | GODIJHARIA | 14214202 | 65.1 | 80 | 80/55/34 | 130 | 112 | 4656 | 3801 | 71.93% | 0.4862 | 0.83895 | 0.47454 | 1.8799 | 0.27506 | 0.11683 | 16.24%
321 | AED, ATHAGARH | 27 | ATHAGARH | 14116 | ATHAGARH TOWN | 14116201 | 25.2 | 100 | 100/55/34 | 260 | 60 | 4152 | 5358 | 53.54% | 0.3878 | 1.0952 | 0.17662 | 0.83819 | 0.060281 | 0.03162 | 5.905%
322 | AED, ATHAGARH | 28 | ATHAGARH | 14116 | KANTOLA | 14116204 | 3.773 | 100 | 100/55/34 | 50 | 165 | 10055 | 539 | 72.42% | 0.3878 | 0.15619 | 1.2421 | 10.5553 | 1.4828 | 0.0043066 | 0.5947%
323 | AED, ATHAGARH | 29 | ATHAGARH | 14116 | ANKULA | 14116203 | 11.5 | 80 | 80/55/34 | 30 | 23 | 1164 | 456 | 62.12% | 0.4862 | 0.45857 | 1.776 | 2.0365 | 2.8786 | 0.011502 | 1.851%
324 | AED, ATHAGARH | 31 | ATHAGARH | 14116 | KARIKOLA | 14116202 | 90.4 | 80 | 80/55/34 | 220 | 170 | 7944 | 5209 | 44.29% | 0.4862 | 0.70668 | 0.17266 | 1.8953 | 0.058382 | 0.098614 | 22.27%
325 | AED, ATHAGARH | 32 | NUAPATANA | 14114 | MANIABANDHA | 14114202 | 32.903 | 80 | 80/55/34 | 104 | 92 | 3948 | 4595 | 39.21% | 0.4862 | 0.47444 | 0.32335 | 1.9925 | 0.14832 | 0.020377 | 5.197%
326 | AED, ATHAGARH | 33 | NUAPATANA | 14114 | NUAPATNA | 14114201 | 28.93 | 80 | 80/55/34 | 110 | 84 | 4847 | 4477 | 39.21% | 0.4862 | 0.47444 | 0.30572 | 2.3128 | 0.13591 | 0.018367 | 4.684%
327 | SED, SALIPUR | 2 | BAHUGRAM | 14098 | BAHUGRAM GOPINATHPUR | 14098202 | 55.709 | 55 | 55/80 | 90 | 98 | 4647 | 4540 | 39.49% | 0.7104 | 0.61331 | 0.37633 | 2.7101 | 0.18856 | 0.047996 | 12.15%
328 | SED, SALIPUR | 3 | BAHUGRAM | 14098 | PATPUR | 14098204 | 33.68 | 55 | 55/80 | 80 | 84 | 3172 | 2259 | 55.45% | 0.7104 | 0.86558 | 0.59451 | 2.0811 | 0.40165 | 0.048836 | 8.806%
329 | SED, SALIPUR | 4 | BAHUGRAM | 14098 | PADMAPUR | 14098203 | 58.754 | 55 | 55 / 80 | 180 | 96 | 5858 | 5609 | 32.69% | 0.7104 | 0.54925 | 0.15577 | 1.7082 | 0.050564 | 0.054294 | 16.61%
330 | SED, SALIPUR | 9 | NISCHINTAKOILI | 14099 | UMARA | 14099201 | 58.7 | 80 | 34/55/80 | 135 | 135 | 6772 | 6242 | 47.24% | 0.4862 | 0.78119 | 0.3001 | 2.6329 | 0.13207 | 0.054543 | 11.55%
331 | SED, SALIPUR | 10 | NISCHINTAKOILI | 14099 | RAMAKRUSNAPUR | 14099203 | 27.6 | 55 | 34/55 | 105 | 52 | 3629 | 3022 | 58.64% | 0.7104 | 0.70011 | 0.47896 | 1.8141 | 0.27931 | 0.047942 | 8.176%
332 | SED, SALIPUR | 11 | NISCHINTAKOILI | 14099 | BUHALA | 14099202 | 19.7 | 55 | 34/55 | 35 | 31 | 1371 | 2018 | 58.64% | 0.7104 | 0.70011 | 1.4369 | 2.056 | 1.9391 | 0.026396 | 4.501%
333 | SED, SALIPUR | 12 | ORIKANTA | 14212 | GOPINATHPUR | 14212201 | 84.6 | 55 | 34/55 | 180 | 168 | 8177 | 6455 | 49.69% | 0.7104 | 0.79304 | 0.23678 | 2.3844 | 0.092209 | 0.14257 | 28.69%
334 | SED, SALIPUR | 13 | ORIKANTA | 14212 | BILAHATA | 14212202 | 56.7 | 55 | 34/55 | 90 | 136 | 7360 | 4348 | 28.74% | 0.7104 | 0.42068 | 0.27389 | 4.2923 | 0.11479 | 0.029737 | 10.35%
335 | SED, SALIPUR | 14 | ORIKANTA | 14212 | SOGAL | 14212203 | 28.09 | 55 | 34/55 | 60 | 77 | 4337 | 2730 | 40.79% | 0.7104 | 0.31229 | 0.58307 | 3.794 | 0.38859 | 0.022165 | 5.434%
336 | SED, SALIPUR | 16 | MAHANGA | 14097 | CHAINPAL | 14097203 | 26.4 | 55 | 34/55 | 55 | 50 | 2240 | 2950 | 54.22% | 0.7104 | 0.74003 | 0.84548 | 2.1377 | 0.74097 | 0.033378 | 6.156%
337 | SED, SALIPUR | 17 | MAHANGA | 14097 | MAHANGA | 14097201 | 110.91 | 55 | 34/55 | 155 | 197 | 9132 | 7447 | 35.63% | 0.7104 | 0.85448 | 0.19712 | 3.0924 | 0.07051 | 0.10598 | 29.75%
338 | SED, SALIPUR | 18 | KOTAPADA | 14096 | JAIPUR/KOTAPADA | 14096201 | 24.6 | 55 | 34/55 | 50 | 78 | 4052 | 3350 | 43.91% | 0.7104 | 0.58628 | 0.7532 | 4.2536 | 0.60448 | 0.02097 | 4.776%
339 | DED, DHENKANAL | 1 | DHENKANAL COLLEGE | 14118 | GOVINDPUR | 14118203 | 68.6 | 55 | 55/34 | 170 | 145 | 8474 | 3869 | 50.34% | 0.7104 | 0.91651 | 0.25395 | 2.6164 | 0.10238 | 0.11449 | 22.75%
340 | DED, DHENKANAL | 2 | DHENKANAL COLLEGE | 14118 | JORANDA | 14118204 | 145.6 | 100 | 100/80/55/34 | 130 | 199 | 11302 | 6198 | 52.2% | 0.3878 | 1.0289 | 0.3444 | 4.5632 | 0.16377 | 0.12408 | 23.77%
341 | DED, DHENKANAL | 4 | DHENKANAL COLLEGE | 14118 | DKL TOWN-2 | 14118202 | 9.1 | 55 | 80/55/34 | 50 | 25 | 2680 | 376 | 43.37% | 0.7104 | 0.2769 | 0.74399 | 2.8134 | 0.59162 | 0.007592 | 1.75%
342 | DED, DHENKANAL | 5 | DHENKANAL COLLEGE | 14118 | SAPTASAJYA | 14118205 | 38.4 | 55 | 55/34 | 50 | 92 | 4854 | 1607 | 43.15% | 0.7104 | 0.47627 | 0.74014 | 5.0955 | 0.58627 | 0.031747 | 7.357%
343 | DED, DHENKANAL | 6 | DAKHINAKALI | 14189 | DEULASAHI | 14189201 | 4.5 | 80 | 80/55/34 | 110 | 40 | 4427 | 2092 | 56.7% | 0.4862 | 0.81792 | 0.44211 | 2.1124 | 0.2448 | 0.0051457 | 0.9075%
344 | DED, DHENKANAL | 9 | GUNDICHAPADA | 14131 | SIMINAI | 14131201 | 61.2 | 80 | 80/55/34 | 230 | 133 | 8361 | 4798 | 45.67% | 0.4862 | 1.1601 | 0.1703 | 1.9081 | 0.05726 | 0.071566 | 15.67%
345 | DED, DHENKANAL | 10 | GUNDICHAPADA | 14131 | G. BHAPUR | 14131205 | 30.6 | 80 | 80/55/34 | 180 | 61 | 3334 | 2006 | 50.31% | 0.4862 | 1.2839 | 0.23971 | 0.97219 | 0.093913 | 0.035945 | 7.145%
346 | DED, DHENKANAL | 12 | GUNDICHAPADA | 14131 | PHD | 14131204 | 54.8 | 55 | 80/55/34 | 160 | 98 | 6608 | 2596 | 65.12% | 0.7104 | 1.1677 | 0.34909 | 2.1678 | 0.16731 | 0.13239 | 20.33%
347 | DED, DHENKANAL | 17 | HINDOL ROAD | 14121 | H.ROAD BAZAR | 14121201 | 14.4 | 80 | 80/55 | 54 | 40 | 3612 | 1007 | 43.88% | 0.4862 | 0.30882 | 0.69691 | 3.5109 | 0.52793 | 0.0085579 | 1.95%
348 | DED, DHENKANAL | 18 | HINDOL ROAD | 14121 | FOUR POLE | 14121204 | 78.2 | 55 | 55/34 | 162 | 128 | 7729 | 3474 | 58.69% | 0.7104 | 0.85653 | 0.31069 | 2.5042 | 0.13936 | 0.16132 | 27.49%
349 | DED, DHENKANAL | 19 | HINDOL ROAD | 14121 | NIMIDHA | 14121202 | 23.6 | 55 | 55/34 | 127 | 100 | 7615 | 2214 | 48.3% | 0.7104 | 0.69438 | 0.32618 | 3.1472 | 0.15035 | 0.032282 | 6.684%
350 | DED, DHENKANAL | 20 | HINDOL ROAD | 14121 | BADALU | 14121203 | 58 | 55 | 55/34 | 176 | 120 | 13195 | 1162 | 16.5% | 0.7104 | 0.60769 | 0.080399 | 3.9351 | 0.021251 | 0.021536 | 13.05%
351 | DED, DHENKANAL | 21 | KHAJURIAKATA | 14122 | BEDAPADA | 14122202 | 128 | 80 | 80/55/34 | 145 | 172 | 7664 | 5126 | 52.89% | 0.4862 | 1.1415 | 0.31286 | 2.7743 | 0.14088 | 0.14636 | 27.67%
352 | DED, DHENKANAL | 25 | HINDOL | 14123 | HINDOL | 14123201 | 83.6 | 55 | 80/55/34 | 110 | 169 | 6470 | 4253 | 39.62% | 0.7104 | 0.034158 | 0.30893 | 3.0872 | 0.13813 | 0.078818 | 19.89%
353 | DED, DHENKANAL | 26 | GONDIA | 14120 | MANDAR | 14120201 | 77 | 55 | 55 | 70 | 117 | 4588 | 4016 | 34.16% | 0.7104 | 0.42976 | 0.41848 | 3.4402 | 0.2238 | 0.047629 | 13.94%
354 | DED, DHENKANAL | 27 | GONDIA | 14120 | PASUPATI | 14120205 | 38 | 55 | 55 | 30 | 45 | 1333 | 1043 | 35.63% | 0.7104 | 0.17096 | 1.0187 | 2.3322 | 1.034 | 0.019947 | 5.598%
355 | DED, DHENKANAL | 29 | GONDIA | 14120 | KAPILASH | 14120202 | 62 | 55 | 55 | 70 | 80 | 3802 | 2660 | 44.32% | 0.7104 | 0.39783 | 0.54299 | 2.8508 | 0.34447 | 0.059029 | 13.32%
356 | DED, DHENKANAL | 30 | GONDIA | 14120 | GONDIA | 14120203 | 28 | 34 | 34 | 45 | 49 | 1601 | 1638 | 45.12% | 1.1325 | 0.31246 | 0.85993 | 1.8674 | 0.76357 | 0.038931 | 8.628%
357 | DED, DHENKANAL | 35 | NIHALPRASAD | 14190 | N.PRASAD | 14190201 | 102 | 55 | 55, 34 & G.I Wire | 98 | 150 | 4987 | 4552 | 54.24% | 0.7104 | 0.53332 | 0.47468 | 2.671 | 0.27519 | 0.15206 | 28.04%
358 | DED, DHENKANAL | 36 | NIHALPRASAD | 14190 | KASHIPUR | 14190202 | 42 | 55 | 55, 34 & G.I Wire | 77 | 105 | 4599 | 3782 | 39.91% | 0.7104 | 0.38791 | 0.44455 | 3.135 | 0.24701 | 0.034696 | 8.693%
359 | DED, DHENKANAL | 37 | KAMAKHYANAGAR | 14124 | TOWN-1 | 14124201 | 6.3 | 55 | 55 | 80 | 36 | 6038 | 1535 | 57.16% | 0.7104 | 1.1211 | 0.61275 | 3.9615 | 0.42292 | 0.0096186 | 1.683%
360 | DED, DHENKANAL | 38 | KAMAKHYANAGAR | 14124 | BAUNSAPALA/TOWN-2 | 14124202 | 22.15 | 55 | 55 | 80 | 59 | 6180 | 2747 | 58.83% | 0.7104 | 0.91368 | 0.63071 | 4.0547 | 0.44437 | 0.035533 | 6.04%
361 | DED, DHENKANAL | 39 | KAMAKHYANAGAR | 14124 | KANPURA/JIRIDAMALI | 14124203 | 15 | 55 | 55 | 5 | 23 | 1095 | 269 | 45.39% | 0.7104 | 0.24882 | 7.7852 | 11.4949 | 50.0439 | 0.010586 | 2.332%
362 | DED, DHENKANAL | 41 | KAMAKHYANAGAR | 14124 | ANALABERENI/ R.N PUR | 14124205 | 47.2 | 55 | 55 | 35 | 76 | 3092 | 1193 | 37.51% | 0.7104 | 0.65137 | 0.91909 | 4.6369 | 0.85959 | 0.028035 | 7.475%
363 | DED, DHENKANAL | 42 | KANKADAHADA | 14191 | DANDADHAR | 14191201 | 30.2 | 55 | 55/34 | 40 | 50 | 2056 | 2019 | 45.47% | 0.7104 | 0.23101 | 0.97484 | 2.6979 | 0.95522 | 0.026035 | 5.726%
364 | DED, DHENKANAL | 43 | KANKADAHADA | 14191 | DOLIA | 14191202 | 92.7 | 55 | 55/34 | 50 | 112 | 2011 | 2971 | 51.37% | 0.7104 | 0.20559 | 0.88115 | 2.1111 | 0.79737 | 0.10423 | 20.29%
365 | DED, DHENKANAL | 44 | KANKADAHADA | 14191 | URBENGI | 14191203 | 78.3 | 55 | 55/34 | 50 | 83 | 1831 | 2895 | 38.27% | 0.7104 | 0.16527 | 0.65642 | 1.9221 | 0.47599 | 0.052557 | 13.73%
366 | DED, DHENKANAL | 46 | BADASUANLA | 14125 | GUNEIBILLI | 14125201 | 75 | 34 | 34 | 90 | 126 | 4688 | 2951 | 35.48% | 1.1325 | 0.16263 | 0.33806 | 2.734 | 0.15904 | 0.086881 | 24.49%
367 | DED, DHENKANAL | 47 | MATHAKARAGOLA | 14126 | BELEISAHI | 14126202 | 10.6 | 34 | 34 | 40 | 22 | 1473 | 1320 | 39.51% | 1.1325 | 0.23987 | 0.84712 | 1.9329 | 0.74352 | 0.011339 | 2.87%
368 | DED, DHENKANAL | 48 | MATHAKARAGOLA | 14126 | JIRAL | 14126201 | 40 | 34 | 34 | 140 | 96 | 5042 | 2944 | 60.66% | 1.1325 | 0.73268 | 0.37161 | 1.8903 | 0.1848 | 0.13028 | 21.48%
369 | DED, DHENKANAL | 49 | MATHAKARAGOLA | 14126 | BALISAHI | 14126203 | 26 | 34 | 34 | 20 | 73 | 2073 | 907 | 64.15% | 1.1325 | 0.19958 | 2.751 | 5.4404 | 6.6048 | 0.061767 | 9.628%
370 | DED, DHENKANAL | 51 | DAYANABIL | 14127 | KANHEIPALA | 14127202 | 65 | 34 | 34 | 50 | 77 | 3424 | 1656 | 51.2% | 1.1325 | 0.3845 | 0.87815 | 3.5944 | 0.79254 | 0.11581 | 22.62%
371 | DED, DHENKANAL | 52 | DAYANABIL | 14127 | SURAPRATAPUR | 14127201 | 18.1 | 34 | 34 | 40 | 24 | 1497 | 1120 | 51.2% | 1.1325 | 0.3845 | 1.0977 | 1.9644 | 1.1835 | 0.030819 | 6.02%
372 | DED, DHENKANAL | 57 | BHUBAN | 14129 | BHUSAL | 14129203 | 36.7 | 55 | 55/34 | 70 | 65 | 2968 | 1778 | 62.57% | 0.7104 | 0.45165 | 0.76666 | 2.2255 | 0.62355 | 0.063251 | 10.11%
373 | DED, DHENKANAL | 59 | BHUBAN | 14129 | BHUBAN MAHULPAL | 14129201 | 89.3 | 100 | 100/55/34 | 200 | 142 | 8216 | 2636 | 58.09% | 0.3878 | 1.3032 | 0.24911 | 2.1562 | 0.099468 | 0.1094 | 18.83%
374 | ANED, ANGUL | 2 | RCMS | 14132 | ANGULTOWN-2 | 14132202 | 9 | 100 | 100/80/55 | 242 | 74 | 11204 | 3390 | 28.97% | 0.3878 | 1.2663 | 0.10267 | 2.4301 | 0.028967 | 0.0047013 | 1.623%
375 | ANED, ANGUL | 3 | RCMS | 14132 | ANGULTOWN-3 | 14132203 | 12 | 100 | 100/80/55 | 265 | 85 | 12122 | 3534 | 45.81% | 0.3878 | 1.3189 | 0.14826 | 2.401 | 0.047238 | 0.012257 | 2.676%
376 | ANED, ANGUL | 4 | RCMS | 14132 | ANGULTOWN-4 | 14132206 | 5 | 100 | 100/80/55 | 135 | 34 | 4111 | 1814 | 43.9% | 0.3878 | 0.48885 | 0.27888 | 1.5984 | 0.11799 | 0.0033108 | 0.7542%
377 | ANED, ANGUL | 5 | RCMS | 14132 | ANGUL RE-1 | 14132205 | 15 | 80 | 80/55/34 | 140 | 105 | 8313 | 1202 | 43.62% | 0.4862 | 0.71477 | 0.26721 | 3.1167 | 0.11056 | 0.012549 | 2.877%
378 | ANED, ANGUL | 7 | RCMS | 14132 | COLLEGE | 14132207 | 4 | 80 | 100/80/55 | 65 | 20 | 2654 | 1396 | 61.1% | 0.4862 | 0.38512 | 0.80619 | 2.1431 | 0.68119 | 0.0044443 | 0.7274%
379 | ANED, ANGUL | 8 | HEMSURPADA | 14187 | SIKHYAKPADA | 14187204 | 4.5 | 80 | 80/55 | 90 | 34 | 3803 | 1505 | 50.02% | 0.4862 | 0.55387 | 0.47663 | 2.2179 | 0.27707 | 0.0038988 | 0.7795%
380 | ANED, ANGUL | 9 | HEMSURPADA | 14187 | HEMUSARAPADA | 14187201 | 5 | 80 | 80/100 | 150 | 66 | 10159 | 2538 | 47.81% | 0.4862 | 1.1067 | 0.27335 | 3.5548 | 0.11445 | 0.0049704 | 1.04%
381 | ANED, ANGUL | 10 | HEMSURPADA | 14187 | MCL | 14187202 | 90.91 | 100 | 100/80/55 | 220 | 224 | 14577 | 10328 | 48.37% | 0.3878 | 1.8483 | 0.18856 | 3.4778 | 0.066157 | 0.089633 | 18.53%
382 | ANED, ANGUL | 11 | HEMSURPADA | 14187 | MEDICAL | 14187203 | 2.1 | 80 | 80 | 20 | 4 | 1063 | 2 | 4.366% | 0.4862 | 0.0836 | 0.18722 | 2.7897 | 0.065487 | 2.1236e-05 | 0.04864%
383 | ANED, ANGUL | 12 | INDUSTRIAL ESTATE | 14133 | TAMRIT | 14133201 | 4 | 80 | 100/80/50 | 90 | 39 | 5990 | 1865 | 45.15% | 0.4862 | 0.6875 | 0.43025 | 3.4934 | 0.23414 | 0.0029287 | 0.6487%
384 | ANED, ANGUL | 16 | BANTALA | 14134 | SABALABHANGA | 14134202 | 54 | 55 | 34/55 | 58 | 89 | 3279 | 3041 | 50.6% | 0.7104 | 0.40658 | 0.74822 | 2.9674 | 0.59751 | 0.061225 | 12.1%
385 | ANED, ANGUL | 17 | BANTALA | 14134 | KHINDA | 14134203 | 88 | 55 | 34/55 | 90 | 155 | 6014 | 5615 | 47.36% | 0.7104 | 0.49717 | 0.45128 | 3.5074 | 0.25318 | 0.1018 | 21.5%
386 | ANED, ANGUL | 19 | JARPADA | 14135 | RAILWAY | 14135205 | 5 | 34 | 34 | 21 | 5 | 500 | 277 | 52.86% | 1.1325 | 0.044465 | 2.1588 | 1.2497 | 4.1601 | 0.0082487 | 1.56%
387 | ANED, ANGUL | 21 | JARPADA | 14135 | KATADA | 14135201 | 21 | 55 | 34/55 | 22 | 38 | 1824 | 1691 | 34.24% | 0.7104 | 0.11822 | 1.335 | 4.3517 | 1.6927 | 0.0097048 | 2.834%
388 | ANED, ANGUL | 22 | JARPADA | 14135 | KANJARA | 14135204 | 32 | 55 | 34/55 | 48 | 89 | 3517 | 3799 | 49.89% | 0.7104 | 0.34174 | 0.89145 | 3.8458 | 0.81404 | 0.033854 | 6.785%
389 | ANED, ANGUL | 23 | JARPADA | 14135 | JAGANNATHPUR | 14135202 | 165 | 80 | 34/80 | 53 | 138 | 3663 | 4572 | 50.12% | 0.4862 | 0.2243 | 0.8111 | 3.6276 | 0.68852 | 0.1232 | 24.58%
390 | ANED, ANGUL | 24 | CHHENDIPADA | 14136 | BAGEDIA | 14136205 | 70 | 55 | 34/55 | 130 | 140 | 5244 | 5592 | 48.74% | 0.7104 | 0.46347 | 0.32157 | 2.1173 | 0.14704 | 0.09812 | 20.13%
391 | ANED, ANGUL | 25 | CHHENDIPADA | 14136 | PIPAL BAHAL | 14136206 | 64 | 55 | 34/55 | 65 | 116 | 3309 | 3896 | 49.92% | 0.7104 | 0.26072 | 0.65867 | 2.672 | 0.47881 | 0.07303 | 14.63%
392 | ANED, ANGUL | 26 | CHHENDIPADA | 14136 | BRAHMANIBIL | 14136202 | 33.5 | 80 | 80/34 | 60 | 136 | 5112 | 3191 | 57.21% | 0.4862 | 0.43368 | 0.81777 | 4.472 | 0.69856 | 0.032523 | 5.685%
393 | ANED, ANGUL | 27 | CHHENDIPADA | 14136 | BAHALASAHI | 14136203 | 62 | 55 | 34/55 | 60 | 135 | 4529 | 3169 | 47.3% | 0.7104 | 0.27069 | 0.67615 | 3.962 | 0.50098 | 0.063073 | 13.33%
394 | ANED, ANGUL | 28 | CHHENDIPADA | 14136 | DUBANALI | 14136201 | 63 | 55 | 34/55 | 90 | 158 | 5110 | 3666 | 55.57% | 0.7104 | 0.36579 | 0.52958 | 2.9801 | 0.33028 | 0.09507 | 17.11%
395 | ANED, ANGUL | 29 | CHHENDIPADA | 14136 | CHHENDIPADA | 14136204 | 8 | 55 | 34/55/80 | 45 | 30 | 2409 | 1982 | 47% | 0.7104 | 0.25535 | 0.89577 | 2.8099 | 0.82107 | 0.0075029 | 1.596%
396 | ANED, ANGUL | 31 | BOINDA | 14137 | BOINDA LOCAL | 14137201 | 7.79 | 34 | 34 | 30 | 23 | 1910 | 1466 | 26.12% | 1.1325 | 0.21164 | 0.7466 | 3.3417 | 0.59525 | 0.0037527 | 1.437%
397 | ANED, ANGUL | 32 | BOINDA | 14137 | LUHAMUNDA | 14137205 | 67.2 | 34 | 34 | 35 | 107 | 3383 | 2143 | 34.46% | 1.1325 | 0.17027 | 0.84444 | 5.0733 | 0.73935 | 0.05473 | 15.88%
398 | ANED, ANGUL | 33 | BOINDA | 14137 | JAMUNALI | 14137203 | 53.22 | 34 | 34 | 35 | 78 | 2059 | 1404 | 44.99% | 1.1325 | 0.12665 | 1.1023 | 3.0878 | 1.1926 | 0.069914 | 15.54%
399 | ANED, ANGUL | 36 | ANANDAPUR | 14138 | KUTULUSINGA | 14138203 | 100.23 | 55 | 34/55 | 50 | 104 | 2529 | 617 | 53.23% | 0.7104 | 0.12017 | 0.913 | 2.6548 | 0.84945 | 0.12006 | 22.56%
400 | ANED, ANGUL | 38 | ANANDAPUR | 14138 | KRUTIBASPUR | 14138202 | 28.19 | 34 | 34 | 30 | 50 | 1384 | 1440 | 50.58% | 1.1325 | 0.14674 | 1.446 | 2.4214 | 1.9619 | 0.044759 | 8.849%
401 | ANED, ANGUL | 39 | ANANDAPUR | 14138 | GHODABANDHANALI | 14138204 | 13.68 | 34 | 34 | 25 | 17 | 932 | 244 | 44.85% | 1.1325 | 0.061337 | 1.5386 | 1.9567 | 2.2015 | 0.016926 | 3.774%
402 | ANED, ANGUL | 40 | ATHAMALIK | 14139 | MANTRI | 14139202 | 39.85 | 55 | 55 | 45 | 52 | 1729 | 1131 | 55.89% | 0.7104 | 0.14353 | 1.0652 | 2.0167 | 1.1208 | 0.051015 | 9.128%
403 | ANED, ANGUL | 43 | ATHAMALIK | 14139 | BINKEI | 14139204 | 64.28 | 55 | 55 | 60 | 88 | 2419 | 2011 | 52.21% | 0.7104 | 0.19539 | 0.74627 | 2.1161 | 0.59478 | 0.077637 | 14.87%
404 | ANED, ANGUL | 44 | ATHAMALIK | 14139 | JADUPUR | 14139203 | 15.73 | 55 | 55 | 20 | 16 | 337 | 321 | 38.48% | 0.7104 | 0.022586 | 1.6503 | 0.88442 | 2.5088 | 0.008904 | 2.314%
405 | ANED, ANGUL | 49 | BAMUR | 14141 | FASIPAL | 14141201 | 49 | 34 | 34 | 20 | 46 | 1145 | 2313 | 44.32% | 1.1325 | 0.17389 | 1.9005 | 3.0049 | 3.2695 | 0.057625 | 13%
406 | ANED, ANGUL | 50 | BAMUR | 14141 | BRAHMANIDEI | 14141202 | 34 | 55 | 55 | 25 | 64 | 2220 | 1664 | 55.03% | 0.7104 | 1.2076 | 1.888 | 4.6609 | 3.2292 | 0.038707 | 7.033%
407 | ANED, ANGUL | 51 | BAMUR | 14141 | NAKCHI | 14141203 | 135 | 55 | 55 | 42 | 101 | 2492 | 2535 | 43.24% | 0.7104 | 0.2261 | 0.88306 | 3.1143 | 0.80045 | 0.10752 | 24.86%
408 | ANED, ANGUL | 52 | BAMUR | 14141 | AMBAPAL | 14141204 | 87 | 34 | 34 | 30 | 87 | 2135 | 1957 | 33.22% | 1.1325 | 0.26229 | 0.94961 | 3.7354 | 0.91133 | 0.064166 | 19.32%
409 | ANED, ANGUL | 54 | BADAKERA | 14227 | DUDHIABEDA | 14227202 | 80 | 55 | 80/55/34 | 120 | 140 | 5929 | 5606 | 50.24% | 0.7104 | 1.1451 | 0.35908 | 2.5933 | 0.17497 | 0.11369 | 22.63%
410 | TED,CHAINPAL | 1 | HATATOTA | 14145 | TALCHER TOWN-1 | 14145203 | 21.67 | 80 | 80/55 | 280 | 105 | 13977 | 4188 | 55.36% | 0.4862 | 1.1673 | 0.16957 | 2.6201 | 0.056917 | 0.037331 | 6.743%
411 | TED,CHAINPAL | 2 | HATATOTA | 14145 | TALCHER TOWN-2 | 14145204 | 14.015 | 80 | 80/55 | 190 | 102 | 12957 | 3594 | 39.01% | 0.4862 | 1.1351 | 0.17607 | 3.5794 | 0.060015 | 0.011722 | 3.005%
412 | TED,CHAINPAL | 4 | HATATOTA | 14145 | HATATOTA RE-2 | 14145202 | 51.3 | 80 | 80/55/34 | 105 | 89 | 4264 | 1977 | 52.43% | 0.4862 | 0.58433 | 0.42824 | 2.1315 | 0.23236 | 0.050735 | 9.677%
413 | TED,CHAINPAL | 5 | HATATOTA | 14145 | HATATOTA RE-1 | 14145201 | 52.2 | 55 | 55 | 80 | 81 | 4468 | 2395 | 45.92% | 0.7104 | 0.69153 | 0.49225 | 2.9315 | 0.2923 | 0.055083 | 12%
414 | TED,CHAINPAL | 7 | CHAINPAL | 14192 | BALHRA | 14192201 | 36.51 | 55 | 80/55/34 | 160 | 75 | 5414 | 2919 | 54.56% | 0.7104 | 0.95588 | 0.29246 | 1.7761 | 0.12692 | 0.066913 | 12.26%
415 | TED,CHAINPAL | 8 | CHAINPAL | 14192 | GOTAMARA | 14192202 | 20.61 | 55 | 80/55/34 | 35 | 28 | 1485 | 445 | 67.1% | 0.7104 | 0.24047 | 1.6442 | 2.227 | 2.4915 | 0.035482 | 5.288%
416 | TED,CHAINPAL | 9 | CHAINPAL | 14192 | BHOGABARENI | 14192203 | 42.5 | 55 | 80/55/34 | 90 | 91 | 5161 | 2316 | 49.21% | 0.7104 | 0.59976 | 0.46894 | 3.0099 | 0.26972 | 0.052374 | 10.64%
417 | TED,CHAINPAL | 10 | KANIHA | 14148 | KANIHA RE-1 | 14148202 | 22 | 80 | 80/55 | 24 | 43 | 1364 | 1190 | 46.83% | 0.4862 | 0.13267 | 1.6735 | 2.9831 | 2.5752 | 0.012598 | 2.69%
418 | TED,CHAINPAL | 11 | KANIHA | 14148 | KANIHA-1 | 14148201 | 8 | 80 | 80 | 27 | 30 | 1442 | 545 | 38.48% | 0.4862 | 0.051377 | 1.2224 | 2.8032 | 1.4399 | 0.0032418 | 0.8424%
419 | TED,CHAINPAL | 12 | KANIHA | 14148 | KANIHA RE-2 | 14148203 | 80 | 80 | 80/55/34 | 120 | 169 | 7288 | 5251 | 59.5% | 0.4862 | 1.3267 | 0.42524 | 3.1878 | 0.22971 | 0.10216 | 17.17%
420 | TED,CHAINPAL | 13 | KANIHA | 14148 | KANIHA-2 | 14148204 | 0.3 | 80 | 80 | 5 | 4 | 241 | 141 | 33.04% | 0.4862 | 0.046085 | 5.6673 | 2.5299 | 26.8281 | 7.7677e-05 | 0.02351%
421 | TED,CHAINPAL | 14 | KANIHA | 14148 | KARADEI | 14148205 | 27.83 | 80 | 80/55 | 86 | 115 | 4873 | 2233 | 50.34% | 0.4862 | 0.62372 | 0.50205 | 2.9741 | 0.30206 | 0.024002 | 4.768%
422 | TED,CHAINPAL | 15 | KANIHA | 14148 | DERANGA | 14148206 | 51 | 80 | 80/55 | 75 | 88 | 4211 | 2479 | 61.11% | 0.4862 | 0.47115 | 0.69884 | 2.947 | 0.53047 | 0.058749 | 9.613%
423 | TED,CHAINPAL | 17 | SAMAL | 14147 | BIJIGULU | 14147202 | 22.925 | 80 | 80/55 | 42 | 34 | 1219 | 647 | 19.78% | 0.4862 | 0.08702 | 0.40397 | 1.5234 | 0.21135 | 0.0032995 | 1.668%
424 | TED,CHAINPAL | 18 | SAMAL | 14147 | SAMAL VILLAGE | 14147201 | 13.53 | 80 | 80/55 | 35 | 29 | 1098 | 492 | 50.54% | 0.4862 | 0.10306 | 1.2384 | 1.6466 | 1.4746 | 0.0094351 | 1.867%
425 | TED,CHAINPAL | 19 | SAMAL | 14147 | COLONY | 14147204 | 1.5 | 55 | 55/34 | 15 | 2 | 350 | 552 | 41.32% | 0.7104 | 0.091933 | 2.3624 | 1.2247 | 4.9372 | 0.00093991 | 0.2275%
426 | TED,CHAINPAL | 20 | SAMAL | 14147 | BARRAGE | 14147203 | 1.8 | 55 | 55/34 | 15 | 2 | 350 | 1 | 0.03544% | 0.7104 | 0.038088 | 0.0020266 | 1.2247 | 0.0004086 | 9.3344e-08 | 0.02634%
427 | TED,CHAINPAL | 23 | PALLAHARA | 14151 | SEA GARH | 14151203 | 9.81 | 55 | 34/55 | 10 | 20 | 721 | 903 | 24.69% | 0.7104 | 0.032821 | 2.1175 | 3.7844 | 4.0107 | 0.0022193 | 0.8989%
428 | TED,CHAINPAL | 24 | PALLAHARA | 14151 | PHOPANDA | 14151204 | 75.37 | 55 | 34/55 | 60 | 144 | 3896 | 2632 | 48% | 0.7104 | 0.19403 | 0.68609 | 3.4082 | 0.51379 | 0.078635 | 16.38%
429 | TED,CHAINPAL | 26 | KHAMAR | 14150 | ODASA | 14150204 | 31.48 | 34 | 34/55 | 32 | 59 | 2516 | 1091 | 59.71% | 1.1325 | 0.15207 | 1.6004 | 4.1269 | 2.3691 | 0.068673 | 11.5%
430 | TED,CHAINPAL | 27 | KHAMAR | 14150 | BARAKOTIA | 14150202 | 79.53 | 55 | 34/55 | 41 | 148 | 3887 | 2865 | 37.31% | 0.7104 | 0.23751 | 0.78037 | 4.9761 | 0.64326 | 0.048508 | 13%
431 | TED,CHAINPAL | 28 | KHAMAR | 14150 | SANKHAMUR | 14150203 | 76.14 | 55 | 34/55 | 74 | 132 | 4640 | 2734 | 56.18% | 0.7104 | 0.39483 | 0.65117 | 3.2911 | 0.46945 | 0.11041 | 19.65%
432 | TED,CHAINPAL | 30 | BALANDA | 14146 | GURUDWAR | 14146203 | 7.01 | 55 | 55/80 | 30 | 23 | 1516 | 674 | 49.35% | 0.7104 | 0.22795 | 1.4108 | 2.6524 | 1.8745 | 0.0066709 | 1.352%
433 | TED,CHAINPAL | 31 | BALANDA | 14146 | JAGANNATHPUR | 14146202 | 28.093 | 80 | 34/55/80 | 65 | 76 | 3983 | 1580 | 60.74% | 0.4862 | 0.78305 | 0.80148 | 3.2163 | 0.67419 | 0.030892 | 5.086%
434 | TED,CHAINPAL | 32 | BALANDA | 14146 | GOBARA | 14146201 | 50.283 | 80 | 34/55/80 | 180 | 93 | 4897 | 2286 | 57.65% | 0.4862 | 0.52267 | 0.2747 | 1.428 | 0.11531 | 0.072521 | 12.58%
435 | TED,CHAINPAL | 33 | BANARPAL | 14142 | KULAD | 14142202 | 22.02 | 55 | 80/55 | 280 | 65 | 5801 | 4454 | 34.29% | 0.7104 | 1.374 | 0.10502 | 1.0874 | 0.029828 | 0.029047 | 8.472%
436 | TED,CHAINPAL | 34 | BANARPAL | 14142 | CHAINPAL | 14142201 | 14 | 55 | 80/55 | 60 | 33 | 2231 | 694 | 35.62% | 0.7104 | 0.2215 | 0.50912 | 1.9517 | 0.30919 | 0.0087899 | 2.468%
437 | TED,CHAINPAL | 37 | PARJANG | 14143 | OLD PARJANG | 14143201 | 61.51 | 55 | 55 & 34 | 83 | 116 | 5100 | 3981 | 56.44% | 0.7104 | 0.7775 | 0.58325 | 3.2252 | 0.38879 | 0.09293 | 16.46%
438 | TED,CHAINPAL | 38 | PARJANG | 14143 | R.N. PUR(SANDA) | 14143203 | 94.9 | 55 | 55 & 34 | 91 | 106 | 3351 | 3461 | 43.09% | 0.7104 | 0.32862 | 0.40612 | 1.9328 | 0.21317 | 0.094494 | 21.93%
439 | TED,CHAINPAL | 39 | PARJANG | 14143 | KANDARSINGHA | 14143206 | 35.5 | 55 | 55 & 34 | 79 | 56 | 2654 | 3869 | 58.38% | 0.7104 | 0.73652 | 0.63374 | 1.7633 | 0.44805 | 0.055994 | 9.592%
440 | TED,CHAINPAL | 40 | PARJANG | 14143 | SARANG | 14143207 | 99.61 | 55 | 55 & 34 | 90 | 130 | 3448 | 3921 | 48.7% | 0.7104 | 0.71027 | 0.46404 | 2.0109 | 0.26507 | 0.12064 | 24.77%
441 | TED,CHAINPAL | 41 | PARJANG | 14143 | DADARAGHATI/ KUALO | 14143204 | 21.97 | 55 | 55 & 34 | 35 | 28 | 1197 | 939 | 57.71% | 0.7104 | 0.25653 | 1.4141 | 1.7951 | 1.8827 | 0.02858 | 4.952%
442 | TED,CHAINPAL | 43 | PARJANG | 14143 | RENGALI | 14143202 | 10.2 | 55 | 55 & 34 | 62 | 23 | 1544 | 2214 | 50.59% | 0.7104 | 0.45881 | 0.69982 | 1.3071 | 0.53176 | 0.011761 | 2.325%
443 | TED,CHAINPAL | 44 | PARJANG | 14143 | NEW PARJANG TOWN | 14143208 | 2.8 | 55 | 55 & 34 | 41 | 12 | 1295 | 590 | 56.58% | 0.7104 | 0.31737 | 1.1835 | 1.6579 | 1.3573 | 0.0036035 | 0.6369%
444 | TED,CHAINPAL | 45 | SARANG | 14144 | IGIT SARANG FDR | 14144201 | 4.65 | 55 | 55 | 35 | 6 | 1125 | 6 | 24.54% | 0.7104 | 0.21006 | 0.60145 | 1.6871 | 0.40969 | 0.0013164 | 0.5363%
445 | TED,CHAINPAL | 48 | PARABIL | 14149 | PARABIL (MAHIDHARPUR) | 14149201 | 48.5 | 55 | 55/34 | 52 | 107 | 3750 | 1800 | 37.93% | 0.7104 | 0.26145 | 0.62557 | 3.7852 | 0.43818 | 0.032414 | 8.546%
446 | TED,CHAINPAL | 49 | BARUAN | 14152 | TUMUNGOLA / DANGARBEDA | 14152201 | 25.18 | 55 | 55/34 | 30 | 54 | 1840 | 1200 | 48.56% | 0.7104 | 0.12518 | 1.3881 | 3.2193 | 1.8191 | 0.023254 | 4.789%
447 | TED,CHAINPAL | 51 | OHPC | 14186 | PGCIL | 14186202 | 12.6 | 55 | 55/34 | 30 | 26 | 877 | 285 | 46.18% | 0.7104 | 0.063335 | 1.3202 | 1.5344 | 1.6583 | 0.010607 | 2.297%
448 | TED,CHAINPAL | 52 | OHPC | 14186 | BAJRAKTOTA | 14186201 | 115.3 | 55 | 100/55/34 | 90 | 205 | 6940 | 4716 | 50.77% | 0.7104 | 0.80641 | 0.48381 | 4.0474 | 0.28402 | 0.14962 | 29.47%
449 | PDP, PARADEEP | 1 | PARADEEP | 14175 | RANGIAGADA | 14175204 | 9.1 | 80 | 34 +55+80mm2 AAAC | 70 | 22 | 1698 | 1336 | 50.93% | 0.4862 | 0.54946 | 0.62394 | 1.2732 | 0.43623 | 0.0075092 | 1.475%
450 | PDP, PARADEEP | 2 | PARADEEP | 14175 | RE-BHUTAMUNDAI | 14175203 | 44 | 55 | 34+55+80mm2 AAAC | 220 | 79 | 5424 | 6183 | 77.07% | 0.7104 | 0.7815 | 0.30045 | 1.2941 | 0.1323 | 0.15893 | 20.62%
451 | PDP, PARADEEP | 5 | PARADEEP | 14175 | PARADEEP GARH | 14175202 | 6 | 55 | 80 +55mm2 AAAC | 190 | 25 | 2736 | 1612 | 28.15% | 0.7104 | 1.2918 | 0.12705 | 0.75583 | 0.038322 | 0.0046821 | 1.664%
452 | PDP, PARADEEP | 7 | KUJANGA | 14179 | TALADANDA | 14179201 | 22 | 55 | 80+55 mm2 AAAC | 85 | 43 | 2640 | 2096 | 76.38% | 0.7104 | 0.79722 | 0.77065 | 1.6302 | 0.62925 | 0.056418 | 7.387%
453 | PDP, PARADEEP | 8 | KUJANGA | 14179 | BAZAR | 14179204 | 6 | 80 | 80+55 mm2 AAAC | 70 | 40 | 2088 | 888 | 31.73% | 0.4862 | 0.21965 | 0.38877 | 1.5656 | 0.19867 | 0.0022548 | 0.7106%
454 | PDP, PARADEEP | 9 | KUJANGA | 14179 | SANTARA | 14179202 | 31 | 55 | 34+55+80mm2 AAAC | 165 | 159 | 9965 | 5559 | 64.59% | 0.7104 | 1.2942 | 0.3357 | 3.17 | 0.1573 | 0.074884 | 11.59%
455 | PDP, PARADEEP | 11 | RAHAMA | 14177 | RAHAMA | 14177201 | 85 | 55 | 34+55+80mm2 AAAC | 225 | 122 | 5997 | 7192 | 29.2% | 0.7104 | 0.77036 | 0.11132 | 1.399 | 0.032178 | 0.078104 | 26.74%
456 | PDP, PARADEEP | 12 | RAHAMA | 14177 | PANKAPAL | 14177202 | 35 | 55 | 34+55 mm2 AAAC | 70 | 56 | 2595 | 2923 | 49.92% | 0.7104 | 0.346 | 0.61157 | 1.9458 | 0.42153 | 0.040778 | 8.169%
457 | PDP, PARADEEP | 13 | RAHAMA | 14177 | PANDUA | 14177203 | 75 | 55 | 34+55+80 mm2 AAAC | 185 | 114 | 4922 | 5151 | 56.49% | 0.7104 | 0.81849 | 0.26187 | 1.3965 | 0.10723 | 0.15526 | 27.49%
458 | PDP, PARADEEP | 15 | ERASAMA | 14178 | PANCHAPALLI | 14178204 | 122 | 55 | 34+55 mm2 AAAC | 80 | 95 | 2491 | 3425 | 28.62% | 0.7104 | 0.31671 | 0.30682 | 1.6343 | 0.13667 | 0.060195 | 21.03%
459 | PDP, PARADEEP | 16 | ERASAMA | 14178 | ERASAMA | 14178203 | 110 | 55 | 34+55 mm2 AAAC | 140 | 114 | 4145 | 5511 | 26.62% | 0.7104 | 0.70055 | 0.1631 | 1.554 | 0.053902 | 0.065552 | 24.62%
460 | PDP, PARADEEP | 22 | TIRTOL | 14176 | KOLAR | 14176203 | 85 | 55 | 34+55 mm2 AAAC | 80 | 87 | 3878 | 3570 | 36.61% | 0.7104 | 0.45217 | 0.39244 | 2.5444 | 0.2017 | 0.061892 | 16.91%
461 | PDP, PARADEEP | 23 | KOLAR(PARUNA) | 14196 | DIGABARINI | 14196201 | 45 | 55 | 34+55 mm2 AAAC | 75 | 116 | 5149 | 2801 | 37.47% | 0.7104 | 0.11169 | 0.42852 | 3.6035 | 0.23261 | 0.033212 | 8.863%
462 | PDP, PARADEEP | 24 | KOLAR(PARUNA) | 14196 | KRISHNANANDAPUR | 14196202 | 95 | 55 | 34+55 mm2 AAAC | 120 | 37 | 1824 | 3649 | 45.39% | 0.7104 | 0.66941 | 0.32444 | 0.79782 | 0.1491 | 0.11505 | 25.34%
463 | KED-01, KENDRAPARA | 1 | KENDRAPARA | 14158 | KENDRAPADATOWN -I | 14158201 | 35 | 34 | 55/34 | 70 | 72 | 2826 | 4506 | 40.76% | 1.1325 | 1.6574 | 0.49935 | 2.119 | 0.29935 | 0.046164 | 11.33%
464 | KED-01, KENDRAPARA | 3 | KENDRAPARA | 14158 | THAKURPATANA | 14158203 | 20 | 55 | 55 | 85 | 87 | 6080 | 4014 | 36.18% | 0.7104 | 0.68148 | 0.36504 | 3.7544 | 0.17961 | 0.01464 | 4.047%
465 | KED-01, KENDRAPARA | 4 | KENDRAPARA | 14158 | TINIMUHANI | 14158205 | 19.4 | 55 | 80/55 | 95 | 54 | 7411 | 2592 | 51.66% | 0.7104 | 0.8261 | 0.46634 | 4.0946 | 0.26724 | 0.026393 | 5.109%
466 | KED-01, KENDRAPARA | 5 | KENDRAPARA | 14158 | BHARATPUR | 14158204 | 50 | 55 | 55/34 | 180 | 107 | 3957 | 3180 | 36.71% | 0.7104 | 0.4321 | 0.17493 | 1.1539 | 0.059466 | 0.054339 | 14.8%
467 | KED-01, KENDRAPARA | 6 | DUHURIA | 14197 | DUHURIA | 14197201 | 5 | 80 | 80 | 30 | 9 | 3854 | 292 | 12.44% | 0.4862 | 0.11971 | 0.35577 | 6.7429 | 0.17241 | 0.00029952 | 0.2407%
468 | KED-01, KENDRAPARA | 7 | DUHURIA | 14197 | LAW COLLEGE | 14197202 | 15 | 55 | 55 | 30 | 38 | 814 | 1608 | 33.68% | 0.7104 | 0.2131 | 0.96289 | 1.4242 | 0.9343 | 0.0071146 | 2.112%
469 | KED-01, KENDRAPARA | 8 | CHHAGHARIA | 14198 | BAGADA | 14198201 | 25 | 55 | 55 | 70 | 32 | 2530 | 2579 | 45.22% | 0.7104 | 0.35861 | 0.55407 | 1.8971 | 0.35641 | 0.024628 | 5.446%
470 | KED-01, KENDRAPARA | 11 | INDUPUR | 14157 | INDUPUR | 14157201 | 2 | 55 | 55 | 6 | 11 | 1567 | 1027 | 17.5% | 0.7104 | 0.12985 | 2.5021 | 13.7081 | 5.5088 | 0.00022373 | 0.1278%
471 | KED-01, KENDRAPARA | 12 | INDUPUR | 14157 | DHUMAT | 14157202 | 38 | 55 | 55 | 21 | 48 | 875 | 2966 | 30.42% | 0.7104 | 0.16673 | 1.2422 | 2.187 | 1.4829 | 0.014018 | 4.609%
472 | KED-01, KENDRAPARA | 13 | INDUPUR | 14157 | NIKIREI | 14157203 | 30 | 55 | 55 | 46 | 62 | 2372 | 3801 | 36.64% | 0.7104 | 0.44035 | 0.68321 | 2.7066 | 0.51006 | 0.018264 | 4.984%
473 | KED-01, KENDRAPARA | 14 | INDUPUR | 14157 | BARI | 14157204 | 18 | 55 | 55 | 33 | 13 | 2865 | 995 | 50.08% | 0.7104 | 0.14949 | 1.3014 | 4.5569 | 1.6153 | 0.01786 | 3.567%
474 | KED-01, KENDRAPARA | 15 | DANPUR | 14164 | CHANDOLA | 14164203 | 30 | 55 | 55 | 30 | 69 | 1669 | 3976 | 49.17% | 0.7104 | 0.22095 | 1.4058 | 2.9201 | 1.8621 | 0.028359 | 5.767%
475 | KED-01, KENDRAPARA | 16 | DANPUR | 14164 | ASURESWAR | 14164204 | 5 | 55 | 55 | 130 | 9 | 3328 | 271 | 55.93% | 0.7104 | 0.65723 | 0.36895 | 1.3437 | 0.18269 | 0.0087078 | 1.557%
476 | KED-01, KENDRAPARA | 17 | DANPUR | 14164 | DANPUR | 14164201 | 28 | 55 | 55 | 90 | 75 | 3307 | 3780 | 29.8% | 0.7104 | 0.4178 | 0.28394 | 1.9286 | 0.12129 | 0.015516 | 5.207%
477 | KED-01, KENDRAPARA | 18 | DANPUR | 14164 | LUNA | 14164202 | 29 | 55 | 55 | 120 | 38 | 255 | 2079 | 43.58% | 0.7104 | 0.43982 | 0.31144 | 0.11154 | 0.13989 | 0.032951 | 7.562%
478 | KED-01, KENDRAPARA | 19 | CHHATA | 14199 | CHHATA-1 | 14199201 | 40 | 55 | 55 | 60 | 64 | 2401 | 2573 | 38.49% | 0.7104 | 0.70954 | 0.55019 | 2.1004 | 0.35221 | 0.028609 | 7.433%
479 | KED-01, KENDRAPARA | 28 | AUL | 14154 | AUL | 14154202 | 29 | 55 | 55 | 120 | 81 | 5888 | 4130 | 46.51% | 0.7104 | 0.73567 | 0.33242 | 2.5754 | 0.15489 | 0.036485 | 7.844%
480 | KED-01, KENDRAPARA | 37 | PATTAMUNDAI | 14153 | BALIPATANA | 14153204 | 18.7 | 55 | 80/55 | 40 | 24 | 2375 | 3741 | 32.02% | 0.7104 | 0.57798 | 0.68646 | 3.1165 | 0.51427 | 0.0086793 | 2.711%
481 | KED-01, KENDRAPARA | 38 | PATTAMUNDAI | 14153 | PATTAMUNDAI BAZAR | 14153202 | 5.5 | 55 | 55/34 | 72 | 74 | 1750 | 2288 | 18.06% | 0.7104 | 0.63205 | 0.21507 | 1.2757 | 0.080019 | 0.0012869 | 0.7128%
482 | KED-01, KENDRAPARA | 39 | SAHUPADA | 14201 | BADAPADA | 14201201 | 47.5 | 55 | 55/34 | 45 | 37 | 2104 | 2569 | 40.58% | 0.7104 | 0.20914 | 0.77348 | 2.4541 | 0.63331 | 0.034361 | 8.467%
483 | KED-01, KENDRAPARA | 40 | SAHUPADA | 14201 | GANGARAMPUR | 14201202 | 50.5 | 55 | 55/34 | 35 | 37 | 1943 | 2483 | 53.93% | 0.7104 | 0.29052 | 1.3215 | 2.9138 | 1.6614 | 0.057974 | 10.75%
484 | KED-01, KENDRAPARA | 43 | ADHAJORI | 14159 | DAMARPUR | 14159203 | 42 | 55 | 55/34 | 60 | 68 | 3160 | 2810 | 19.5% | 0.7104 | 0.17697 | 0.27877 | 2.7644 | 0.11792 | 0.010057 | 5.157%
485 | KED-01, KENDRAPARA | 44 | DANDISAHI | 14162 | DANDISAHI | 14162201 | 52 | 55 | 55 | 50 | 51 | 2109 | 3871 | 24.12% | 0.7104 | 0.28972 | 0.41371 | 2.2139 | 0.21967 | 0.016108 | 6.679%
486 | KED-01, KENDRAPARA | 50 | RAJANAGAR | 14160 | KEREDAGADA | 14160203 | 60 | 34 | 55/34 | 80 | 91 | 3946 | 3543 | 53.69% | 1.1325 | 0.45866 | 0.57561 | 2.589 | 0.38018 | 0.13128 | 24.45%
487 | KED-01, KENDRAPARA | 52 | RAJANAGAR | 14160 | MADANPUR | 14160204 | 25 | 34 | 55/34 | 60 | 42 | 2116 | 1456 | 78.8% | 1.1325 | 0.31926 | 1.1264 | 1.8511 | 1.2403 | 0.10038 | 12.74%
488 | KED-02, MARSAGHAI | 1 | MARSAGHAI | 14165 | MARSHAGHAI | 14165202 | 25.7 | 55 | 55/34 | 80 | 62 | 4042 | 3184 | 28.59% | 0.7104 | 0.4913 | 0.30654 | 2.652 | 0.13648 | 0.012662 | 4.428%
489 | KED-02, MARSAGHAI | 2 | MARSAGHAI | 14165 | SILIPUR | 14165203 | 66.2 | 55 | 55/34 | 120 | 78 | 3549 | 2712 | 36.71% | 0.7104 | 0.34836 | 0.26235 | 1.5523 | 0.10753 | 0.057821 | 15.75%
490 | KED-02, MARSAGHAI | 3 | MARSAGHAI | 14165 | ANGULAI | 14165201 | 46.53 | 55 | 55/34 | 50 | 116 | 5699 | 6390 | 17.94% | 0.7104 | 0.62945 | 0.30773 | 5.9826 | 0.1373 | 0.0090091 | 5.022%
491 | KED-02, MARSAGHAI | 4 | GARDAPUR | 14168 | GARDAPUR-1 | 14168201 | 38.7 | 55 | 55/34/25 | 105 | 83 | 5689 | 2981 | 38.6% | 0.7104 | 0.3527 | 0.31527 | 2.8438 | 0.14257 | 0.034312 | 8.89%
492 | KED-02, MARSAGHAI | 5 | GARDAPUR | 14168 | GARDAPUR-2 | 14168202 | 24.8 | 55 | 55/34/25 | 55 | 56 | 3838 | 2053 | 37.37% | 0.7104 | 0.20098 | 0.58269 | 3.6627 | 0.38816 | 0.016426 | 4.396%
493 | KED-02, MARSAGHAI | 6 | KORUA | 14163 | NAGANPUR | 14163203 | 44 | 55 | 55/34 | 80 | 92 | 2725 | 3938 | 48.71% | 0.7104 | 0.40068 | 0.5222 | 1.7879 | 0.3226 | 0.051242 | 10.52%
494 | KED-02, MARSAGHAI | 8 | KORUA | 14163 | BANAKUNDA | 14163204 | 62.4 | 55 | 55/34/25 | 90 | 107 | 5201 | 4163 | 42.92% | 0.7104 | 0.52096 | 0.40903 | 3.0332 | 0.21565 | 0.061483 | 14.32%
495 | KED-02, MARSAGHAI | 9 | KORUA | 14163 | NARENDRAPUR | 14163202 | 4 | 55 | 55/34 | 120 | 10 | 495 | 463 | 42.95% | 0.7104 | 0.62026 | 0.30696 | 0.21651 | 0.13677 | 0.0044437 | 1.035%
496 | KED-02, MARSAGHAI | 11 | LUNA | 14166 | ANKO | 14166202 | 102 | 55 | 55/34 | 110 | 178 | 8155 | 6936 | 38.29% | 0.7104 | 0.72677 | 0.29856 | 3.8913 | 0.13102 | 0.091212 | 23.82%
497 | KED-02, MARSAGHAI | 12 | LUNA | 14166 | OSTARA | 14166203 | 38 | 55 | 55/34 | 70 | 78 | 4036 | 4207 | 30.98% | 0.7104 | 0.41757 | 0.37959 | 3.0263 | 0.19119 | 0.020081 | 6.481%
498 | KED-02, MARSAGHAI | 13 | LUNA | 14166 | KARANJA | 14166204 | 29 | 55 | 55/34 | 50 | 58 | 2650 | 2147 | 54.4% | 0.7104 | 0.29899 | 0.93316 | 2.7819 | 0.88327 | 0.036121 | 6.64%
499 | KED-02, MARSAGHAI | 14 | LUNA | 14166 | NALADIA | 14166205 | 44 | 55 | 55/34 | 85 | 81 | 3901 | 3359 | 48.36% | 0.7104 | 0.49171 | 0.488 | 2.4089 | 0.28811 | 0.051663 | 10.68%
500 | KED-02, MARSAGHAI | 17 | MAHAKALPADA | 14167 | MAHAKALPADA | 14167203 | 33 | 55 | 55/34 | 40 | 60 | 3098 | 2772 | 40.62% | 0.7104 | 0.48288 | 0.87097 | 4.0652 | 0.78106 | 0.023262 | 5.727%
501 | KED-02, MARSAGHAI | 18 | MAHAKALPADA | 14167 | DASAMAUJI | 14167205 | 35 | 55 | 55/34 | 42 | 68 | 2361 | 2105 | 30.31% | 0.7104 | 0.038307 | 0.61898 | 2.9506 | 0.43031 | 0.014986 | 4.944%
502 | KED-02, MARSAGHAI | 19 | BADIHI | 14228 | BIJAYANAGAR-1- BADIHI | 14228201 | 80 | 55 | 55/34 | 55 | 132 | 4880 | 3579 | 46.82% | 0.7104 | 0.26974 | 0.73006 | 4.6571 | 0.57241 | 0.078136 | 16.69%
503 | KED-02, MARSAGHAI | 20 | BADIHI | 14228 | BABAR | 14228202 | 45 | 55 | 55/34 | 32 | 60 | 2098 | 1700 | 14.46% | 0.7104 | 0.12065 | 0.38742 | 3.4412 | 0.19756 | 0.005135 | 3.552%
504 | KED-02, MARSAGHAI | 21 | BADIHI | 14228 | JAMBOO | 14228203 | 98 | 55 | 55/34 | 52 | 170 | 3878 | 4795 | 9.508% | 0.7104 | 0.19394 | 0.15681 | 3.9144 | 0.051035 | 0.0076284 | 8.023%
505 | JED, JAGATSINGHAPUR | 4 | JAGATSINGHPUR | 14169 | PUNANGA | 14169204 | 45.98 | 55 | 55/34 | 100 | 83 | 6070 | 4867 | 43.28% | 0.7104 | 1.2436 | 0.37118 | 3.186 | 0.18446 | 0.047841 | 11.05%
506 | JED, JAGATSINGHAPUR | 6 | NUAPOLA | 14181 | TARIKUNDA | 14181201 | 60 | 55 | 55/34 | 45 | 38 | 1971 | 2773 | 43.04% | 0.7104 | 0.40654 | 0.82028 | 2.299 | 0.70234 | 0.048135 | 11.18%
507 | JED, JAGATSINGHAPUR | 11 | BALIKUDA | 14174 | SANGRAMPUR | 14174202 | 40.75 | 34 | 34 | 88 | 46 | 2106 | 3035 | 27.15% | 1.1325 | 0.30464 | 0.26459 | 1.2561 | 0.10892 | 0.030909 | 11.39%
508 | JED, JAGATSINGHAPUR | 12 | BALIKUDA | 14174 | BALIKUDA | 14174203 | 6.9 | 34 | 34 | 30 | 15 | 1080 | 1269 | 36.99% | 1.1325 | 0.27822 | 1.0575 | 1.8896 | 1.1062 | 0.0061773 | 1.67%
509 | JED, JAGATSINGHAPUR | 20 | BIRIDI | 14171 | BALIA | 14171201 | 38 | 80 | 55/80 | 76 | 98 | 4757 | 4850 | 28.97% | 0.4862 | 0.38067 | 0.32695 | 3.2853 | 0.1509 | 0.012787 | 4.413%
510 | JED, JAGATSINGHAPUR | 22 | BIRIDI | 14171 | RANIPADA | 14171203 | 26 | 80 | 55/80 | 60 | 48 | 2444 | 2412 | 63.8% | 0.4862 | 0.75866 | 0.9119 | 2.138 | 0.84763 | 0.030628 | 4.801%
511 | JED, JAGATSINGHAPUR | 24 | 22MAUJA | 14193 | PARBATIPUR | 14193202 | 35 | 55 | 55 | 40 | 68 | 2391 | 3386 | 17.98% | 0.7104 | 0.24172 | 0.38545 | 3.1375 | 0.19595 | 0.0061895 | 3.443%
512 | JED, JAGATSINGHAPUR | 29 | NAUGAON | 14194 | ROHIA | 14194201 | 32 | 34 | 34 | 30 | 39 | 1253 | 1528 | 44.59% | 1.1325 | 0.18887 | 1.2747 | 2.1922 | 1.5549 | 0.040268 | 9.031%
513 | JED, JAGATSINGHAPUR | 32 | NAUGAON | 14194 | ALANAHAT | 14194204 | 47.1 | 34 | 34 | 66 | 86 | 3861 | 4115 | 12.53% | 1.1325 | 0.39321 | 0.16278 | 3.0705 | 0.053753 | 0.0099169 | 7.917%
514 | JED, JAGATSINGHAPUR | 33 | NAUAPADA | 14195 | PETEIPUR | 14195201 | 75 | 55 | 55 | 48 | 37 | 2800 | 2395 | 43.23% | 0.7104 | 0.35407 | 0.77237 | 3.0618 | 0.63172 | 0.061574 | 14.24%
515 | JED, JAGATSINGHAPUR | 34 | NAUAPADA | 14195 | NALIBERA | 14195202 | 65 | 55 | 55 | 52 | 39 | 2500 | 2335 | 37.67% | 0.7104 | 0.15893 | 0.62122 | 2.5235 | 0.43298 | 0.042926 | 11.4%
[16 empty] | 278.7661 |  |  |  | 15.9559 | 5.724%

## Annexure-J9
Annexure-J9
11 KV TECHNICAL LOSS ESTIMATION USING NAPLAN SOFTWARE TOOL BY DF,ENZENE
SL NO | 33KV / 11 KV PRIMARY DISTRIBUTION S/S NAME | 11 KV FEEDER NAME | PEAK LOAD (MW) | CONNECTED LOAD (KVA) | NO OF DTRS | LENGTH (KM) | TYPE OF CONDUCTOR |  | %TECH LOSS | TAIL END VOLTAGE KV | ANNUAL ENERGY INPUT(KWH) A | LOAD FACTOR | LOSS LOAD FACTOR | TOTAL I2R LOSS (KWH) B | TOTAL NO LOAD LOSS(KWH) C | TOTAL ENERGY LOSS(KWH) D=B+C | % ENERGY LOSS E=(D/A)
1 | CHENDIPADA | CHENDIPADA | 0.9 | 1597 | 27 | 6.976 | RABBIT(6.976) |  | 1.4239 | 10.5556 | 2574260 | 0.32187 | 0.16908 | 19254.7795 | 39157.2 | 58411.9795 | 2.269%
2 |  | DUBANALI | 1.8 | 4304 | 123 | 59.695 | RABBIT(59.695) |  | 10.045 | 9.9 | 7168720 | 0.40897 | 0.23977 | 422176.8574 | 114720.96 | 536897.8174 | 7.489%
3 |  | PIPALA BAHALA | 1.4 | 2712 | 111 | 71.558 |  |  | 16.9532 | 9.23 | 2744010 | 0.18568 | 0.079838 | 200023.6144 | 74372.4 | 274396.0144 | 10%
4 |  | BAGEDIA | 3.2 | 4458 | 128 | 59.175 |  |  | 16.188 | 9.313 | 6232313 | 0.18576 | 0.079881 | 433851.5808 | 113004 | 546855.5808 | 8.775%
5 | RCMS | TOWN-4 | 3.5 | 3058 | 30 | 6.169 | RABBIT(6.14) | XLPE 100 sqmm (0.028) | 2.2613 | 10.4522 | 6923600 | 0.22065 | 0.10027 | 71151.1185 | 70605.6 | 141756.7185 | 2.047%
6 |  | TOWN-2 | 4.9 | 9147 | 65 | 7.535 | RABBIT(7.533) | DOG(0.02) | 8.0675 | 9.9858 | 7053000 | 0.15106 | 0.06129 | 230867.7629 | 83220 | 314087.7629 | 4.453%
7 |  | TOWN-3 | 5.7 | 3761 | 23 | 4.207 | RABBIT(4.183) | XLPE 100 sqmm (0.024) | 7.7073 | 9.7229 | 18048320 | 0.3336 | 0.17798 | 742141.7543 | 81608.16 | 823749.9143 | 4.564%
8 |  | RE-I | 3.5 | 11733 | 120 | 18.734 | RABBIT(18.727) | XLPE 100 sqmm (0.007) | 9.44 | 10.01 | 6201787.395 | 0.18317 | 0.078439 | 250800.7583 | 264569.52 | 515370.2783 | 8.31%
9 |  | COLLEGE | 1.8 | 2267 | 19 | 3.867 | RABBIT(3.792) | XLPE 100 sqmm (0.075) | 1.6376 | 10.7052 | 1467800 | 0.091461 | 0.033294 | 8749.664 | 51946.8 | 60696.464 | 4.135%
10 |  | R.E-II | 3.4 | 6797 | 165 | 63.402 | RABBIT(61.617) | Weasal (1.750), XLPE (0.035) | 13.8981 | 9.0101 | 11752400 | 0.34338 | 0.18555 | 882618.0404 | 176820.6 | 1059438.6404 | 9.015%
11 | KENDRAPARA | TOWN-I | 5.1 | 7292 | 59 | 6.754 | DOG(6.754) |  | 3.0781 | 10.3884 | 20655127 | 0.44801 | 0.2749 | 390122.6738 | 80854.8 | 470977.4738 | 2.28%
12 |  | TOWN-II | 3.33 | 6100 | 65 | 17.962 | DOG(17.001) |  | 3.5621 | 10.3796 | 14321481 | 0.47346 | 0.29896 | 322120.414 | 89352 | 411472.414 | 2.873%
13 |  | TINIMUHANI | 2 | 2273 | 23 | 5.615 | DOG(5.618) |  | 1.1369 | 10.6931 | 9482429 | 0.53508 | 0.36094 | 72722.7106 | 39420 | 112142.7106 | 1.183%
14 |  | THAKURPATNA | 2.8 | 5254 | 113 | 38.939 |  |  | 11.0515 | 9.46 | 8314720 | 0.29971 | 0.15279 | 468449.2079 | 176076 | 644525.2079 | 7.752%
15 |  | BHARATPUR | 2.3 | 2872 | 58 | 31.628 | RABBIT(7.721) | WEASEL (23.907) | 6.4254 | 10.23 | 10850562 | 0.50372 | 0.32873 | 454988.8358 | 89614.8 | 544603.6358 | 5.019%
16 | MARSHAGHAI | MARSHAGHAI | 2.6 | 3708 | 68 | 12.615 | WEASEL(12.615) |  | 4.6088 | 10.117 | 5317880 | 0.21689 | 0.097993 | 110736.5507 | 92943.6 | 203680.1507 | 3.83%
17 |  | SILIPUR | 2.1 | 3798 | 85 | 28.342 | WEASEL(28.217) | XLPE 90 sqmm (0.125) | 7.2783 | 9.9473 | 3902000 | 0.19649 | 0.085971 | 124261.8053 | 103087.68 | 227349.4853 | 5.826%
18 |  | ANGULAI | 2 | 6285 | 130 | 48.516 | XLPE 90 sqmm(0.45896) , Rabbit(14.39) | Weasel (33.66) | 9.2147 | 9.913 | 6688000 | 0.34656 | 0.18804 | 334388.1245 | 161551.92 | 495940.0445 | 7.415%
19 | LUNA | OSTEARA | 1.6 | 4115 | 80 | 28.653 | WEASEL (28.223) | XLPE 90 sqmm(0.43) | 8.0941 | 10.0298 | 5454380 | 0.35743 | 0.19666 | 242906.2554 | 160921.2 | 403827.4554 | 7.404%
20 |  | NALADIA | 1.5 | 3927 | 82 | 31.741 | WEASEL(31.883) | XLPE 120sqmm (0.12) | 13.2759 | 9.3368 | 4952430 | 0.32491 | 0.17137 | 346778.7644 | 94608 | 441386.7644 | 8.913%
21 |  | DASAMAUJI | 1.5 | 2411 | 50 | 20.029 | WEASEL(20.004), SQUIRREL(0.025) | RABBIT (0.18) | 6.3502 | 10.0881 | 3012960 | 0.21205 | 0.095091 | 85798.4193 | 62984.4 | 148782.8193 | 4.938%
22 |  | PATKURA | 3.8 | 9282 | 180 | 83.845 | RABBIT (28.531) | WEASEL (55.514) | 20.829 | 8.1268 | 11708680 | 0.2784 | 0.13778 | 1206916.6345 | 235731.6 | 1442648.2345 | 12.32%
23 |  | ANKUA | 2.6 | 7453 | 75 | 63.058 | RABBIT(22.955) | WEASEL(40.013) | 15.3646 | 9.13 | 7866760 | 0.29233 | 0.14752 | 609943.3175 | 202093.2 | 812036.5175 | 10.32%
[11 empty] | 182693619.395 |  |  |  |  | 10691034.0839 | 5.852%
Average Technical Loss %

## Annexure-J10
Annexure-J10
11 KV TECHNICAL LOSS ESTIMATION USING GIS BASED INTEGRATED NETWORK ANALYSIS(NA) SOFTWARE BY R-APDRP CELL
SL NO | EA_MONTH | EA_TOWN | SUBSTATION_NAME | SUBSTATION_CODE | ASSETNAME | ASSETID | MAIN_METER_NO | TOTAL_UNITS | NO_OF_DT | CONSUMER_HT | CONSUMER_LT | CONSUMER_COUNT | TECHNICAL_ LOSS_NA (%) | TECHNICAL LOSS IN UNITS
1 | 2019-04-01 | DHENKANAL | 33/11 kV COLLEGE SS | 14118 | 11 kV JORANDA | 04/14118/204 | CSC17363 | 144822.6 | 17 | 3 | 503 | 506 | 4.33 | 6270.8186
2 | 2019-04-01 | DHENKANAL | 33/11 kV COLLEGE SS | 14118 | 11 kV SAPTASAJYA | 04/14118/205 | 11266468 | 328200 | 14 | 2 | 202 | 204 | 4.66 | 15294.12
3 | 2019-04-01 | DHENKANAL | 33/11 kV COLLEGE SS | 14118 | 11 kV DKL TOWN-2 | 04/14118/202 | CSC08715 | 404840 | 12 | 2 | 710 | 712 | 5.67 | 22954.428
4 | 2019-04-01 | DHENKANAL | 33/11 kV COLLEGE SS | 14118 | 11 kV GOVINDPUR | 04/14118/203 | CSC17540 | 222240 | 7 | 1 | 464 | 465 | 6.87 | 15267.888
5 | 2019-04-01 | JATNI | 33/11 kV JATANI SS | 14033 | 11 kV JATNI TOWN | 06/14033/204 | CSD30662 | 523000 | 21 | 3 | 667 | 670 | 4.22 | 22070.6
6 | 2019-04-01 | JATNI | 33/11 kV JATANI SS | 14033 | 11 kV JATNI RURAL | 06/14033/205 | VMF00007 | 637800 | 65 | 14 | 1860 | 1874 | 6.36 | 40564.08
7 | 2019-04-01 | JATNI | 33/11 kV JATANI SS | 14033 | 11 kV BACHHARA | 06/14033/201 | CSD30514 | 660520 | 27 | 3 | 1913 | 1916 | 6.96 | 45972.192
8 | 2019-04-01 | JATNI | 33/11 kV JATANI SS | 14033 | 11 kV KUSUMATI | 06/14033/203 | CSD30464 | 797600 | 39 | 3 | 2226 | 2229 | 7.15 | 57028.4
10 | 2019-04-01 | KHORDHA | 33/11 kV OIL MILL SS | 14043 | 11 kV INDUSTRIAL | 08/14043/204 | CSD30466 | 987600 | 76 | 44 | 62 | 106 | 4.7 | 46417.2
11 | 2019-04-01 | PATTAMUNDAI | 33/11 kV PATTAMUNDAI SS | 14153 | 11 kV BAZAR | 10/14153/202 | X0614097 | 770562 | 33 | 4 | 1617 | 1621 | 7.05 | 54324.621
[8 empty] | 5477184.6 |  |  |  |  | 5.955% | 326164.3476

## Annexure-J11
Annexure-J11
TOTAL DTR CAPACITY AND LENGTH OF LT LINE OF THE SYSTEM
1 | No of 11/0.4kv transformer | [6 empty] | Bhubaneswar No-I Circle |  |  |  |  | Bhubaneswar No-II Circle |  |  |  |  | Cuttack Circle | [5 empty] | Paradip Circle |  |  |  |  | Dhenkanal Circle |  |  |  | CESU Total
|  | urban | rural | KVA | Total KVA urban | Total KVA rural |  | BCDD-I ,BBSR | BCDD-II ,BBSR | BED-BBSR | NED-Nimapara | Total | PED -Puri | NED-Nayagarh | KED-Khurda | BED-Balugaon | Total | CDD-I- CTC | CDD-II- CTC | CED- CTC | AED-Athagarh | SED- Salipur | Total | KED-I- Kendrapara | KED-II- Marshaghai | PDP- Paradip | JED-J .S.Pur | Total | DED-Dkl | TED-Chainpal | AED-Angul | Total
| 1000KVA | 39 | 3 | 1000 | 39000 | 3000 |  | 5 | 18 | 7 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 42
| 800KVA | 3 | 0 | 800 | 2400 | 0 |  | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
| 750KVA | 27 | 29 | 750 | 20250 | 21750 |  | 4 | 8 | 10 | 0 | 22 | 27 | 0 | 0 | 0 | 27 | 5 | 0 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 56
| 500KVA | 1037 | 352 | 500 | 518500 | 176000 |  | 183 | 259 | 338 | 26 | 806 | 113 | 32 | 33 | 4 | 182 | 185 | 72 | 36 | 13 | 15 | 321 | 11 | 1 | 4 | 0 | 16 | 10 | 15 | 39 | 64 | 1389
| 350KVA | 13 | 9 | 350 | 4550 | 3150 |  | 9 | 0 | 4 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22
| 315KVA | 21 | 10 | 315 | 6615 | 3150 |  | 4 | 7 | 7 | 0 | 18 | 4 | 0 | 0 | 0 | 4 | 3 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 31
| 300KVA | 0 | 1 | 300 | 0 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
| 250KVA | 2310 | 1355 | 250 | 577500 | 338750 |  | 420 | 642 | 550 | 68 | 1680 | 267 | 88 | 148 | 50 | 553 | 464 | 234 | 138 | 51 | 21 | 908 | 81 | 2 | 39 | 34 | 156 | 121 | 122 | 125 | 368 | 3665
| 200KVA | 144 | 118 | 200 | 28800 | 23600 |  | 10 | 22 | 32 | 5 | 69 | 23 | 8 | 15 | 7 | 53 | 46 | 34 | 15 | 3 | 5 | 103 | 0 | 1 | 7 | 12 | 20 | 5 | 8 | 4 | 17 | 262
| 150KVA | 96 | 54 | 150 | 14400 | 8100 |  | 22 | 21 | 32 | 0 | 75 | 7 | 0 | 0 | 0 | 7 | 18 | 3 | 14 | 0 | 1 | 36 | 19 | 2 | 3 | 0 | 24 | 1 | 4 | 3 | 8 | 150
| 100KVA | 2835 | 8422 | 100 | 283500 | 842200 |  | 503 | 883 | 901 | 723 | 3010 | 682 | 692 | 714 | 373 | 2461 | 251 | 297 | 720 | 420 | 400 | 2088 | 806 | 332 | 409 | 418 | 1965 | 562 | 679 | 492 | 1733 | 11257
| 63KVA | 1193 | 10757 | 63 | 75159 | 677691 |  | 99 | 472 | 407 | 899 | 1877 | 917 | 734 | 1049 | 702 | 3402 | 97 | 118 | 947 | 578 | 630 | 2370 | 805 | 255 | 454 | 643 | 2157 | 664 | 737 | 743 | 2144 | 11950
| 50KVA | 1 | 12 | 50 | 50 | 600 |  | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 1 | 8 | 0 | 1 | 0 | 0 | 1 | 2 | 1 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 1 | 13
| 25KVA | 1663 | 16765 | 25 | 41575 | 419125 |  | 111 | 570 | 669 | 1490 | 2840 | 1240 | 1981 | 951 | 1064 | 5236 | 161 | 152 | 915 | 698 | 667 | 2593 | 1304 | 632 | 620 | 938 | 3494 | 1382 | 1510 | 1373 | 4265 | 18428
| 16KVA | 61 | 1325 | 16 | 976 | 21200 |  | 61 | 0 | 0 | 5 | 66 | 0 | 244 |  | 319 | 563 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 1 | 309 | 195 | 245 | 749 | 1386
| Total | 9443 | 39212 | 48655 | 1613275 | 2538616 |  | 1431 | 2902 | 2959 | 3216 | 10508 | 3283 | 3783 | 2910 | 2520 | 12496 | 1235 | 916 | 2808 | 1763 | 1740 | 8462 | 3027 | 1226 | 1537 | 2046 | 7836 | 3055 | 3272 | 3026 | 9353 | 48655
2 | No of 11/0.23kv transformer
| 25KVA | 24 | 1852 | 25 | 600 | 46300 |  | 0 | 0 | 4 | 0 | 4 | 0 | 26 | 165 | 540 | 731 | 0 | 20 | 303 | 271 | 186 | 780 | 116 | 55 | 19 | 171 | 361 | 0 | 0 | 0 | 0 | 1876
| 16KVA | 1338 | 11997 | 16 | 21408 | 191952 |  | 61 | 450 | 569 | 953 | 2033 | 701 | 704 | 1121 | 555 | 3081 | 81 | 177 | 1026 | 916 | 516 | 2716 | 1098 | 779 | 781 | 939 | 3597 | 476 | 786 | 646 | 1908 | 13335
| 10KVA | 55 | 6262 | 10 | 550 | 62620 |  | 0 | 38 | 12 | 538 | 588 | 531 | 1825 | 97 | 212 | 2665 | 0 | 5 | 35 | 18 | 13 | 71 | 13 | 4 | 14 | 29 | 60 | 805 | 1029 | 1099 | 2933 | 6317
| Total | 1417 | 20111 | 21528 | 22558 | 300872 |  | 61 | 488 | 585 | 1491 | 2625 | 1232 | 2555 | 1383 | 1307 | 6477 | 81 | 202 | 1364 | 1205 | 715 | 3567 | 1227 | 838 | 814 | 1139 | 4018 | 1281 | 1815 | 1745 | 4841 | 21528
| All Total | 10860 | 59323 | 70183 | 1635833 | 2839488 |  | 1492 | 3390 | 3544 | 4707 | 13133 | 4515 | 6338 | 4293 | 3827 | 18973 | 1316 | 1118 | 4172 | 2968 | 2455 | 12029 | 4254 | 2064 | 2351 | 3185 | 11854 | 4336 | 5087 | 4771 | 14194 | 70183
3 | LT lines ( bare ) (KM)
|  | urban 3ph | rural 3ph
| 3P5W | 613.352 | 442.492 |  |  |  | 5 | 280.12 | 207.012 | 75.35 | 17.65 | 580.132 | 27.26 | 31.412 | 58.18 | 25.3 | 142.152 | 0 | 50.87 | 4.5 | 20.6 | 14.86 | 90.83 | 20.89 | 2.5 | 0.1 | 32.55 | 56.04 | 28.78 | 53.31 | 104.6 | 186.69 | 1055.844
| 3P4W | 1403.88 | 8629.46 |  |  |  | 4 | 218.19 | 465.32 | 135.55 | 677.45 | 1496.51 | 577.35 | 336 | 664.32 | 356.61 | 1934.28 | 232.06 | 352.76 | 824.36 | 283.03 | 576.37 | 2268.58 | 857.23 | 654.35 | 375.88 | 714.04 | 2601.5 | 798.32 | 420.2 | 513.95 | 1732.47 | 10033.34
| 3P3W | 0 | 109.57 |  |  |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 17.72 | 0 | 0 | 17.72 | 0 | 0 | 0 | 0 | 13.1 | 13.1 | 71.85 | 4.9 | 0 | 0 | 76.75 | 0 | 2 | 0 | 2 | 109.57
| 2P4W | 2.37 | 88.62 |  |  |  | 4 | 0 | 2.18 | 0.19 | 0 | 2.37 | 0 | 29.71 | 0 | 21.03 | 50.74 | 0 | 0 | 0 | 0.8 | 0 | 0.8 | 7.25 | 0 | 0 | 0 | 7.25 | 29.63 | 0.2 | 0 | 29.83 | 90.99
| 2P3W | 385.85 | 3577.321 |  |  |  | 3 | 73.78 | 106.32 | 87.6 | 467.75 | 735.45 | 485.5 | 211.961 | 221.8 | 64.81 | 984.071 | 59.75 | 58.4 | 1.2 | 145.86 | 97.58 | 362.79 | 202.29 | 180 | 174.4 | 375.25 | 931.94 | 250.66 | 260.42 | 437.84 | 948.92 | 3963.171
| 1P3W | 31.87 | 91.45 |  |  |  | 3 | 0 | 0.96 | 28.14 | 0 | 29.1 | 0 | 6.99 | 0 | 5.25 | 12.24 | 0 | 2.77 | 0 | 21 | 2.1 | 25.87 | 18.15 | 0 | 0 | 0 | 18.15 | 37.77 | 0.19 | 0 | 37.96 | 123.32
| 1P2W | 522.33 | 10669.715 |  |  |  | 2 | 99.25 | 119.12 | 129.26 | 917.78 | 1265.41 | 970.2 | 262.1 | 813.39 | 122.005 | 2167.695 | 0 | 174.7 | 461.87 | 884.7 | 1021.26 | 2542.53 | 844.8 | 410 | 664.85 | 1007.58 | 2927.23 | 884.17 | 598.3 | 806.71 | 2289.18 | 11192.045
| Total | 2959.652 | 23608.628 |  |  |  |  | 671.34 | 900.912 | 456.09 | 2080.63 | 4108.972 | 2060.31 | 895.893 | 1757.69 | 595.005 | 5308.898 | 291.81 | 639.5 | 1291.93 | 1355.99 | 1725.27 | 5304.5 | 2022.46 | 1251.75 | 1215.23 | 2129.42 | 6618.86 | 2029.33 | 1334.62 | 1863.1 | 5227.05 | 26568.28
4 | L.T. Lines (ABC) (KM)
| 3P5W | 1620.602 | 1045.518 |  |  |  | 5 | 333.69 | 386.15 | 412.76 | 78.65 | 1211.25 | 185.65 | 73.988 | 185 | 184.56 | 629.198 | 231.01 | 256.992 | 61.8 | 59.34 | 19.36 | 628.502 | 53.9 | 0 | 26.35 | 37.8 | 118.05 | 32.98 | 56.26 | 55.95 | 79.12 | 2666.12
| 3P4W | 830.05 | 7736.127 |  |  |  | 4 | 240.25 | 310.85 | 99.81 | 735.12 | 1386.03 | 339.67 | 839.87 | 481.67 | 758.18 | 2419.39 | 34.28 | 144.86 | 506.3 | 393.27 | 218.437 | 1297.147 | 366.3 | 143.65 | 268.35 | 793.65 | 1571.95 | 567.65 | 556.48 | 767.53 | 1891.66 | 8566.177
| 3P3W | 0 | 162.14 |  |  |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.35 | 0 | 9.35 | 0 | 0 | 0 | 0 | 0 | 0 | 71.85 | 0 | 0 | 0 | 71.85 | 0 | 2.04 | 78.9 | 80.94 | 162.14
| 2P4W | 3.66 | 61.84 |  |  |  | 4 | 0 | 2.96 | 0 | 0 | 2.96 | 0 | 0.88 | 0 | 4.42 | 5.3 | 0 | 0.7 | 0.75 | 0 | 0 | 1.45 | 7.25 | 0 | 0 | 0 | 7.25 | 29.63 | 18.91 | 0 | 48.54 | 65.5
| 2P3W | 93.986 | 1959.48 |  |  |  | 3 | 48.2 | 12.096 |  | 5 | 65.296 | 571.6 | 173.29 | 37.6 | 129.04 | 911.53 | 25.15 | 8.54 | 11.23 | 17.72 | 27.17 | 89.81 | 202.29 | 11.25 | 174.4 | 108.32 | 496.26 | 222.57 | 11.38 | 256.62 | 490.57 | 2053.466
| 1P3W | 33.66 | 1119.95 |  |  |  | 3 | 29.31 | 3.5 | 0 | 0 | 32.81 | 383.79 | 15 | 0 | 3.25 | 402.04 | 0 | 0.85 | 0 | 0.35 | 0 | 1.2 | 18.15 | 0 | 661.64 | 0 | 679.79 | 37.77 | 0 | 0 | 37.77 | 1153.61
| 1P2W | 425.82 | 12213.36 |  |  |  | 2 | 45.46 | 124.76 | 117.87 | 324.3 | 612.39 | 103.89 | 1185.84 | 992.4 | 983.55 | 3265.68 | 0.37 | 137.36 | 1713.6 | 777.71 | 793.57 | 3422.61 | 843.75 | 965 |  | 1091.11 | 2899.86 | 868.41 | 897.1 | 673.13 | 2438.64 | 12639.18
| Total | 3007.778 | 24298.415 |  |  |  |  | 696.91 | 840.316 | 630.44 | 1143.07 | 3310.736 | 1584.6 | 2288.868 | 1706.02 | 2063 | 7642.488 | 290.81 | 549.302 | 2293.68 | 1248.39 | 1058.537 | 5440.719 | 1563.49 | 1119.9 | 1130.74 | 2030.88 | 5845.01 | 1759.01 | 1542.17 | 1832.13 | 5133.31 | 27372.263
| All Total | 5967.43 | 47907.043 |  |  |  |  | 1368.25 | 1741.228 | 1086.53 | 3223.7 | 7419.708 | 3644.91 | 3184.761 | 3463.71 | 2658.005 | 12951.386 | 582.62 | 1188.802 | 3585.61 | 2604.38 | 2783.807 | 10745.219 | 3585.95 | 2126.36 | 2345.97 | 4160.3 | 12218.58 | 3788.34 | 2876.79 | 3695.23 | 10360.36 | 53695.253
53874.473
| Particulars |  |  | Urban | Rural | Total=Urban+Rural | [28 empty] | 63.7665
| Total DTR Capacity in KVA |  | a | 1635833 | 2839488 | 4475321
|  | Bare Line in KM | b | 2959.652 | 23608.628 | 26568.28
|  | ABC in KM | c | 3007.778 | 24298.415 | 27306.193 | [5 empty] | urban 1ph (3Ph*no of W) | rural 1ph (3Ph*no of W)
| Total LT Line in KM |  | d=b+c | 5967.43 | 47907.043 | 53874.473 | [5 empty] | 3066.76 | 2212.46
|  | bare- km/kva | e=b/a | 0.0018093 | 0.0083144 | 0.010124 | [5 empty] | 5615.52 | 34517.84
|  | abc-km/kva | f=c/a | 0.0018387 | 0.0085573 | 0.010396 | [5 empty] | 0 | 328.71
| LT Line in KM/KVA |  | g=e+f or d/a | 0.0036479 | 0.016872 | 0.02052 | [5 empty] | 9.48 | 354.48
|  | bare- km/100kva | p=e*100 | 0.18093 | 0.83144 | 1.0124 | [5 empty] | 1157.55 | 10731.963
|  | abc-km/100kva | q=f*100 | 0.18387 | 0.85573 | 1.0396 | [5 empty] | 95.61 | 274.35
| LT Line in KM/100KVA |  | s=p+q or g*100 | 0.36479 | 1.6872 | 2.052 | [5 empty] | 1044.66 | 21339.43
[12 empty] | 10989.58 | 69759.233
| LT line loading |  | A | 40% | 25%
| Average current in LT line |  | I=A*139 | 55.6 | 34.75 |  |  |  | 42.3712 |  |  | 8103.01 | 5227.59 | [20 empty] | 2665290.25
|  | Resistance at 60C for Bare Conductor | R1 in Ohm | 1.1326 | 1.1326 | [6 empty] | 3320.2 | 30944.508
|  | Resistance at 60C for AB Cable | R2 in Ohm | 0.733 | 0.733 | [6 empty] | 0 | 486.42
|  | Line loss in Units for Bare Conductor | C1=I*I*R1*(24*30)*p | 456100.2612 | 818746.3615 | [6 empty] | 14.64 | 247.36 | [20 empty] | 37.9763
|  | Line loss in Units for AB Conductor | C2=I*I*R2*(24*30)*q | 299980.3915 | 544616.8864 | [6 empty] | 281.958 | 5878.44 | [20 empty] | 1996558.8523
| Total Loss in LT Line |  | C=C1+C2 | 756080.6527 | 1363363.2479 | [6 empty] | 100.98 | 3359.85 | [20 empty] | 37.0595
[12 empty] | 851.64 | 24426.72
[12 empty] | 12672.428 | 70570.888
| 100KVA DT output |  | D=100*0.9*A*(24*30)*1000 | 25920000 | 16200000 |  |  |  |  | 1364205.2 |  | 23662.008 | 140330.121 | [20 empty] | 19174.75
| Loss(%) |  | E=(C/D)*100 | 2.917% | 8.416% |  |  |  |  | 0.30483 |  | 163992.129 | [21 empty] | 0.27321
| KVA represntation |  | F= E*a | 47716.8859 | 238966.2705 | 286683.1564
| Total Loss (%) |  | L=F/a |  |  | 6.406%
| total LT line of CESU |  |  | 163992.129 | kms
| average loading |  |  | 40% | 40 % loading
| average kva |  |  | 63.7665 | = upgraded to 63 KVA | [30 empty] | 47.0588
| maximum current |  |  | 91 | Amps
| average loading amp |  |  | 36.4 | (40% loading)
| average resistance |  |  | 0.79066 | ohm
91.0405
| total loss |  |  | 41.2311 | mu | [29 empty] | 30.9538
| avg input to cesu LT |  |  | 473.4167 | mu
| percentage loss |  |  | 8.709%

## Annexure-J12
Annexure-J12
LOAD FLOW STUDY IN LT LINES USING CYMDIST SOFTWARE BY DF, FEDCO
Sl No | 11kV Feeder name | DT location | Transformer rating | Loading (%) | VA (%) | Total Thru Power (kW) | Total Dw Losses (kW) | LT network Length in Metre | % Technical Losses
1 | BALUGAON | NEAR_PONDBGDS134 | 63KVA | 6.3 | 96.84 | 3 | 0.14 | 721.88 | 4.667%
2 | BALUGAON | RAUGHNATHPUR_TALABBGDS45 | 16KVA | 6.8 | 97.53 | 1 | 0.04 | 483.92 | 4%
3 | BALUGAON | NEAR_PAIRMARY_SCHOOL___CBGDS136 | 16KVA | 9.1 | 96.74 | 1 | 0.04 | 412.9 | 4%
4 | BALUGAON | NEAR_MAN_GATE_INS_CHILIKBGDS143 | 100KVA | 10.6 | 96.57 | 9 | 0.24 | 293.91 | 2.667%
5 | BALUGAON | RAMPUR_CHAK_RELWE_CROSINBGDS157 | 250KVA | 11.9 | 98.86 | 24 | 0.54 | 1511.75 | 2.25%
6 | BALUGAON | SANTI_NAGER_NEAR_CHILKABGDS99 | 63KVA | 19.1 | 97.93 | 10 | 0.26 | 685.47 | 2.6%
7 | BALUGAON | NEAR_ROADBGDS07 | 200KVA | 19.4 | 98.11 | 31 | 1.11 | 689.41 | 3.581%
8 | BALUGAON | MAIN_ROADBGDS83 | 250KVA | 20 | 98.18 | 40 | 1.11 | 1336.27 | 2.775%
9 | BALUGAON | OPPISET_TALABBGDS46 | 63KVA | 20.2 | 96.42 | 10 | 0.21 | 153.98 | 2.1%
10 | BALUGAON | NEAR_TALABBGDS28 | 16KVA | 20.5 | 96.98 | 3 | 0.05 | 442.86 | 1.667%
11 | BALUGAON | MAIN_ROAD_BALUGAON._NEARBGDS101 | 500KVA | 21.2 | 97.85 | 86 | 6.75 | 746.65 | 7.849%
12 | BALUGAON | GHUMU_SAR_PADARBGDS19 | 100KVA | 21.3 | 97 | 17 | 0.87 | 736.4 | 5.118%
13 | BALUGAON | SANTRAPURBGDS77 | 100KVA | 21.6 | 95.42 | 17 | 0.42 | 435.99 | 2.471%
14 | BALUGAON | NEAR_P.SCHOOLBGDS75 | 100KVA | 22.2 | 95.39 | 18 | 0.64 | 947.56 | 3.556%
15 | BALUGAON | NEAR_PONDBGDS133 | 100KVA | 22.6 | 96.26 | 18 | 0.67 | 899.85 | 3.722%
16 | BALUGAON | NEAR_BRAHMPUR_ROADBGDS110 | 16KVA | 22.7 | 97.42 | 3 | 0.06 | 498.7 | 2%
17 | BALUGAON | VILLEGE_IN_OUTSIDEBGDS43 | 63KVA | 23.1 | 96.31 | 12 | 0.26 | 383.9 | 2.167%
18 | BALUGAON | SAMANTRA_PURBGDS94 | 250KVA | 23.7 | 97.8 | 48 | 2.32 | 624.14 | 4.833%
19 | BALUGAON | KOLURIBGDS66 | 100KVA | 23.8 | 95.5 | 19 | 0.52 | 678.86 | 2.737%
20 | BALUGAON | NEAR_SCHOOLBGDS128 | 16KVA | 24.9 | 96.26 | 3 | 0.05 | 380.55 | 1.667%
21 | BALUGAON | MAIN_ROAD__OPPSITE_INDIABGDS100 | 250KVA | 25 | 97.77 | 51 | 2.4 | 710.14 | 4.706%
22 | BALUGAON | BALUGAON_RAILWE_STATIONBGDS151 | 250KVA | 25.9 | 97.92 | 53 | 4.24 | 580.31 | 8%
23 | BALUGAON | NEAR_MAIN_ROADBGDS52 | 100KVA | 26.8 | 95.92 | 22 | 0.63 | 373.67 | 2.864%
24 | BALUGAON | VILLEGE_IN_OUTSIDEBGDS69 | 63KVA | 27.1 | 95.32 | 14 | 0.6 | 559.28 | 4.286%
25 | BALUGAON | NEAR_ROADBGDS15 | 250KVA | 27.2 | 97.18 | 55 | 3.55 | 2605.85 | 6.455%
26 | BALUGAON | NEAE_RAILWAY_STATIONBGDS160 | 100KVA | 28.1 | 97.84 | 23 | 1.18 | 1382.53 | 5.13%
27 | BALUGAON | NEAR_BRAHMPUR_ROADBGDS109 | 25KVA | 29.1 | 97.13 | 7 | 0.73 | 313.66 | 10.43%
28 | BALUGAON | VILLEGE_ROADBGDS70 | 16KVA | 29.5 | 95.15 | 4 | 0.07 | 349.03 | 1.75%
29 | BALUGAON | NEAR_CHILKABGDS118 | 16KVA | 29.5 | 96.41 | 4 | 0.06 | 332.76 | 1.5%
30 | BALUGAON | DANGUA_OPPOSITE__SCHOOLBGDS56 | 63KVA | 30.3 | 95.51 | 15 | 0.43 | 969.46 | 2.867%
31 | BALUGAON | NEARR_CHILKA_FOREST_OFFIBGDS96 | 63KVA | 30.5 | 97.49 | 16 | 0.56 | 941.76 | 3.5%
32 | BALUGAON | NEAR_PONDBGDS140 | 100KVA | 30.9 | 95.86 | 25 | 0.77 | 1239.42 | 3.08%
33 | BALUGAON | NEAR_CHILKABGDS159 | 16KVA | 31.8 | 96.33 | 4 | 0.06 | 151.23 | 1.5%
34 | BALUGAON | NEAR_PONDBGDS127 | 16KVA | 31.8 | 96.01 | 4 | 0.07 | 685.56 | 1.75%
35 | BALUGAON | NEAR_POND_&TEMPLEBGDS22 | 63KVA | 31.9 | 96.51 | 16 | 0.37 | 531.25 | 2.312%
36 | BALUGAON | NEAR_BARKULBGDS124 | 100KVA | 32.3 | 96.01 | 26 | 0.72 | 1963.47 | 2.769%
37 | BALUGAON | NEAR_BALUGAON_TRAIN_STATBGDS05 | 100KVA | 32.8 | 97.67 | 27 | 1.51 | 613.16 | 5.593%
38 | BALUGAON | NEAR_JALESHWARBGDS33 | 100KVA | 33.1 | 96.41 | 27 | 1.08 | 804.66 | 4%
39 | BALUGAON | NEAR_TALABBGDS27 | 25KVA | 33.4 | 96.43 | 7 | 0.74 | 444.99 | 10.57%
40 | BALUGAON | NEAR_BAPUJI_CLUBBGDS37 | 25KVA | 33.4 | 96.32 | 7 | 0.74 | 497.61 | 10.57%
41 | BALUGAON | MAIN_ROADBGDS54 | 63KVA | 34.9 | 95.46 | 18 | 0.5 | 2860.16 | 2.778%
42 | BALUGAON | GHIOKHOLA_SCHOOLBGDS25 | 100KVA | 35 | 96.44 | 28 | 0.89 | 492.27 | 3.179%
43 | BALUGAON | RAHANBELIBGDS60 | 63KVA | 35 | 95.14 | 18 | 0.57 | 880.25 | 3.167%
44 | BALUGAON | NEAR_UTTARNI_ROAD___GOPABGDS09 | 250KVA | 35 | 97.12 | 72 | 9.46 | 2937.53 | 13.14%
45 | BALUGAON | BGDS20 | 100KVA | 36.4 | 96.45 | 29 | 1.14 | 812.88 | 3.931%
46 | BALUGAON | KUMANDALBGDS74 | 10KVA | 36.4 | 94.63 | 3 | 0.05 | 667.34 | 1.667%
47 | BALUGAON | RAMPUR_SCHOOL_OPPISET_RABGDS06 | 100KVA | 37 | 97.86 | 30 | 0.72 | 818.4 | 2.4%
48 | BALUGAON | NEAR_JUBO_JYOTI_YOUTH__CBGDS73 | 16KVA | 38.6 | 94.78 | 5 | 0.09 | 507.94 | 1.8%
49 | BALUGAON | NEAR_PONDBGDS148 | 100KVA | 39.4 | 95.47 | 32 | 1.3 | 531.53 | 4.062%
50 | BALUGAON | KOLURIBGDS67 | 16KVA | 40.9 | 94.86 | 5 | 0.09 | 669.74 | 1.8%
51 | BALUGAON | NEAR_PAIRMARY_SCHOOL___TBGDS139 | 100KVA | 43 | 95.42 | 35 | 1.29 | 1031.68 | 3.686%
52 | BALUGAON | NEAR_CHILKAROAD___SAMBHUBGDS89 | 100KVA | 43.4 | 97.12 | 35 | 0.98 | 391.02 | 2.8%
53 | BALUGAON | BAMPUR_ROADBGDS112 | 10KVA | 43.5 | 96.36 | 4 | 0.06 | 187.52 | 1.5%
54 | BALUGAON | NEAR_PONDBGDS39 | 100KVA | 44.2 | 95.73 | 36 | 1.74 | 1000 | 4.833%
55 | BALUGAON | NEAR_THAKUR_RANI_DEVU_MABGDS92 | 100KVA | 44.2 | 97.06 | 36 | 0.77 | 858.91 | 2.139%
56 | BALUGAON | GOPAL_AUTO_GRAZEBGDS10 | 250KVA | 44.6 | 96.77 | 92 | 13.21 | 2051.11 | 14.36%
57 | BALUGAON | NEAR__PONDBGDS31 | 63KVA | 46.2 | 95.83 | 24 | 0.8 | 635.86 | 3.333%
58 | BALUGAON | BALUGAON_RAILWE_STATIONBGDS153 | 100KVA | 46.3 | 97.17 | 37 | 1.69 | 585.81 | 4.568%
59 | BALUGAON | NEAR_MANDIRBGDS21 | 100KVA | 47.2 | 96.04 | 39 | 3.94 | 1212.66 | 10.1%
60 | BALUGAON | CHILKA_ROADBGDS88 | 100KVA | 47.3 | 96.97 | 38 | 0.98 | 724.21 | 2.579%
61 | BALUGAON | NEAR_TEMPLE___BALUGAON_RBGDS115 | 100KVA | 47.3 | 95.64 | 38 | 1.63 | 1777.44 | 4.289%
62 | BALUGAON | NEAR_ANGANWARI_SCHOOLBGDS24 | 25KVA | 48.1 | 95.84 | 10 | 0.83 | 168.79 | 8.3%
63 | BALUGAON | NEAR_POND_&_WATER_TANKBGDS18 | 25KVA | 48.2 | 95.92 | 10 | 0.84 | 367.93 | 8.4%
64 | BALUGAON | KALIJAYSHAIBGDS104 | 250KVA | 50.2 | 96.61 | 102 | 7.98 | 3481.69 | 7.824%
65 | BALUGAON | VILLEGE_ROADBGDS123 | 100KVA | 50.3 | 95.35 | 41 | 2.44 | 713.29 | 5.951%
66 | BALUGAON | BALUGAON_RAILWE_STATIONBGDS154 | 100KVA | 52.2 | 96.96 | 43 | 3.58 | 698.39 | 8.326%
67 | BALUGAON | BIDHARPURBGDS119 | 25KVA | 53.9 | 95.53 | 12 | 0.86 | 217.65 | 7.167%
68 | BALUGAON | NEAR_ANGANWARI_SCHOOLBGDS26 | 16KVA | 54.5 | 95.7 | 7 | 0.12 | 353.5 | 1.714%
69 | BALUGAON | NEAR_PONDBGDS80 | 63KVA | 55.4 | 94.16 | 28 | 1.25 | 865.3 | 4.464%
70 | BALUGAON | BRAMPUR_ROADBGDS114 | 100KVA | 55.5 | 95.82 | 45 | 4.37 | 926.55 | 9.711%
71 | BALUGAON | NEAR_JUBO_JYOTI_YOUTH_CLBGDS71 | 63KVA | 56.8 | 93.98 | 29 | 1.75 | 912.73 | 6.034%
72 | BALUGAON | NEAR_PONDBGDS23 | 16KVA | 56.9 | 95.63 | 7 | 0.14 | 438.03 | 2%
73 | BALUGAON | NEAR_PONDBGDS141 | 16KVA | 56.9 | 94.88 | 7 | 0.14 | 468.67 | 2%
74 | BALUGAON | BRAMPUR__ROADBGDS111 | 100KVA | 58 | 96.12 | 47 | 2.98 | 383.07 | 6.34%
75 | BALUGAON | MAIN_ROADBGDS29 | 63KVA | 58.4 | 95.42 | 30 | 2.33 | 815.9 | 7.767%
76 | BALUGAON | MAIN_ROADBGDS44 | 16KVA | 61.4 | 94.92 | 8 | 0.15 | 668.12 | 1.875%
77 | BALUGAON | M/S_MRUTI_RICEBGDS48 | 16KVA | 61.4 | 94.74 | 8 | 0.15 | 205.9 | 1.875%
78 | BALUGAON | NEAR_PONDBGDS120 | 16KVA | 63.9 | 94.99 | 8 | 0.18 | 599.71 | 2.25%
79 | BALUGAON | NEAR_KALIJI_COMERCIAL_COBGDS108 | 25KVA | 65.4 | 95.72 | 14 | 0.88 | 870.05 | 6.286%
80 | BALUGAON | NEAR_PONDBGDS161 | 16KVA | 66.2 | 94.91 | 9 | 0.2 | 807.3 | 2.222%
81 | BALUGAON | NEAR_P.B._COLLAGEBGDS63 | 63KVA | 67 | 93.77 | 35 | 3.15 | 1081.27 | 9%
82 | BALUGAON | NEAR_MAIN_ROADBGDS53 | 16KVA | 68.4 | 94.34 | 9 | 0.2 | 527.38 | 2.222%
83 | BALUGAON | NEAR_PRAIMARY_SCHOOLBGDS76 | 16KVA | 70.7 | 93.53 | 9 | 0.2 | 1191.05 | 2.222%
84 | BALUGAON | NEAR_PAIRMARY_SCHOOL___TBGDS138 | 16KVA | 70.7 | 94.35 | 9 | 0.21 | 693.34 | 2.333%
85 | BALUGAON | NEAR_CHILKABGDS116 | 100KVA | 70.9 | 94.85 | 58 | 2.07 | 1141.01 | 3.569%
86 | BALUGAON | NEAR_PONDBGDS129 | 100KVA | 72.9 | 94.45 | 59 | 2.94 | 1684.78 | 4.983%
87 | BALUGAON | KHETRAPELABGDS58 | 16KVA | 73 | 93.82 | 9 | 0.22 | 965.95 | 2.444%
88 | BALUGAON | NEAR_JUBO_JYOTI_YOUTH_CLBGDS72 | 63KVA | 79.8 | 93.03 | 41 | 2.4 | 919.09 | 5.854%
89 | BALUGAON | NEAR_TEMPLEBGDS131 | 16KVA | 89.1 | 93.79 | 12 | 0.31 | 830.82 | 2.583%
90 | BALUGAON | BAKSA_BALIBGDS47 | 10KVA | 90.8 | 93.14 | 7 | 0.19 | 187.75 | 2.714%
91 | BALUGAON | NEAR_PONDBGDS32 | 16KVA | 91.3 | 94.19 | 12 | 0.31 | 690.35 | 2.583%
[6 empty] | 2159 | 122.08 |  | 5.654%

## Annexure-K
Annexure-K
Grievances Redressal Forum (GRF) Cases up to September-2019
Sl. No. | Name of the GRFs. | Sept, 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019-09-19 | Total Cases | Disposed off | Pending
1 | GRF, Bhubaneswar | 46 | 159 | 126 | 82 | 122 | 190 | 230 | 103 | 123 | 121 | 199 | 434 | 344 | 538 | 620 | 654 | 4091 | 4080 | 11
2 | GRF, Cuttack | 39 | 208 | 157 | 106 | 161 | 135 | 195 | 589 | 614 | 634 | 820 | 917 | 950 | 1470 | 1049 | 797 | 8841 | 8836 | 5
3 | GRF, Dhenkanal | 17 | 48 | 45 | 30 | 102 | 50 | 141 | 213 | 247 | 258 | 577 | 740 | 979 | 826 | 819 | 660 | 5752 | 5748 | 4
4 | GRF, Khurda | - | - | 17 | 77 | 134 | 123 | 117 | 202 | 339 | 354 | 356 | 632 | 524 | 560 | 941 | 833 | 5209 | 5199 | 10
5 | GRF, Paradeep | - | - | 54 | 123 | 421 | 376 | 205 | 183 | 327 | 251 | 489 | 501 | 236 | 674 | 913 | 579 | 5332 | 5332 | 0
| Grand Total | 102 | 415 | 399 | 418 | 940 | 874 | 888 | 1290 | 1650 | 1618 | 2441 | 3224 | 3033 | 4068 | 4342 | 3523 | 29225 | 29195 | 30

## Annexure-L
Annexure-L
Sub-station wise Actual Energy and Demand from April-19 to Oct-19
NAME OF THE DISCOM: CESU
TOTAL CONTRACT DEMAND IN MVA:1560
TOTAL ENERGY CONSUMED (MU):5306.87MU
Sl No. | Name of Grid/EHT/Traction | Energy (MU) / Peak Demand (MVA) | 2019-04-04 | 2019-05-04 | 2019-06-04 | 2019-07-04 | 2019-08-04 | 2019-09-04 | 2019-10-04 | Total Energy/Maximum Demand | Average MD
1 | Angul Grid | MU | 18.4264 | 21.7722 | 19.6145 | 18.4887 | 17.2703 | 15.8863 | 15.9698 | 127.4282
|  | MVA | 48.2352 | 42.0817 | 46.3724 | 39.7743 | 40.8027 | 53.2784 | 31.5767 | 53.2784 | 43.1602
2 | Arugul Grid | MU | 4.8244 | 1.4 | 1.5199 | 2.8589 | 2.5692 | 3.7904 | 3.2981 | 20.2609
|  | MVA | 16.2361 | 9.9684 | 5.5314 | 8.948 | 8.4564 | 9.5962 | 14.3977 | 16.2361 | 10.4478
3 | Badagada Grid | MU | 19.2068 | 8.8612 | 15.7784 | 14.6728 | 15.9131 | 17.2412 | 17.0292 | 108.7027
|  | MVA | 57.0448 | 37.4095 | 49.8512 | 40.6832 | 43.9186 | 58.0505 | 63.8589 | 63.8589 | 50.1167
4 | Balugoan Grid | MU | 9.9413 | 9.9551 | 10.4628 | 10.104 | 9.8928 | 9.3494 | 8.8124 | 68.5178
|  | MVA | 19.6708 | 24.4579 | 17.6924 | 56.1092 | 16.9923 | 18.2739 | 20.064 | 56.1092 | 24.7515
5 | Banki | MU | 6.2552 | 6.1281 | 5.58 | 4.56 | 5.8402 | 5.8443 | 5.0568 | 39.2647
|  | MVA | 11.9696 | 21.923 | 13.9382 | 6.9593 | 13.849 | 19.86 | 12.3132 | 21.923 | 14.4018
6 | Bhubaneswar Grid | MU | 55.8186 | 46.3995 | 56.4196 | 55.4526 | 53.4996 | 49.2278 | 47.9613 | 364.7791
|  | MVA | 127.3405 | 131.5872 | 126.9966 | 147.3669 | 156.6486 | 113.7302 | 126.045 | 156.6486 | 132.8164
7 | Bidanasi Grid | MU | 44.6334 | 43.7059 | 47.6467 | 42.2169 | 42.5591 | 38.9564 | 37.2626 | 296.981
|  | MVA | 77.8351 | 128.7197 | 116.5419 | 85.0212 | 116.7259 | 103.5057 | 88.1885 | 128.7197 | 102.3626
8 | Boinda Grid | MU | 9.6116 | 10.1191 | 8.6398 | 9.1731 | 8.8397 | 8.4655 | 8.1868 | 63.0357
|  | MVA | 18.0798 | 22.5896 | 20.5189 | 16.4365 | 20.1147 | 19.8527 | 18.1334 | 22.5896 | 19.3894
9 | Chainpal grid | MU | 29.6715 | 32.6312 | 28.3225 | 29.0278 | 27.5008 | 26.6046 | 26.1077 | 199.8661
|  | MVA | 94.4812 | 82.8194 | 66.5636 | 93.571 | 68.1845 | 67.5664 | 57.3511 | 94.4812 | 75.791
10 | Chandaka grid | MU | 69.38 | 48.671 | 66.013 | 64.5363 | 60.0458 | 60.8223 | 53.3613 | 422.8298
|  | MVA | 126.8293 | 165.7415 | 164.869 | 115.9052 | 152.6264 | 151.2337 | 112.0907 | 165.7415 | 141.328
11 | Chandikhole grid | MU | 7.8092 | 6.8521 | 7.4545 | 8.0516 | 7.7994 | 7.877 | 7.4291 | 53.2729
|  | MVA | 0.64281 | 17.0063 | 16.8709 | 0.67 | 16.7238 | 17.4809 | 15.4967 | 17.4809 | 12.1273
12 | Chandpur Grid | MU | 6.3927 | 4.7963 | 6.8506 | 6.8041 | 6.7762 | 6.3585 | 6.1013 | 44.0797
|  | MVA | 15.8024 | 15.9992 | 13.6098 | 16.9829 | 12.6647 | 13.3695 | 11.4013 | 16.9829 | 14.2614
13 | Choudwar grid | MU | 33.3073 | 22.1902 | 31.7525 | 33.0922 | 32.3565 | 31.4451 | 30.5049 | 214.6486
|  | MVA | 91.5896 | 72.4164 | 89.0972 | 88.9237 | 71.7616 | 86.4923 | 70.3728 | 91.5896 | 81.5219
14 | Cuttack grid | MU | 27.8725 | 21.7204 | 26.9456 | 26.0756 | 23.2268 | 25.2417 | 24.5514 | 175.634
|  | MVA | 75.5196 | 56.1175 | 85.1159 | 81.8692 | 68.5147 | 60.2399 | 67.5934 | 85.1159 | 70.71
15 | Dhenkanal grid | MU | 27.0584 | 28.857 | 26.1804 | 26.099 | 25.2686 | 24.6105 | 22.8468 | 180.9207
|  | MVA | 51.7188 | 67.6896 | 64.5699 | 67.5189 | 52.0946 | 59.3734 | 49.8726 | 67.6896 | 58.9768
16 | Jagatsinghpur grid | MU | 19.3327 | 12.115 | 18.8333 | 19.4161 | 19.4334 | 18.6206 | 18.3187 | 126.0698
|  | MVA | 42.1018 | 39.1248 | 40.3344 | 41.886 | 40.9548 | 48.6723 | 40.8073 | 48.6723 | 41.9831
17 | Kalarangi grid | MU | 9.5671 | 9.392 | 8.3282 | 9.2709 | 9.7094 | 8.9043 | 8.4922 | 63.6642
|  | MVA | 19.5159 | 22.1675 | 19.1016 | 20.6117 | 32.9144 | 19.7645 | 18.8377 | 32.9144 | 21.8448
18 | Kamakshyanagar | MU | 10.7502 | 11.8461 | 11.189 | 11.4671 | 11.4801 | 11.0727 | 10.7377 | 78.5428
|  | MVA | 24.6397 | 28.4723 | 24.2423 | 32.8603 | 23.4953 | 21.9915 | 25.7325 | 32.8603 | 25.9191
19 | Kendrapada Grid | MU | 15.9814 | 15.1463 | 16.9908 | 16.8914 | 16.2951 | 16.1497 | 15.2765 | 112.7313
|  | MVA | 48.8146 | 49.5044 | 57.4619 | 37.4948 | 39.5049 | 47.2219 | 47.6582 | 57.4619 | 46.8087
20 | Khajuriakanta Grid | MU | 3.7913 | 4.2465 | 3.7783 | 3.8069 | 3.7276 | 3.4483 | 3.3764 | 26.1753
|  | MVA | 9.6813 | 16.0006 | 15.3248 | 10.1157 | 9.1481 | 11.0135 | 7.5151 | 16.0006 | 11.257
21 | Khuntuni Grid | MU | 1.7758 | 1.589 | 1.6189 | 1.7817 | 2.0359 | 2.1275 | 2.1154 | 13.0443
|  | MVA | 3.8709 | 3.8084 | 3.7258 | 4.8511 | 6.0061 | 6.0352 | 6.6068 | 6.6068 | 4.9863
22 | Khurda grid | MU | 43.941 | 23.9291 | 39.207 | 39.3277 | 40.949 | 36.8697 | 37.5528 | 261.7763
|  | MVA | 106.1839 | 94.9392 | 85.3502 | 86.7787 | 83.2701 | 85.3212 | 95.3614 | 106.1839 | 91.0292
23 | Konark Grid | MU | 3.9855 | 0.55443 | 1.4285 | 1.836 | 2.1076 | 2.1693 | 2.1914 | 14.2728
|  | MVA | 12.058 | 8.1795 | 8.0667 | 5.4219 | 5.3611 | 4.6483 | 6.094 | 12.058 | 7.1185
24 | Mania | MU | 1.2718 | 1.3169 | 1.2198 | 1.1412 | 0.81433 | 1.0027 | 0.91496 | 7.6817
|  | MVA | 5.9791 | 6.2895 | 6.1625 | 7.8415 | 5.5041 | 5.7341 | 5.9744 | 7.8415 | 6.2122
25 | Marshaghai | MU | 7.8619 | 7.7278 | 8.5092 | 8.8045 | 8.3214 | 8.2609 | 7.9832 | 57.4688
|  | MVA | 16.7891 | 17.7378 | 18.0621 | 18.4982 | 17.7924 | 18.0769 | 18.9565 | 18.9565 | 17.9876
26 | Mendhasala Grid | MU | 1.1585 | 0.59263 | 1.067 | 1.053 | 1.0717 | 0.99269 | 0.97527 | 6.9108
|  | MVA | 3.1197 | 2.418 | 2.7898 | 3.3115 | 2.114 | 3.3847 | 3.2455 | 3.3847 | 2.9119
27 | Narsinghpur | MU | 2.4554 | 2.9008 | 2.6166 | 2.4838 | 1.7293 | 2.2859 | 2.1497 | 16.6215
|  | MVA | 4.9896 | 5.9396 | 6.171 | 5.3584 | 5.0206 | 5.618 | 4.9213 | 6.171 | 5.4312
28 | Nayagad Grid | MU | 27.7035 | 32.1783 | 30.0621 | 28.2094 | 26.7085 | 26.3033 | 23.9881 | 195.1533
|  | MVA | 68.6054 | 71.3821 | 71 | 58.3802 | 64.5239 | 70.9204 | 47.0131 | 71.3821 | 64.5464
29 | Nimapada Grid | MU | 27.4693 | 3.3238 | 14.378 | 21.9257 | 24.453 | 24.634 | 24.5646 | 140.7483
|  | MVA | 55.7405 | 51.3585 | 42.4788 | 49.5628 | 49.13 | 48.3885 | 50.5717 | 55.7405 | 49.6044
30 | Nuapatna grid | MU | 18.7258 | 18.8735 | 18.3368 | 18.5306 | 19.1779 | 17.4695 | 16.4248 | 127.5388
|  | MVA | 35.9747 | 49.1043 | 54.8036 | 38.5677 | 47.8009 | 35.7082 | 42.3732 | 54.8036 | 43.4761
31 | Olaver-2 | MU | 3.5947 | 3.7716 | 4.1468 | 4.2113 | 3.9587 | 4.0035 | 3.7914 | 27.478
|  | MVA | 9.2 | 9.7933 | 13.7982 | 9.4168 | 9.0726 | 10.4785 | 8.7179 | 13.7982 | 10.0682
32 | Paradeep grid | MU | 13.3064 | 11.977 | 14.2415 | 14.4041 | 13.3183 | 13.8795 | 13.5901 | 94.7169
|  | MVA | 29.7391 | 27.0834 | 30.6558 | 35.8106 | 37.9409 | 35.6474 | 33.4492 | 37.9409 | 32.9038
33 | Pattamundai grid | MU | 13.0602 | 13.2552 | 14.1197 | 14.4874 | 13.7117 | 13.7946 | 13.0906 | 95.5194
|  | MVA | 27.9394 | 28.1865 | 30.2343 | 29.4823 | 29.0897 | 29.4712 | 28.2099 | 30.2343 | 28.9448
34 | Phulnakhara Grid | MU | 14.97 | 2.2834 | 9.7639 | 11.501 | 12.4935 | 12.2792 | 12.2904 | 75.5813
|  | MVA | 37.0452 | 31.9384 | 23.599 | 24.3189 | 24.2196 | 24.2944 | 27.8598 | 37.0452 | 27.6107
35 | Puri grid | MU | 21.5256 | 5.8762 | 12.2739 | 10.6918 | 18.0561 | 21.7566 | 22.4762 | 112.6565
|  | MVA | 63.6446 | 41.0947 | 71.3585 | 50.2119 | 46.4392 | 49.9543 | 64.8263 | 71.3585 | 55.3614
36 | Rairakhol Bamur fdr | MU | 1.7809 | 1.9098 | 1.6597 | 1.7382 | 1.6938 | 1.6148 | 1.5041 | 11.9014
|  | MVA | 4.3118 | 4.132 | 4.1227 | 4.4184 | 4.4974 | 4.2059 | 4.1022 | 4.4974 | 4.2558
37 | Ransinghpur grid | MU | 48.2721 | 37.0645 | 46.8709 | 42.0653 | 41.1731 | 40.3353 | 38.6448 | 294.426
|  | MVA | 102.1143 | 117.9486 | 132.3566 | 111.8587 | 84.5431 | 83.7838 | 77.2766 | 132.3566 | 101.4117
38 | Rengali S/Y | MU | 6.2288 | 6.7392 | 6.4931 | 6.7718 | 6.8377 | 6.6489 | 6.5379 | 46.2573
|  | MVA | 30.2257 | 21.4483 | 24.9691 | 19.5655 | 23.0081 | 21.9153 | 15.5879 | 30.2257 | 22.3886
39 | Salipur Grid | MU | 15.3626 | 11.9395 | 15.3168 | 15.612 | 15.252 | 15.3669 | 14.5545 | 103.4043
|  | MVA | 31.5399 | 31.1281 | 38.5749 | 31.738 | 33.0086 | 30.6239 | 34.6296 | 38.5749 | 33.0347
40 | Samangara | MU | 6.8256 | 0.51114 | 3.098 | 4.8673 | 0.96206 | 0.004374 | 0.00311 | 16.2716
|  | MVA | 19.7371 | 16.4629 | 23.7238 | 18.718 | 8.7155 | 0.057296 | 0.051608 | 23.7238 | 12.4952
41 | Shamuka | MU | 9.0191 | 0.67063 | 6.5597 | 14.1006 | 12.971 | 9.6981 | 10.8096 | 63.8288
|  | MVA | 24.229 | 21.0111 | 47.2021 | 40.9379 | 36.9228 | 19.6622 | 31.8651 | 47.2021 | 31.69
42 | Tirtol | MU | 2.8521 | 2.7314 | 2.7704 | 3.1969 | 3.697 | 2.9149 | 3.2754 | 21.4381
|  | MVA | 11.1416 | 11.8165 | 9.801 | 11.1893 | 12.2264 | 8.6867 | 10.2223 | 12.2264 | 10.7262
43 | Infocity-II | MU | 10.0085 | 3.6912 | 9.3174 | 9.6929 | 9.5901 | 8.8738 | 9.1018 | 60.2756
|  | MVA | 26.6362 | 25.8945 | 31.286 | 28.4256 | 29.136 | 27.1549 | 33.3571 | 33.3571 | 28.8415
44 | Unit-8 GIS | MU | 0 | 6.2716 | 5.0291 | 2.9514 | 5.7633 | 2.5492 | 6.4092 | 28.9738
|  | MVA | 0 | 19.9666 | 19.9155 | 13.9014 | 17.0751 | 13.042 | 19.3253 | 19.9666 | 14.7466
45 | MCl feeder | MU | 15.3553 | 15.5019 | 15.333 | 14.4754 | 13.2996 | 12.861 | 14.0398 | 100.866
|  | MVA | 32.3165 | 62.6062 | 62.7994 | 47.5287 | 46.2322 | 33.6535 | 50.3045 | 62.7994 | 47.9201
46 | Arati Steel | MU | 0.01856 | 0.1042 | 0.00693 | 0.00271 | 0.2224 | 0.02428 | 0.02848 | 0.40756
|  | MVA | 6.0906 | 5.5785 | 7.4944 | 6.7676 | 6.24 | 6.3246 | 7.3366 | 7.4944 | 6.5475
47 | BPPL (S/W) | MU | 0.0056 | 0.02588 | 2e-05 | 0 | 0.0001 | 0 | 0 | 0.0316
|  | MVA | 0.69754 | 4.6965 | 0.08 | 0.65605 | 0.04 | 0 | 0 | 4.6965 | 0.88144
48 | FCI feeder | MU | 0.26253 | 0.31324 | 0.28868 | 0.27549 | 0.31794 | 0.32029 | 0.33995 | 2.1181
|  | MVA | 15.4573 | 0.75472 | 0.72111 | 14.0215 | 0.58241 | 0.60133 | 0.65115 | 15.4573 | 4.6842
49 | Rawmet | MU | 16.1881 | 15.086 | 16.0647 | 16.3745 | 16.4208 | 16.185 | 16.4514 | 112.7705
|  | MVA | 25.7805 | 25.0964 | 24.6725 | 24.8456 | 25.7066 | 24.9942 | 25.8151 | 25.8151 | 25.273
50 | GSAL | MU | 0.01935 | 0.01822 | 0.01974 | 0.01764 | 0.01784 | 0.01662 | 0.01618 | 0.12559
|  | MVA | 0.12 | 0.089443 | 0.12649 | 0.089443 | 0.089443 | 0.056569 | 0.089443 | 0.12649 | 0.094404
51 | Hind Metalies MGM | MU | 0.061588 | 0.018233 | 0.000367 | 0.083387 | 0.21514 | 0.06492 | 0.13363 | 0.57726
|  | MVA | 1.979 | 2.0983 | 0.84128 | 1.667 | 0.84804 | 1.9558 | 2.394 | 2.394 | 1.6833
52 | Navchrome feeder | MU | 0.007331 | 7.2e-05 | 0.000331 | 0.000666 | 0 | 6e-06 | 6e-06 | 0.008412
|  | MVA | 4.8407 | 0.075 | 0.1875 | 0.25 | 0 | 0.0125 | 0.0125 | 4.8407 | 0.76831
53 | Hindmetalics SGEL | MU | 0.063027 | 0.065191 | 0.056545 | 0.042027 | 0.07773 | 0.048856 | 0.076683 | 0.43006
|  | MVA | 2.1034 | 2.0181 | 1.9765 | 1.9517 | 2.0894 | 2.27 | 2.0669 | 2.27 | 2.068
54 | Meramundali Bhusan | MU | 33.9052 | 32.5657 | 16.5227 | 11.2943 | 8.1533 | 9.2238 | 11.6251 | 123.2902
|  | MVA | 122.1646 | 139.5993 | 109.2591 | 91.24 | 180.4369 | 98 | 103.4122 | 180.4369 | 120.5874
55 | Meramundali 132kv BRG Feeder | MU | 6.9242 | 8.3517 | 4.0248 | 10.4537 | 8.4723 | 6.6204 | 5.5236 | 50.3708
|  | MVA | 24.6322 | 24.5719 | 21.2151 | 24.4554 | 24.6405 | 24.3319 | 23.9168 | 24.6405 | 23.9663
56 | Meramundali GKEL LILO(400 KV) | MU | 0.3525 | 0.1314 | 0.0431 | 0.2866 | 0.4178 | 0.2524 | 0 | 1.4838
|  | MVA | 18.124 | 20.2781 | 18.868 | 18.3521 | 13.1939 | 14.8 | 0 | 20.2781 | 14.8023
57 | Meramundali JSPL | MU | 0.13395 | 0.061859 | 0.017954 | 0.00111 | 0.14384 | 0.057281 | 0.018782 | 0.43478
|  | MVA | 12.1247 | 30.6353 | 14.4964 | 0.56869 | 89.2381 | 39.2842 | 2.1518 | 89.2381 | 26.9284
58 | Meramundali 132kv Rungta Feeder | MU | 0.0684 | 0.07106 | 0.08295 | 0.09144 | 0.09508 | 0.10156 | 0.10586 | 0.61635
|  | MVA | 0.44181 | 0.48166 | 0.48 | 0.48662 | 0.46819 | 0.52 | 0.45607 | 0.52 | 0.47634
59 | Essar | MU | 0.23087 | 0.036063 | 0.33304 | 0.23512 | 3.7625 | 3.8e-05 | 0.12958 | 4.7272
|  | MVA | 32.6829 | 29.65 | 31.4125 | 34.925 | 30.9 | 28.8 | 34.1 | 34.925 | 31.7815
60 | IFFCO feeder | MU | 1.7012 | 2.9556 | 0.90805 | 0.77775 | 0.95887 | 0.70936 | 1.2402 | 9.251
|  | MVA | 19.4276 | 25.3892 | 16.8801 | 19.7028 | 19.6489 | 18.1824 | 18.1887 | 25.3892 | 19.6314
61 | IOCL feeder | MU | 0.27916 | 0.30876 | 0.29574 | 0.31057 | 0.25611 | 0.2533 | 0.28458 | 1.9882
|  | MVA | 1.3361 | 1.4723 | 1.2948 | 1.2969 | 1.3244 | 1.2433 | 1.183 | 1.4723 | 1.3073
62 | PPL feeder | MU | 4.2186 | 4.6809 | 5.428 | 3.1981 | 1.3672 | 0.39642 | 2.6363 | 21.9255
|  | MVA | 13.3208 | 25.4034 | 18.2218 | 13.8479 | 13.4502 | 13.8881 | 13.4698 | 25.4034 | 15.9431
63 | PPT Feeder | MU | 7.6504 | 7.8126 | 7.7637 | 7.737 | 7.277 | 7.0697 | 6.8701 | 52.1806
|  | MVA | 32.1434 | 17.3179 | 30.0201 | 29.9868 | 29.6557 | 32.9915 | 28.5008 | 32.9915 | 28.6594
64 | Salipur 132KV OCL Feeder | MU | 4.6749 | 2.9792 | 3.9947 | 4.2756 | 3.5495 | 4.2544 | 4.2957 | 28.024
|  | MVA | 9.184 | 9.0652 | 9.0782 | 9.2345 | 9.3729 | 9.2111 | 9.4875 | 9.4875 | 9.2334
65 | Solari traction | MU | 4.4857 | 4.3311 | 4.6611 | 4.6086 | 4.4212 | 3.8674 | 4.2739 | 30.6489
|  | MVA | 14.9151 | 13.1303 | 14.5474 | 16.9249 | 14.3856 | 13.7766 | 13.4805 | 16.9249 | 14.4515
66 | Boinda Traction | MU | 0 | 0 | 0.07534 | 0.98914 | 0.88029 | 0.96269 | 1.0312 | 3.9387
|  | MVA | 0 | 0 | 7.4431 | 9.1406 | 10.6615 | 14.0384 | 11.0668 | 14.0384 | 7.4786
67 | Chainpal Traction | MU | 2.9017 | 3.0583 | 3.1869 | 3.1942 | 2.8202 | 2.9153 | 3.0249 | 21.1014
|  | MVA | 23.5802 | 18.1498 | 12.5817 | 24.7795 | 13.2112 | 12.437 | 13.0347 | 24.7795 | 16.8249
68 | choudwar Rly Feeder | MU | 5.2236 | 4.7583 | 5.6308 | 5.952 | 5.3542 | 5.086 | 5.1634 | 37.1683
|  | MVA | 15.063 | 17.1583 | 24.3472 | 23.1102 | 22.4503 | 17.0586 | 21.0856 | 24.3472 | 20.039
69 | Joranda Rly. | MU | 4.2969 | 3.9303 | 4.6959 | 4.8713 | 4.4179 | 4.2347 | 4.1096 | 30.5566
|  | MVA | 16.4579 | 17.4279 | 16.7974 | 18.3602 | 18.6539 | 15.642 | 16.0299 | 18.6539 | 17.0527
70 | Hindmetalics Traction | MU | 3.0419 | 2.9257 | 3.426 | 3.4628 | 3.326 | 3.0696 | 3.0484 | 22.3004
|  | MVA | 12.1273 | 17.4979 | 20.4106 | 22.4036 | 22.6873 | 13.9271 | 16.1044 | 22.6873 | 17.8797
71 | Jagatsinghpur Traction | MU | 5.1808 | 4.1478 | 4.9841 | 4.891 | 4.1498 | 4.0757 | 4.2072 | 31.6364
|  | MVA | 15.1457 | 13.2148 | 15.5926 | 15.1383 | 11.9549 | 12.7775 | 13.6912 | 15.5926 | 13.9307
72 | Kaipadar trac | MU | 5.9994 | 4.9342 | 6.2683 | 6.1721 | 6.417 | 6.0827 | 6.0742 | 41.9479
|  | MVA | 20.7595 | 16.2306 | 18.9789 | 19.4535 | 19.8919 | 20.5247 | 17.7734 | 20.7595 | 19.0875
73 | Pallahara | MU | 1.3446 | 1.3608 | 1.1966 | 1.3361 | 1.2431 | 0.71874 | 0.000104 | 7.2
|  | MVA | 41.3459 | 3.3555 | 3.172 | 41.1224 | 3.1319 | 3.0826 | 0.025 | 41.3459 | 13.605
74 | Chandpur PAN Time Finance (Solar) | MU | 0.12841 | 0.089653 | 0.084186 | 0.076028 | 0.064231 | 0.070261 | 0.088178 | 0.60095
|  | MVA | 0.68969 | 0.71313 | 0.93563 | 0.66625 | 0.65625 | 0.70594 | 0.68281 | 0.93563 | 0.72138
75 | Dhenkanal SCAW Feeder | MU | 0.1454 | 0.057603 | 0 | 0.16398 | 0.11772 | 0.081742 | 0.054325 | 0.62076
|  | MVA | 5.4582 | 3.92 | 0.04 | 4.9909 | 4.5193 | 4.7008 | 3.3089 | 5.4582 | 3.8483
76 | Barang | MU | 0.115 | 0.044499 | 0.083351 | 0.056712 | 0.065499 | 0.069249 | 0.093498 | 0.52781
|  | MVA | 7.216 | 0.6596 | 0.6584 | 3.2062 | 0.6712 | 0.6856 | 0.6888 | 7.216 | 1.9694
77 | MGM Solar | MU | 0.10858 | 0.032952 | 0.074513 | 0.074413 | 0.07443 | 0.076203 | 0.091965 | 0.53306
|  | MVA | 0 | 0.61125 | 0.65156 | 0.67 | 0.6775 | 0.73 | 0.71 | 0.73 | 0.57862
78 | Angul PGCIL Stn. Tertiary | MU | 0.15415 | 0.16707 | 0.16364 | 0.14958 | 0.1556 | 0.14381 | 0.11364 | 1.0475
|  | MVA | 0.21409 | 0.22455 | 0.22728 | 0.20105 | 0.20914 | 0.19974 | 0.15275 | 0.22728 | 0.20409
79 | Pandiabil PG | MU | 0.040194 | 0.04212 | 0.043017 | 0.03802 | 0.0411 | 0.049693 | 0.037484 | 0.29163
|  | MVA | 0.055825 | 0.56061 | 0.059746 | 0.051102 | 0.055242 | 0.069018 | 0.050382 | 0.56061 | 0.12885
80 | Rengali PGCIL Stn.Tertiary | MU | 0.046663 | 0.073715 | 0.15762 | 0.02084 | 0.0359 | 0.033278 | 0.020798 | 0.38882
|  | MVA | 0.06481 | 0.099079 | 0.21892 | 0.028011 | 0.048253 | 0.046219 | 0.027954 | 0.21892 | 0.076178
| TOTAL MU |  | 858.1209 | 689.5258 | 794.3218 | 799.4413 | 785.46 | 755.7484 | 740.8693 | 5423.4876
| Station Consumption |  | 0.49004 | 0.491 | 0.46877 | 0.44677 | 0.40346 | 0.41809 | 0.40991
| Import by Solar Entities as per SLDC statement |  | 0.001419 | 0.000755 | 0.001525 | 0.001771 | 0.003005 | 0.001645 | 0.001675
| Open access energy |  | 18.345 | 16.166 | 17.4312 | 15.8472 | 14.1962 | 15.3358 | 16.1541
| Net Energy |  | 839.2844 | 672.868 | 776.4204 | 783.1456 | 770.8573 | 739.9929 | 724.3037 | 5306.8723
| SUM OF PEAK DEMAND IN MVA |  | 2256.6245 | 2320.6887 | 2361.5995 | 2260.3942 | 2326.5374 | 2124.9038 | 2021.3553
| SMD OF CESU IN MVA |  | 1554.54 | 1534.436 | 1559.769 | 1486.194 | 1414.482 | 1387.297 | 1367.352 | 1559.769

## Annexure-M
Annexure-M
Sub-station wise Monthly Projection of Energy and Demand from Nov-19 to Mar-20
NAME OF THE DISCOM: CESU
TOTAL CONTRACT DEMAND IN MVA:1660
TOTAL ENERGY REQUIREMENT (MU):3689.45 MU
Sl No. | Name of Grid/EHT/Traction | Energy (MU) / Peak Demand (MVA) | 2019-11-04 | 2019-12-04 | 2020-01-04 | 2020-02-04 | 2020-03-04 | Total Energy/Maximum Demand | Average MD
1 | Angul Grid | MU | 16.97 | 17.5414 | 17.3217 | 15.5038 | 18.9576 | 86.2944
|  | MVA | 46.8315 | 44.8722 | 38.3087 | 42.1128 | 52.73 | 52.73 | 44.971
2 | Arugul Grid | MU | 1.684 | 1.6402 | 1.535 | 1.656 | 2.7601 | 9.2752
|  | MVA | 7.6119 | 5.8117 | 6.3901 | 7.2689 | 12.8662 | 12.8662 | 7.9898
3 | Badagada Grid | MU | 17.5248 | 14.8097 | 11.7782 | 16.9273 | 20.2037 | 81.2437
|  | MVA | 97.3032 | 66.348 | 46.9804 | 72.744 | 77.9647 | 97.3032 | 72.2681
4 | Balugoan Grid | MU | 8.3766 | 7.6117 | 7.3587 | 7.4162 | 10.4424 | 41.2056
|  | MVA | 18.4601 | 30.0516 | 25.9106 | 66.7856 | 35.1702 | 66.7856 | 35.2756
5 | Banki | MU | 5.5282 | 5.1097 | 5.2013 | 5.0214 | 7.0033 | 27.8639
|  | MVA | 15.6671 | 13.5352 | 14.8176 | 17.9283 | 20.6949 | 20.6949 | 16.5286
6 | Bhubaneswar Grid | MU | 44.7265 | 43.6241 | 44.8439 | 38.9995 | 56.2953 | 228.4892
|  | MVA | 142.2665 | 146.0479 | 126.619 | 153.1074 | 170.5722 | 170.5722 | 147.7226
7 | Bidanasi Grid | MU | 37.1927 | 32.7197 | 30.6322 | 30.6724 | 46.3518 | 177.5687
|  | MVA | 102.9332 | 114.9071 | 110.315 | 99.8895 | 130.6005 | 130.6005 | 111.7291
8 | Boinda Grid | MU | 10.4914 | 12.0865 | 12.5124 | 10.5179 | 10.887 | 56.4953
|  | MVA | 31.3246 | 37.7912 | 36.0399 | 33.9052 | 30.081 | 37.7912 | 33.8284
9 | Chainpal grid | MU | 27.9357 | 31.4794 | 29.61 | 24.3571 | 30.1568 | 143.539
|  | MVA | 79.4884 | 86.1713 | 88.1327 | 76.0733 | 60.0051 | 88.1327 | 77.9742
10 | Chandaka grid | MU | 53.0911 | 50.1353 | 46.7811 | 49.4931 | 67.8971 | 267.3977
|  | MVA | 187.8404 | 125.1237 | 134.7973 | 129.7558 | 201.9027 | 201.9027 | 155.884
11 | Chandikhole grid | MU | 7.8387 | 8.3014 | 8.7102 | 8.0029 | 9.1895 | 42.0427
|  | MVA | 19.7185 | 21.1026 | 20.8733 | 21.1784 | 21.4277 | 21.4277 | 20.8601
12 | Chandpur Grid | MU | 5.8126 | 5.1934 | 5.1365 | 5.0144 | 6.8588 | 28.0157
|  | MVA | 16.9082 | 16.4216 | 19.1333 | 14.9209 | 15.9152 | 19.1333 | 16.6598
13 | Choudwar grid | MU | 33.4842 | 34.3755 | 34.3725 | 32.2021 | 37.5308 | 171.965
|  | MVA | 80.5395 | 95.6072 | 81.3448 | 100.62 | 117.9343 | 117.9343 | 95.2091
14 | Cuttack grid | MU | 21.5568 | 20.0942 | 18.5476 | 19.7764 | 24.9157 | 104.8908
|  | MVA | 68.4456 | 67.3005 | 66.274 | 62.6017 | 63.3164 | 68.4456 | 65.5876
15 | Dhenkanal grid | MU | 26.5045 | 28.405 | 27.7468 | 24.2072 | 29.69 | 136.5534
|  | MVA | 74.6009 | 75.4825 | 95.3519 | 61.9318 | 70.4836 | 95.3519 | 75.5702
16 | Jagatsinghpur grid | MU | 17.2993 | 16.2083 | 16.5394 | 15.6405 | 20.7047 | 86.3923
|  | MVA | 59.6727 | 50.2547 | 39.0605 | 49.0194 | 56.7267 | 59.6727 | 50.9468
17 | Kalarangi grid | MU | 9.7428 | 10.6627 | 11.5306 | 9.4557 | 10.5899 | 51.9818
|  | MVA | 28.1295 | 29.8779 | 38.7392 | 26.2444 | 26.396 | 38.7392 | 29.8774
18 | Kamakshyanagar | MU | 12.1333 | 12.9461 | 13.5524 | 10.6879 | 10.2434 | 59.563
|  | MVA | 33.2153 | 44.6012 | 29.869 | 38.0525 | 28.9286 | 44.6012 | 34.9333
19 | Kendrapada Grid | MU | 14.488 | 12.7697 | 12.7769 | 12.5424 | 16.8505 | 69.4276
|  | MVA | 46.4301 | 57.0825 | 37.1238 | 40.8794 | 54.7749 | 57.0825 | 47.2581
20 | Khajuriakanta Grid | MU | 3.7757 | 4.1617 | 4.2085 | 3.5619 | 4.075 | 19.7828
|  | MVA | 11.8986 | 11.6119 | 18.321 | 10.7761 | 13.6373 | 18.321 | 13.249
21 | Khuntuni Grid | MU | 1.78 | 2 | 2 | 2.5 | 2.5 | 10.78
|  | MVA | 5 | 4.5 | 4 | 6 | 6 | 6 | 5.1
22 | Khurda grid | MU | 43.9803 | 45.4337 | 45.9123 | 44.4834 | 53.8594 | 233.6691
|  | MVA | 127.3334 | 141.2068 | 125.2217 | 140.4643 | 155.2709 | 155.2709 | 137.8994
23 | Konark Grid | MU | 3.5977 | 3.6781 | 3.7599 | 3.9001 | 5.1555 | 20.0913
|  | MVA | 18.1599 | 12.3807 | 10.1258 | 16.237 | 16.265 | 18.1599 | 14.6337
24 | Mania | MU | 2.5409 | 2.1297 | 0.97542 | 1.3016 | 1.3391 | 8.2867
|  | MVA | 8.1528 | 8.1312 | 8.1168 | 7.5348 | 8.3985 | 8.3985 | 8.0668
25 | Marshaghai | MU | 7.0781 | 6.2992 | 6.3414 | 5.9391 | 8.2318 | 33.8896
|  | MVA | 21.0905 | 17.0834 | 19.3986 | 20.1916 | 21.5709 | 21.5709 | 19.867
26 | Mendhasala Grid | MU | 0.53463 | 1.0436 | 0.92729 | 0.86976 | 1.207 | 4.5823
|  | MVA | 1.9833 | 3.3573 | 3.5573 | 3.3083 | 4.2076 | 4.2076 | 3.2828
27 | Narsinghpur | MU | 1.7 | 2 | 2.3 | 2.5 | 2.5 | 11
|  | MVA | 4 | 4 | 4.5 | 5 | 5 | 5 | 4.5
28 | Nayagad Grid | MU | 22.2625 | 21.7216 | 21.9246 | 21.1493 | 29.1134 | 116.1715
|  | MVA | 63.5966 | 57.8506 | 96.2256 | 96.5669 | 73.9757 | 96.5669 | 77.6431
29 | Nimapada Grid | MU | 25.2049 | 23.7636 | 24.1598 | 25.1971 | 30.8362 | 129.1616
|  | MVA | 78.9266 | 64.6843 | 89.7162 | 79.3045 | 71.7163 | 89.7162 | 76.8696
30 | Nuapatna grid | MU | 20.8882 | 22.5604 | 22.2977 | 19.1876 | 20.7689 | 105.7028
|  | MVA | 75.0746 | 73.0928 | 72.1062 | 55.6244 | 55.2807 | 75.0746 | 66.2357
31 | Olaver-2 | MU | 3.1935 | 2.6149 | 2.47 | 2.4477 | 3.5722 | 14.2982
|  | MVA | 10.1158 | 10.0621 | 10.3861 | 10.3459 | 11.432 | 11.432 | 10.4684
32 | Paradeep grid | MU | 12.7557 | 12.1211 | 11.6079 | 11.2207 | 15.3122 | 63.0177
|  | MVA | 38.8528 | 49.3949 | 31.6875 | 31.173 | 41.6835 | 49.3949 | 38.5583
33 | Pattamundai grid | MU | 11.4747 | 9.7132 | 9.6032 | 9.9352 | 13.1877 | 53.914
|  | MVA | 33.8239 | 29.7866 | 28.6247 | 38.0734 | 48.1057 | 48.1057 | 35.6828
34 | Phulnakhara Grid | MU | 12.8279 | 12.597 | 12.8712 | 12.1788 | 16.1476 | 66.6225
|  | MVA | 35.905 | 34.79 | 38.5255 | 35.7268 | 41.4862 | 41.4862 | 37.2867
35 | Puri grid | MU | 10.4402 | 9.67 | 15.9678 | 15.9406 | 23.7859 | 75.8045
|  | MVA | 34.4653 | 42.7662 | 51.7344 | 51.5207 | 72.5898 | 72.5898 | 50.6153
36 | Rairakhol Bamur fdr | MU | 2.0658 | 2.3536 | 2.3881 | 1.9376 | 1.9817 | 10.7266
|  | MVA | 6.6652 | 6.5003 | 6.6546 | 6.2567 | 5.8241 | 6.6652 | 6.3802
37 | Ransinghpur grid | MU | 39.7985 | 34.6577 | 31.9633 | 35.5002 | 48.8196 | 190.7394
|  | MVA | 139.7874 | 84.2876 | 94.3572 | 107.275 | 120.2973 | 139.7874 | 109.2009
38 | Rengali S/Y | MU | 5.4668 | 4.2407 | 6.7688 | 6.6048 | 8.2959 | 31.3769
|  | MVA | 23.3975 | 28.8471 | 22.9942 | 27.5563 | 34.6668 | 34.6668 | 27.4924
39 | Salipur Grid | MU | 14.4531 | 14.2524 | 14.2242 | 13.5058 | 17.2009 | 73.6364
|  | MVA | 50.6346 | 46.6069 | 39.8358 | 42.7914 | 48.7555 | 50.6346 | 45.7248
40 | Samangara | MU | 15.7705 | 15.6849 | 9.4545 | 7.3039 | 8.3256 | 56.5394
|  | MVA | 42.5495 | 37.1716 | 23.7846 | 22.1312 | 27.1 | 42.5495 | 30.5474
41 | Shamuka | MU | 8.951 | 6.1873 | 5.6704 | 8.0374 | 9.1208 | 37.9668
|  | MVA | 25.47 | 32.7416 | 31.7999 | 35.5481 | 47.9412 | 47.9412 | 34.7002
42 | Tirtol | MU | 2.8664 | 2.0076 | 2.5759 | 2.684 | 3.0321 | 13.1659
|  | MVA | 12.8854 | 10.9405 | 10.2571 | 11.6771 | 14.0003 | 14.0003 | 11.9521
43 | Infocity-II | MU | 8.5717 | 8.7831 | 8.7592 | 8.422 | 10.5672 | 45.1033
|  | MVA | 19.6763 | 37.8268 | 29.1514 | 34.4738 | 35.5891 | 37.8268 | 31.3435
44 | Unit-8 GIS | MU | 5 | 4.5 | 4 | 6 | 6.5 | 26
|  | MVA | 15 | 15 | 14 | 16 | 17 | 17 | 15.4
45 | MCl feeder | MU | 13.0768 | 13.0768 | 13.0768 | 13.0768 | 13.0768 | 65.384
|  | MVA | 31 | 31 | 31 | 31 | 31 | 31 | 31
46 | Arati Steel | MU | 0.012488 | 0.012488 | 0.012488 | 0.012488 | 0.012488 | 0.06244
|  | MVA | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11
47 | BPPL (S/W) | MU | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.0084
|  | MVA | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556
48 | FCI feeder | MU | 0.24638 | 0.24638 | 0.24638 | 0.24638 | 0.24638 | 1.2319
|  | MVA | 1 | 1 | 1 | 1 | 1 | 1 | 1
49 | Rawmet | MU | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 10.0333
|  | MVA | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
50 | GSAL | MU | 0.036882 | 0.036882 | 0.036882 | 0.036882 | 0.036882 | 0.18441
|  | MVA | 5 | 5 | 5 | 5 | 5 | 5 | 5
51 | Hind Metalies MGM | MU | 0.082548 | 0.082548 | 0.082548 | 0.082548 | 0.082548 | 0.41274
|  | MVA | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778
52 | Navchrome feeder | MU | 0.0003176 | 0.0003176 | 0.0003176 | 0.0003176 | 0.0003176 | 0.001588
|  | MVA | 3 | 3 | 3 | 3 | 3 | 3 | 3
53 | Hindmetalics SGEL | MU | 0.019988 | 0.019988 | 0.019988 | 0.019988 | 0.019988 | 0.099941
|  | MVA | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22
54 | Meramundali Bhusan | MU | 10.038 | 10.038 | 10.038 | 10.038 | 10.038 | 50.1898
|  | MVA | 112 | 112 | 112 | 112 | 112 | 112 | 112
55 | Meramundali 132kv BRG Feeder | MU | 7.2078 | 7.2078 | 7.2078 | 7.2078 | 7.2078 | 36.0392
|  | MVA | 31 | 31 | 31 | 31 | 31 | 31 | 31
56 | Meramundali JSPL | MU | 0.075043 | 0.075043 | 0.075043 | 0.075043 | 0.075043 | 0.37522
|  | MVA | 20 | 20 | 20 | 20 | 20 | 20 | 20
57 | Meramundali 132kv Rungta Feeder | MU | 0.05673 | 0.05673 | 0.05673 | 0.05673 | 0.05673 | 0.28365
|  | MVA | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
58 | Essar | MU | 0.17056 | 0.17056 | 0.17056 | 0.17056 | 0.17056 | 0.85281
|  | MVA | 27 | 27 | 27 | 27 | 27 | 27 | 27
59 | IFFCO feeder | MU | 1.1398 | 1.1398 | 1.1398 | 1.1398 | 1.1398 | 5.699
|  | MVA | 11 | 11 | 11 | 11 | 11 | 11 | 11
60 | IOCL feeder | MU | 0.14036 | 0.14036 | 0.14036 | 0.14036 | 0.14036 | 0.70179
|  | MVA | 17 | 17 | 17 | 17 | 17 | 17 | 17
61 | PPL feeder | MU | 2.2329 | 2.2329 | 2.2329 | 2.2329 | 2.2329 | 11.1645
|  | MVA | 14 | 14 | 14 | 14 | 14 | 14 | 14
62 | PPT Feeder | MU | 6.8559 | 6.8559 | 6.8559 | 6.8559 | 6.8559 | 34.2794
|  | MVA | 18 | 18 | 18 | 18 | 18 | 18 | 18
63 | Salipur 132KV OCL Feeder | MU | 0.13167 | 0.13167 | 0.13167 | 0.13167 | 0.13167 | 0.65833
|  | MVA | 10 | 10 | 10 | 10 | 10 | 10 | 10
64 | Solari traction | MU | 4.1102 | 4.1102 | 4.1102 | 4.1102 | 4.1102 | 20.5511
|  | MVA | 15 | 15 | 15 | 15 | 15 | 15 | 15
65 | Boinda Traction | MU | 0.48826 | 0.48826 | 0.48826 | 0.48826 | 0.48826 | 2.4413
|  | MVA | 8 | 8 | 8 | 8 | 8 | 8 | 8
66 | Chainpal Traction | MU | 2.5437 | 2.5437 | 2.5437 | 2.5437 | 2.5437 | 12.7186
|  | MVA | 10 | 10 | 10 | 10 | 10 | 10 | 10
67 | choudwar Rly Feeder | MU | 4.9583 | 4.9583 | 4.9583 | 4.9583 | 4.9583 | 24.7917
|  | MVA | 20 | 20 | 20 | 20 | 20 | 20 | 20
68 | Joranda Rly. | MU | 4.1427 | 4.1427 | 4.1427 | 4.1427 | 4.1427 | 20.7134
|  | MVA | 18 | 18 | 18 | 18 | 18 | 18 | 18
69 | Hindmetalics Traction | MU | 3.0399 | 3.0399 | 3.0399 | 3.0399 | 3.0399 | 15.1996
|  | MVA | 16 | 16 | 16 | 16 | 16 | 16 | 16
70 | Jagatsinghpur Traction | MU | 4.5827 | 4.5827 | 4.5827 | 4.5827 | 4.5827 | 22.9136
|  | MVA | 16 | 16 | 16 | 16 | 16 | 16 | 16
71 | Kaipadar trac | MU | 5.6764 | 4.5827 | 4.5827 | 4.5827 | 4.5827 | 24.0073
|  | MVA | 19 | 19 | 19 | 19 | 19 | 19 | 19
72 | Pallahara | MU | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 3.5
|  | MVA | 3 | 3 | 3 | 3 | 3 | 3 | 3
73 | Chandpur PAN Time Finance (Solar) | MU | 0.020519 | 0.020519 | 0.020519 | 0.020519 | 0.024296 | 0.10637
|  | MVA | 1 | 1 | 1 | 1 | 1 | 1 | 1
74 | Dhenkanal SCAW Feeder | MU | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 0.52639
|  | MVA | 5 | 5 | 5 | 5 | 5 | 5 | 5
75 | Barang | MU | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.29269
|  | MVA | 1 | 1 | 1 | 1 | 1 | 1 | 1
76 | MGM Solar | MU | 0.097705 | 0.091445 | 0.10755 | 0.10966 | 0.11721 | 0.52358
|  | MVA | 0.6825 | 0.67563 | 0.67281 | 0.715 | 0.69906 | 0.715 | 0.689
77 | Angul PGCIL Stn. Tertiary | MU | 0.16364 | 0.14958 | 0.1556 | 0.14381 | 0.11364 | 0.72628
|  | MVA | 0.22728 | 0.20105 | 0.20914 | 0.19974 | 0.15275 | 0.22728 | 0.19799
78 | Pandiabil PG | MU | 0.043017 | 0.03802 | 0.0411 | 0.049693 | 0.037484 | 0.20931
|  | MVA | 0.059746 | 0.051102 | 0.055242 | 0.069018 | 0.050382 | 0.069018 | 0.057098
79 | Rengali PGCIL Stn.Tertiary | MU | 0.15762 | 0.02084 | 0.0359 | 0.033278 | 0.020798 | 0.26844
|  | MVA | 0.21892 | 0.028011 | 0.048253 | 0.046219 | 0.027954 | 0.21892 | 0.073872
80 | Essar Power | MU | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.06
|  | MVA | 5 | 5 | 5 | 5 | 5 | 5 | 5
| TOTAL MU |  | 733.7931 | 713.0665 | 702.8361 | 683.6164 | 856.1342 | 3689.4462
| SUM OF PEAK DEMAND IN MVA |  | 2537.6842 | 2468.6316 | 2416.8131 | 2502.2706 | 2721.8799
| SMD OF CESU IN MVA |  | 1547.3684 | 1505.2632 | 1473.6665 | 1525.7748 | 1659.6829 | 1659.6829

## Annexure-N
Annexure-N
Sub-station wise Monthly Projection of Energy and Demand for FY-2020-21
NAME OF THE DISCOM: CESU
TOTAL CONTRACT DEMAND IN MVA:1957 MVA
TOTAL ENERGY REQUIREMENT (MU):9550.33MU
Sl No. | Name of Grid/EHT/Traction | Energy (MU) / Peak Demand (MVA) | 2020-04-04 | 2020-05-04 | 2020-06-04 | 2020-07-04 | 2020-08-04 | 2020-09-04 | 2020-10-04 | 2020-11-04 | 2020-12-04 | 2021-01-04 | 2021-02-04 | 2021-03-04 | Total Energy/Maximum Demand | Avg. MD
1 | Angul Grid | MU | 18.8585 | 30.23 | 23.4977 | 18.6813 | 17.3098 | 15.43 | 17.5866 | 17.7977 | 18.6559 | 18.2397 | 16.29 | 17.7078 | 230.2851
|  | MVA | 74.6117 | 63.3353 | 67.8989 | 55.0165 | 56.3983 | 74.1125 | 48.3159 | 50.9897 | 48.2246 | 42.5922 | 47.5443 | 58.4883 | 74.6117 | 57.294
2 | Arugul Grid | MU | 4.9375 | 1.9549 | 1.8208 | 2.8887 | 2.5751 | 3.6934 | 3.632 | 1.7942 | 1.7444 | 1.6163 | 1.74 | 2.5781 | 30.9754
|  | MVA | 25.1145 | 15.003 | 8.0991 | 12.377 | 11.6886 | 13.3488 | 22.0302 | 8.2877 | 6.2459 | 7.1047 | 8.2064 | 14.2713 | 25.1145 | 12.6481
3 | Badagada Grid | MU | 19.6572 | 12.3733 | 18.9022 | 14.8256 | 15.9495 | 16.8 | 18.7532 | 18.6718 | 15.7507 | 12.4024 | 17.7858 | 18.8718 | 200.7435
|  | MVA | 88.2388 | 56.3034 | 72.9925 | 56.2737 | 60.7052 | 80.7508 | 97.7114 | 105.9428 | 71.3049 | 52.2335 | 82.1262 | 86.4787 | 105.9428 | 75.9218
4 | Balugoan Grid | MU | 10.1744 | 13.9008 | 12.5341 | 10.2092 | 9.9154 | 9.1102 | 9.7046 | 8.9249 | 8.0954 | 7.7487 | 7.7923 | 9.754 | 117.8641
|  | MVA | 30.4274 | 36.8104 | 25.9053 | 77.6111 | 23.4872 | 25.4198 | 30.7002 | 20.0992 | 32.2968 | 28.8079 | 75.3992 | 39.0109 | 77.6111 | 37.1646
5 | Banki | MU | 6.4019 | 8.557 | 6.6848 | 4.6075 | 5.8536 | 5.6947 | 5.5688 | 5.89 | 5.4344 | 5.477 | 5.276 | 6.5416 | 71.9872
|  | MVA | 18.515 | 32.9953 | 20.4084 | 9.6262 | 19.1423 | 27.6262 | 18.8407 | 17.0582 | 14.5465 | 16.4744 | 20.2406 | 22.9549 | 32.9953 | 19.8691
6 | Bhubaneswar Grid | MU | 57.1274 | 64.7899 | 67.5894 | 56.0302 | 53.622 | 47.9682 | 52.8171 | 47.6538 | 46.3959 | 47.2206 | 40.9773 | 52.584 | 634.7759
|  | MVA | 196.9744 | 198.0459 | 185.9493 | 203.8402 | 216.5231 | 158.2036 | 192.8632 | 154.8984 | 156.9591 | 140.777 | 172.8543 | 189.1994 | 216.5231 | 180.5907
7 | Bidanasi Grid | MU | 45.6799 | 61.0287 | 57.0797 | 42.6566 | 42.6565 | 37.9596 | 41.0352 | 39.627 | 34.7987 | 32.2556 | 32.2279 | 43.296 | 510.3014
|  | MVA | 120.3979 | 193.7302 | 170.6414 | 117.6027 | 161.3411 | 143.9809 | 134.9384 | 112.0727 | 123.4919 | 122.6499 | 112.7727 | 144.8626 | 193.7302 | 138.2069
8 | Boinda Grid | MU | 9.837 | 14.1298 | 10.3503 | 9.2687 | 8.8599 | 8.2489 | 9.0157 | 11.1781 | 12.8545 | 13.1755 | 11.0513 | 10.1693 | 128.139
|  | MVA | 27.9665 | 33.9986 | 30.044 | 22.7352 | 27.803 | 27.6159 | 27.7462 | 34.106 | 40.6146 | 40.0697 | 38.2781 | 33.366 | 40.6146 | 32.0286
9 | Chainpal grid | MU | 30.3672 | 45.5645 | 33.9298 | 29.3301 | 27.5637 | 25.9238 | 28.7509 | 29.7641 | 33.4796 | 31.1793 | 25.5923 | 28.1687 | 369.6142
|  | MVA | 146.1466 | 124.6478 | 97.4628 | 129.4289 | 94.2461 | 93.9877 | 87.7536 | 86.5463 | 92.6092 | 97.9873 | 85.8849 | 66.5579 | 146.1466 | 100.2716
10 | Chandaka grid | MU | 71.0068 | 67.9617 | 79.0821 | 65.2085 | 60.1832 | 59.266 | 58.7637 | 56.5659 | 53.3209 | 49.2604 | 52.003 | 63.421 | 736.0433
|  | MVA | 196.1837 | 249.4501 | 241.4023 | 160.322 | 210.9635 | 210.3725 | 171.5115 | 204.5188 | 134.4717 | 149.8697 | 146.491 | 223.9513 | 249.4501 | 191.6257
11 | Chandikhole grid | MU | 7.9923 | 9.568 | 8.9303 | 8.1354 | 7.8172 | 7.6755 | 8.1812 | 8.3517 | 8.8289 | 9.1718 | 8.4087 | 8.5837 | 101.6448
|  | MVA | 20 | 25.5955 | 24.7025 | 24 | 23.116 | 24.3166 | 23.7116 | 21.4693 | 22.6792 | 23.2072 | 23.9099 | 23.7677 | 25.5955 | 23.373
12 | Chandpur Grid | MU | 6.5426 | 6.6974 | 8.2069 | 6.875 | 6.7917 | 6.1958 | 6.719 | 6.193 | 5.5234 | 5.4087 | 5.2687 | 6.4066 | 76.8288
|  | MVA | 24.4437 | 24.0796 | 19.9275 | 23.491 | 17.5054 | 18.5975 | 17.4453 | 18.4095 | 17.6484 | 21.2727 | 16.8453 | 17.6533 | 24.4437 | 19.7766
13 | Choudwar grid | MU | 34.0883 | 30.9852 | 38.0387 | 33.4369 | 32.4305 | 30.6404 | 33.5933 | 35.6757 | 36.5597 | 36.1942 | 33.8352 | 35.0565 | 410.5348
|  | MVA | 141.6738 | 108.9906 | 130.4567 | 123.0007 | 99.1904 | 120.3145 | 107.6785 | 87.6906 | 102.75 | 90.4403 | 113.5974 | 130.8132 | 141.6738 | 113.0497
14 | Cuttack grid | MU | 28.526 | 30.3292 | 32.2802 | 26.3471 | 23.2799 | 24.5958 | 27.0371 | 22.9677 | 21.371 | 19.5306 | 20.7793 | 23.2731 | 300.3173
|  | MVA | 116.8162 | 84.4599 | 124.6273 | 113.2429 | 94.7025 | 83.7962 | 103.4255 | 74.5229 | 72.3285 | 73.6845 | 70.6757 | 70.2308 | 124.6273 | 90.2094
15 | Dhenkanal grid | MU | 27.6929 | 40.2944 | 31.3636 | 26.3709 | 25.3264 | 23.9808 | 25.1599 | 28.2392 | 30.2099 | 29.2173 | 25.4348 | 27.7327 | 341.0226
|  | MVA | 80.0004 | 101.8765 | 94.5437 | 93.3933 | 72.0063 | 82.591 | 76.3107 | 81.2248 | 81.1218 | 106.0137 | 69.9194 | 78.1807 | 106.0137 | 84.7652
16 | Jagatsinghpur grid | MU | 19.786 | 16.9168 | 22.5619 | 19.6183 | 19.4778 | 18.1442 | 20.1733 | 18.4316 | 17.2382 | 17.416 | 16.4337 | 19.3398 | 225.5375
|  | MVA | 65.1244 | 58.885 | 59.0579 | 57.9374 | 56.6086 | 67.7052 | 62.4398 | 64.971 | 54.0092 | 43.4281 | 55.3416 | 62.9215 | 67.7052 | 59.0358
17 | Kalarangi grid | MU | 9.7914 | 13.1145 | 9.977 | 9.3675 | 9.7316 | 8.6765 | 9.352 | 10.3805 | 11.3403 | 12.1417 | 9.9353 | 9.8918 | 123.7
|  | MVA | 30.1879 | 33.3633 | 27.9687 | 28.5104 | 45.495 | 27.4933 | 28.8238 | 30.6271 | 32.1101 | 43.0709 | 29.6292 | 29.2785 | 45.495 | 32.2132
18 | Kamakshyanagar | MU | 11.0023 | 16.5413 | 13.4042 | 11.5865 | 11.5063 | 10.7893 | 11.8248 | 12.9274 | 13.7687 | 14.2706 | 11.2299 | 9.5681 | 148.4194
|  | MVA | 38.1135 | 42.8524 | 35.4957 | 45.4529 | 32.4758 | 30.5911 | 39.3737 | 36.1645 | 47.9334 | 33.2088 | 42.9603 | 32.0877 | 47.9334 | 38.0591
19 | Kendrapada Grid | MU | 16.3562 | 21.1496 | 20.3546 | 17.0674 | 16.3324 | 15.7364 | 16.8232 | 15.4362 | 13.5811 | 13.4541 | 13.1785 | 15.7397 | 195.2092
|  | MVA | 75.5081 | 74.5068 | 84.1361 | 51.8634 | 54.6045 | 65.6877 | 72.9225 | 50.5526 | 61.3471 | 41.2748 | 46.1518 | 60.7565 | 84.1361 | 61.6093
20 | Khajuriakanta Grid | MU | 3.8802 | 5.9296 | 4.5263 | 3.8466 | 3.7361 | 3.36 | 3.7183 | 4.0228 | 4.4262 | 4.4315 | 3.7426 | 3.8063 | 49.4265
|  | MVA | 14.9754 | 24.0817 | 22.4386 | 13.9922 | 12.6447 | 15.3203 | 11.4989 | 12.9551 | 12.4795 | 20.3696 | 12.1659 | 15.1266 | 24.0817 | 15.6707
21 | Khuntuni grid | MU | 1.8175 | 2.2188 | 1.9394 | 1.8003 | 2.0406 | 2.073 | 2.3296 | 1.8 | 1.8 | 1.8 | 1.8 | 2 | 23.4192
|  | MVA | 5.9877 | 5.7319 | 5.4553 | 6.7101 | 8.3018 | 8.3953 | 10.1091 | 8 | 8 | 8 | 8 | 10.5315 | 10.5315 | 7.7686
22 | Khurda grid | MU | 44.9713 | 33.4134 | 46.9692 | 39.7373 | 41.0427 | 35.9262 | 41.3547 | 46.8589 | 48.3205 | 48.3456 | 46.7393 | 50.3087 | 523.9878
|  | MVA | 164.2487 | 142.8887 | 124.9704 | 120.0337 | 115.0978 | 118.6854 | 145.9138 | 138.6394 | 151.7564 | 139.2234 | 158.5806 | 172.2271 | 172.2271 | 141.0221
23 | Konark Grid | MU | 4.0789 | 3 | 1.7113 | 1.8552 | 2.1124 | 2.1138 | 2.4133 | 3.8332 | 3.9118 | 3.9592 | 4.0978 | 4.8156 | 37.9026
|  | MVA | 18.6518 | 12.3107 | 11.8113 | 7.4997 | 7.4102 | 6.466 | 9.3246 | 19.7724 | 13.3057 | 11.258 | 18.3311 | 18.0412 | 19.7724 | 12.8485
24 | Mania Grid | MU | 1.3016 | 1.8389 | 1.4613 | 1.153 | 0.8162 | 0.97707 | 1.0076 | 2.7072 | 2.2651 | 1.0271 | 1.3676 | 1.2508 | 17.1735
|  | MVA | 9.2486 | 9.466 | 9.0231 | 10.8465 | 7.6078 | 7.9764 | 9.1415 | 8.8766 | 8.7387 | 9.0244 | 8.5066 | 9.3157 | 10.8465 | 8.981
25 | Marshaghai | MU | 8.0462 | 10.7907 | 10.1938 | 8.8962 | 8.3404 | 8.0495 | 8.7915 | 7.5414 | 6.6994 | 6.6775 | 6.2403 | 7.6891 | 97.956
|  | MVA | 25.97 | 26.6963 | 26.4467 | 25.5871 | 24.5931 | 25.1458 | 29.0056 | 22.9631 | 18.3597 | 21.5677 | 22.7958 | 23.9266 | 29.0056 | 24.4215
26 | Mendhasala Grid | MU | 1.1857 | 0.82752 | 1.2782 | 1.0639 | 1.0742 | 0.96729 | 1.074 | 0.56962 | 1.1099 | 0.97644 | 0.91387 | 1.1274 | 12.1681
|  | MVA | 4.8256 | 3.6392 | 4.0848 | 4.5805 | 2.9221 | 4.7082 | 4.9659 | 2.1594 | 3.6081 | 3.9551 | 3.735 | 4.6671 | 4.9659 | 3.9876
27 | Narasinghpur Grid | MU | 2.5129 | 4.0505 | 3.1347 | 2.5097 | 1.7333 | 2.2274 | 2.3674 | 2 | 2 | 2 | 2 | 2.5 | 29.0359
|  | MVA | 7.7181 | 8.9394 | 9.0357 | 7.4118 | 6.9396 | 7.8149 | 7.5302 | 6 | 6 | 6 | 7 | 7.2254 | 9.0357 | 7.3012
28 | Nayagad Grid | MU | 28.3531 | 44.9322 | 36.0137 | 28.5032 | 26.7696 | 25.6302 | 26.4167 | 23.7196 | 23.1018 | 23.0866 | 22.2219 | 27.1941 | 335.9428
|  | MVA | 106.121 | 107.434 | 103.9586 | 80.7524 | 89.1864 | 98.6532 | 71.9355 | 69.2434 | 62.1726 | 106.9851 | 109.0216 | 82.0542 | 109.0216 | 90.6265
29 | Nimapada Grid | MU | 28.1134 | 25 | 17.2246 | 22.154 | 24.5089 | 24.0037 | 27.0516 | 26.8545 | 25.2736 | 25.4403 | 26.4749 | 28.8033 | 300.9027
|  | MVA | 86.2212 | 77.2974 | 62.1977 | 68.556 | 67.9085 | 67.3105 | 77.3805 | 85.9345 | 69.5168 | 99.7478 | 89.5328 | 79.548 | 99.7478 | 77.596
30 | Nuapatna grid | MU | 19.1648 | 26.354 | 21.967 | 18.7236 | 19.2218 | 17.0224 | 18.0877 | 22.2553 | 23.9939 | 23.4794 | 20.1607 | 19.3997 | 249.8305
|  | MVA | 55.6468 | 73.9047 | 80.2438 | 53.3474 | 66.0715 | 49.6717 | 64.8359 | 81.7405 | 78.5536 | 80.1688 | 62.7985 | 61.3176 | 81.7405 | 67.3584
31 | Olaver-2 | MU | 3.679 | 5.2664 | 4.9677 | 4.2551 | 3.9678 | 3.9011 | 4.1753 | 3.4025 | 2.7811 | 2.6009 | 2.5718 | 3.3367 | 44.9053
|  | MVA | 14.2309 | 14.7395 | 20.2035 | 13.0255 | 12.5404 | 14.576 | 13.3394 | 11.014 | 10.8139 | 11.5474 | 11.6803 | 12.6804 | 20.2035 | 13.3659
32 | Paradeep grid | MU | 13.6184 | 16.7241 | 17.061 | 14.5541 | 13.3488 | 13.5243 | 14.966 | 13.5906 | 12.8913 | 12.2231 | 11.7897 | 14.3028 | 168.5942
|  | MVA | 46.0014 | 40.7621 | 44.8864 | 49.5339 | 52.4427 | 49.5871 | 51.181 | 42.3025 | 53.0852 | 35.2306 | 35.1935 | 46.2355 | 53.0852 | 45.5368
33 | Pattamundai grid | MU | 13.3664 | 18.5089 | 16.9151 | 14.6383 | 13.7431 | 13.4416 | 14.4159 | 12.2257 | 10.3304 | 10.1121 | 10.439 | 12.3183 | 160.4549
|  | MVA | 43.2176 | 42.4222 | 44.2693 | 40.7804 | 40.2085 | 40.9957 | 43.1643 | 36.8271 | 32.012 | 31.8254 | 42.9839 | 53.359 | 53.359 | 41.0054
34 | Phulnakhara Grid | MU | 15.321 | 13 | 11.6969 | 11.6208 | 12.5221 | 11.965 | 13.5347 | 13.6675 | 13.3974 | 13.5533 | 12.7964 | 15.0831 | 158.1582
|  | MVA | 57.3027 | 48.069 | 34.5538 | 33.6383 | 33.4768 | 33.7946 | 42.6286 | 39.093 | 37.3891 | 42.8332 | 40.3346 | 46.0166 | 57.3027 | 40.7609
35 | Puri grid | MU | 22.0304 | 8.2052 | 14.7039 | 10.8032 | 18.0974 | 21.1999 | 24.7517 | 11.1235 | 10.2845 | 16.8141 | 16.749 | 22.2178 | 196.9806
|  | MVA | 98.4476 | 61.8498 | 104.4836 | 69.4539 | 64.1893 | 69.4885 | 99.1915 | 37.5255 | 45.9612 | 57.5191 | 58.1655 | 80.5169 | 104.4836 | 70.5661
36 | Rairakhol Bamur fdr | MU | 1.8227 | 2.6668 | 1.9882 | 1.7563 | 1.6977 | 1.5735 | 1.6564 | 2.201 | 2.5031 | 2.5147 | 2.0358 | 1.851 | 24.2672
|  | MVA | 6.6696 | 6.2189 | 6.0364 | 6.1116 | 6.2163 | 5.8507 | 6.2769 | 7.257 | 6.986 | 7.3987 | 7.0636 | 6.4601 | 7.3987 | 6.5455
37 | Ransinghpur grid | MU | 49.404 | 51.755 | 56.1503 | 42.5034 | 41.2673 | 39.3032 | 42.5573 | 42.4034 | 36.8599 | 33.6573 | 37.3006 | 45.6012 | 518.7628
|  | MVA | 157.9537 | 177.5191 | 193.7974 | 154.7248 | 116.8572 | 116.5469 | 118.2419 | 152.1992 | 90.5847 | 104.9077 | 121.1108 | 133.4343 | 193.7974 | 136.4898
38 | Rengali S/Y | MU | 6.3748 | 9.4102 | 7.7786 | 6.8424 | 6.8533 | 6.4787 | 7.1998 | 5.8246 | 4.5101 | 7.1275 | 6.9397 | 7.749 | 83.0887
|  | MVA | 46.7542 | 32.2809 | 36.5599 | 27.0634 | 31.8023 | 30.4851 | 23.8513 | 25.4749 | 31.0023 | 25.5653 | 31.1103 | 38.4526 | 46.7542 | 31.7002
39 | Salipur Grid | MU | 15.7228 | 16.6718 | 18.3492 | 15.7746 | 15.2869 | 14.9737 | 16.028 | 15.3991 | 15.158 | 14.9781 | 14.1908 | 16.0669 | 188.5998
|  | MVA | 48.787 | 46.8495 | 56.4816 | 43.9005 | 45.6251 | 42.5992 | 52.9872 | 55.1304 | 50.0889 | 44.29 | 48.3105 | 54.0798 | 56.4816 | 49.0941
40 | Samangara | MU | 6.9857 | 7 | 3.7113 | 4.918 | 4 | 7 | 7 | 7 | 7 | 7 | 7.6743 | 7.7767 | 77.066
|  | MVA | 30.5301 | 24.7775 | 34.7365 | 25.8911 | 20 | 20 | 20 | 18 | 18 | 18 | 20 | 30.0594 | 34.7365 | 23.3329
41 | Shamuka | MU | 9.2305 | 8 | 7.8584 | 14.2474 | 13.0007 | 9.45 | 11.904 | 9.5368 | 6.5804 | 5.9709 | 8.445 | 8.5195 | 112.7437
|  | MVA | 37.4782 | 31.6228 | 69.1136 | 56.626 | 51.0354 | 27.351 | 48.7572 | 27.7315 | 35.1877 | 35.3556 | 40.1329 | 53.1766 | 69.1136 | 42.7974
42 | Tirtol | MU | 2.9189 | 3.814 | 3.3189 | 3.2302 | 3.7054 | 2.8403 | 3.607 | 3.054 | 2.1351 | 2.7124 | 2.8201 | 2.8322 | 36.9886
|  | MVA | 17.2341 | 17.7845 | 14.3507 | 15.4772 | 16.8996 | 12.0836 | 15.6412 | 14.0295 | 11.7579 | 11.404 | 13.1831 | 15.5292 | 17.7845 | 14.6146
43 | Infocity-II | MU | 10.2432 | 9 | 11.162 | 9.7938 | 9.612 | 8.6467 | 10.0233 | 9.1328 | 9.3412 | 9.2235 | 8.8491 | 9.8706 | 114.8982
|  | MVA | 41.2018 | 38.9726 | 45.8092 | 39.3188 | 40.2724 | 37.7736 | 51.0402 | 21.4234 | 40.6529 | 32.411 | 38.92 | 39.4756 | 51.0402 | 38.9393
44 | Unit-8 GIS | MU | 9 | 8.7573 | 6.0248 | 6 | 5.7765 | 6 | 7.058 | 6 | 6 | 6 | 7 | 7 | 80.6166
|  | MVA | 30 | 30.0508 | 29.1604 | 19.2287 | 23.6016 | 18.1419 | 29.5699 | 20 | 20 | 20 | 22 | 23 | 30.0508 | 23.7294
45 | MCl feeder | MU | 13.8558 | 13.8558 | 13.8558 | 13.8558 | 13.8558 | 13.8558 | 13.8558 | 13.8558 | 13.8558 | 13.8558 | 13.8558 | 13.8558 | 166.27
|  | MVA | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
46 | Arati Steel | MU | 0.039167 | 0.039167 | 0.039167 | 0.039167 | 0.039167 | 0.039167 | 0.039167 | 0.039167 | 0.039167 | 0.039167 | 0.039167 | 0.039167 | 0.47
|  | MVA | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11 | 11.11
47 | BPPL (S/W) | MU | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.04
|  | MVA | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556 | 5.556
48 | FCI feeder | MU | 0.2825 | 0.2825 | 0.2825 | 0.2825 | 0.2825 | 0.2825 | 0.2825 | 0.2825 | 0.2825 | 0.2825 | 0.2825 | 0.2825 | 3.39
|  | MVA | [12 empty] | 1 | 1 | bar: 2020-04-04 to 2021-03-04
49 | Rawmet | MU | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 17.11
|  | MVA | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
50 | GSAL | MU | 0.0325 | 0.0325 | 0.0325 | 0.0325 | 0.0325 | 0.0325 | 0.0325 | 0.0325 | 0.0325 | 0.0325 | 0.0325 | 0.0325 | 0.39
|  | MVA | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
51 | Hind Metalies MGM | MU | 0.091667 | 0.091667 | 0.091667 | 0.091667 | 0.091667 | 0.091667 | 0.091667 | 0.091667 | 0.091667 | 0.091667 | 0.091667 | 0.091667 | 1.1
|  | MVA | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778 | 2.778
52 | Navchrome feeder | MU | 0.00083333 | 0.00083333 | 0.00083333 | 0.00083333 | 0.00083333 | 0.00083333 | 0.00083333 | 0.00083333 | 0.00083333 | 0.00083333 | 0.00083333 | 0.00083333 | 0.01
|  | MVA | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
53 | Hindmetalics SGEL | MU | 0.050833 | 0.050833 | 0.050833 | 0.050833 | 0.050833 | 0.050833 | 0.050833 | 0.050833 | 0.050833 | 0.050833 | 0.050833 | 0.050833 | 0.61
|  | MVA | 2.222 | 2.222 | 2.222 | 2.222 | 2.222 | 2.222 | 2.222 | 2.222 | 2.222 | 2.222 | 2.222 | 2.222 | 2.222 | 2.222
54 | Meramundali Bhusan | MU | 11.0375 | 11.0375 | 11.0375 | 11.0375 | 11.0375 | 11.0375 | 11.0375 | 11.0375 | 11.0375 | 11.0375 | 11.0375 | 11.0375 | 132.45
|  | MVA | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
55 | Meramundali 132kv BRG Feeder | MU | 7.3325 | 7.3325 | 7.3325 | 7.3325 | 7.3325 | 7.3325 | 7.3325 | 7.3325 | 7.3325 | 7.3325 | 7.3325 | 7.3325 | 87.99
|  | MVA | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
56 | Meramundali JSPL | MU | 0.0725 | 0.0725 | 0.0725 | 0.0725 | 0.0725 | 0.0725 | 0.0725 | 0.0725 | 0.0725 | 0.0725 | 0.0725 | 0.0725 | 0.87
|  | MVA | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
57 | Meramundali 132kv Rungta Feeder | MU | 0.075833 | 0.075833 | 0.075833 | 0.075833 | 0.075833 | 0.075833 | 0.075833 | 0.075833 | 0.075833 | 0.075833 | 0.075833 | 0.075833 | 0.91
|  | MVA | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
58 | Essar | MU | 0.1775 | 0.1775 | 0.1775 | 0.1775 | 0.1775 | 0.1775 | 0.1775 | 0.1775 | 0.1775 | 0.1775 | 0.1775 | 0.1775 | 2.13
|  | MVA | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
59 | IFFCO feeder | MU | 1.3008 | 1.3008 | 1.3008 | 1.3008 | 1.3008 | 1.3008 | 1.3008 | 1.3008 | 1.3008 | 1.3008 | 1.3008 | 1.3008 | 15.61
|  | MVA | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 22 | 16.5
60 | IOCL feeder | MU | 0.27917 | 0.27917 | 0.27917 | 0.27917 | 0.27917 | 0.27917 | 0.27917 | 0.27917 | 0.27917 | 0.27917 | 0.27917 | 0.27917 | 3.35
|  | MVA | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 28 | 22.5
61 | PPL feeder | MU | 2.7592 | 2.7592 | 2.7592 | 2.7592 | 2.7592 | 2.7592 | 2.7592 | 2.7592 | 2.7592 | 2.7592 | 2.7592 | 2.7592 | 33.11
|  | MVA | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 25 | 19.5
62 | PPT Feeder | MU | 7.2142 | 7.2142 | 7.2142 | 7.2142 | 7.2142 | 7.2142 | 7.2142 | 7.2142 | 7.2142 | 7.2142 | 7.2142 | 7.2142 | 86.57
|  | MVA | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
63 | Salipur 132KV OCL Feeder | MU | 0.52583 | 0.52583 | 0.52583 | 0.52583 | 0.52583 | 0.52583 | 0.52583 | 0.52583 | 0.52583 | 0.52583 | 0.52583 | 0.52583 | 6.31
|  | MVA | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
64 | Solari traction | MU | 4.2867 | 4.2867 | 4.2867 | 4.2867 | 4.2867 | 4.2867 | 4.2867 | 4.2867 | 4.2867 | 4.2867 | 4.2867 | 4.2867 | 51.44
|  | MVA | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
65 | Boinda Traction | MU | 0.63083 | 0.63083 | 0.63083 | 0.63083 | 0.63083 | 0.63083 | 0.63083 | 0.63083 | 0.63083 | 0.63083 | 0.63083 | 0.63083 | 7.57
|  | MVA | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
66 | Chainpal Traction | MU | 2.8908 | 2.8908 | 2.8908 | 2.8908 | 2.8908 | 2.8908 | 2.8908 | 2.8908 | 2.8908 | 2.8908 | 2.8908 | 2.8908 | 34.69
|  | MVA | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
67 | choudwar Rly Feeder | MU | 5.1775 | 5.1775 | 5.1775 | 5.1775 | 5.1775 | 5.1775 | 5.1775 | 5.1775 | 5.1775 | 5.1775 | 5.1775 | 5.1775 | 62.13
|  | MVA | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
68 | Joranda Rly. | MU | 4.2808 | 4.2808 | 4.2808 | 4.2808 | 4.2808 | 4.2808 | 4.2808 | 4.2808 | 4.2808 | 4.2808 | 4.2808 | 4.2808 | 51.37
|  | MVA | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
69 | Hindmetalics Traction | MU | 3.1533 | 3.1533 | 3.1533 | 3.1533 | 3.1533 | 3.1533 | 3.1533 | 3.1533 | 3.1533 | 3.1533 | 3.1533 | 3.1533 | 37.84
|  | MVA | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
70 | Jagatsinghpur Traction | MU | 4.625 | 4.625 | 4.625 | 4.625 | 4.625 | 4.625 | 4.625 | 4.625 | 4.625 | 4.625 | 4.625 | 4.625 | 55.5
|  | MVA | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
71 | Kaipadar trac | MU | 5.9917 | 5.9917 | 5.9917 | 5.9917 | 5.9917 | 5.9917 | 5.9917 | 5.9917 | 5.9917 | 5.9917 | 5.9917 | 5.9917 | 71.9
|  | MVA | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
72 | Pallahara | MU | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 8.4
|  | MVA | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
73 | Chandpur PAN Time Finance (Solar) | MU | 0.020519 | 0.020519 | 0.020519 | 0.020519 | 0.024296 | 0.020519 | 0.020519 | 0.020519 | 0.020519 | 0.024296 | 0.020519 | 0.024296 | 0.25756
|  | MVA | [12 empty] | 1 | 1 | bar: 2020-04-04 to 2021-03-04
74 | Dhenkanal SCAW Feeder | MU | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 0.10528 | 1.2633
|  | MVA | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
75 | Barang | MU | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.058538 | 0.70245
|  | MVA | [12 empty] | 1 | 1 | bar: 2020-04-04 to 2021-03-04
76 | MGM Solar | MU | 0.097705 | 0.091445 | 0.10755 | 0.10966 | 0.11721 | 0.097705 | 0.091445 | 0.10755 | 0.10966 | 0.11721 | 0.10966 | 0.11721 | 1.274
|  | MVA | 0.6825 | 0.67563 | 0.67281 | 0.715 | 0.69906 | 0.6825 | 0.67563 | 0.67281 | 0.715 | 0.69906 | 0.715 | 0.69906 | 0.715 | 0.69201
77 | Angul PGCIL Stn. Tertiary | MU | 0.16364 | 0.14958 | 0.1556 | 0.14381 | 0.11364 | 0.16364 | 0.14958 | 0.1556 | 0.14381 | 0.11364 | 0.14381 | 0.11364 | 1.71
|  | MVA | 0.22728 | 0.20105 | 0.20914 | 0.19974 | 0.15275 | 0.22728 | 0.20105 | 0.20914 | 0.19974 | 0.15275 | 0.19974 | 0.15275 | 0.22728 | 0.19437
78 | Pandiabil PGCIL Stn. Tertiary | MU | 0.043017 | 0.03802 | 0.0411 | 0.049693 | 0.037484 | 0.043017 | 0.03802 | 0.0411 | 0.049693 | 0.037484 | 0.049693 | 0.037484 | 0.5058
|  | MVA | 0.059746 | 0.051102 | 0.055242 | 0.069018 | 0.050382 | 0.059746 | 0.051102 | 0.055242 | 0.069018 | 0.050382 | 0.069018 | 0.050382 | 0.069018 | 0.057532
79 | Rengali PGCIL Stn. Tertiary | MU | 0.15762 | 0.02084 | 0.0359 | 0.033278 | 0.020798 | 0.15762 | 0.02084 | 0.0359 | 0.033278 | 0.020798 | 0.033278 | 0.020798 | 0.59096
|  | MVA | 0.21892 | 0.028011 | 0.048253 | 0.046219 | 0.027954 | 0.21892 | 0.028011 | 0.048253 | 0.046219 | 0.027954 | 0.046219 | 0.027954 | 0.21892 | 0.067741
80 | Essar Power | MU | 0.0091667 | 0.0091667 | 0.0091667 | 0.0091667 | 0.0091667 | 0.0091667 | 0.0091667 | 0.0091667 | 0.0091667 | 0.0091667 | 0.0091667 | 0.0091667 | 0.11
|  | MVA | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
81 | Talcher Fertilizers Ltd | MU | 2020-11-04: 0.394; 2020-12-04: 0.394; 2021-01-04: 0.394; 2021-02-04: 0.394; 2021-03-04: 0.394 | 1.97
|  | MVA | 2020-11-04: 2; 2020-12-04: 2; 2021-01-04: 2; 2021-02-04: 2; 2021-03-04: 2 | 2 | 2
82 | M/S Ultra Tech Cement Pvt. Ltd | MU | 2020-09-04: 0.65714; 2020-10-04: 0.65714; 2020-11-04: 0.65714; 2020-12-04: 0.65714; 2021-01-04: 0.65714; 2021-02-04: 0.65714; 2021-03-04: 0.65714 | 4.6
|  | MVA | 2020-09-04: 5; 2020-10-04: 5; 2020-11-04: 5; 2020-12-04: 5; 2021-01-04: 5; 2021-02-04: 5; 2021-03-04: 5 | 5 | 5
| TOTAL MU |  | 837.9189 | 922.0099 | 903.5221 | 782.5162 | 770.2386 | 738.7849 | 797.4262 | 773.0736 | 751.5016 | 740.9239 | 720.4756 | 811.937 | 9550.3283
| SUM OF PEAK DEMAND IN MVA |  | 3179.7224 | 3155.8604 | 3209.48 | 2896.513 | 2841.45 | 2813.7877 | 2932.6765 | 2740.096 | 2647.4015 | 2680.3516 | 2814.1813 | 3028.8843
| SMD OF CESU IN MVA |  | 1938.8551 | 1924.3051 | 1957 | 1766.1664 | 1732.5915 | 1715.7242 | 1788.2174 | 1670.7902 | 1614.2692 | 1634.3607 | 1715.9642 | 1846.8807 | 1957

## Annexure-O
|  | CESU | [12 empty] | CESU | [12 empty] | CESU
|  | Power Purchae, Sales and Loss Calculation | [12 empty] | Power Purchae, Sales and Loss Calculation | [12 empty] | Power Purchae, Sales and Loss Calculation
Sl No | Division | Previous Financial Year 2018-19 (Actual) | [12 empty] | Current Financial Year 2019-20 ( Estimated) | [12 empty] | Target for Financial Year 2020-21 (Estimated)
|  | Power Purchase (MU) | Power Sale (MU) |  |  |  | Billing (Rs. Lakh) |  |  |  | Collection (Rs. Lakh) |  |  |  | Power Purchase (MU) | Power Sale (MU) |  |  |  | Billing (Rs. Lakh) |  |  |  | Collection (Rs. Lakh) |  |  |  | Power Purchase (MU) | Power Sale (MU) |  |  |  | Billing (Rs. Lakh) |  |  |  | Collection (Rs. Lakh) | [7 empty] | 2020-21
|  |  | LT | HT | EHT | Total | LT | HT | EHT | Total | LT | HT | EHT | Total |  | LT | HT | EHT | Total | LT | HT | EHT | Total | LT | HT | EHT | Total |  | LT | HT | EHT | Total | LT | HT | EHT | Total | LT | HT | EHT | Total | 2017-18 |  | 2018-19 |  | Dist Loss % | ATC Loss %
1 | BCDD-1 | 363.8755 | 234.14 | 102.05 | 0 | 336.19 | 13150.75 | 6885.12 | 0 | 20035.87 | 13602.2673 | 6904.76 | 0 | 20507.0273 | 372.6641 | 239.3966 | 118.9077 | 0 | 358.3043 | 15084.0171 | 7911.1213 | 0 | 22995.1384 | 14631.9966 | 7832.0101 | 0 | 22464.0066 | 396.9904 | 242.3027 | 128.9146 | 0 | 371.2173 | 16486.3598 | 8439.5279 | 0 | 24925.8877 | 16321.4962 | 8355.1326 | 0 | 24676.6288 | 7.609% | 5.436% | 3.853% | 6.074% | 6.492% | 7.427%
2 | BCDD-2 | 837.1293 | 428.31 | 335.98 | 0 | 764.29 | 22309.26 | 20703.79 | 0 | 43013.05 | 22929.9098 | 19983.19 | 0 | 42913.0998 | 857.3482 | 433.5117 | 391.4806 | 0 | 824.9923 | 25427.7573 | 22895.7183 | 0 | 48323.4755 | 24556.407 | 22666.7611 | 0 | 47223.1681 | 913.3131 | 422.0454 | 424.4267 | 0 | 846.4721 | 27791.7449 | 24424.9892 | 0 | 52216.7341 | 27513.8275 | 24180.7393 | 0 | 51694.5668 | 8.701% | 8.913% | 3.774% | 5.965% | 7.319% | 8.245%
3 | BED | 555.6243 | 359.57 | 102.48 | 0 | 462.05 | 18802.87 | 6567.81 | 0 | 25370.68 | 19395.3669 | 6239.14 | 0 | 25634.5069 | 569.0441 | 398.3567 | 119.4087 | 0 | 517.7654 | 21508.1824 | 7148.4879 | 0 | 28656.6703 | 21231.516 | 7077.003 | 0 | 28308.519 | 606.1894 | 444.7925 | 129.4578 | 0 | 574.2503 | 23507.7719 | 7625.956 | 0 | 31133.7279 | 23272.6942 | 7549.6964 | 0 | 30822.3906 | 16.84% | 15.98% | 9.011% | 10.12% | 5.269% | 6.216%
4 | NEDN | 412.745 | 167.634 | 12.45 | 0 | 180.084 | 7490.84 | 760.22 | 0 | 8251.06 | 5496.5345 | 792.64 | 0 | 6289.1745 | 422.7139 | 208.7166 | 14.5066 | 0 | 223.2233 | 6095.2942 | 908.1664 | 0 | 7003.4606 | 6009.96 | 899.0848 | 0 | 6909.0448 | 450.3073 | 263.0464 | 15.7275 | 0 | 278.7738 | 6661.9662 | 968.8255 | 0 | 7630.7917 | 6595.3466 | 959.1372 | 0 | 7554.4838 | 56.37% | 66.74% | 47.19% | 47.9% | 38.09% | 38.71%
5 | PED | 466.687 | 269.26 | 28.61 | 0 | 297.87 | 11971.85 | 1849.55 | 0 | 13821.4 | 10707.9108 | 2167.68 | 0 | 12875.5908 | 477.9588 | 318.305 | 33.3361 | 0 | 351.6411 | 11874.3667 | 2483.617 | 0 | 14357.9837 | 11708.1256 | 2458.7808 | 0 | 14166.9064 | 509.1583 | 365.4093 | 36.1416 | 0 | 401.5509 | 12978.3121 | 2649.5049 | 0 | 15627.8171 | 12848.529 | 2623.0099 | 0 | 15471.5389 | 36.17% | 40.54% | 26.43% | 27.41% | 21.13% | 21.92%
6 | NED | 221.61 | 166.916 | 5.2 | 0 | 172.116 | 6560.22 | 401.21 | 0 | 6961.43 | 6252.3922 | 452.03 | 0 | 6704.4222 | 226.9625 | 184.9212 | 6.059 | 0 | 190.9802 | 6933.4904 | 517.9129 | 0 | 7451.4033 | 6836.4216 | 512.7338 | 0 | 7349.1553 | 241.7779 | 206.4771 | 6.5689 | 0 | 213.046 | 7578.0886 | 552.5058 | 0 | 8130.5944 | 7502.3077 | 546.9807 | 0 | 8049.2884 | 22.33% | 25.2% | 15.85% | 17.01% | 11.88% | 12.76%
7 | KED | 730.401 | 244.76 | 244.76 | 66.81 | 556.33 | 10482.68 | 14625.9 | 4056.25 | 29164.83 | 10390.9151 | 14625.85 | 4079.56 | 29096.3251 | 748.0422 | 279.1622 | 285.1919 | 64.8654 | 629.2195 | 11522.8394 | 16757.5518 | 3661.7695 | 31942.1607 | 11411.5196 | 16589.9763 | 3661.7695 | 31663.2654 | 796.8719 | 311.7037 | 309.193 | 62.4188 | 683.3154 | 12594.1037 | 17876.8369 | 3565.665 | 34036.6056 | 12468.1627 | 17698.0685 | 3530.0083 | 33696.2396 | 23.83% | 24.01% | 15.88% | 16.62% | 14.25% | 15.11%
8 | BEDB | 249.069 | 121.68 | 12.6 | 50.52 | 184.8 | 4644.31 | 805.46 | 3067.31 | 8517.08 | 4338.6874 | 730.61 | 3054.56 | 8123.8574 | 255.0847 | 134.8056 | 14.6814 | 47.6861 | 197.1731 | 4811.3181 | 837.0956 | 2694.5916 | 8343.0053 | 4743.9596 | 828.7247 | 2694.5916 | 8267.2759 | 271.7358 | 150.5197 | 15.9169 | 45.8874 | 212.324 | 5258.6205 | 893.0076 | 2623.871 | 8775.4991 | 5206.0343 | 884.0776 | 2597.6323 | 8687.7441 | 25.8% | 29.23% | 22.7% | 23.4% | 21.86% | 22.65%
9 | CED | 510.215 | 185.6 | 84.72 | 17.57 | 287.89 | 8807.03 | 5271.92 | 1137.3 | 15216.25 | 6285.8095 | 5449.39 | 1361.47 | 13096.6695 | 522.5381 | 215.6206 | 98.7149 | 12.4957 | 326.8312 | 6970.5481 | 6243.6327 | 685.7299 | 13899.9107 | 6872.9604 | 6181.1964 | 685.7299 | 13739.8867 | 556.6477 | 250.7552 | 107.0225 | 12.0244 | 369.802 | 7618.5914 | 6660.6629 | 667.7327 | 14946.987 | 7542.4055 | 6594.0563 | 661.0554 | 14797.5171 | 43.57% | 51.43% | 37.45% | 38.17% | 33.57% | 34.23%
10 | CDD-I | 369.1247 | 252.4 | 59.56 | 0 | 311.96 | 12975.29 | 4064.72 | 0 | 17040.01 | 13796.911 | 3759.13 | 0 | 17556.041 | 378.04 | 279.6263 | 69.3987 | 0 | 349.0251 | 15299.8641 | 4307.0191 | 0 | 19606.8832 | 15085.666 | 4263.9489 | 0 | 19349.6149 | 402.7173 | 307.2219 | 75.2392 | 0 | 382.4611 | 16722.2738 | 4594.6973 | 0 | 21316.9712 | 16555.0511 | 4548.7504 | 0 | 21103.8015 | 15.49% | 12.93% | 7.675% | 8.887% | 5.03% | 5.98%
11 | CDD-II | 412.8727 | 207.73 | 71.39 | 59.24 | 338.36 | 10890.42 | 4715.32 | 3668.55 | 19274.29 | 11656.5436 | 4379.81 | 3655.26 | 19691.6136 | 422.8447 | 230.1378 | 83.1829 | 57.8671 | 371.1878 | 12926.3378 | 5018.1626 | 3319.046 | 21263.5464 | 12797.5445 | 4967.9809 | 3319.046 | 21084.5714 | 450.4467 | 256.9646 | 90.1834 | 55.6844 | 402.8324 | 14128.0837 | 5353.3401 | 3231.9364 | 22713.3602 | 13986.8029 | 5299.8067 | 3199.617 | 22486.2266 | 18.05% | 16.27% | 12.22% | 12.96% | 10.57% | 11.46%
12 | AED | 330.651 | 103.92 | 21.32 | 38.1 | 163.34 | 4678.67 | 1295.3 | 2529.92 | 8503.89 | 3253.9698 | 1295.23 | 2480.18 | 7029.3798 | 338.6371 | 115.1298 | 24.8419 | 33.364 | 173.3357 | 3608.4378 | 1484.0084 | 2115.7027 | 7208.1489 | 3572.3534 | 1469.1683 | 2115.7027 | 7157.2244 | 360.7422 | 143.5503 | 26.9325 | 32.1055 | 202.5883 | 3943.9099 | 1583.1296 | 2060.1753 | 7587.2147 | 3904.4708 | 1567.2983 | 2039.5736 | 7511.3426 | 50.6% | 59.17% | 48.81% | 49.18% | 43.84% | 44.4%
13 | SED | 216.642 | 109.97 | 1.13 | 0 | 111.1 | 4958.05 | 92.22 | 0 | 5050.27 | 2708.7269 | 68.1 | 0 | 2776.8269 | 221.8745 | 121.8324 | 1.3167 | 0 | 123.1491 | 3003.7994 | 78.0255 | 0 | 3081.8249 | 2961.7462 | 77.2452 | 0 | 3038.9915 | 236.3577 | 136.0342 | 1.4275 | 0 | 137.4617 | 3283.059 | 83.237 | 0 | 3366.296 | 3250.2284 | 82.4047 | 0 | 3332.6331 | 48.72% | 71.8% | 44.5% | 45.27% | 41.84% | 42.42%
14 | KED-I | 286.651 | 172.7 | 5.48 | 0 | 178.18 | 7619.38 | 352.14 | 0 | 7971.52 | 7314.6034 | 439.82 | 0 | 7754.4234 | 293.5744 | 191.3291 | 6.3852 | 0 | 197.7144 | 8111.4126 | 503.9233 | 0 | 8615.3359 | 7997.8529 | 498.8841 | 0 | 8496.7369 | 312.738 | 213.632 | 6.9226 | 0 | 220.5546 | 8865.5208 | 537.5818 | 0 | 9403.1026 | 8776.8656 | 532.206 | 0 | 9309.0715 | 37.84% | 39.53% | 32.65% | 33.58% | 29.48% | 30.18%
15 | KED-II | 105.337 | 58.86 | 0.53 | 0 | 59.39 | 2446.47 | 45.94 | 0 | 2492.41 | 2298.8871 | 43.32 | 0 | 2342.2071 | 107.8812 | 65.2092 | 0.61755 | 0 | 65.8268 | 2549.3141 | 49.6338 | 0 | 2598.948 | 2513.6237 | 49.1375 | 0 | 2562.7612 | 114.9233 | 72.8105 | 0.66952 | 0 | 73.4801 | 2786.3208 | 52.949 | 0 | 2839.2698 | 2758.4576 | 52.4195 | 0 | 2810.8771 | 43.62% | 47.02% | 38.98% | 39.83% | 36.06% | 36.7%
16 | PDP | 424.9382 | 111.86 | 18.82 | 209.82 | 340.5 | 4827.57 | 1115.23 | 13796.37 | 19739.17 | 3852.8794 | 1027.98 | 13868.62 | 18749.4794 | 435.2016 | 123.9263 | 21.9289 | 192.2995 | 338.1547 | 4272.5891 | 1177.807 | 12084.8229 | 17535.2189 | 4212.7728 | 1166.0289 | 12084.8229 | 17463.6246 | 463.6101 | 138.3722 | 23.7744 | 185.0463 | 347.1928 | 4669.8065 | 1256.4761 | 11767.6522 | 17693.9348 | 4623.1084 | 1243.9113 | 11649.9757 | 17516.9954 | 19.87% | 23.89% | 22.3% | 22.62% | 25.11% | 25.86%
17 | JED | 195.322 | 113.02 | 0.64 | 0 | 113.66 | 4898.41 | 37.76 | 0 | 4936.17 | 4728.1308 | 32.3 | 0 | 4760.4308 | 200.0396 | 125.2114 | 0.74572 | 0 | 125.9572 | 5243.1851 | 37.0077 | 0 | 5280.1928 | 5169.7805 | 36.6376 | 0 | 5206.4181 | 213.0975 | 139.8071 | 0.80848 | 0 | 140.6156 | 5730.6377 | 39.4795 | 0 | 5770.1172 | 5673.3313 | 39.0847 | 0 | 5712.416 | 41.81% | 43.88% | 37.03% | 37.91% | 34.01% | 34.67%
18 | DED | 628.699 | 209.64 | 92.14 | 52.78 | 354.56 | 9514.79 | 5386.02 | 3338.05 | 18238.86 | 8953.8788 | 5733.77 | 3580.46 | 18268.1088 | 643.8838 | 232.2538 | 107.3606 | 49.2413 | 388.8557 | 9929.2609 | 6569.4608 | 2925.0488 | 19423.7705 | 10554.7713 | 6503.7662 | 2925.0488 | 19983.5862 | 685.9144 | 268.3273 | 116.3958 | 47.384 | 432.107 | 10852.3722 | 7008.254 | 2848.2798 | 20708.906 | 10743.8485 | 6938.1714 | 2819.797 | 20501.8169 | 43.6% | 43.51% | 39.61% | 37.87% | 37% | 37.63%
19 | ANED | 325.405 | 143.16 | 20.845 | 0.88 | 164.885 | 6705.64 | 1323.01 | 149.16 | 8177.81 | 6372.9977 | 1231.73 | 52.85 | 7657.5777 | 333.2644 | 158.6026 | 24.2884 | 2.4955 | 185.3865 | 7067.234 | 1411.2533 | 498.4086 | 8976.8959 | 6968.2927 | 1397.1408 | 498.4086 | 8863.8421 | 355.0188 | 185.0907 | 26.3324 | 2.4014 | 213.8245 | 7724.2661 | 1505.515 | 485.3277 | 9715.1088 | 7647.0235 | 1490.4598 | 480.4744 | 9617.9577 | 49.33% | 52.55% | 44.37% | 45.07% | 39.77% | 40.37%
20 | TED | 1141.004 | 149.39 | 33.94 | 749.97 | 933.3 | 6986.37 | 2337.21 | 45614.23 | 54937.81 | 6212.0481 | 2209.38 | 45511.02 | 53932.4481 | 1168.5623 | 165.5047 | 39.5466 | 514.2755 | 719.3267 | 6888.7515 | 2531.3947 | 32558.88 | 41979.0262 | 6794.009 | 2506.0808 | 32558.88 | 41858.9698 | 1244.8423 | 194.7973 | 42.8747 | 494.8779 | 732.5498 | 7529.1904 | 2700.4739 | 31704.36 | 41934.0242 | 7453.8985 | 2673.4691 | 31387.3164 | 41514.684 | 18.2% | 19.7% | 38.44% | 38.62% | 41.15% | 41.74%
| Total | 8784.0026 | 3810.52 | 1254.645 | 1245.69 | 6310.855 | 180720.87 | 78635.85 | 77357.14 | 336713.86 | 170549.37 | 77565.86 | 77643.98 | 325759.21 | 8996.16 | 4221.56 | 1461.9 | 974.59 | 6658.05 | 189128 | 88871 | 60544 | 338543 | 186631.2793 | 87982.29 | 60544 | 335157.5693 | 9583.4 | 4713.66 | 1584.93 | 937.83 | 7236.42 | 206711 | 94806.95 | 58955 | 360472.95 | 204643.89 | 93858.8805 | 58365.45 | 356868.2205 | 28.16% | 30.49% | 25.99% | 26.73% | 24.49% | 25.25%

## Annexure-P
|  | CESU | [15 empty] | CESU | [15 empty] | CESU
|  | Calculation of Total and Average Cost of Supply | [15 empty] | Calculation of Total and Average Cost of Supply | [15 empty] | Calculation of Total and Average Cost of Supply
Sl No | Division | Previous Financial Year 2018-19 (Actual) | [15 empty] | Current Financial Year 2019-20 ( Estimated) | [15 empty] | Proposed for Financial Year 2020-21 (Estimated)
|  | Input Cost (BSP+TC+SLDC Charges) (Rs. Cr) | Emp. Cost (Rs. Cr) | R& M (Rs. Cr) | A&G (Rs. Cr) | Sub-total (Rs. Cr) | Other Cost (Rs. Cr) | Total Cost of Supply (Rs. Cr.) | Sales (MU) |  | Avg. Billing (p/u) |  | Avg. Coll. (p/u) |  | Avg. O&M Cost (p/u) |  | Avg. Cost of Supply (P/u) | Input Cost (BSP+TC+SLDC Charges) (Rs. Cr) | Emp. Cost (Rs. Cr) | R& M (Rs. Cr) | A&G (Rs. Cr) | Sub-total (Rs. Cr) | Other Cost (Rs. Cr) | Total Cost of Supply (Rs. Cr.) | Sales (MU) |  | Avg. Billing (p/u) |  | Avg. Coll. (p/u) |  | Avg. O&M Cost (p/u) |  | Avg. Cost of Supply (P/u) | Input Cost (BSP+TC+SLDC Charges) (Rs. Cr) | Emp. Cost (Rs. Cr) | R& M (Rs. Cr) | A&G (Rs. Cr) | Sub-total (Rs. Cr) | Other Cost (Rs. Cr) | Total Cost of Supply (Rs. Cr.) | Sales (MU) |  | Avg. Billing (p/u) |  | Avg. Coll. (p/u) |  | Avg. O&M Cost (p/u) |  | Avg. Cost of Supply (P/u)
[9 empty] | LT | Overall | LT | Overall | LT | Overall | LT | Overall | [8 empty] | LT | Overall | LT | Overall | LT | Overall | LT | Overall | [8 empty] | LT | Overall | LT | Overall | LT | Overall | LT | Overall
1 | 2 | 3 | 4 | 5 | 6 | 7=3+4+5+6 | 8 | 9=7+8 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 3 | 4 | 5 | 6 | 7=3+4+5+6 | 8 | 9=7+8 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 3 | 4 | 5 | 6 | 7=3+4+5+6 | 8 | 9=7+8 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
| BCDD-I,BBSR | 110.6233 | 39.1416 | 1.3103 | 6.7191 | 157.7942 | 8.6897 | 166.4838 | 234.14 | 336.19 | 5.6166 | 5.9597 | 5.8095 | 6.0998 | 2.0146 | 1.4031 | 4.5753 | 106.5897 | 52.0702 | 5.1093 | 9.3587 | 173.1279 | 9.5107 | 182.6387 | 239.3966 | 358.3043 | 6.3008 | 6.4178 | 6.112 | 6.2695 | 2.7794 | 1.857 | 4.9009 | 113.5462 | 54.6727 | 5.9167 | 11.1313 | 185.2668 | 10.1922 | 195.459 | 242.3027 | 371.2173 | 6.804 | 6.7146 | 6.736 | 6.6475 | 2.9959 | 2.0017 | 4.9235
| BCDD-II,BBSR | 254.499 | 46.1605 | 3.0144 | 15.4579 | 319.1318 | 19.9914 | 339.1233 | 428.31 | 764.29 | 5.2087 | 5.6278 | 5.3536 | 5.6148 | 1.509 | 0.84566 | 4.051 | 245.2195 | 61.4075 | 11.7545 | 21.5305 | 339.9121 | 21.8803 | 361.7924 | 433.5117 | 824.9923 | 5.6694 | 5.7528 | 5.4751 | 5.6219 | 2.1843 | 1.1478 | 4.2199 | 261.2235 | 64.4767 | 13.6119 | 25.6085 | 364.9206 | 23.448 | 388.3686 | 422.0454 | 846.4721 | 6.3337 | 6.0491 | 6.2703 | 5.9886 | 2.392 | 1.2569 | 4.2523
| BED,BBSR | 168.9176 | 41.3442 | 2.0007 | 10.2598 | 222.5223 | 13.2688 | 235.7911 | 359.57 | 462.05 | 5.2293 | 5.4909 | 5.394 | 5.548 | 1.4908 | 1.1601 | 4.2437 | 162.7585 | 55.0003 | 7.8018 | 14.2904 | 239.851 | 14.5225 | 254.3735 | 398.3567 | 517.7654 | 5.3992 | 5.5347 | 5.3298 | 5.4674 | 1.9353 | 1.4889 | 4.4702 | 173.3808 | 57.7493 | 9.0346 | 16.997 | 257.1616 | 15.563 | 272.7247 | 444.7925 | 574.2503 | 5.2851 | 5.4216 | 5.2323 | 5.3674 | 2.1032 | 1.6181 | 4.499
| NmED Nimapara | 125.4803 | 40.5275 | 1.4862 | 7.6215 | 175.1155 | 9.8567 | 184.9722 | 167.634 | 180.084 | 4.4686 | 4.5818 | 3.2789 | 3.4924 | 2.9609 | 2.7562 | 4.4815 | 120.905 | 53.9139 | 5.7955 | 10.6156 | 191.2301 | 10.788 | 202.0181 | 208.7166 | 223.2233 | 3.1465 | 3.3634 | 3.1024 | 3.3181 | 3.3694 | 3.1504 | 4.7791 | 128.7958 | 56.6085 | 6.7113 | 12.6262 | 204.7418 | 11.561 | 216.3028 | 263.0464 | 278.7738 | 2.7048 | 2.9122 | 2.6778 | 2.8831 | 3.6387 | 3.4022 | 4.8034
| PED Puri | 141.8794 | 46.3936 | 1.6805 | 8.6176 | 198.571 | 11.1449 | 209.7159 | 269.26 | 297.87 | 4.4462 | 4.6401 | 3.9768 | 4.3226 | 2.1055 | 1.9032 | 4.4937 | 136.7062 | 61.7176 | 6.553 | 12.0029 | 216.9798 | 12.1979 | 229.1777 | 318.305 | 351.6411 | 3.7305 | 4.0831 | 3.6783 | 4.0288 | 2.5219 | 2.2828 | 4.7949 | 145.6282 | 64.8023 | 7.5884 | 14.2763 | 232.2953 | 13.0719 | 245.3672 | 365.4093 | 401.5509 | 3.5517 | 3.8919 | 3.5162 | 3.8529 | 2.7228 | 2.4646 | 4.8191
| NED Nayagarh | 67.3725 | 30.8495 | 0.79799 | 4.0921 | 103.1122 | 5.2922 | 108.4044 | 166.916 | 172.116 | 3.9303 | 4.0446 | 3.7458 | 3.8953 | 2.1412 | 2.0765 | 4.8917 | 64.916 | 41.0393 | 3.1117 | 5.6997 | 114.7667 | 5.7923 | 120.559 | 184.9212 | 190.9802 | 3.7494 | 3.9017 | 3.6969 | 3.8481 | 2.6958 | 2.6103 | 5.3118 | 69.1527 | 43.0904 | 3.6034 | 6.7792 | 122.6258 | 6.2073 | 128.8331 | 206.4771 | 213.046 | 3.6702 | 3.8164 | 3.6335 | 3.7782 | 2.8917 | 2.7999 | 5.3286
| KED Khurda | 222.0521 | 42.5264 | 2.6301 | 13.4871 | 280.6958 | 17.4426 | 298.1384 | 244.76 | 556.33 | 4.2828 | 5.2424 | 4.2453 | 5.23 | 2.396 | 1.0541 | 4.0818 | 213.9557 | 56.5731 | 10.2559 | 18.7855 | 299.5703 | 19.0907 | 318.661 | 279.1622 | 629.2195 | 4.1277 | 5.0765 | 4.0878 | 5.0321 | 3.0668 | 1.3606 | 4.2599 | 227.9193 | 59.4007 | 11.8765 | 22.3436 | 321.54 | 20.4585 | 341.9986 | 311.7037 | 683.3154 | 4.0404 | 4.9811 | 4 | 4.9313 | 3.3536 | 1.4879 | 4.2918
| BED Balugaon | 75.7205 | 16.8954 | 0.89686 | 4.5992 | 98.1119 | 5.948 | 104.0599 | 121.68 | 184.8 | 3.8168 | 4.6088 | 3.5657 | 4.396 | 1.8402 | 1.2117 | 4.178 | 72.9596 | 22.476 | 3.4973 | 6.4059 | 105.3388 | 6.51 | 111.8488 | 134.8056 | 197.1731 | 3.5691 | 4.2313 | 3.5191 | 4.1929 | 2.4019 | 1.6422 | 4.3848 | 77.7212 | 23.5994 | 4.0499 | 7.6192 | 112.9897 | 6.9764 | 119.9662 | 150.5197 | 212.324 | 3.4936 | 4.1331 | 3.4587 | 4.0917 | 2.6163 | 1.7887 | 4.4148
| CED CTC | 155.1125 | 37.1692 | 1.8372 | 9.4213 | 203.5403 | 12.1844 | 215.7247 | 185.6 | 287.89 | 4.7452 | 5.2854 | 3.3868 | 4.5492 | 2.6093 | 1.6822 | 4.2281 | 149.4568 | 49.4464 | 7.1642 | 13.1225 | 219.1899 | 13.3356 | 232.5255 | 215.6206 | 326.8312 | 3.2328 | 4.2529 | 3.1875 | 4.204 | 3.2341 | 2.1336 | 4.4499 | 159.211 | 51.9178 | 8.2962 | 15.6079 | 235.0328 | 14.2911 | 249.324 | 250.7552 | 369.802 | 3.0383 | 4.0419 | 3.0079 | 4.0015 | 3.5164 | 2.3199 | 4.479
| CDD-I CTC | 112.2191 | 40.523 | 1.3292 | 6.816 | 160.8873 | 8.815 | 169.7023 | 252.4 | 311.96 | 5.1408 | 5.4622 | 5.4663 | 5.6277 | 1.9282 | 1.5601 | 4.5974 | 108.1274 | 53.9079 | 5.183 | 9.4937 | 176.712 | 9.6479 | 186.3599 | 279.6263 | 349.0251 | 5.4715 | 5.6176 | 5.3949 | 5.5439 | 2.4527 | 1.965 | 4.9296 | 115.1842 | 56.6022 | 6.0021 | 11.2918 | 189.0803 | 10.3392 | 199.4195 | 307.2219 | 382.4611 | 5.4431 | 5.5736 | 5.3886 | 5.5179 | 2.6427 | 2.1172 | 4.9518
| CDD-II CTC | 125.5191 | 34.1338 | 1.4867 | 7.6239 | 168.7635 | 9.8598 | 178.6233 | 207.73 | 338.36 | 5.2426 | 5.6964 | 5.6114 | 5.8197 | 2.0818 | 1.2781 | 4.3264 | 120.9424 | 45.4084 | 5.7973 | 10.6189 | 182.7671 | 10.7914 | 193.5584 | 230.1378 | 371.1878 | 5.6168 | 5.7285 | 5.5608 | 5.6803 | 2.6864 | 1.6656 | 4.5775 | 128.8356 | 47.6779 | 6.7134 | 12.6301 | 195.8571 | 11.5646 | 207.4216 | 256.9646 | 402.8324 | 5.4981 | 5.6384 | 5.4431 | 5.582 | 2.9122 | 1.8056 | 4.6048
| AED Athagarh | 100.5225 | 27.0529 | 1.1906 | 6.1056 | 134.8717 | 7.8962 | 142.7679 | 103.92 | 163.34 | 4.5022 | 5.2063 | 3.1312 | 4.3035 | 3.3053 | 2.1029 | 4.3178 | 96.8573 | 35.9886 | 4.6428 | 8.5042 | 145.9929 | 8.6423 | 154.6352 | 115.1298 | 173.3357 | 3.1342 | 4.1585 | 3.1029 | 4.1291 | 4.2678 | 2.8347 | 4.5664 | 103.1786 | 37.7873 | 5.3765 | 10.1149 | 156.4572 | 9.2615 | 165.7188 | 143.5503 | 202.5883 | 2.7474 | 3.7451 | 2.7199 | 3.7077 | 4.6277 | 3.0737 | 4.5938
| SED Salipur | 65.8622 | 22.5337 | 0.7801 | 4.0004 | 93.1764 | 5.1736 | 98.35 | 109.97 | 111.1 | 4.5085 | 4.5457 | 2.4632 | 2.4994 | 2.4838 | 2.4585 | 4.5397 | 63.4607 | 29.9767 | 3.042 | 5.5719 | 102.0513 | 5.6624 | 107.7138 | 121.8324 | 123.1491 | 2.4655 | 2.5025 | 2.431 | 2.4677 | 3.1675 | 3.1336 | 4.8547 | 67.6024 | 31.4749 | 3.5227 | 6.6273 | 109.2273 | 6.0681 | 115.2954 | 136.0342 | 137.4617 | 2.4134 | 2.4489 | 2.3893 | 2.4244 | 3.4166 | 3.38 | 4.878
| KED-I Kendrapara | 87.1459 | 32.335 | 1.0322 | 5.2931 | 125.8063 | 6.8455 | 132.6517 | 172.7 | 178.18 | 4.4119 | 4.4739 | 4.2354 | 4.352 | 2.2386 | 2.1697 | 4.6276 | 83.9684 | 43.0154 | 4.025 | 7.3725 | 138.3814 | 7.4923 | 145.8736 | 191.3291 | 197.7144 | 4.2395 | 4.3575 | 4.1802 | 4.2975 | 2.8439 | 2.7521 | 4.9689 | 89.4485 | 45.1653 | 4.661 | 8.7689 | 148.0438 | 8.0291 | 156.0729 | 213.632 | 220.5546 | 4.1499 | 4.2634 | 4.1084 | 4.2208 | 3.0625 | 2.9636 | 4.9905
| KED-II Marsaghai | 32.0239 | 14.8109 | 0.3793 | 1.9451 | 49.1593 | 2.5155 | 51.6748 | 58.86 | 59.39 | 4.1564 | 4.1967 | 3.9057 | 3.9438 | 2.9112 | 2.8852 | 4.9057 | 30.8563 | 19.7031 | 1.4791 | 2.7092 | 54.7476 | 2.7532 | 57.5009 | 65.2092 | 65.8268 | 3.9094 | 3.9482 | 3.8547 | 3.8932 | 3.6638 | 3.6294 | 5.33 | 32.8701 | 20.6878 | 1.7128 | 3.2223 | 58.4931 | 2.9505 | 61.4435 | 72.8105 | 73.4801 | 3.8268 | 3.864 | 3.7885 | 3.8254 | 3.9293 | 3.8925 | 5.3465
| PDP Paradeep | 129.1872 | 20.6638 | 1.5301 | 7.8466 | 159.2277 | 10.1479 | 169.3757 | 111.86 | 340.5 | 4.3157 | 5.7971 | 3.4444 | 5.5065 | 2.6856 | 0.88225 | 3.9859 | 124.4768 | 27.4891 | 5.9667 | 10.9292 | 168.8618 | 11.1067 | 179.9686 | 123.9263 | 338.1547 | 3.4477 | 5.1856 | 3.3994 | 5.1644 | 3.5816 | 1.3126 | 4.1353 | 132.6006 | 28.863 | 6.9096 | 12.9992 | 181.3725 | 11.9025 | 193.275 | 138.3722 | 347.1928 | 3.3748 | 5.0963 | 3.3411 | 5.0453 | 3.9356 | 1.4423 | 4.1689
| JED Jagatsinghapur | 59.3806 | 23.9427 | 0.70333 | 3.6067 | 87.6333 | 4.6645 | 92.2978 | 113.02 | 113.66 | 4.3341 | 4.3429 | 4.1834 | 4.1883 | 2.4998 | 2.4857 | 4.7254 | 57.2155 | 31.8511 | 2.7426 | 5.0236 | 96.8327 | 5.1052 | 101.9379 | 125.2114 | 125.9572 | 4.1875 | 4.1921 | 4.1288 | 4.1335 | 3.164 | 3.1453 | 5.0959 | 60.9496 | 33.443 | 3.176 | 5.9751 | 103.5436 | 5.471 | 109.0146 | 139.8071 | 140.6156 | 4.099 | 4.1035 | 4.058 | 4.0624 | 3.4018 | 3.3816 | 5.1157
| DED Dhenkanal | 191.1333 | 40.3069 | 2.2639 | 11.6092 | 245.3132 | 15.0139 | 260.3271 | 209.64 | 354.56 | 4.5386 | 5.1441 | 4.2711 | 5.1523 | 2.5844 | 1.5281 | 4.1407 | 184.1642 | 53.6204 | 8.8278 | 16.1698 | 262.7823 | 16.4325 | 279.2148 | 232.2538 | 388.8557 | 4.2752 | 4.9951 | 4.5445 | 5.1391 | 3.385 | 2.0218 | 4.3364 | 196.1835 | 56.3004 | 10.2228 | 19.2324 | 281.9391 | 17.6099 | 299.549 | 268.3273 | 432.107 | 4.0445 | 4.7925 | 4.004 | 4.7446 | 3.6923 | 2.2053 | 4.3671
| AnED Angul | 98.9277 | 31.056 | 1.1717 | 6.0087 | 137.1642 | 7.771 | 144.9351 | 143.16 | 164.885 | 4.684 | 4.9597 | 4.4517 | 4.6442 | 2.6709 | 2.319 | 4.454 | 95.3206 | 41.3139 | 4.5692 | 8.3692 | 149.5729 | 8.5052 | 158.0781 | 158.6026 | 185.3865 | 4.4559 | 4.8423 | 4.3936 | 4.7813 | 3.4206 | 2.9264 | 4.7433 | 101.5416 | 43.3788 | 5.2912 | 9.9544 | 160.166 | 9.1146 | 169.2806 | 185.0907 | 213.8245 | 4.1732 | 4.5435 | 4.1315 | 4.4981 | 3.6963 | 3.1623 | 4.7682
| TED Chainpal | 346.8812 | 22.1233 | 4.1086 | 21.0691 | 394.1822 | 27.2382 | 421.4204 | 149.39 | 933.3 | 4.6766 | 5.8864 | 4.1583 | 5.7787 | 3.1663 | 0.50681 | 3.6934 | 334.2333 | 29.4308 | 16.0213 | 29.346 | 409.0314 | 29.8127 | 438.8442 | 165.5047 | 719.3267 | 4.1623 | 5.8359 | 4.105 | 5.8192 | 4.5194 | 1.0398 | 3.7554 | 356.0467 | 30.9017 | 18.553 | 34.9043 | 440.4056 | 31.9495 | 472.3552 | 194.7973 | 732.5498 | 3.8651 | 5.7244 | 3.8265 | 5.6671 | 5.0971 | 1.1727 | 3.7945
| Total | 2670.46 | 650.49 | 31.63 | 162.2 | 3514.78 | 209.76 | 3724.54 | 3810.52 | 6310.855 | 4.7427 | 5.3355 | 4.4758 | 5.1619 | 2.2158 | 1.3379 | 4.2401 | 2573.09 | 865.35 | 123.34 | 225.92 | 3787.7 | 229.58 | 4017.28 | 4221.56 | 6658.05 | 4.4801 | 5.0847 | 4.4209 | 5.0339 | 2.8772 | 1.8243 | 4.4655 | 2741.02 | 908.6 | 142.83 | 268.71 | 4061.16 | 246.03 | 4307.19 | 4713.66 | 7236.42 | 4.3854 | 4.9814 | 4.3415 | 4.9316 | 3.1271 | 1.9828 | 4.4944
| Note : | 1 | Total Divisional employees = Employees cost of the division plus proportionate allocation of Corporate and Circle office employees cost on the basis of divisional LT Inputs(MU).
|  | 2 | Total Divisional R&M Cost =R&M Cost of the division plus proportionate allocation of Corporate and Circle office R&M Cost on the basis of divisional LT Inputs(MU).
|  | 3 | Total Divisional A&G Cost= A&G Cost of the division plus proportionate allocation of Corporate and Circle office A&G Cost on the basis of divisional LT Inputs(MU).
|  | 4 | Divisional LT Inputs(MU) =Divisional total Input (MU) minus EHT Sale (MU) minus 8% HT Loss(MU) minus HT Sales(MU)
|  | 5 | Divisional other costs = Proportionate allocation of total cost of Depreciation , Interest , Return on Equity and other cost if any on the basis of total Divisional Inputs(MU)

## Annexure-Q
Miscellaneous Receipt & Revenue out go
Amount in Rs. Lac
Revenue out go due to TOD bebefit
Category of Consumer | FY18-19 | FY19-20
LT | 3.6644 | 2.3851
HT | 285.8883 | 164.9847
EHT | 444.5414 | 169.3117
TOTAL | 734.0942 | 336.6815
Revenue out go due to Improvement of Power Factor(NA)
Category of Consumer | FY18-19 | FY19-20
LT | 0.22635 | 0.12866
HT | 333.3272 | 184.3378
EHT | 73.6966 | 66.2073
TOTAL | 407.2501 | 250.6737
Revenue out go due to promt payment rebate
Category of Consumer | FY18-19 | FY19-20
LT | 1962.4119 | 1111.7891
HT | 780.2377 | 375.9872
EHT | 676.2458 | 304.2957
TOTAL | 3418.8954 | 1792.072
Revenue billed for imposition of power factor penalty
Category of Consumer | FY18-19 | FY19-20
LT | 0.049816 | 0.034024
HT | 587.3039 | 328.6414
EHT | 81.5857 | 384.0903
TOTAL | 668.9395 | 712.7657
Revenue billed for imposition of Over Drawal penalty
Category of Consumer | FY18-19 | FY19-20
LT | 3.5245 | 2.1149
HT | 348.7059 | 339.0143
EHT | 689.2945 | 291.4
TOTAL | 1041.5248 | 632.5291
Revenue billed for imposition of DPS
Category of Consumer | FY18-19 | FY19-20
LT | 3826.2148 | 1386.0943
HT | 941.1681 | 629.0609
EHT | 121.976 | 47.323
TOTAL | 4889.3589 | 2062.4782
Miscellaneous billed (Meter Rent)
Category of Consumer | FY18-19 | FY19-20
LT | 2134.2544 | 1052.0082
HT | 953.7827 | 490.0487
EHT | 1213.9989 | 549.4415
TOTAL | 4302.036 | 2091.4984
Reliability Surcharge Charged
Category of Consumer | FY18-19 | FY19-20
LT | 0 | 0
HT | 132.4753 | 66.481
EHT | 1209.3975 | 547.1235
TOTAL | 1341.8728 | 613.6045