## ANNEXURE IV
99.9797 |  | TRANSMISSION SYSTEM OUTAGE DATA
PERIOD : 2018-19
Sl. No. | Name of the Transmission Element | OUTAGE |  | RESTORATION |  | OUTAGE PERIOD | DURATION OF OUTAGE ATTRIBUTABLE TO | [5 empty] | Deemed Availability | Reason of Outage | MVA capacity for ICTs / Autos | Ckm and number of Sub-Conductor for lines | Time considered for availability (hrs) (365 X 24) | Element wise availbility (C19 - C7 - C8/60) / C19 | ( OH l x Cktkm l x NSC l ) ( OH t x MVA t x 2.5 ) | (THY x Ckt KM X NSC) (THY X MVA x 2.5)
|  | DATE | TIME | DATE | TIME |  | UTILITY ITSELF |  | OTHERS |  | System Constraints/Natural Calamities
|  | dd/mm/yy | hh:mm | dd/mm/yy | hh:mm | hh:mm | Hrs | Min | Hrs | Min | Hrs | Min
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
400KV LINES
1 | 400 kV Indravati - Indravati PG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.97 | 8760 | 100% | 0 | 69554.4
2 | 400kV Lapanga -IBTPS Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.491 | 3528 | 100% | 0 | 172808.496
|  | 14.03.19 | 13:39 | 15.03.19 | 16:46 | 27:07 | 0 | 0 | [5 empty] | At Lapanga-Bus bar protection(zone-1) operated.[Both Main CB and Tie CB tripped. D/P RELAY:- DIST FWD, Z3, DIST-42.5KM, IL1-13.591 KA , IL2-12.845 KA , IL3-93.925A.]. Generation was not there.
3 | 400kV Lapanga -IBTPS Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.491 | 3528 | 100% | 0 | 172808.496
|  | 14.03.19 | 13:39 | 15.03.19 | 16:46 | 27:07 | 0 | 0 | [5 empty] | At Lapanga- Both Main CB and Tie CB got tripped. D/P RELAY:- DIST FWD , Z1, DIST-0.9KM , IL1-36.116 KA , IL2-31.166 KA , IL3-44.200A. Also Busbar protection (Zone I) Operated. AT IBTPS- PUTT protection operated.( Permissive trip transfer trip means zone2 pickup plus carrier received. Generation was not there.
4 | 400kV Meramundali -New Duburi Ckt- I |  |  |  |  | 0.045833 | 1 | 6 | [7 empty] | 96.6 | 8760 | 99.99% | 212.52 | 1692432
|  | 26.02.19 | 17:25 | 26.02.19 | 18:31 | 1:06 | 1 | 6 | [5 empty] | At Meramundali-Tripped on DT (distance trip)signal from Mendhasal end. (Associated tie breaker(402 Dia) at Meramundali S/S didn’t trip due to mechanical problem in R-ph limb. Hence LBB of tie breaker (402 dia) operated) (LBB of Mendhasal feeder main beaker at Meramundali end operated) At New Duburi -R,Y, B ph pick up, DT received, M/T.
5 | 400kV Meramundali -New Duburi Ckt- II |  |  |  |  | 0.40417 | 21 | 27 | [7 empty] | 96.6 | 8760 | 99.76% | 4144.14 | 1692432
|  | 26.02.19 | 17:25 | 26.02.19 | 18:46 | 1:21 | 1 | 6 | [5 empty] | At Meramundali-Tripped on DT (distance trip)signal from Mendhasal end. (Associated tie breaker(402 Dia) at Meramundali S/S didn’t trip due to mechanical problem in R-ph limb. Hence LBB of tie breaker (402 dia) operated) (LBB of Mendhasal feeder main beaker at Meramundali end operated) At New Duburi -R,Y, B ph pick up, DT received, M/T.
|  | 12.03.19 | 14:38 | 12.03.19 | 17:42 | 3:04 | 3 | 4 | [5 empty] | Relay indication at Mrdl end:-B-E,zone-1,Dist-56.4 Km,fault current-7.2 Ka. At N.Duburi end:-B-E,Zone-1,Dist-72.1 km,Fault current-2.96 Ka.
|  | 13.03.19 | 11:18 | 13.03.19 | 16:35 | 5:17 | 5 | 17
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
6 | 400kV Meramundali -Lapanga-Vedant Ckt- I |  |  |  |  | 0.19583 | 0 | 0 | [7 empty] | 209 | 8760 | 100% | 0 | 3661680
|  | 26.02.19 | 17:25 | 26.02.19 | 18:27 | 1:02 | 0 | 0 | [5 empty] | At Meramundali-Tripped on DT (distance trip)signal from Mendhasal end. (Associated tie breaker(402 Dia) at Meramundali S/S didn’t trip due to mechanical problem in R-ph limb. Hence LBB of tie breaker (402 dia) operated). Power flow resumed through ckt-II. (LBB of Mendhasal feeder main beaker at Meramundali end operated) At New Duburi -R,Y, B ph pick up, DT received, M/T.
|  | 15.03.19 | 11:59 | 15.03.19 | 15:39 | 3:40 | 0 | 0 | [5 empty] | At Meramundali-Tripped on Y-N, DTT TRIPPED, Iy- 1.73 KA, DIST- 286.1 KM At Lapanga-Tripped on Bus Bar protection Central Unit of Bus II (Zone II) Operated.Power flow resumed through ckt-II.
7 | 400kV Meramundali -Lapanga-Vedant Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 209 | 8760 | 100% | 0 | 3661680
|  | 14.03.19 | 13:39 | 15.03.19 | 19:17 | 29:38 | 0 | 0 | [5 empty] | At Lapanga- Busbar protection (Zone I) Operated. On 15.03.19 at 11:59 hrs tripped at At Meramundali end on Yph-N, ZONE-2 , 214.1KM, Fault Current= 2.36KA.Power flow resumed through ckt-I.
8 | 400kV Meramundali -Mendhasal Ckt- I |  |  |  |  | 0.25903 | 16 | 27 | [7 empty] | 100.451 | 8760 | 99.81% | 3304.8379 | 1759901.52
|  | 03.02.19 | 4:26 | 03.02.19 | 5:01 | 0:24 | 0 | 24 | [5 empty] | AT Meramanduli-Master trip,3 ph pole trip, At Mendhasal:-Dt recive.
|  | 26.02.19 | 17:25 | 26.02.19 | 18:48 | 1:23 | 0 | 0 | [5 empty] | At Meramundali-Tripped on DT (distance trip)signal from Mendhasal end. (Associated tie breaker(402 Dia) at Meramundali S/S didn’t trip due to mechanical problem in R-ph limb. Hence LBB of tie breaker (402 dia) operated). Mendhasal availed power supply from Pandiabil. (LBB of Mendhasal feeder main beaker at Meramundali end operated) At New Duburi -R,Y, B ph pick up, DT received, M/T.
|  | 29.03.19 | 13:11 | 29.03.19 | 17:37 | 4:26 | 4 | 3 | [5 empty] | At Mendhasal-Tripped on D/P
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
9 | 400 kV Meramundali - JSPL Ckt- I |  |  |  |  | 0.049306 | 0 | 0 | [7 empty] | 37.916 | 8760 | 100% | 0 | 664288.32
|  | 26.02.19 | 17:25 | 26.02.19 | 18:36 | 1:11 | 0 | 0 | [5 empty] | At Meramundali-Tripped on DT (distance trip)signal from Mendhasal end. (Associated tie breaker(402 Dia) at Meramundali S/S didn’t trip due to mechanical problem in R-ph limb. Hence LBB of tie breaker (402 dia) operated)Power flow resumed through ckt-II. (LBB of Mendhasal feeder main beaker at Meramundali end operated) At New Duburi -R,Y, B ph pick up, DT received, M/T.
10 | 400 kV Meramundali - JSPL Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 37.916 | 8760 | 100% | 0 | 664288.32
11 | 400kV Rengali - Kuchei PG-Kolaghat |  |  |  |  | 0 | 0 | 0 | [7 empty] | 241.5 | 8760 | 100% | 0 | 4231080
1081.935
220KV LINES
12 | 220kV Atri-Pandiabil Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 25.2 | 8760 | 100% | 0 | 220752
13 | 220kV Pandiabil-Samagara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 47.4 | 8760 | 100% | 0 | 415224
14 | 220kV Atri-Pandiabil Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 25.2 | 8760 | 100% | 0 | 220752
15 | 220kV Pandiabil-Samagara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 47.4 | 8760 | 100% | 0 | 415224
16 | 220kV Balasore- Bhadrak |  |  |  |  | 0 | 0 | 0 | [7 empty] | 67.95 | 8760 | 100% | 0 | 595242
17 | 220kV Balimela-Jayanagar-I |  |  |  |  | 0.027083 | 5 | 52 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 92.072 | 8760 | 99.93% | 540.1557 | 806550.72
|  | 25.05.18 | 16:29 | 25.05.18 | 17:08 | 0:39 | 1 | 18 | [5 empty] | At Balimela-Tripped [Earthwire snapped from gantry tower to Loc. No.-1454 at Jayanagar end]
|  | 21.02.19 | 6:38 | 13.03.2019 | 20:16 | 493:38 | 4 | 34 | [5 empty] | At Balimela-Tripped 14PY, 7PY ( phase O/C), 10PY (short circuit) relay operated ,and cause tripping of all running units at Balimela. At jayanagar-Tripped on R-Y-Ground , Zone-2(106.9KM), IA-1.3A, IB-603A,IC-300A. (Due to bursting of (R-ph) CT of 220KV Jayanagar-Balimela ckt-I at Balimela PH End.)
18 | 220kV Balimela-Jayanagar-II |  |  |  |  | 0.13403 | 2 | 56 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 92.072 | 8760 | 99.97% | 270.0779 | 806550.72
|  | 25.05.18 | 16:30 | 25.05.18 | 17:45 | 1:15 | 1 | 18 | [5 empty] | At Jayanagar-'R'ph, Ý', 'B'ph. At Balimela-Tripped
|  | 21.02.19 | 6:38 | 21.02.19 | 8:16 | 1:38 | 1 | 38 | [5 empty] | At Jayanagar-Tripped on R-Y-B-Ground , Zone-2(97.62KM), IA-1.69A, IB-1.91A,IC-313A.
|  | 24.02.19 | 12:30 | 24.02.19 | 12:50 | 0:20 |  |  | 0 | 20 |  |  |  | At Jayanagar-Tripped on Y-ph, Zone-2, Dist.- 115.0.Fault current in IA= 450.1, IB=1.626KA, IC=370.5A with heavy jerk at S/Y with the tripping of only running unit #5 . At Balimela end:- 6PY, 7PY ( phase O/C), 17PY ( tripping ) relay operated (CT bust at Balimela PH)
19 | 220kV Balimela-Jayanagar-III |  |  |  |  | 0.34861 | 3 | 20 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 93.46 | 8760 | 99.96% | 311.5333 | 818709.6
|  | 25.05.18 | 16:30 | 25.05.18 | 17:10 | 0:40 | 1 | 18
|  | 21.02.19 | 6:38 | 21.02.19 | 8:40 | 2:02 | 2 | 2 | [5 empty] | At Jayanagar-Tripped on R-Y-B-Ground , Zone-2(100.5KM), IA-1.709KA, IB-1.85KA,IC-152.8A.
|  | 24.02.19 | 12:30 | 24.02.19 | 18:10 | 5:40 |  |  | 5 | 40 |  |  |  | At Jayanagar-Tripped on Y-ph, Zone-2, Dist.- 115.0.Fault current in IA= 450.1, IB=1.626KA, IC=370.5A with heavy jerk at S/Y with the tripping of only running unit #5 . At Balimela end:- 6PY, 7PY ( phase O/C), 17PY ( tripping ) relay operated (CT bust at Balimela PH)
20 | 220kV Balimela-Malkangiri |  |  |  |  | 0 | 0 | 0 | [5 empty] | At Balimela-Over Voltage |  | 22.41 | 8760 | 100% | 0 | 196311.6
21 | 220kV Balimela PH -Balimela |  |  |  |  | 0.40556 | 0 | 0 | [7 empty] | 0.2 | 8760 | 100% | 0 | 1752
|  | 07.02.19 | 9:45 | 07.02.19 | 10:11 | 0:26 |  |  | 0 | 26 |  |  |  | At BHEP-Tripped
|  | 08.02.19 | 10:58 | 08.02.19 | 11:57 | 0:59 |  |  | 0 | 59 |  |  |  | At BHEP-Tripped
|  | 21.02.19 | 6:36 | 21.02.19 | 8:53 | 2:17 |  |  | 2 | 17 |  |  |  | At BHEP-Tripped
|  | 24.02.19 | 12:30 | 24.02.19 | 18:32 | 6:02 |  |  | 6 | 2 |  |  |  | At Jayanagar-Tripped on Y-ph, Zone-2, Dist.- 115.0.Fault current in IA= 450.1, IB=1.626KA, IC=370.5A with heavy jerk at S/Y with the tripping of only running unit #5 . At Balimela end:- 6PY, 7PY ( phase O/C), 17PY ( tripping ) relay operated (CT bust at Balimela PH)
22 | 220kV Balimela PH -Upper Sileru |  |  |  |  | 0.25139 | 0 | 0 | [7 empty] | 24.76 | 8760 | 100% | 0 | 216897.6
|  | 24.02.19 | 12:30 | 24.02.19 | 18:32 | 6:02 |  |  | 6 | 2 |  |  |  | At Jayanagar-Tripped on Y-ph, Zone-2, Dist.- 115.0.Fault current in IA= 450.1, IB=1.626KA, IC=370.5A with heavy jerk at S/Y with the tripping of only running unit #5 . At Balimela end:- 6PY, 7PY ( phase O/C), 17PY ( tripping ) relay operated (CT bust at Balimela PH)
23 | 220kV Barkote-Bonai |  |  |  |  | 0.59306 | 0 | 0 | [7 empty] | 55.807 | 8760 | 100% | 0 | 488869.32
|  | 25.02.19 | 1:40 | 25.02.19 | 15:54 | 14:14 | 0 | 0 | [5 empty] | Tripped On D/P at Tarkera
24 | 220kV Bonai-Tarkera |  |  |  |  | 0 | 0 | 0 | [7 empty] | 47.467 | 8760 | 100% | 0 | 415810.92
25 | 220kV Bhanjanagar-Meramundali-I |  |  |  |  | 0.063194 | 12 | 9 | [7 empty] | 134.14 | 8760 | 99.86% | 1629.801 | 1175066.4
|  | 31.01.19 | 6:12 | 31.01.19 | 6:21 | 0:09 | 0 | 9 | [5 empty] | Sel 311C D/P Relay:Cgt=B-Phase To Earth Fault,Z=1,Location=78Km,Ic=1666 Amp. Rel 316 *4 D/P Relay: 2=Trip.5,6=B-Phase To Earth Fault.9= Zone-1.Distance=86.22Km.
|  | 16.02.19 | 2:35 | 16.02.19 | 3:11 | 0:36 | 0 | 0 | [5 empty] | Tripped
|  | 18.02.19 | 6:03 | 18.02.19 | 6:49 | 0:46 | 0 | 0 | [5 empty] | Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
26 | 220kV Bhanjanagar-Meramundali-II |  |  |  |  | 0.013889 | 0 | 0 | [7 empty] | 134.14 | 8760 | 100% | 0 | 1175066.4
|  | 06.02.19 | 13:34 | 06.02.19 | 13:54 | 0:20 | 0 | 0 | [5 empty] | SEL 311C D.P relay: CGT=B-phase to earth ault,Z=1,location=60.13Km, IC=1649 Amp. REL 316 *4 D.P relay: 2=trip.5,6=B-phase to earth fault.9= zone-1.Distance=69.71Km.
27 | 220kV Bhanjanagar-Mendhasal ckt |  |  |  |  | 0.0020833 | 0 | 0 | [7 empty] | 136.47 | 8760 | 100% | 0 | 1195477.2
|  | 18.02.19 | 12:44 | 18.02.19 | 12:47 | 0:03 | 0 | 0 | [5 empty] | Tripped on DP
28 | 220kV Bhanjanagar-Nayagarh ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 63 | 8760 | 100% | 0 | 551880
29 | 220kV Bidanasi -Mendhasal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
30 | 220kV Bidanasi -Mendhasal Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
31 | 220kV Bidanasi -Cuttack Ckt-I |  |  |  |  | 0.0034722 | 12 | 11 | [7 empty] | 9.3 | 8760 | 99.86% | 113.305 | 81468
|  | 03.01.19 | 13:49 | 03.01.19 | 13:52 | 0:03 | 0 | 3 | [5 empty] | At Cuttack-Tripped At Jagatsinghpur -Tripped
|  | 03.01.19 | 13:56 | 03.01.19 | 13:57 | 0:01 | 0 | 1
|  | 03.01.19 | 16:37 | 03.01.19 | 16:38 | 0:01 | 0 | 1
|  | 16.03.19 | 0.6 | 16.03.19 | 0.62014 | 00:29 | 0 | 6 | [5 empty] | At Bidanasi-Tripped. [tripped from Mendhasal end]P/S availed from 132KV Jagatsinghpur feeder at 14:30hrs.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
32 | 220kV Bidanasi -Cuttack Ckt-II |  |  |  |  | 0.0034722 | 12 | 11 | [7 empty] | 9.3 | 8760 | 99.86% | 113.305 | 81468
|  | 03.01.19 | 13:49 | 03.01.19 | 13:52 | 0:03 | 0 | 3 | [5 empty] | At Cuttack-Tripped At Jagatsinghpur -Tripped
|  | 03.01.19 | 13:56 | 03.01.19 | 13:57 | 0:01 | 0 | 1
|  | 03.01.19 | 16:37 | 03.01.19 | 16:38 | 0:01 | 0 | 1
|  | 16.03.19 | 0.6 | 16.03.19 | 0.62014 | 00:29 | 0 | 6 | [5 empty] | At Bidanasi-Tripped. [tripped from Mendhasal end]P/S availed from 132KV Jagatsinghpur feeder at 14:30hrs.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
33 | 220kV Bisra-Tarkera-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.335 | 8760 | 100% | 0 | 134334.6
34 | 220kV Budhipadar-Aditya Aluminium Ckt.-I |  |  |  |  | 0.15486 | 3 | 43 | [7 empty] | 20.507 | 8760 | 99.96% | 76.2177 | 179641.32
|  | 28.01.19 | 2:35 | 28.01.19 | 6:18 | 3:43 | 3 | 43 | [5 empty] | R Ph ,E/F,Zone-1,15.37 Km If=8.013 Ka,Iy-1.428 Ka,Iz-1.227 Ka
35 | 220kV Budhipadar-Aditya Aluminium Ckt.-II |  |  |  |  | 0.25278 | 3 | 43 | [5 empty] | At Budhipadar-LBB |  | 20.507 | 8760 | 99.96% | 76.2177 | 179641.32
|  | 28.01.19 | 5:42 | 28.01.19 | 11:46 | 6:04 | 3 | 43 | [5 empty] | B Ph-E,Dist-15.85 Km,Ir-2.339 Ka,
36 | 220kV Budhipadar-Basundhara Ckt-I |  |  |  |  | 0.048611 | 0 | 0 | [7 empty] | 35.29 | 8760 | 100% | 0 | 309140.4
|  | 20.05.18 | 18:50 | 20.05.18 | 20:00 | 1:10 | 0 | 0 | [5 empty] | At Budhipadar-D/P,Dist.-17 k.m. Power Supply resumed through ckt-II.
37 | 220kV Budhipadar-Basundhara Ckt-II |  |  |  |  | 0.045833 | 0 | 0 | [7 empty] | 35.29 | 8760 | 100% | 0 | 309140.4
|  | 22.05.18 | 15:18 | 22.05.18 | 16:24 | 1:06 | 0 | 0 | [5 empty] | At Budhipadar-'Y' ph, E/F, Dist.-18.5 k.m.Power supply resumed through ckt-I.
38 | 220kV Budhipadar-IbTPS -I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 100% | 0 | 227760
39 | 220kV Budhipadar-IbTPS -II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 100% | 0 | 227760
40 | 220kV Budhipadar-IbTPS -III |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 100% | 0 | 222328.8
41 | 220kV Budhipadar-IbTPS -IV |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 100% | 0 | 222328.8
42 | 220kV Budhipadar-Raigarh-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 60 | 8760 | 100% | 0 | 525600
43 | 220kV Budhipadar-Korba-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 60 | 8760 | 100% | 0 | 525600
44 | 220kV Budhipadar-Lapanga-I |  |  |  |  | 0.24167 | 0 | 0 | [7 empty] | 20 | 8760 | 100% | 0 | 175200
|  | 30.09.18 | 17:19 | 30.09.18 | 23:07 | 5:48 | 0 | 0 | [5 empty] | Lapanga availed power supply from Katapali end.
45 | 220kV Budhipadar-Lapanga-II |  |  |  |  | 0.24167 | 0 | 0 | [7 empty] | 20 | 8760 | 100% | 0 | 175200
|  | 30.09.18 | 17:19 | 30.09.18 | 23:07 | 5:48 | 0 | 0 | [5 empty] | Lapanga availed power supply from Katapali end.
46 | 220kV Budhipadar-SPS Feeder-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.424 | 8760 | 100% | 0 | 117594.24
47 | 220kV Budhipadar-SPS Feeder-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.424 | 8760 | 100% | 0 | 117594.24
48 | 220kV Budhipadar-Bhusan Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.92 | 8760 | 100% | 0 | 130699.2
49 | 220kV Budhipadar-Bhusan Ckt II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.92 | 8760 | 100% | 0 | 130699.2
50 | 220kV Chandaka -Mendhasal Ckt-I |  |  |  |  | 0.38125 | 0 | 31 | [7 empty] | 19 | 8760 | 99.99% | 9.8167 | 166440
|  | 13.05.18 | 3:36 | 13.05.18 | 12:45 | 9:09 | 0 | 31 | [5 empty] | At Chandaka-Master trip Bus bar protection. Power flow resumed through ckt-iV after 30 minutes.
51 | 220kV Chandaka- Mendhasal ckt II |  |  |  |  | 0.044444 | 0 | 33 | [7 empty] | 19.9 | 8760 | 99.99% | 10.945 | 174324
|  | 13.05.18 | 3:36 | 13.05.18 | 4:38 | 1:02 | 0 | 31 | [5 empty] | At Chandaka-Master trip Bus bar protection.Power flow resumed through ckt-iV after 30 minutes.
|  | 21.02.19 | 13:29 | 21.02.19 | 13:31 | 0:02 | 0 | 2 | [5 empty] | At Chandaka-Tripped on O/C,Relay pick up-R,Y, B phase,high speed relay tripped ,Y ph-1.8 KA, B ph-1.8 KA.
52 | 220kV Chandaka- Mendhasal ckt III |  |  |  |  | 0.020833 | 0 | 30 | [7 empty] | 19.9 | 8760 | 99.99% | 9.95 | 174324
|  | 13.05.18 | 3:36 | 13.05.18 | 4:06 | 0:30 | 0 | 30 | [5 empty] | At Chandaka-O/C, E/F, Bus bar protection.Power flow resumed through ckt-iV after 30 minutes.
53 | 220kV Chandaka- Chandaka-B |  |  |  |  | 0.13125 | 13 | 27 | [7 empty] | 0.1 | 8760 | 99.85% | 1.345 | 876
|  | 13.05.18 | 3:36 | 13.05.18 | 4:06 | 0:30 | 0 | 30 | [5 empty] | At Chandaka-O/C, E/F, Bus bar protection
|  | 10.10.18 | 11:52 | 10.10.18 | 12:03 | 0:11 | 0 | 9 | [5 empty] | At Chanadaka-Tripped on E/F
|  | 15.10.18 | 13:34 | 15.10.18 | 13:56 | 0:22 | 0 | 22 | [5 empty] | At Chandaka-Tripped
|  | 21.02.19 | 13:29 | 21.02.19 | 15:35 | 2:06 | 0 | 26 | [5 empty] | At Chandaka B-Tripped on Directional/overcurrent relay,E/F,R ph. -169.6 Amp,Yph-192.1 Amp ,B ph-584.8 Amp,Fault current-381.2 Amp.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
54 | 220kV Chandaka-B-Mendhasal ckt IV |  |  |  |  | 0 | 0 | 0 | [7 empty] | 18.96 | 8760 | 100% | 0 | 166089.6
55 | 220kV Duburi-Duburi (New) Ckt - I |  |  |  |  | 0.20833 | 0 | 7 | [7 empty] | 6.38 | 8760 | 100% | 0.74433 | 55888.8
|  | 03.02.19 | 14:35 | 03.02.19 | 19:35 | 5:00 | 0 | 7 | [5 empty] | CB Didn'T Close At Old Duburi Gss End As Old Duburi Tripped Due To Fault In 220 Kv New Duburi-Balasore Feeder
56 | 220kV Duburi-Duburi (New) Ckt - II |  |  |  |  | 0.23681 | 0 | 7 | [7 empty] | 6.38 | 8760 | 100% | 0.74433 | 55888.8
|  | 03.02.19 | 14:13 | 03.02.19 | 19:42 | 5:29 | 0 | 7 | [5 empty] | Directional IDMT over current relay(63 R),Directional IDMT over current relay (67 B),Master trip,Relay-86,Trip circuit Supervision Relay. Power Flow resumed through Meramundi Duburi ckt after 7 minutes.
|  | 22.02.19 | 10:46 | 22.02.19 | 10:58 | 0:12 | 0 | 0 | [5 empty] | For Attending Hot Spot At Line Isolator At Old Duburi End
57 | 220kV Duburi-NINL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6 | 8760 | 100% | 0 | 52560
58 | 220kV Indravati PH-Therubali-I (TVL) |  |  |  |  | 0.015972 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 100% | 0 | 755112
|  | 22.02.19 | 12:23 | 22.02.19 | 12:46 | 0:23 | 0 | 0 | [5 empty] | Zone-1,L1-N, 15.401Km, 86M2A,86M2B, 86M2C, 186A, 186B. Power flow resumed through alternate circuits.
59 | 220kV Indravati PH-Therubali-II |  |  |  |  | 0.014583 | 0 | 42 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 100% | 60.34 | 755112
|  | 17.03.19 | 16:47 | 17.03.19 | 17:08 | 0:21 | 0 | 42 | [5 empty] | CG-T,186A,186B
60 | 220kV Indravati PH-Therubali-III |  |  |  |  | 0.92708 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 91 | 8760 | 100% | 0 | 797160
|  | 21.03.19 | 18:21 | 22.03.19 | 16:36 | 22:15 | 0 | 0 | [5 empty] | At Theruvali-Tripped on BCT,Z-1,18.33KM [Due to B phaseJummper snapped]
61 | 220kV Indravati PH-Therubali-IV |  |  |  |  | 0.99514 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 91 | 8760 | 100% | 0 | 797160
|  | 20.03.19 | 18:25 | 20.03.19 | 17.03.19 | 0:18 | 0 | 0 | [5 empty] | BGT, Z-1,70.52KM. Power flow resumed through alternate circuits.
|  | 22.03.19 | 12:20 | 23.03.19 | 10:56 | 23:35 | 0 | 0 | [5 empty] | ¦At Indravati end:-DP relay display.Zone-1,B-N-3.6 kM, CGT,Z-2,80.52KM AT Theruvali End:-DP display,Zone-II, B-N,80.5 Km, Fault current:-2 kamp. Power flow resumed through alternate circuits.
62 | 220kV Jayanagar-Jeypore PG-I |  |  |  |  | 0.020833 | 0 | 30 | [7 empty] | 7.73 | 8760 | 99.99% | 3.865 | 67714.8
|  | 25.05.18 | 16:30 | 25.05.18 | 17:00 | 0:30 | 0 | 30 | [5 empty] | At Jeypore-Tripped
63 | 220kV Jayanagar-Jeypore PG-II |  |  |  |  | 0.023611 | 0 | 34 | [7 empty] | 7.73 | 8760 | 99.99% | 4.3803 | 67714.8
|  | 25.05.18 | 16:30 | 25.05.18 | 17:04 | 0:34 | 0 | 34 | [5 empty] | At Jeypore-Tripped
64 | 220kV Jayanagar-Laxmipur ckt-I |  |  |  |  | 0.15278 | 0 | 34 | [7 empty] | 65 | 8760 | 99.99% | 36.8333 | 569400
|  | 25.05.18 | 16:29 | 25.05.18 | 19:45 | 3:16 | 0 | 34 | [5 empty] | At Jayanagar-'R'ph, Zn.-I, Dist.-4.168 k.m. ['R'ph. LA burst at Jayanagar]
|  | 02.02.19 | 22:11 | 02.02.19 | 22:35 | 0:24 | 0 | 0 | [5 empty] | Tripped on Z-I, R-Ph, Dist-6.627KM, IA-9.250KA, IB-249.02A, IC-324.2A
65 | 220kV Jayanagar-Laxmipur ckt-II |  |  |  |  | 0.022917 | 0 | 33 | [7 empty] | 65 | 8760 | 99.99% | 35.75 | 569400
|  | 25.05.18 | 16:30 | 25.05.18 | 17:03 | 0:33 | 0 | 33 | [5 empty] | At Laxmipur-O/C in 'R'ph, 'Ý' ph, E/F, D/P, Dist.-21.4 k.m.
66 | 220kV Jindal-Jamsedpur DVC |  |  |  |  | 0.11111 | 1 | 49 | [7 empty] | 20.8 | 8760 | #REF! | 37.7867 | 182208
|  | 31.08.18 | 13:50 | 31.08.18 | 16:00 | 2:10 | 1 | 23 | [5 empty] | At Jamshedpur-Tripped
|  | 05.09.18 | 12:52 | 05.09.18 | 13:22 | 0:30 | 0 | 26 | [5 empty] | At JSPL-E/F
67 | 220kV Joda-RCPur PG |  |  |  |  | 1900-01-04 13:28 | 33 | 0 | [7 empty] | 15.5 | 8760 | 99.62% | 511.5 | 135780
|  | 28.11.18 | 5.54 | 28.11.18 | 9.22 | 3.28 | 3 | 28 | [5 empty] | fdr. tripped at both ends. At Joda end:- D.P, Zone-1, Dist = 28.038Km, L2-N, IL1=423.40A, IL2=3249.82A, IL3=209.74A, IN=3738.76A At RCPUR end:- D.P, Dist=102Km, Zone-1, Y-ph tripped, fault current magnitude IB=1.923KA Charging of fdr. delayed as C.B. Could not be closed either by remote or local mode. After rectification done by E&MR team, fdr charged & stood ok.
|  | 25.02.19 | 0:54 | 25.02.19 | 18:26 | 17:32 | 17 | 32 | [5 empty] | fdr. tripped at both ends. At Joda end:- D.P, Dist = -1.000Km, L2-N, IL1=315.95A, IL2=162.61A, IL3=311.37A, IN=417.17A B/U (O/C, E/F), IL1=0.05KA, IL2=1.31KA, IL3=0.05KA At RCPUR end:- D.P, Dist=82.13Km, O/C, E/F, fault current magnitude :- IA= 309.6A, IB=458.5A, IC= 314.0A A big tree has fallen over Y-Ph conductor between Loc-169 & 170, near KNPS raea.
|  | 21.02.19 | 13:32 | 21.02.19 | 13:57 | 0:25 | 0 | 0 | [5 empty] | At Joda end:- D.P, Dist = 83.503Km, L1-N, IL1=1117.65A, IL2=337.39A, IL3=443.32A, IN=1485.99A B/U (O/C, E/F), IL1=1.55KA, IL2=0.05KA, IL3=0.05KA At RCPUR end:- D.P, Zone-1, Dist=76.86Km, O/C, E/F, fault current magnitude :- IA= 1.542KA, IB=327.5A, IC= 414.4A
|  | 25.02.19 | 0:54 | 25.02.19 | 18:26 | 17:32 | 0 | 0 | [5 empty] | Fdr. tripped at both ends. At Joda end:- D.P, Dist = -1.000Km, L2-N, IL1=315.95A, IL2=162.61A, IL3=311.37A, IN=417.17A B/U (O/C, E/F), IL1=0.05KA, IL2=1.31KA, IL3=0.05KA At RCPUR end:- D.P, Dist=82.13Km, O/C, E/F, fault current magnitude :- IA= 309.6A, IB=458.5A, IC= 314.0A
|  | 26.03.19 | 8:15 | 27.03.19 | 3:31 | 19:16 |  |  | 19 | 16 |  |  |  | Fdr. tripped at both ends. At Joda end:- D.P, Dist = 209.78Km, L1-L2, Zone-2, IL1=65.17A, IL2=1199.53A, IL3=825.97A, IN=460.37A At RCPUR end:- D.P, Zone-1, Master trip, O/C, fault current magnitude :- IA= 104.2A, IB=5.823KA, IC= 820.7A (Y ph CT busted at Ramachandarapur end.)
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
68 | 220kV Joda-Jindal |  |  |  |  | 0.018056 | 0 | 26 | [7 empty] | 21 | 8760 | 100% | 9.1 | 183960
|  | 05.09.18 | 12:52 | 05.09.18 | 13:18 | 0:26 | 0 | 26 | [5 empty] | At Joda-O/C
69 | 220kV Joda-TSIL Ckt. |  |  |  |  | 0.0125 | 0 | 18 | [7 empty] | 7.3 | 8760 | 100% | 2.19 | 63948
|  | 20.09.18 | 8:09 | 20.09.18 | 8:27 | 0:18 | 0 | 18 | [5 empty] | At Joda-D/P O/C
70 | 220kV Katapalli- HINDALCO Ckt-I |  |  |  |  | 0.026389 | 0 | 38 | [7 empty] | 10 | 8760 | #REF! | 6.3333 | 87600
|  | 07.01.19 | 15:40 | 07.01.19 | 16:18 | 0:38 | 0 | 38 | [5 empty] | At Katapali-Tripped on Dp Relay.Main I & Ii ,Dp Zone-1 ,Dist-746.5 Mtr,Ili=2.609Ka,Il2=3.09 Ka,Il3=438.5Amp,Fault Duration80 Msec( R-Ph Jumper Snapped At Loc No-4 Of 220 Kv Of Ckt And Fallen On Y-Ph.220 Kv New Bargarh ,)
71 | 220kV Katapalli- HINDALCO Ckt-II |  |  |  |  | 0.026389 | 0 | 38 | [7 empty] | 10 | 8760 | 99.99% | 6.3333 | 87600
|  | 07.01.19 | 15:40 | 07.01.19 | 16:18 | 0:38 | 0 | 38 | [5 empty] | At Katapali-Tripped on Dp Relay.Main I & Ii ,Dp Zone-1 ,Dist-746.5 Mtr,Ili=2.609Ka,Il2=3.09 Ka,Il3=438.5Amp,Fault Duration80 Msec( R-Ph Jumper Snapped At Loc No-4 Of 220 Kv Of Ckt And Fallen On Y-Ph.220 Kv New Bargarh ,)
72 | 220kV Katapalli- Bargarh New Ckt-I |  |  |  |  | 0.0097222 | 1 | 31 | [7 empty] | 52.035 | 8760 | 100% | 78.9197 | 455826.6
|  | 05.01.19 | 10:52 | 05.01.19 | 11:06 | 0:14 | 0 | 14 | [5 empty] | bus bar protection.220 Kv Balangir(New)-Bolangir PG feeder was already in shutdown for annual maintaince
|  | 07.01.19 | 15:55 | 07.01.19 | 17:37 | 1:42 | 1 | 17 | [5 empty] | H/T
73 | 220kV Bargarh New- New Bolangir Ckt-I |  |  |  |  | 0.0097222 | 0 | 14 | [7 empty] | 65.885 | 8760 | 99.98% | 15.3732 | 577152.6
|  | 05.01.19 | 10:52 | 05.01.19 | 11:06 | 0:14 | 0 | 14 | [5 empty] | bus bar protection.220 Kv Balangir(New)-Bolangir PG feeder was already in shutdown for annual maintaince
74 | 220kV Katapalli- Bolangir PG |  |  |  |  | 0.94028 | 0 | 15 | [7 empty] | 118.45 | 8280 | 100% | 29.6125 | 980766
|  | 07.01.19 | 15:40 | 08.01.19 | 14:14 | 22:34 | 0 | 15 | [5 empty] | DP Relay.Main I & II ,DP zone-1 ,Dist-746.5 mtr,ILI=2.609KA,IL2=3.09 KA,IL3=438.5Amp,Fault duration80 msec. R-ph Jumper snapped at Loc No-4 of 220 Kv of ckt and fallen on y-ph.220 Kv new bargarh ,
75 | 220kV Bolangir PG- Bolangir Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8280 | 100% | 0 | 24840
76 | 220kV Kuchei PG-Balasore Ckt I |  |  |  |  | 0.084028 | 0 | 0 | [7 empty] | 76.859 | 8760 | 100% | 0 | 673284.84
|  | 27.02.19 | 12:15 | 27.02.19 | 14:16 | 2:01 | 0 | 0 | [5 empty] | At Balasore end :- DP zone -1, Yph -E/F, 21.814 KM, If - 3.49 KA At Baripada(PG ) end : zone -1, Yph E/F, 3 KA, Dist - 45 KM
77 | 220kV Kuchei PG-Balasore Ckt-II |  |  |  |  | 0.44097 | 10 | 35 | [7 empty] | 76.859 | 8760 | 99.88% | 813.4244 | 673284.84
|  | 02.03.19 | 5:23 | 02.03.19 | 15:58 | 10:35 | 10 | 35 | [5 empty] | At Balasore-Tripped on O/C , E/F( B phase). [Due to snapping of R ph and Y ph Jumper of said fdr.]
78 | 220kV Lapanga-Katapali-I |  |  |  |  | 0.010417 | 0 | 15 | [7 empty] | 49.72 | 8760 | 100% | 12.43 | 435547.2
|  | 07.01.19 | 15:40 | 07.01.19 | 15:55 | 0:15 | 0 | 15
79 | 220kV Lapanga-Katapali-II |  |  |  |  | 0.010417 | 0 | 15 | [7 empty] | 49.72 | 8760 | 100% | 12.43 | 435547.2
|  | 07.01.19 | 15:40 | 07.01.19 | 15:55 | 0:15 | 0 | 15
80 | 220kV Laxmipur - Therubali ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 56 | 8760 | 100% | 0 | 490560
81 | 220kV Laxmipur - Therubali ckt-II |  |  |  |  | 0.030556 | 0 | 0 | [7 empty] | 56 | 8760 | 100% | 0 | 490560
|  | 08.02.19 | 14:53 | 08.02.19 | 15:37 | 0:44 | 0 | 0 | [5 empty] | Zone-1, C-G, 3.74Km
82 | 220kV Laxmipur - Utkal Alumina ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.04 | 8760 | 100% | 0 | 271910.4
83 | 220kV Laxmipur - Utkal Alumina ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.04 | 8760 | 100% | 0 | 271910.4
84 | 220kV Mendhasala-Godi Sahi-Bidanasi-II |  |  |  |  | 0.65556 | 0 | 4 | [7 empty] | 32.991 | 8760 | 100% | 2.1994 | 289001.16
|  | 23.01.19 | 2:10 | 23.01.19 | 17:54 | 15:44 | 0 | 4 | [5 empty] | At Mendhasala End-Dp Zone,-I Y Ph-E.12.13 Ka Distance-3.8 Km
85 | 220kV Meramundali-Godi sahi-Bidanasi-II |  |  |  |  | 0.0048611 | 0 | 7 | [7 empty] | 90.942 | 8760 | 100% | 10.6099 | 796651.92
|  | 19.12.18 | 17:05 | 19.12.18 | 17:12 | 0:07 | 0 | 7 | [5 empty] | Tripped on Back-UP due to spraking at R-phase C-Isolator
86 | 220kV Meramundali-Bhusan Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
87 | 220kV Meramundali-Bhusan Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
88 | 220kV Meramundali-Duburi-I |  |  |  |  | 0.021528 | 0 | 7 | [7 empty] | 95.556 | 8760 | 100% | 11.1482 | 837070.56
|  | 03.02.19 | 14:13 | 03.02.19 | 14:23 | 0:13 | 0 | 7 | [5 empty] | At Meramanduli end-Group A, Group b single phase Trip Relay,O/C Trip,E/f Trip Main 2 Protection,O/C Trip,I>2,Fqault Time-2 s.
|  | 27.02.19 | 15:33 | 27.02.19 | 15:51 | 0:18 | 0 | 0 | [5 empty] | Differential Protection
89 | 220kV Meramundali-Duburi-II |  |  |  |  | 0.0090278 | 0 | 7 | [7 empty] | 95.556 | 8760 | 100% | 11.1482 | 837070.56
|  | 03.02.19 | 14:13 | 03.02.19 | 14:23 | 0:13 | 0 | 7 | [5 empty] | At Meramanduli end-Group A, Group b single phase Trip Relay,O/C Trip,E/f Trip Main 2 Protection,O/C Trip,I>2,Fqault Time-2 s.
90 | 220kV NALCO-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
91 | 220kV NALCO-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
92 | 220kV Nayagarh-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 68.58 | 8760 | 100% | 0 | 600760.8
93 | 220kV Narendrapur-Atri Ckt-I |  |  |  |  | 0.50208 | 0 | 0 | [7 empty] | 150.35 | 8760 | 100% | 0 | 1317066
|  | 11.10.18 | 4:44 | 11.10.18 | 16:47 | 12:03 |  |  |  |  | 12 | 3 |  | At Narendrapur end-Tripped with main-I & II protection operated, M/R operated and DP relay showing Zone-I, C-G, Dist-60.34KM. At atri end C-G, Zone-I, Dist-105KM.,
94 | 220kV Atri-Mendhasal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.85 | 8760 | 100% | 0 | 217686
95 | 220kV Narendrapur-Atril Ckt-II |  |  |  |  | 0.0069444 | 0 | 35 | [7 empty] | 150.35 | 8760 | 99.99% | 87.7042 | 1317066
|  | 21.02.19 | 13:36 | 21.02.19 | 13:46 | 0:10 | 0 | 10 | [5 empty] | Directional O/C fault
|  | 01.03.19 | 14:42 | 01.03.19 | 15:07 | 00:25 | 0 | 25 | [5 empty] | At Atri end:-DT operated,Master Trip.
96 | 220kV Atri-Infocity-II Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 21.3 | 8760 | 100% | 0 | 186588
97 | 220kV Infocity-II-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.47 | 8760 | 100% | 0 | 47917.2
98 | 220kV New Duburi -Balasore |  |  |  |  | 0.27361 | 0 | 7 | [7 empty] | 140.97 | 8760 | 100% | 16.4465 | 1234897.2
|  | 03.02.19 | 14:15 | 03.02.19 | 19:03 | 4:48 | 0 | 7 | [5 empty] | AT Balasore - Bph ,E/F ,Zone 1, Il3=2.5Ka,Dist-70.9Km PU Time=16109 ms,Dist=70.9 KM,IL3=2.5 Ka,General trip,E/F,B Phase,Zone -1,86.1 & 86.2 optd. AT NEW DUBURI : FAULT MAGNITUDE: 2.5KA FAULT DISTANCE: 70KM
|  | 26.02.19 | 20:13 | 26.02.19 | 21:59 | 1:46 | 0 | 0 | [5 empty] | R-Phase Earth Fault
99 | 220kV New Duburi New-Bhadrakh |  |  |  |  | 0.20903 | 17 | 1 | [7 empty] | 76.22 | 8760 | 99.81% | 1297.0103 | 667687.2
|  | 20.03.19 | 15:54 | 20.03.19 | 16:13 | 0:19 | 0 | 19 | [5 empty] | At Bhadrak-Tripped
|  |  | 16:14 |  | 20:35 | 4:21 | 4 | 21
|  |  | 20:39 |  | 21:00 | 0:21 | 0 | 21
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
100 | 220kV New Duburi-Paradeep Ckt-I |  |  |  |  | 0.74236 | 14 | 6 | [7 empty] | 113.433 | 8760 | 99.84% | 1599.4053 | 993673.08
|  | 07.04.18 | 0:22 | 07.04.18 | 8:42 | 8:20 | 0 | 15 | [5 empty] | At New Duburi-'R'ph. To E/F, Zn.-I, Dist.-98.6 k.m. [Line patrolling was done but no fault found] Power flow resumed through ckt-II after 15 minutes.
|  | 19.10.18 | 12:41 | 19.10.18 | 13:24 | 0:43 | 0 | 43 | [5 empty] | CKT-I-O/C,E/F,B-G,D=-1.3KM,Z-4,CKT-II-O/C,E/F,B-G,Z-4,D=-1.3KM (MAIN BUS-I CONDUCTOR SNAPPED AT Y-PH BUS COUPLER SECTION TO 50MVA,INSULATOR & HARDWARE FITTING PUNCTURE)
|  | 22.01.19 | 3:04 | 22.01.19 | 3:42 | 0:38 | 0 | 6 | [5 empty] | At New Duburi-DP Relay Operated At Both Ends ,Zone-II,B Ph -E/F,Fault Current-2.03 Ka.Distance-99.7 Km. At Paradeep-TRIPPED ON E/F,C-N,D-14.8KM,Z-1 (DUE TO SEVERE FOG) At Kendrapara-Trip On E/F With M/R
|  | 22.01.19 | 3:45 | 22.01.19 | 11:02 | 7:17 | 0 | 12
|  | 25.01.19 | 10:48 | 25.01.19 | 11:13 | 0:25 | 0 | 24 | [5 empty] | At Paradeep-220KV MAIN BUS-I B-PH BUS CONDUCTOR(SECTION) AFTER(ESSAR-II&50MVA) SNAPPED DUE TO PUNCTURE OF INSULATOR & PULL OUT THE WHOLE SYSTEM At Kendrapara-Trip On E/F With M/R
|  | 27.02.19 | 1:42 | 27.02.19 | 1:51 | 0:09 | 0 | 9 | [5 empty] | At New Duburi-Tripped onDP relay,R ph E/F,Zone-I,21.9 Km,If-7 KA At Paradeep-Tripped
|  | 27.02.19 | 1:56 | 27.02.19 | 2:08 | 0:12 | 0 | 12 | [5 empty] | At Paradeep-Tripped
|  | 27.02.19 | 2:35 | 27.02.19 | 2:40 | 0:05 | 0 | 5 | [5 empty] | At Paradeep-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
101 | 220kV New Duburi-Paradeep Ckt-II |  |  |  |  | 0.075694 | 13 | 48 | [7 empty] | 113.433 | 8760 | 99.84% | 1565.3754 | 993673.08
|  | 07.04.18 | 0:22 | 07.04.18 | 0:37 | 0:15 | 0 | 15 | [5 empty] | At Paradeep-Tripped
|  | 19.10.18 | 12:41 | 19.10.18 | 13:24 | 0:43 | 0 | 43 | [5 empty] | CKT-I-O/C,E/F,B-G,D=-1.3KM,Z-4,CKT-II-O/C,E/F,B-G,Z-4,D=-1.3KM (MAIN BUS-I CONDUCTOR SNAPPED AT Y-PH BUS COUPLER SECTION TO 50MVA,INSULATOR & HARDWARE FITTING PUNCTURE)
|  | 25.01.19 | 10:48 | 25.01.19 | 11:13 | 0:25 | 0 | 24 | [5 empty] | At Paradeep-220KV MAIN BUS-I B-PH BUS CONDUCTOR(SECTION) AFTER(ESSAR-II&50MVA) SNAPPED DUE TO PUNCTURE OF INSULATOR & PULL OUT THE WHOLE SYSTEM At Kendrapara-Trip On E/F With M/R
|  | 27.02.19 | 1:42 | 27.02.19 | 1:51 | 0:09 | 0 | 9 | [5 empty] | At Paradeep-Tripped
|  | 27.02.19 | 1:56 | 27.02.19 | 2:08 | 0:12 | 0 | 12 | [5 empty] | At Paradeep-Tripped
|  | 27.02.19 | 2:35 | 27.02.19 | 2:40 | 0:05 | 0 | 5 | [5 empty] | At New Duburi-Tripped due to Unbalanced Current At Paradeep-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
102 | 220kV Paradeep - IOCL Ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6 | 8760 | 100% | 0 | 52560
103 | 220kV Paradeep - ESSAR Steel Ckt -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.868 | 8760 | 100% | 0 | 77683.68
104 | 220kV Paradeep - ESSAR Steel Ckt -II |  |  |  |  | 0.10903 | 2 | 21 | [7 empty] | 8.868 | 8760 | 99.97% | 20.8398 | 77683.68
|  | 20.09.18 | 10:23 | 20.09.18 | 13:00 | 2:37 | 2 | 21
|  | 19.10.18 | 12:41 | 19.10.18 | 14:25 | 1:44 | 0 | 0 | [5 empty] | Tripped On o/c
105 | 220kV Rengali PH-Nalco-TTPS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 71.337 | 8760 | 100% | 0 | 624912.12
106 | 220kV Rengali GD-Rengali PG -I |  |  |  |  | 0.080556 | 0 | 0 | [7 empty] | 0.4 | 8760 | 100% | 0 | 3504
|  | 24.02.19 | 1:44 | 24.02.19 | 3:40 | 1:56 | 0 | 0 | [5 empty] | NUMERICAL B/U RELAY OPERATED,IA=152.6A,IB=116.3A,IC=1148.1A,IN=0.00A, IG=1406.69A
107 | 220kV Rengali GD-Rengali PG -II |  |  |  |  | 0.0083333 | 0 | 12 | [7 empty] | 0.4 | 8760 | 100% | 0.08 | 3504
|  | 17.03.19 | 15:49 | 17.03.19 | 16:01 | 0:12 | 0 | 12 | [5 empty] | Pilot Wire Protection Relay Operated
108 | 220kV Rengali GD-Chandiposh (T)-Tarkera |  |  |  |  | 0.35208 | 19 | 6 | [7 empty] | 162.08 | 8760 | 99.78% | 3095.728 | 1419820.8
|  | 25.02.19 | 1:44 | 25.02.19 | 3:05 | 1:21 | 0 | 0 | [5 empty] | Tripped at Tarkera
|  | 15.03.19 | 19:39 | 15.03.19 | 19:53 | 0:14 | 0 | 14 | [5 empty] | DP Relay Operated,Z3 Start,Fault Abs Dist=130.13Km , Fault Real Dist=97.11%,Loop=L1-N,Il1=3565.77A,In=3672.43A
|  | 17.03.19 | 15:49 | 17.03.19 | 22:41 | 6:52 | 6 | 52 | [5 empty] | Numerical B/U Relay Operated,Ia=55.8A,Ib=2330.8A,Ic=2297.1A,In=1150.84A, Ig=1396.97A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
109 | 220kV Rengali GD-Barkote |  |  |  |  | 0.076389 | 0 | 0 | [7 empty] | 47.884 | 8760 | 100% | 0 | 419463.84
|  | 24.02.19 | 1:44 | 24.02.19 | 3:34 | 1:50 | 0 | 0 | [5 empty] | DP RELAY OPERATED,VA=1.02VN,VB=1.02VN,VC=0.82VN,IA=0.24IN,IB=0.24IN,IC=3.10IN
110 | 220kV Rengali PH-Rengali GD -I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
111 | 220kV Rengali PH-Rengali GD -II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
112 | 220kV Rengali PH -STPS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.5 | 8760 | 100% | 0 | 258420
113 | 220kV STPS (Kaniha)-TTPS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.5 | 8760 | 100% | 0 | 302220
114 | 220kV STPS-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
115 | 220kV STPS-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
116 | 220kV Tarkera-Budhipadar-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 109 | 8760 | 100% | 0 | 954840
117 | 220kV Tarkera-Budhipadar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 109 | 8760 | 100% | 0 | 954840
118 | 220kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
119 | 220kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
120 | 220kV Therubali-Narendrapur-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 196 | 8760 | 100% | 0 | 1716960
|  | 28.03.19 | 13:37 | 29.03.19 | 20:01 | 30:24 |  |  | 30 | 24 |  |  |  | AGT ,Zone-1,Reference-152.46 km,Fault current-107.5 amp [R phase CT bust at Narendrapur end.]
121 | 220kV Therubali-Narendrapur-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 196 | 8760 | 100% | 0 | 1716960
|  | 11.10.18 | 2:15 | 11.10.18 | 14:07 | 11:52 |  |  |  |  | 8 | 32 |  | At Narendrapur-Tripped with M/R operated. Facia showing Main- II protetion operated, Trip ckt I & II faulty.(Due to Cyclonic strom Titli)
122 | 220kV Therubali-Bhanjanagar-I |  |  |  |  | 0.019444 | 0 | 28 | [7 empty] | 171.46 | 8760 | 99.99% | 80.0147 | 1501989.6
|  | 31.03.19 | 20:14 | 31.03.19 | 20:38 | 0:28 | 0 | 28 | [5 empty] | CGT,Z=1,D=90.83Km.
123 | 220kV Therubali-Bhanjanagar-II |  |  |  |  | 0.029167 | 0 | 0 | [7 empty] | 171.46 | 8760 | 100% | 0 | 1501989.6
|  | 08.02.19 | 14:53 | 08.02.19 | 15:35 | 0:42 | 0 | 0 | [5 empty] | Tripped on Zone-1,C-N (Due to Snapping of B- Phase jumper of 220KV Therubali-Laxmipur ckt-2 connecting Tie CT to Isolator.)
124 | 220kV TTPS-Meramundali-I |  |  |  |  | 0.021528 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
|  | 24.03.19 | 14:19 | 24.03.19 | 14:50 | 0:31 |  |  | 0 | 31 |  |  |  | At Meramanduli end:-DP display,Zone-II,b-N,Distance-12.33 km. Fault current-10.35 kA.
125 | 220kV TTPS-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
126 | 220kV TTPS-Joda-I |  |  |  |  | 0.0875 | 2 | 46 | [7 empty] | 154 | 8760 | 99.97% | 426.0667 | 1349040
|  | 31.08.18 | 13:43 | 31.08.18 | 15:08 | 1:25 | 2 | 46 | [5 empty] | At both ends-D/P
|  | 15.03.19 | 18:22 | 15.03.19 | 19:03 | 0:41 | 0 | 0 | [5 empty] | At JODA end-D.P. Relay, Faultloop=L3_L1, Distance=142.31Km, Zone-2, IL1=1492.75A, IL2=177.19A, IL3=1512.55A,IN=1077.67A, B/U (E/F) (IA=1.416KA,IB=126.7A,IC=1.456KA, IN=1.00KA). At TTPS-1 end=D.P relay,Fault loop=L3_L1, IL1=5KA,IL3=8KA, Distance=31.73 Km. Power fllow resumed through ckt-II.
127 | 220kV TTPS-Joda-II |  |  |  |  | 0.057639 | 2 | 46 | [7 empty] | 154 | 8760 | 99.97% | 426.0667 | 1349040
|  | 31.08.18 | 13:43 | 31.08.18 | 15:06 | 1:23 | 2 | 46 | [5 empty] | At both ends-D/P
128 | 220kV U. Kolab-Jayanagar-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
129 | 220kV U. Kolab-Jayanagar-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
130 | 220kV U. Kolab-Therubali-Jayanagar Ckt-III |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 128 | 8760 | 100% | 0 | 1121280
6067.651
132 KV
131 | 132kV Akhusing-Mohana |  |  |  |  | 0.0090278 | 13 | 41 | [7 empty] | 70 | 8760 | 99.84% | 957.8333 | 613200
|  | 10.10.18 | 12:36 | 10.10.18 | 12:49 | 0:13 | 0 | 13 | [5 empty] | At Mohana-Tripped
|  | 11.10.18 | 7:07 | 12.10.18 | 15:22 | 32:15 |  |  |  |  | 32 | 15 |  | AT Akhusingh-Tripped on E/F (Due to Cyclonic strom Titli.)
|  | 21.02.19 | 18:30 | 21.02.19 | 18:39 | 0:09 | 0 | 9 | [5 empty] | Tripped due to M/R relay operated.
|  | 22.02.19 | 5:37 | 22.02.19 | 5:46 | 0:09 | 0 | 9 | [5 empty] | Tripped a Berhampur
|  | 23.02.19 | 13:47 | 23.02.19 | 13:50 | 0:03 | 0 | 3 | [5 empty] | Tripped at Akhusingh
|  | 23.02.19 | 16:16 | 23.02.19 | 17:04 | 0:48 | 0 | 48 | [5 empty] | Tripped
|  | 26.02.19 | 11:25 | 26.02.19 | 11:41 | 0:16 | 0 | 16 | [5 empty] | Tripped at Akhusingh
|  | 26.02.19 | 19:11 | 26.02.19 | 19:14 | 0:03 | 0 | 3 | [5 empty] | Tripped at Akhusingh
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
132 | 132kV Akhusing-Parlakhemundi |  |  |  |  | 0 | 20 | 49 | [7 empty] | 76.9 | 8760 | 99.76% | 1600.8017 | 673644
|  | 11.10.18 | 9:17 | 12.10.18 | 15:39 | 30:22 |  |  |  |  | 30 | 22 |  | AT Akhusingh-Tripped on E/F (Due to Cyclonic strom Titli.)
|  | 23.10.18 | 12:13 | 23.10.18 | 20:34 | 8:21 | 8 | 21 | [5 empty] | At Akhusingh-Tripped (Jumper snapped)
|  | 20.03.19 | 19:42 | 20.03.19 | 20:10 | 0:28 | 0 | 28 | [5 empty] | I/C BKR Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
133 | 132kV Angul-Boinda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 38.5 | 8760 | 100% | 0 | 337260
134 | 132kV Angul-Nandira (MCL)- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.826 | 8760 | 100% | 0 | 94835.76
135 | 132kV Angul-Nandira (MCL)- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.826 | 8760 | 100% | 0 | 94835.76
136 | 132kV Arya Iron - BRPL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.008 | 8760 | 100% | 0 | 78910.08
137 | 132kV Arya Steel - Nalda(T) |  |  |  |  | 0.0125 | 0 | 18 | [7 empty] | 15.26 | 8760 | 100% | 4.578 | 133677.6
|  | 07.04.18 | 17:58 | 07.04.18 | 18:16 | 0:18 | 0 | 18 | [5 empty] | At Joda-'R'ph. to E/F
138 | 132 kV Aska-Aska New -Chatrapur-I |  |  |  |  | 0.010417 | 0 | 15 | [7 empty] | 56.25 | 8760 | 100% | 14.0625 | 492750
|  | 15.11.18 | 11:07 | 15.11.18 | 11:22 | 0:15 | 0 | 15 | [5 empty] | Tripped due to Chatrapur Grid reserve bus Y- phase disc insulator brust. At Purushottampur-Distance Relay indication,Distance Loop-L1-2,Distance-17.1Km
|  | 18.02.19 | 18:36 | 25.02.19 | 18:08 | 167:28 | 0 | 0 | [5 empty] | RYB ZONE-1, 132KV SIDE- MASTER RELAY,R PHASE CT BLASTED
139 | 132 kV Aska-Purusottampur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.61 | 8760 | 100% | 0 | 250623.6
140 | 132kV Atri - Argul Ckt-I |  |  |  |  | 0.0083333 | 0 | 12 | [7 empty] | 19.4 | 8760 | 100% | 3.88 | 169944
|  | 06.12.18 | 16:40 | 06.12.18 | 16:52 | 0:12 | 0 | 12 | [5 empty] | At Argul-Fault trip
141 | 132kV Atri - Argul Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.4 | 8760 | 100% | 0 | 169944
142 | 132kV Atri - Banki |  |  |  |  | 0.0034722 | 12 | 28 | [7 empty] | 20.9 | 8760 | 99.86% | 260.5533 | 183084
|  | 03.10.18 | 11:40 | 03.10.18 | 11:45 | 0:05 | 0 | 5 | [5 empty] | Tripped on LBB
|  | 10.10.18 | 11:40 | 10.10.18 | 11:45 | 0:05 | 0 | 5 | [5 empty] | LBB
|  | 25.10.18 | 2:57 | 25.10.18 | 3:15 | 0:18 | 0 | 18 | [5 empty] | At Banki-Tripped on 86B relay faulty
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
143 | 132 kV Badagada-Nimapara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 36.87 | 8760 | 100% | 0 | 322981.2
144 | 132 kV Balasore-Betanati-Udala-Baripada |  |  |  |  | 0.013889 | 0 | 20 | [7 empty] | 146.808 | 8760 | 100% | 48.936 | 1286038.08
|  | 26.02.19 | 1:26 | 26.02.19 | 1:46 | 0:20 | 0 | 20 | [5 empty] | AT Balasore-Fault Distance:Ia=30 A Ib-4532 A ,Ic-4515 A Distance=14.88 KmTripped on O/C(Distance protection operated)
145 | 132 kV Balasore-Balasore (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.565 | 8760 | 100% | 0 | 31229.4
146 | 132 kV Balasore-Basta |  |  |  |  | 0.065278 | 0 | 34 | [7 empty] | 32.91 | 8760 | 99.99% | 18.649 | 288291.6
|  | 04.01.19 | 3:04 | 04.01.19 | 4:38 | 1:34 | 0 | 34 | [5 empty] | At Balasore- Tripped On D/P Zone-1 With Fault Location 18.23 Km From Bls Grid Endwith Fault Current 4143 Amp. At Basta-Tripped.
147 | 132 kV Balasore-Ispat Alloy |  |  |  |  | 0.10764 | 14 | 35 | [7 empty] | 6.45 | 8760 | 99.83% | 94.0625 | 56502
|  | 19.12.18 | 13:01 | 19.12.18 | 13:17 | 0:16 | 0 | 16 | [5 empty] | TRIPPED ON B-PH O/C
|  | 27.01.19 | 15:45 | 27.01.19 | 16:05 | 0:20 | 0 | 20 | [5 empty] | At Balesore End-E/F,Started Phase-Bcn,
|  | 02.02.19 | 6:45 | 02.02.19 | 7:13 | 0:28 | 0 | 28 | [5 empty] | Tripped On E/F & O/C
|  | 02.02.19 | 7:15 | 02.02.19 | 8:07 | 0:52 | 0 | 52 | [5 empty] | Tripped On E/F
|  | 18.02.19 | 17:48 | 18.02.19 | 18:27 | 0:39 | 0 | 39 | [5 empty] | Tripped On E/F & O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
148 | 132 kV Balasore-Birla Tyre |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.598 | 8760 | 100% | 0 | 22758.48
149 | 132 kV Balasore-Soro |  |  |  |  | 0.055556 | 0 | 19 | [7 empty] | 29.995 | 8760 | 100% | 9.4984 | 262756.2
|  | 10.04.18 | 16:01 | 10.04.18 | 17:21 | 1:20 | 0 | 19 | [5 empty] | At Balasore-'R' ph, E/F.At 16:20 hrs. Soro availed P/S from Bhadrak Auto
150 | 132 kV Balasore-Somnathpur |  |  |  |  | 0.20208 | 0 | 9 | [7 empty] | 4 | 8760 | 100% | 0.6 | 35040
|  | 17.08.18 | 11:49 | 17.08.18 | 16:40 | 4:51 | 0 | 9 | [5 empty] | At Somnathpur-O/C, E/F ['B' ph. LA damaged at stork end.]
151 | 132 kV Somnathpur-Stork |  |  |  |  | 0.20208 | 4 | 51 | [7 empty] | 0.1 | 8760 | 99.94% | 0.485 | 876
|  | 17.08.18 | 11:49 | 17.08.18 | 16:40 | 4:51 | 4 | 51 | [5 empty] | At Somnathpur-O/C, E/F ['B' ph. LA damaged at stork end.]
152 | 132 kV Somnathpur-EMAMI |  |  |  |  | 0.00625 | 0 | 9 | [7 empty] | 6 | 8760 | 100% | 0.9 | 52560
|  | 17.08.18 | 11:49 | 17.08.18 | 11:58 | 0:09 | 0 | 9 | [5 empty] | At Balasore - 'B' ph. to E/F, Zn.-II
153 | 132kV Balugaon-Chandpur |  |  |  |  | 0.023611 | 15 | 26 | [7 empty] | 43.52 | 8760 | 99.82% | 671.6587 | 381235.2
|  | 11.10.18 | 3:20 | 11.10.18 | 3:54 | 0:34 |  |  |  |  | 0 | 34 |  | Failed from N.Pur due to very severe cyclonic storm ''TITLI” & P/S
|  | 16.10.18 | 5:50 | 16.10.18 | 6:39 | 0:49 | 0 | 49 | [5 empty] | Failed at both end (N.pur & Balugaon) with Bph-G fault and Zone-1 Indication.132KV CHP_BLGN Line Breakdown & P/S
|  | 20.10.18 | 12:46 | 20.10.18 | 13:09 | 0:23 | 0 | 23 | [5 empty] | At Chatrapur-Tripped with Zone-II Indication.132KV CHP_BLGN Line Breakdown.
|  | 15.11.18 | 11:07 | 15.11.18 | 11:34 | 0:27 | 0 | 27 | [5 empty] | Failed from Chatrapur end due to snapping of Reserve Bus & P/S availed from Chandpur Grid at 11:34 Hrs
|  | 16.11.18 | 11:19 | 16.11.18 | 11:27 | 0:08 | 0 | 8 | [5 empty] | At Chhatrapur-L3-N with M/R fault dist.-15.99KM.
|  | 01.12.18 | 2:00 | 01.12.18 | 2:36 | 0:36 | 0 | 36 | [5 empty] | At Balugaon-Tripped on o/c (R-Y-B)ph., zone-1,fault distance- 8.01k.m, fault loop- L2-N,Yph-G fault and Zone-1 Indication(Loc-40.26 KM). At Narendrapur-Tripped with DP relay & M/R operated. DP relay showing Y-phase to E/F, Zone-I, Dist-30.22KM.
|  | 17.01.19 | 23:12 | 17.01.19 | 23:41 | 0:29 | 0 | 29 | [5 empty] | Failed At Both End (Chhatrapur & Balugaon) With Bph-G Fault, Zone-1 Indication(Loc-5.68Km) In Dp & M/T Relay Optd.
|  | 18.02.19 | 16:23 | 18.02.19 | 16:33 | 0:10 | 0 | 10 | [5 empty] | Failed at both end (Chhatrapur & Balugaon) with Yph-G fault , Zone-1 Indication (Loc-35.21km) in DP & M/T relay optd.
|  | 22.02.19 | 12:12 | 22.02.19 | 12:21 | 0:09 | 0 | 9 | [5 empty] | At Chhatrapur-Tripped on L2-L3 ,M/R,RYB zone-1,fault distance-44.19km At Balugaon-Ybph fault , Zone-1 Indication (Loc= -246.06km) in DP & M/T relay optd.
|  | 31.03.19 | 19:12 | 31.03.19 | 19:27 | 0:15 | 0 | 15 | [5 empty] | At Chhatrapur-Zone-1 Indication (Loc-102.3km in DP & M/T relay optd.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
154 | 132 kv Balugaon-Solari(T) |  |  |  |  | 0.023611 | 15 | 26 | [7 empty] | 14.5 | 8760 | 99.82% | 223.7833 | 127020
|  | 11.10.18 | 3:20 | 11.10.18 | 3:54 | 0:34 |  |  |  |  | 0 | 34 |  | Failed from N.Pur due to very severe cyclonic storm ''TITLI” & P/S
|  | 16.10.18 | 5:50 | 16.10.18 | 6:39 | 0:49 | 0 | 49 | [5 empty] | Failed at both end (N.pur & Balugaon) with Bph-G fault and Zone-1 Indication.132KV CHP_BLGN Line Breakdown & P/S
|  | 20.10.18 | 12:46 | 20.10.18 | 13:09 | 0:23 | 0 | 23 | [5 empty] | At Chatrapur-Tripped with Zone-II Indication.132KV CHP_BLGN Line Breakdown.
|  | 15.11.18 | 11:07 | 15.11.18 | 11:34 | 0:27 | 0 | 27 | [5 empty] | Failed from Chatrapur end due to snapping of Reserve Bus
|  | 16.11.18 | 11:19 | 16.11.18 | 11:27 | 0:08 | 0 | 8 | [5 empty] | At Chhatrapur-L3-N with M/R fault dist.-15.99KM.
|  | 01.12.18 | 2:00 | 01.12.18 | 2:36 | 0:36 | 0 | 36 | [5 empty] | At Balugaon-Tripped on o/c (R-Y-B)ph., zone-1,fault distance- 8.01k.m, fault loop- L2-N,Yph-G fault and Zone-1 Indication(Loc-40.26 KM). At Narendrapur-Tripped with DP relay & M/R operated. DP relay showing Y-phase to E/F, Zone-I, Dist-30.22KM.
|  | 17.01.19 | 23:12 | 17.01.19 | 23:41 | 0:29 | 0 | 29 | [5 empty] | Failed At Both End (Chhatrapur & Balugaon) With Bph-G Fault, Zone-1 Indication(Loc-5.68Km) In Dp & M/T Relay Optd.
|  | 18.02.19 | 16:23 | 18.02.19 | 16:33 | 0:10 | 0 | 10 | [5 empty] | Failed at both end (Chhatrapur & Balugaon) with Yph-G fault , Zone-1 Indication (Loc-35.21km) in DP & M/T relay optd.
|  | 22.02.19 | 12:12 | 22.02.19 | 12:21 | 0:09 | 0 | 9 | [5 empty] | At Chhatrapur-Tripped on L2-L3 ,M/R,RYB zone-1,fault distance-44.19km At Balugaon-Ybph fault , Zone-1 Indication (Loc= -246.06km) in DP & M/T relay optd.
|  | 31.03.19 | 19:12 | 31.03.19 | 19:27 | 0:15 | 0 | 15 | [5 empty] | At Chhatrapur-Zone-1 Indication (Loc-102.3km in DP & M/T relay optd.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
155 | 132 kv Banki-Nuapatna |  |  |  |  | 0.0034722 | 12 | 33 | [7 empty] | 21.014 | 5160 | 99.76% | 263.7257 | 108432.24
|  | 10.10.18 | 11:40 | 10.10.18 | 11:45 | 0:05 | 0 | 5 | [5 empty] | LBB
|  | 25.10.18 | 2:55 | 25.10.18 | 16:40 | 13:45 | 0 | 18 | [5 empty] | At Banki-Tripped on 86B relay faulty
|  | 20.03.19 | 16:45 | 20.03.19 | 16:55 | 0:10 | 0 | 10 | [5 empty] | Tripped due to SOTF protection
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
156 | 132 kV Bargarh-Barpalli |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20 | 8760 | 100% | 0 | 175200
157 | 132 kV Bargarh-ACC Ckt I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.87 | 8760 | 100% | 0 | 25141.2
158 | 132 kV Bargarh-ACC Ckt II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.87 | 8760 | 100% | 0 | 25141.2
159 | 132 kV Bargarh-Katapalli |  |  |  |  | 0.053472 | 16 | 32 | [7 empty] | 32.32 | 8760 | 99.81% | 534.3573 | 283123.2
|  | 07.01.19 | 15:55 | 07.01.19 | 17:12 | 1:17 | 1 | 17 | [5 empty] | H/T
|  | 16.01.19 | 16:49 | 16.01.19 | 16:55 | 0:06 | 0 | 6 | [5 empty] | At Katapali-Tripped
|  | 22.01.19 | 9:09 | 22.01.19 | 9:22 | 0:13 | 0 | 13 | [5 empty] | At Katapali-Tripped
|  | 06.02.19 | 12:44 | 06.02.19 | 12:55 | 0:11 | 0 | 0 | [5 empty] | Tripped at Katapali
|  | 08.02.19 | 15:06 | 08.02.19 | 15:14 | 0:08 | 0 | 0 | [5 empty] | Tripped at Katapali
|  | 11.02.19 | 6:24 | 11.02.19 | 6:29 | 0:05 | 0 | 0 | [5 empty] | Tripped at Katapali
|  | 17.02.19 | 19:07 | 17.02.19 | 19:13 | 0:06 | 0 | 0 | [5 empty] | Tripped at Katapali
|  | 18.02.19 | 14:42 | 18.02.19 | 14:59 | 0:17 | 0 | 0 | [5 empty] | Tripped at Katapali
|  | 06.03.19 | 8:05 | 06.03.19 | 10:34 | 2:29 | 2 | 29 | [5 empty] | At Bargarh-Tripped
|  | 17.03.19 | 21:53 | 17.03.19 | 22:20 | 00:27 | 0 | 27 | [5 empty] | At Bargarh-Tripped on E/F and Master relay with the tripping of 40MVA TRF-II. [Due To 132 Kv Cement -II Earth Fault Trip]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
160 | 132 kV Bargarh New-Ghens Ckt -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.53 | 8472 | 100% | 0 | 250178.16
161 | 132 kV Bargarh New-Ghens Ckt -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.53 | 8472 | 100% | 0 | 250178.16
162 | 132kV Baripada-Kuchei PG |  |  |  |  | 0.10625 | 2 | 33 | [7 empty] | 3.1 | 8760 | 99.97% | 7.905 | 27156
|  | 04.10.18 | 18:29 | 04.10.18 | 21:02 | 2:33 | 2 | 33 | [5 empty] | ICT Failure at PGCIL end.Power supply of Grid, s/s, Baripada Avail restricted Load From Grid, Balasore
163 | 132 kV Barpalli-Bolangir New |  |  |  |  | 0.045833 | 12 | 58 | [7 empty] | 60 | 8760 | 99.85% | 778 | 525600
|  | 17.04.18 | 14:55 | 17.04.18 | 15:02 | 0:07 | 0 | 7 | [5 empty] | At New Bolangir-Tripped
|  | 19.02.19 | 16:58 | 19.02.19 | 17:08 | 0:10 | 0 | 10 | [5 empty] | At Sadeipali-Tripped on O/L
|  | 19.02.19 | 17:11 | 19.02.19 | 17:18 | 0:07 | 0 | 7
|  | 20.02.19 | 17:06 | 20.02.19 | 17:15 | 0:09 | 0 | 7 | [5 empty] | At Sadeipali-Tripped on O/L
|  | 20.02.19 | 21:31 | 20.02.19 | 21:37 | 0:06
|  | 26.03.19 | 11:25 | 26.03.19 | 11:32 | 0:07 | 0 | 7 | [5 empty] | At Balangir-Tripped
|  | 29.03.19 | 17:37 | 29.03.19 | 17:57 | 0:20 | 0 | 20 | [5 empty] | At Balangir-Tripped on O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
164 | 132 kV Barpalli-Dunguripalli RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.6 | 8760 | 100% | 0 | 119136
165 | 132 kV Basta-Jaleswar |  |  |  |  | 0.44306 | 10 | 38 | [7 empty] | 23.81 | 8760 | 99.88% | 253.1797 | 208575.6
|  | 04.10.18 | 18:42 | 05.01.18 | 5:20 | 10:38 | 10 | 38 | [5 empty] | At Jaleswar -H/T
166 | 132kV BCMohanty-Bamnipal(Tisco) |  |  |  |  | 0.56667 | 13 | 36 | [7 empty] | 10 | 8760 | 99.84% | 136 | 87600
|  | 14.05.18 | 3:46 | 14.05.18 | 11:18 | 7:32 | 7 | 32 | [5 empty] | At B.C. Mohanty-D/P, Zn.-I, Dist.-2.2 k.m. ['B'ph. insulator damaged at Loc No.-7]
|  | 23.06.18 | 1:45 | 23.06.18 | 7:49 | 6:04 | 6 | 4 | [5 empty] | At B.C.Mohanty-D/P ['Y'ph. LA burst at B.C.Mohanty end]
167 | 132kV BCMohanty-Tomka (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.86 | 8760 | 100% | 0 | 103893.6
168 | 132kV Beekay Stel-Bhalulata |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.4 | 8760 | 100% | 0 | 240024
169 | 132kV Berhampur-Aska |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.98 | 8760 | 100% | 0 | 297664.8
170 | 132kV Berhampur-Digpahandi |  |  |  |  | 0.26806 | 12 | 23 | [7 empty] | 31.882 | 8760 | 99.86% | 394.8054 | 279286.32
|  | 11.10.18 | 2:42 | 11.10.18 | 2:54 | 0:12 |  |  |  |  | 0 | 12 |  | Tripped on O/C on R,Y,B phases in zone-1
|  | 11.10.18 | 3:20 | 11.10.18 | 8:30 | 5:10 |  |  |  |  | 5 | 10 |  | Tripped on O/C on R,Y,B phases in zone-2
|  | 11.10.18 | 12:01 | 11.10.18 | 12:42 | 0:41 |  |  |  |  | 0 | 41 |  | At Digapahandi-Tripped
|  | 16.10.18 | 5:50 | 16.10.18 | 6:02 | 0:12 | 0 | 12 | [5 empty] | At Digapahandi-Tripped
|  | 26.10.18 | 0:45 | 26.10.18 | 0:56 | 0:11 | 0 | 11 | [5 empty] | At Digapahandi-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
171 | 132kV Bhadrak-FACOR |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.564 | 8760 | 100% | 0 | 39980.64
172 | 132kV Bhadrak-Damara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 64.7 | 8760 | 100% | 0 | 566772
173 | 132kV Bhadrak-Damara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35.7 | 8760 | 100% | 0 | 312732
174 | 132kV Bhadrak-Bhdrak Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.086 | 8760 | 100% | 0 | 70833.36
175 | 132kV Bhadrak-Jajpur Town |  |  |  |  | 0 | 0 | 0 | [7 empty] | 40.519 | 8760 | 100% | 0 | 354946.44
176 | 132kV Bhanjanagar-Aska-I |  |  |  |  | 1899-12-31 03:37 | 0 | 0 | [7 empty] | 33.72 | 8760 | 100% | 0 | 295387.2
|  | 27.03.19 | 21:00 | 28.03.19 | 18:55 | 21:55 | 0 | 0 | [5 empty] | R,Y,B, Zone-1, Dist = -1 km,SOTF, PT Fuse Fail
|  | 28.03.19 | 10:13 | 28.03.19 | 15:55 | 5:42 | 0 | 0 | [5 empty] | Tripped at Aska end due to P.T supply fail.The Ckt. was idle charge condition from Bhanjanagar end from 21:00Hr of date-27-03-19.
177 | 132kV Bhanjanagar-Aska-II |  |  |  |  | 1899-12-31 20:56 | 0 | 0 | [7 empty] | 33.72 | 8760 | 100% | 0 | 295387.2
|  | 23.02.19 | 9:47 | 23.02.19 | 21:05 | 11:18 | 0 | 0 | [5 empty] | 132KV SIDE- PT FUSE FAIL at Aska
|  | 24.02.19 | 8:28 | 25.02.19 | 18:08 | 33:38 | 0 | 0 | [5 empty] | 132KV SIDE- PT FUSE FAIL at Aska
178 | 132KV Bhanjanagar-Phulabani |  |  |  |  | 0.33472 | 20 | 2 | [7 empty] | 86.5 | 8760 | 99.77% | 1732.8833 | 757740
|  | 05.09.18 | 12:40 | 05.09.18 | 17:59 | 5:19 | 5 | 19 | [5 empty] | At Bhanjanagar-E/F
|  | 03.10.18 | 13:21 | 03.10.18 | 14:18 | 0:57 | 0 | 57 | [5 empty] | At Bhanjanagar-TRIPPED
|  | 15.10.18 | 12:33 | 15.10.18 | 13:06 | 0:33 | 0 | 33 | [5 empty] | At -Phulbani (BRUSTING OF 33 K.V b-PHASE la OF 12.5 mva trf-2)
|  | 07.11.18 | 9:38 | 07.11.18 | 9:48 | 0:10 | 0 | 10 | [5 empty] | At Bhanjanagar-Tripped on O/C
|  | 20.11.18 | 17:52 | 20.11.18 | 18:04 | 0:12 | 0 | 12 | [5 empty] | At Bhanjanagar-Tripped on O/C
|  | 28.12.18 | 10:36 | 28.12.18 | 11:13 | 0:37 | 0 | 37 | [5 empty] | At Phulbani-Tripped
|  | 23.02.19 | 19:59 | 23.02.19 | 20:13 | 0:14 | 0 | 14
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
179 | 132kV Bhawanipatna-Junagarh |  |  |  |  | 0.12292 | 14 | 57 | [7 empty] | 25.158 | 8760 | 99.83% | 376.1121 | 220384.08
|  | 02.10.18 | 15:08 | 02.10.18 | 15:24 | 0:16 | 0 | 16 | [5 empty] | TRIPPED IN O/C IN Y PHASE (DP RELAY ,LBB,TRIP RELAY 86)OPERATED
|  | 03.10.18 | 18:42 | 03.10.18 | 18:52 | 0:10 | 0 | 10 | [5 empty] | At Therubali-Tripped on over load.
|  | 04.10.18 | 19:10 | 04.10.18 | 19:17 | 0:07 | 0 | 7 | [5 empty] | At Therubali-Tripped on over load.
|  | 06.10.18 | 17:55 | 06.10.18 | 18:05 | 0:10 | 0 | 10 | [5 empty] | At Therubali-Tripped on over load.
|  | 07.10.18 | 8:25 | 07.10.18 | 8:38 | 0:13 | 0 | 13 | [5 empty] | At Bolangir-Tripped on over load
|  | 07.10.18 | 9:55 | 07.10.18 | 10:05 | 0:10 | 0 | 10 | [5 empty] | At Bolangir-Tripped on over load
|  | 11.10.18 | 7:20 | 11.10.18 | 8:11 | 0:51 | 0 | 51 | [5 empty] | At Theruvali-Tripped on D/P( due to tree falls on rphase conductor betwwen loc 45 and 46 during cyclone titli)
|  | 12.10.18 | 17:30 | 12.10.18 | 17:50 | 0:20 | 0 | 20 | [5 empty] | At-Bhawanipatna Tripped
|  | 26.10.18 | 18:20 | 26.10.18 | 18:28 | 0:08 | 0 | 8 | [5 empty] | At Theruvali-Tripped
|  | 06.12.18 | 15:35 | 06.12.18 | 15:42 | 0:07 | 0 | 7 | [5 empty] | At Bhwanipatna-Tripped
|  | 31.03.19 | 20:45 | 31.03.19 | 21:10 | 0:25 | 0 | 25 | [5 empty] | Tripped on Master trip relay
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
180 | 132kV Bhubaneswar-Phulnakhara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23.14 | 8760 | 100% | 0 | 202706.4
181 | 132kV Bhogarai - Jaleswar ckt - II |  |  |  |  | 0.060417 | 0 | 0 | [7 empty] | 31.707 | 8760 | 100% | 0 | 277753.32
|  | 26.02.19 | 11:00 | 26.02.19 | 11:41 | 0:41 | 0 | 0 | [5 empty] | At Bhograi-D/P Optd.,R-Ph Ground,15.4Km,Ir-1073.1A,Iy-195.0A,Ib-233.4A
|  | 17.03.19 | 18:25 | 17.03.19 | 19:11 | 0:46 |  |  | 0 | 46 |  |  |  | At Kuchei-Tripped.
182 | 132kV Bidanasi-Bhubaneswar Power-Chandaka |  |  |  |  | 0.35903 | 8 | 37 | [7 empty] | 35.34 | 8760 | 99.9% | 304.513 | 309578.4
|  | 28.02.18 | 4:20 | 28.02.18 | 12:57 | 8:37 | 8 | 37 | [5 empty] | At Chandaka-H/T ['Y' ph. insulator damaged at Loc. No.-13]
183 | 132kV Boinda-Rairakhol |  |  |  |  | 0.0013889 | 0 | 2 | [7 empty] | 60 | 8760 | 100% | 2 | 525600
|  | 26.02.19 | 19:07 | 26.02.19 | 19:09 | 0:02 | 0 | 2 | [5 empty] | At Rairakhol-Tripped On E/F
184 | 132kV Bolani - Arya Iron |  |  |  |  | 0.030556 | 0 | 44 | [7 empty] | 3.17 | 8760 | 99.99% | 2.3247 | 27769.2
|  | 07.04.18 | 17:58 | 07.04.18 | 18:16 | 0:18 | 0 | 18 | [5 empty] | At Joda-'R'ph. to E/F
|  | 06.03.19 | 14:37 | 06.03.19 | 15:03 | 0:26 | 0 | 26 | [5 empty] | Tripped on E/F at ROURKELA Grid S/S end. D.P Relay operated at Rourkela Grid S/S end
185 | 132kV Bolangir-Sonepur |  |  |  |  | 0.39097 | 9 | 23 | [7 empty] | 53.845 | 8760 | 99.89% | 505.2456 | 471682.2
|  | 05.02.19 | 10:00 | 05.02.19 | 12:28 | 2:28 | 2 | 28 | [5 empty] | Ac supplied failed from Balangir
|  | 10.02.19 | 7:17 | 10.02.19 | 14:12 | 6:55 | 6 | 55 | [5 empty] | Ac supplied failed from Balangir
186 | 132 kV Bolangir New - Bolangir Ckt - I |  |  |  |  | 0.0090278 | 12 | 41 | [7 empty] | 3.78 | 8760 | 99.86% | 47.943 | 33112.8
|  | 16.10.18 | 9:56 | 16.10.18 | 10:09 | 0:13 | 0 | 13 | [5 empty] | At Sadeipali-Tripped on over current on RYB-ph and Earth fault.
|  | 23.10.18 | 12:36 | 23.10.18 | 12:46 | 0:10 | 0 | 10 | [5 empty] | At Sadeipali-Tripped on Back up o/c & e/f protection operated and transformer running over 90% load indication
|  | 05.03.19 | 18:51 | 05.03.19 | 18:54 | 0:03 | 0 | 3 | [5 empty] | At Bolangir(New)-Tripped
|  | 31.03.19 | 16:14 | 31.03.19 | 16:22 | 0:08 | 0 | 8 | [5 empty] | Source failure
|  | 10.03.19 | 19:17 | 10.03.19 | 19:25 | 0:08 | 0 | 7 | [5 empty] | At Sadeipali-Tripped on O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
187 | 132 kV Bolangir New - Bolangir Ckt - II |  |  |  |  | 0.010417 | 0 | 23 | [7 empty] | 3.008 | 8760 | 100% | 1.1531 | 26350.08
|  | 16.10.18 | 9:56 | 16.10.18 | 10:11 | 0:15 | 0 | 13 | [5 empty] | At Sadeipali-Tripped on over current on RYB-ph and Earth fault.
|  | 23.10.18 | 12:36 | 23.10.18 | 12:46 | 0:10 | 0 | 10 | [5 empty] | At Sadeipali-Tripped on Back up o/c & e/f protection operated and transformer running over 90% load indication
188 | 132kV Bolangir New-Patnagarh Ckt - I |  |  |  |  | 0.018056 | 0 | 26 | [7 empty] | 39.805 | 8760 | 100% | 17.2488 | 348691.8
|  | 04.11.18 | 3:06 | 04.11.18 | 3:32 | 0:26 | 0 | 26 | [5 empty] | At Sadeipali-Tripped on D/P.
189 | 132kV Bolangir New-Patnagarh Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 39.805 | 8760 | 100% | 0 | 348691.8
190 | 132kVBolani-Arya Iron |  |  |  |  | 0.0125 | 0 | 18 | [7 empty] | 3.2 | 8760 | 100% | 0.96 | 28032
|  | 07.04.18 | 17:58 | 07.04.18 | 18:16 | 0:18 | 0 | 18 | [5 empty] | At Joda-'R'ph. to E/F
191 | 132kV BRPL-Mesco |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5 | 8760 | 100% | 0 | 43800
192 | 132kV Budhipadar-Lapanga-Jharsuguda Ckt-I |  |  |  |  | 0.018056 | 37 | 24 | [7 empty] | 7 | 8760 | 99.57% | 261.8 | 61320
|  | 12.05.18 | 23:29 | 13.05.18 | 0:05 | 00:36 | 0 | 36 | [5 empty] | At Budhipadar-'R' ph, E/F, Zn.-II
|  | 26.02.19 | 13:43 | 26.02.19 | 14:09 | 0:26 | 0 | 0 | [5 empty] | Dir O/C,
|  | 17.03.19 | 14:52 | 17.03.19 | 15:40 | 24:48 | 24 | 48 | [5 empty] | At Budhipadhar-Tripped on D/P. [Due to snapping of R phase jumper of 132 kV Budhipadhar-Lapanga fdr at LOC-161]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
193 | 132kV Budhipadar-Jharsuguda Ckt-II |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 7 | 8760 | 100% | 0.93333 | 61320
|  | 12.05.18 | 23:29 | 12.05.18 | 23:37 | 0:08 | 0 | 8 | [5 empty] | At Budhipadar-'R' ph, E/F
194 | 132kV Budhipadar-Rajgangpur ckt-II |  |  |  |  | 0.074306 | 13 | 21 | [7 empty] | 80 | 8760 | 99.85% | 1068 | 700800
|  | 06.04.18 | 17:31 | 06.04.18 | 18:19 | 0:48 | 0 | 27 | [5 empty] | At Rajgangpur-'B' ph, E/F, Zn.-I, Dist.-5.34 k.m.Weather condition was rainy with lightning
|  | 10.10.18 | 10:59 | 10.10.18 | 11:15 | 0:16 | 0 | 11 | [5 empty] | AT BUDHIPADAR END -Tripped on D/P,ZONE 2, RYB- PHASE TRIP , L1-243A,L2-1117A,L3-276A, L2N LOOP. AT RAJGANGPUR -132KV RAILWAY -II FEEDER EARTH WIRE AND Y-PHASE CONDUCTOR SNAPING AT LOC. NO- 09
|  | 15.03.19 | 12:40 | 15.03.19 | 13:23 | 0:43 | 0 | 43 | [5 empty] | AGT,ZONE 1,LOC 7.14KM, Ia=3956A, Ig=4352A [HEAVY LIGHTENING AND RAIN]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
195 | 132kV Budhipadar-Sundargarh-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.61 | 8760 | 100% | 0 | 276903.6
196 | 132kV Budhipadar-Sundargarh-II |  |  |  |  | 0 | 1 | 0 | [7 empty] | 31.61 | 8760 | 99.99% | 31.61 | 276903.6
197 | 132kV Budhipadar-MCL(Jorbaga)-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23 | 8760 | 100% | 0 | 201480
198 | 132kV Budhipadar-MCL(Jorbaga)-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23 | 8760 | 100% | 0 | 201480
199 | 132kV Budhipadar-MSP |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.592 | 8760 | 100% | 0 | 5185.92
200 | 132kV Budhipadar-Brajarajnagar (Remja) |  |  |  |  | 0.038889 | 1 | 14 | [5 empty] | At Budhipadar-'R'ph. to E/F |  | 11.745 | 8760 | 99.99% | 14.4855 | 102886.2
|  | 09.06.18 | 14:59 | 09.06.18 | 15:55 | 0:56 | 0 | 56 | [5 empty] | At Budhipadar-'R'ph. to E/F
|  | 17.10.18 | 21:11 | 17.10.18 | 21:39 | 0:18 | 0 | 18 | [5 empty] | failure from Budhipadhar end.
201 | 132kV Budhipadar - Kalunga-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 100 | 8760 | 100% | 0 | 876000
202 | 132kV Burla-Chipilima Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.9 | 8760 | 100% | 0 | 174324
203 | 132kV Burla-Hindalco-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9 | 8760 | 100% | 0 | 78840
204 | 132kV Burla-Hindalco-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9 | 8760 | 100% | 0 | 78840
205 | 132kV Burla-Katapali-Chipilima Ckt-II |  |  |  |  | 0.023611 | 1 | 8 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 22.66 | 8760 | 99.99% | 25.6813 | 198501.6
|  | 07.01.19 | 15:40 | 07.01.19 | 16:14 | 0:34 | 1 | 8 | [5 empty] | At Katapali-Tripped on Dp Relay.Main I & Ii ,Dp Zone-1 ,Dist-746.5 Mtr,Ili=2.609Ka,Il2=3.09 Ka,Il3=438.5Amp,Fault Duration80 Msec( R-Ph Jumper Snapped At Loc No-4 Of 220 Kv Of Ckt And Fallen On Y-Ph.220 Kv New Bargarh ,)
206 | 132kV Burla-Katapalli |  |  |  |  | 0.023611 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 7 | 8760 | 100% | 0 | 61320
|  | 07.01.19 | 15:40 | 07.01.19 | 16:14 | 0:34 | 1 | 8 | [5 empty] | At Katapali-Tripped on Dp Relay.Main I & Ii ,Dp Zone-1 ,Dist-746.5 Mtr,Ili=2.609Ka,Il2=3.09 Ka,Il3=438.5Amp,Fault Duration80 Msec( R-Ph Jumper Snapped At Loc No-4 Of 220 Kv Of Ckt And Fallen On Y-Ph.220 Kv New Bargarh ,)
207 | 132kV Burla-Lapanga-Budhipadar-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 63.25 | 8760 | 100% | 0 | 554070
208 | 132kV Burla-Lapanga-Budhipadar-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 63.25 | 8760 | 100% | 0 | 554070
209 | 132kV Burla-Sambalpur |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 19.9 | 8760 | 100% | 0 | 174324
210 | 132kV Chainpal-Angul |  |  |  |  | 0.075694 | 15 | 6 | [7 empty] | 14.931 | 8760 | 99.83% | 225.4581 | 130795.56
|  | 16.04.18 | 18:36 | 16.04.18 | 19:56 | 1:20 | 1 | 20 | [5 empty] | At Chainpal-Tripped.Due to bursting of 132 kV side CT of 20 MVA Trf.-III at Chainpal the disturbance occurred.
|  | 26.02.19 | 8:10 | 27.02.19 | 17:29 | 33:19 | 1 | 17 | [5 empty] | Tripped on E/F,O/C-B ph ,Bursting of CT
|  | 30.03.19 | 11:46 | 30.03.19 | 12:15 | 0:29 | 0 | 29 | [5 empty] | O/C-B Ph & E/F.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
211 | 132kV Chainpal-FCI-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7 | 8760 | 100% | 0 | 61320
212 | 132kV Chainpal-FCI-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7 | 8760 | 100% | 0 | 61320
213 | 132kV Chainpal-Talcher Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.448 | 2088 | 100% | 0 | 935.424
214 | 132kV Chandaka-Bhubaneswar-I |  |  |  |  | 0.061806 | 13 | 7 | [7 empty] | 5.5 | 8760 | 99.85% | 72.1417 | 48180
|  | 13.05.18 | 3:36 | 13.05.18 | 4:29 | 0:53 | 0 | 31 | [5 empty] | At Chandaka-. After 31 minutes power flow resumed through Ckt-II
|  | 16.06.18 | 12:00 | 16.06.18 | 12:10 | 0:10 | 0 | 10 | [5 empty] | At Chandaka-D/P
|  | 21.02.19 | 13:29 | 21.02.19 | 13:55 | 0:26 | 0 | 26 | [5 empty] | At Bhubaneswar-Tripped on DP Relay operated with Gr-1, B-C-N, , dist trip – Z1, Dist-3.371 kms, Ia=186.6 A, Ib=1.69 kA, Ic =1.625 kA. At Chandaka-DP Relay operated with Gr-1, B-C-N, , dist trip – Z1, Dist-3.51 kms, Ia=195.6 A, Ib=12.66 kA, Ic =8.815 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
215 | 132kV Chandaka-Bhubaneswar-II |  |  |  |  | 0.12778 | 12 | 50 | [7 empty] | 5.5 | 8760 | 99.85% | 70.5833 | 48180
|  | 16.06.18 | 12:00 | 16.06.18 | 14:24 | 2:24 | 0 | 10 | [5 empty] | At Bhubaneswar-O/C, E/F. Power flow resumed through ckt-I after 10 minutes
|  | 17.07.18 | 15:51 | 17.07.18 | 16:05 | 0:14 | 0 | 14 | [5 empty] | At Bhubaneswar-E/F, O/C
|  | 21.02.19 | 13:29 | 21.02.19 | 13:55 | 0:26 | 0 | 26 | [5 empty] | At Chandaka-Tripped,DP indications.Gr-1,B-C,Dist trip-4.55 Km. Ia=404 A, Ib=8.42 KA, Ic=8.1999 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
216 | 132kV Chandaka-Mendhasal |  |  |  |  | 0.042361 | 0 | 31 | [7 empty] | 18.5 | 8760 | 99.99% | 9.5583 | 162060
|  | 13.05.18 | 3:38 | 13.05.18 | 4:39 | 1:01 | 0 | 31 | [5 empty] | At Mendhasal-'R' ph, E/F, Dist.-2.2 k.m.
|  | 21.02.19 | 13:29 | 21.02.19 | 14:00 | 0:31 | 0 | 26 | [5 empty] | At Chandaka-Tripped on DP Relay operated with Gr-1, B-C-N, , dist. trip – Z4, Dist-11.35 kms, Ia=343.4 A, Ib=2.38 kA, Ic =1.820 kA
|  | 23.02.19 | 13:44 | 23.02.19 | 13:50 | 0:06 | 0 | 0 | [5 empty] | Tripped on DP at Khurda
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
217 | 132kV Chandaka-Pratapsasan-Nimapara |  |  |  |  | 0.0027778 | 13 | 18 | [7 empty] | 65.8 | 8760 | 99.85% | 875.14 | 576408
|  | 15.10.18 | 13:58 | 15.10.18 | 14:02 | 0:04 | 0 | 4 | [5 empty] | At Chandaka-Tripped
|  | 15.10.18 | 16:31 | 15.10.18 | 16:39 | 0:08 | 0 | 8 | [5 empty] | At Chandaka-Tripped
|  | 20.10.18 | 13:33 | 20.10.18 | 13:48 | 0:15 | 0 | 15 | [5 empty] | fault trip
|  | 20.10.18 | 15:35 | 20.10.18 | 15:45 | 0:10 | 0 | 10 | [5 empty] | Load diversion to Ransinghpur through Nimapara R/B.
|  | 21.02.19 | 13:26 | 21.02.19 | 13:58 | 0:32 | 0 | 26 | [5 empty] | O/C ,E/F. at Chandaka
|  | 31.03.19 | 20:20 | 31.03.19 | 20:35 | 0:15 | 0 | 15 | [5 empty] | D/P, E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
218 | 132kV Chandaka-Ransingpur |  |  |  |  | 0 | 14 | 35 | [7 empty] | 28.25 | 8760 | 99.83% | 411.9792 | 247470
|  | 16.06.18 | 17:36 | 17.06.18 | 01:53 | 08:17 | 0 | 52 | [5 empty] | At Chandaka-D/P, Zn.-I, 'R' ph. To E/F, Dist.-18.45 k.m. [Earth wire snapped].At 18:18 hrs. Ransingpur availed P/S from Nimapara end
|  | 10.10.18 | 11:52 | 10.10.18 | 12:01 | 0:09 | 0 | 9 | [5 empty] | At Chanadaka-Tripped on E/F
|  | 15.10.18 | 13:34 | 15.10.18 | 14:37 | 1:03 | 0 | 28 | [5 empty] | At Chandaka-Tripped
|  | 20.10.18 | 12:21 | 20.10.18 | 12:26 | 0:05 | 0 | 41 | [5 empty] | At Chandaka-Tripped
|  | 20.10.18 | 13:17 | 20.10.18 | 15:29 | 2:12 | [7 empty] | fault trip
|  | 21.02.19 | 13:29 | 21.02.19 | 13:54 | 0:25 | 0 | 25 | [5 empty] | At Chandaka-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
219 | 132kV Chandaka B-Unit-8 |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.4 | 24 | 100% | 0 | 273.6
220 | 132kV Chandpur - Khurda |  |  |  |  | 0.0048611 | 0 | 7 | [7 empty] | 35.93 | 8760 | 100% | 4.1918 | 314746.8
|  | 31.03.19 | 16:56 | 31.03.19 | 17:03 | 0:07 | 0 | 7 | [5 empty] | Tripped at Atri end with DP relay but didn't show any distance
221 | 132kV Chandikhol-Kendrapada |  |  |  |  | 0.028472 | 19 | 4 | [7 empty] | 31.6 | 8760 | 99.78% | 602.5067 | 276816
|  | 19.10.18 | 12:27 | 19.10.18 | 13:08 | 0:41 | 0 | 41 | [5 empty] | At Kendrapada-Tripped BUS insulator punture at paradeep end .
|  | 12.11.18 | 18:54 | 12.11.18 | 18:58 | 0:04 | 0 | 4 | [5 empty] | At Kendrapara-H/T
|  | 03.12.18 | 15:37 | 03.12.18 | 15:51 | 0:14 | 0 | 14 | [5 empty] | At Kendrapara-TRIPPED ON E/F , M/R WITH VT FUSE
|  | 03.12.18 | 15:51 | 03.12.18 | 18:01 | 2:10 | [7 empty] | TRIP ON E/F , M/R WITH SOTF
|  | 13.01.19 | 13:12 | 13.01.19 | 13:37 | 0:25 | 0 | 25 | [5 empty] | Trip On E/F With M/R
|  | 19.01.19 | 4:27 | 19.01.19 | 4:31 | 0:04 | 0 | 4 | [5 empty] | At Kendrapara-Tripped (Due to busting of R ph LA at Terkera Grid.)
|  | 19.01.19 | 4:55 | 19.01.19 | 5:07 | 0:12 | 0 | 12 | [5 empty] | Line Faulty Didn'T Stand From Kdp Side
|  | 19.01.19 | 5:46 | 19.01.19 | 5:51 | 0:05 | 0 | 5 | [5 empty] | Line Faulty Didn'T Stand From Kdp Side
|  | 19.01.19 | 5:58 | 19.01.19 | 6:09 | 0:11 | 0 | 11 | [5 empty] | Line Faulty Didn'T Stand From Kdp Side
|  | 19.01.19 | 6:54 | 19.01.19 | 7:04 | 0:10 | 0 | 10 | [5 empty] | Line Faulty Didn'T Stand From Kdp Side
|  | 22.01.19 | 1:28 | 22.01.19 | 11:17 | 9:49 | 4 | 14 | [5 empty] | At Kendrapara-Tripped on D/P Operated . Chandikhol availed supply from Jajpur end at 05:42hrs.
|  | 25.01.19 | 10:48 | 25.01.19 | 11:11 | 0:23 | 0 | 23 | [5 empty] | At Paradeep-220KV MAIN BUS-I B-PH BUS CONDUCTOR(SECTION) AFTER(ESSAR-II&50MVA) SNAPPED DUE TO PUNCTURE OF INSULATOR & PULL OUT THE WHOLE SYSTEM At Kendrapara-Trip On E/F With M/R
|  | 14.02.19 | 6:25 | 14.02.19 | 6:46 | 0:21 | 0 | 21 | [5 empty] | At Kendrapada-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
222 | 132kV Chatrapur-Balugaon |  |  |  |  | #REF! | 22 | 20 | [7 empty] | 54.19 | 8760 | 99.75% | 1210.2433 | 474704.4
|  | 20.10.18 | 12:46 | 20.10.18 | 15:21 | 2:35 | 0 | 23 | [5 empty] | 132 KV Chatrapur-Balugon circuit.Chatrapur and Balugaon availed powersupply from Khurdha.
|  | 11.10.18 | 3:20 | 11.10.18 | 8:25 | 5:05 |  |  |  |  | 5 | 5 |  | Failed from N.Pur due to very severe cyclonic storm ''TITLI” & P/S
|  | 16.10.18 | 5:50 | 16.10.18 | 13:10 | 7:20 | 7 | 20 | [5 empty] | Failed at both end (N.pur & Balugaon) with Bph-G fault and Zone-1 Indication.132KV CHP_BLGN Line Breakdown & P/S
|  | 20.10.18 | 12:46 | 20.10.18 | 15:22 | 2:36 | 0 | 23 | [5 empty] | At Chatrapur-Tripped with Zone-II Indication.132KV CHP_BLGN Line Breakdown.
|  | 15.11.18 | 11:07 | 15.11.18 | 20:00 | 8:53 | 0 | 27 | [5 empty] | Failed from Chatrapur end due to snapping of Reserve Bus & P/S availed from Chandpur Grid at 11:34 Hrs
|  | 16.11.18 | 11:19 | 16.11.18 | 11:27 | 0:08 | 0 | 8 | [5 empty] | At Chhatrapur-L3-N with M/R fault dist.-15.99KM.
|  | 01.12.18 | 2:00 | 01.12.18 | 17:46 | 15:46 | 0 | 36 | [5 empty] | At Balugaon-Tripped on o/c (R-Y-B)ph., zone-1,fault distance- 8.01k.m, fault loop- L2-N,Yph-G fault and Zone-1 Indication(Loc-40.26 KM). At Narendrapur-Tripped with DP relay & M/R operated. DP relay showing Y-phase to E/F, Zone-I, Dist-30.22KM.132KVBalugaon-Chatrapur Line Breakdown & P/S availed from Chandpur Grid at 02:36 Hrs
|  | 17.01.19 | 23:12 | 17.01.19 | 23:41 | 0:29 | 0 | 29 | [5 empty] | Failed At Both End (Chhatrapur & Balugaon) With Bph-G Fault, Zone-1 Indication(Loc-5.68Km) In Dp & M/T Relay Optd.
|  | 18.02.19 | 16:23 | 18.02.19 | 16:33 | 0:10 | 0 | 10 | [5 empty] | Tripped on Y-G ,M/R,RYB zone-1,fault distance-7.09km
|  | 22.02.19 | 12:12 | 22.02.19 | 12:21 | 0:09 | 0 | 9 | [5 empty] | At Chhatrapur-Tripped on L2-L3 ,M/R,RYB zone-1,fault distance-44.19km At Balugaon-Ybph fault , Zone-1 Indication (Loc= -246.06km) in DP & M/T relay optd.
|  | 31.03.19 | 19:12 | 31.03.19 | 19:27 | 0:15 | 0 | 15 | [5 empty] | At Chhatrapur-Zone-1 Indication (Loc-102.3km in DP & M/T relay optd.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
223 | 132kV Chatrapur-Ganjam |  |  |  |  | 0.013889 | 18 | 36 | [7 empty] | 12.6 | 8760 | 99.79% | 234.36 | 110376
|  | 15.11.18 | 2:44 | 15.11.18 | 3:04 | 0:20 | 0 | 20 | [5 empty] | At Ganjam-Tripped with D/P
|  | 15.11.18 | 2:44 | 15.11.18 | 3:04 | 0:20 | 0 | 20 | [5 empty] | R-phase-G with with M/R at Narendrapur end.
|  | 15.11.18 | 11:07 | 15.11.18 | 11:34 | 0:27 | 0 | 27 | [5 empty] | Tripped due to Chatrapur Grid reserve bus Y- phase disc insulator brust. At Purushottampur-Distance Relay indication,Distance Loop-L1-2,Distance-17.1Km
|  | 15.11.18 | 14:40 | 15.11.18 | 20:09 | 5:29 | 5 | 29 | [5 empty] | At GChhatrapur-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
224 | 132kV Chatrapur-IRE-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.8 | 8760 | 100% | 0 | 50808
225 | 132kV Chatrapur-IRE-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.8 | 8760 | 100% | 0 | 50808
226 | 132kV Chatrapur-Rambha (T) |  |  |  |  | 0.0041667 | 0 | 7 | [7 empty] | 28.904 | 8760 | 100% | 3.3721 | 253199.04
|  | 24.11.18 | 13:57 | 24.11.18 | 14:03 | 0:06 | 0 | 6 | [5 empty] | At Chhatrapur-Tripped on O/C R- Phase with M/R.
|  | 06.02.19 | 11:47 | 06.02.19 | 11:48 | 0:01 | 0 | 1 | [5 empty] | Tripped on O/C R-Phase
227 | 132kV Chhend-Adhunik Metalics |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.44 | 8760 | 100% | 0 | 214094.4
228 | 132kV Chhend-Nuagaon(T) |  |  |  |  | 0.010417 | 0 | 24 | [7 empty] | 35 | 8760 | 100% | 14 | 306600
|  | 15.12.18 | 21:51 | 15.12.18 | 22:06 | 0:15 | 0 | 15 | [5 empty] | Tripped 86B & 67A Relay operated.
|  | 17.12.18 | 14:15 | 17.12.18 | 14:24 | 0:09 | 0 | 9 | [5 empty] | Tripped on D.P
229 | 132kV Chipilima-Katapalli Ckt-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 100% | 0 | 110901.6
230 | 132kV Chipilima-Katapalli Ckt-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 100% | 0 | 110901.6
231 | 132kV Choudwar-Bidanasi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.414 | 8760 | 100% | 0 | 135026.64
232 | 132kV Choudwar-Kendrapara Road Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.6 | 8760 | 100% | 0 | 40296
233 | 132kV Cuttack-Jagatsingpur |  |  |  |  | 0.0034722 | 12 | 5 | [7 empty] | 35.112 | 8760 | 99.86% | 424.27 | 307581.12
|  | 03.01.19 | 13:49 | 03.01.19 | 13:52 | 0:03 | 0 | 3
|  | 03.01.19 | 13:56 | 03.01.19 | 13:57 | 0:01 | 0 | 1
|  | 03.01.19 | 16:37 | 03.01.19 | 16:38 | 0:01 | 0 | 1
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
234 | 132kV Cuttack-Phulnakhara |  |  |  |  | 0.011111 | 12 | 13 | [7 empty] | 20.256 | 8760 | 99.86% | 247.4608 | 177442.56
|  | 01.01.19 | 12:44 | 01.01.19 | 12:47 | 0:03
|  | 03.01.19 | 13:49 | 03.01.19 | 13:52 | 0:03 | 0 | 3 | [5 empty] | At Cuttack-Tripped At Jagatsinghpur -Tripped
|  | 03.01.19 | 13:56 | 03.01.19 | 13:57 | 0:01 | 0 | 1
|  | 03.01.19 | 16:37 | 03.01.19 | 16:38 | 0:01 | 0 | 1
|  | 23.01.19 | 2:10 | 23.01.19 | 2:14 | 0:04 | 0 | 4 | [5 empty] | At Cuttack-Tripped
|  | 18.02.19 | 11:24 | 18.02.19 | 11:28 | 0:04 | 0 | 4 | [5 empty] | At Cuttack -Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
235 | 132kV Dabugaon -Umerkote |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.89 | 8760 | 100% | 0 | 401996.4
236 | 132kV Dhenkanal-Khuntuni-Grid Steel -ICCL |  |  |  |  | 0.18056 | 4 | 20 | [7 empty] | 39.58 | 8760 | 99.95% | 171.5133 | 346720.8
|  | 06.12.18 | 15:37 | 06.12.18 | 19:57 | 4:20 | 4 | 20 | [5 empty] | At Dhenkanal-Tripped on E/F, L2-N, I2=1.7kA, 32.964km
237 | 132kV Dhenkanal-Joranda (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.345 | 8760 | 100% | 0 | 169462.2
238 | 132kV Digapahandi-Chikiti ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.5 | 840 | 100% | 0 | 24780
239 | 132kV Digapahandi-Chikiti ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.5 | 840 | 100% | 0 | 24780
240 | 132kV Duburi-BC Mohanty |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.974 | 8760 | 100% | 0 | 96132.24
241 | 132kV Duburi-BRPL |  |  |  |  | 0.020139 | 0 | 29 | [7 empty] | 4.43 | 8760 | 99.99% | 2.1412 | 38806.8
|  | 25.10.18 | 2:10 | 25.10.18 | 2:30 | 0:20 | 0 | 20 | [5 empty] | At Duburi- Back up Relay:-R-Phase O/C Pick up,Y-Phase O/C Pick up,E/F Pick Up,86 – Master Trip relay.
|  | 25.10.18 | 2:39 | 25.10.18 | 2:48 | 0:09 | 0 | 9 | [5 empty] | At Duburi- Back up Relay:-R-Phase O/C Pick up,Y-Phase O/C Pick up,E/F Pick Up,86 – Master Trip relay.
242 | 132kV Duburi-Jajpur Road-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.2 | 8760 | 100% | 0 | 115632
243 | 132kV Duburi-Jajpur Road-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.2 | 8760 | 100% | 0 | 115632
244 | 132kV Duburi-Jakhapura (T) |  |  |  |  | 0.0048611 | 0 | 7 | [7 empty] | 12.851 | 8760 | 100% | 1.4993 | 112574.76
|  | 23.03.19 | 11:22 | 23.03.19 | 11:29 | 0:07 | 0 | 7 | [5 empty] | At Duburi-Tripped on DP, E/F, O/C
245 | 132kV Duburi-Mesco |  |  |  |  | 0.11111 | 2 | 40 | [7 empty] | 6.65 | 8760 | 99.97% | 17.7333 | 58254
|  | 25.10.18 | 2:10 | 25.10.18 | 4:50 | 2:40 | 2 | 40 | [5 empty] | Grid Earthwire snapped and fell over the Bus Bar inside Mesco S/Y
246 | 132kV ICCL-Choudwar |  |  |  |  | 0.022917 | 0 | 0 | [7 empty] | 0.5 | 8760 | 100% | 0 | 4380
|  | 20.02.19 | 23:59 | 20.02.19 | 0:32 | 0:33 | 0 | 0 | [5 empty] | E/F at Choudwar
247 | 132kV ICCL-Mania-OCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.2 | 8760 | 100% | 0 | 176952
248 | 132kV Jabamayee FAlloys-Duburi-II |  |  |  |  | 0 | 0 | 25 | [7 empty] | 12 | 8760 | 100% | 5 | 105120
|  | 01.03.19 | 6:15 | 01.03.19 | 15:07 | 00:25 | 0 | 25 | [5 empty] | At Duburi-Tripped on DP, 67NX, 86B [Snapping of B- Phase Jumper at Loc. No. 276.]
249 | 132kVJagatsinghpur-Gorakhnath (T) |  |  |  |  | 0.27222 | 18 | 52 | [7 empty] | 16.53 | 8760 | 99.78% | 311.866 | 144802.8
|  | 26.10.18 | 15:19 | 26.10.18 | 21:51 | 6:32 | 6 | 32 | [5 empty] | At Paradeep-Tripped (PUNCTURED INSULATOR AT 21 PA.)
|  | 15.01.19 | 4:25 | 15.01.19 | 4:42 | 0:17 | 0 | 17 | [5 empty] | At Jagatsinghpur-Tripped on O/C & E/F By Creating Heavy Sound.(Delay In Patrolling Due To Fog)
|  | 22.01.19 | 3:04 | 22.01.19 | 3:07 | 0:03 | 0 | 3 | [5 empty] | Tripped On O/C & E/F Indication.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
250 | 132kVJajpur Road-Anandpur Ckt-I |  |  |  |  | 0.22986 | 0 | 0 | [7 empty] | 30 | 8760 | 100% | 0 | 262800
|  | 12.02.19 | 11:34 | 12.02.19 | 17:05 | 5:31 | 0 | 0 | [5 empty] | At Jajpur Road-Tripped on D/P RELAY , IA=93.01A, IB=7.5KA,IC=53.94A, VAN=83.99 KV,VBN=765.6 V,VCN=78.48 KV ,ZONE-1 (Due to puncture of 132KV LA )
251 | 132kVJajpur Road-Anandpur Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30 | 8760 | 100% | 0 | 262800
252 | 132kVJajpur Road-Chandikhol |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.71 | 8760 | 100% | 0 | 304059.6
253 | 132kVJajpur Road-Jajpur Town |  |  |  |  | 0 | 0 | 0 | [7 empty] | 25.451 | 8760 | 100% | 0 | 222950.76
254 | 132kVJajpur Road-Kendrapada Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 63.11 | 8760 | 100% | 0 | 552843.6
255 | 132kVJaleswar-Bhogarai |  |  |  |  | 0.010417 | 0 | 15 | [7 empty] | 57.934 | 8760 | 100% | 14.4835 | 507501.84
|  | 04.10.18 | 18:30 | 04.10.18 | 18:45 | 0:15 | 0 | 15 | [5 empty] | At Bhograi -H/T
256 | 132kVJaleswar-Jaleswar (T) |  |  |  |  | 0.0097222 | 0 | 14 | [7 empty] | 2.34 | 8760 | 100% | 0.546 | 20498.4
|  | 04.10.18 | 18:28 | 04.10.18 | 18:42 | 0:14 | 0 | 14 | [5 empty] | At Kuchei-Tripped
257 | 132kVJaynagar-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.272 | 8760 | 100% | 0 | 396582.72
258 | 132kVJaynagar-Jaynagar(T) |  |  |  |  | 0.0041667 | 18 | 29 | [7 empty] | 40 | 8760 | 99.79% | 739.3333 | 350400
|  | 15.11.18 | 19:19 | 15.11.18 | 19:25 | 0:06 | 0 | 6 | [5 empty] | Y-Ph-N,Z-I, Dist-21.97Km.
|  | 15.11.18 | 19:25 | 15.11.18 | 22:51 | 3:26 | 3 | 26 | [5 empty] | B-Ph,Y-Ph-N,Z-I, Dist-23.65Km.
|  | 25.02.19 | 9:01 | 25.02.19 | 11:58 | 2:57 | 2 | 57 | [5 empty] | Tripped on Zone-2, Y-ph, B-PH, Dist-116.06KM & Fault current-IA-83.03A, IB-1.297KA, 1.244KA.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
259 | 132kVJaynagar-Podagada-Rayagada |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 112.236 | 8760 | 100% | 39.2826 | 983187.36
|  | 14.04.18 | 20:33 | 14.04.18 | 20:54 | 0:21 | 0 | 21 | [5 empty] | At Jayanagar-D/P, 'R' ph. to E/F, Dist.-105.78 k.m.
|  | 15.02.19 | 13:15 | 15.02.19 | 14:31 | 1:16 | 1 | 16 | [5 empty] | At Jayanagar-Tripped on A-Ph, B-Ph, Zone-I, Dist.- 6.81
260 | 132kVJaynagar-Sunabeda |  |  |  |  | 0.30069 | 0 | 58 | [7 empty] | 40 | 8760 | 99.99% | 38.6667 | 350400
|  | 26.05.18 | 13:39 | 26.05.18 | 20:52 | 7:13 | 0 | 58 | [5 empty] | At Jayanagar-'B' ph. to E/F, Zn.-II, Dist.-30.405 k.m ['Y' ph insulator damaged at Loc. No-91]
261 | 132kVJaynagar-Tentulikhunti |  |  |  |  | 0.19167 | 16 | 36 | [7 empty] | 56.4 | 8760 | 99.81% | 936.24 | 494064
|  | 17.11.18 | 17:51 | 17.11.18 | 18:32 | 0:41 | 0 | 41 | [5 empty] | Zone-1 fault
|  | 03.01.19 | 11:33 | 03.01.19 | 11:52 | 0:19 | 0 | 19 | [5 empty] | Incomer failure
|  | 10.01.19 | 11:03 | 10.01.19 | 11:20 | 0:17 | 0 | 17 | [5 empty] | Incomer failure
|  | 15.02.19 | 16:13 | 15.02.19 | 16:24 | 0:17 | 0 | 17 | [5 empty] | Incomer failure
|  | 15.02.19 | 11:53 | 15.02.19 | 12:15 | 0:22 | 0 | 22 | [5 empty] | Incomer failure
|  | 15.02.19 | 15:40 | 15.02.19 | 15:57 | 0:17 | 0 | 17 | [5 empty] | At Jayanagar-Tripped
|  | 15.02.19 | 16:54 | 15.02.19 | 17:04 | 0:10 | 0 | 10 | [5 empty] | Incomer failure
|  | 15.02.19 | 12:08 | 15.02.19 | 12:27 | 0:19 | 0 | 19 | [5 empty] | Incomer failure
|  | 15.02.19 | 17:29 | 15.02.19 | 17:50 | 0:21 | 0 | 21 | [5 empty] | Incomer failure
|  | 16.02.19 | 16:13 | 16.02.19 | 16:23 | 0:10 | 0 | 10 | [5 empty] | At Jayanagar-Tripped
|  | 23.02.19 | 16:49 | 23.02.19 | 16:59 | 0:10 | 0 | 10 | [5 empty] | At Jayanagar-Tripped
|  | 26.02.19 | 12:07 | 26.02.19 | 12:29 | 0:22 | 0 | 22 | [5 empty] | At Jayanagar-Tripped
|  | 26.02.19 | 17:30 | 26.02.19 | 17:50 | 0:20 | 0 | 20 | [5 empty] | At Jayanagar-Tripped
|  | 28.02.19 | 9:50 | 28.02.19 | 10:09 | 0:19 | 0 | 19 | [5 empty] | At Jayanagar-Tripped
|  | 28.02.19 | 17:33 | 28.02.19 | 17:45 | 0:12 | 0 | 12 | [5 empty] | At Jayanagar-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
262 | 132kVJharsuguda-Jharsuguda(T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.15 | 8760 | 100% | 0 | 1314
263 | 132kVJharsuguda-L & T |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.56 | 8760 | 100% | 0 | 276465.6
264 | 132kVJoda- Banaspani(T) |  |  |  |  | 0.055972 | 13 | 20 | [7 empty] | 2.99 | 8760 | 99.85% | 39.8667 | 26192.4
|  | 21.01.19 | 15:50 | 21.01.19 | 15:55 | 0:05 | 0 | 5 | [5 empty] | At Joda end:- B/U (O/C), Tripped Phase-A, IA=199.9A, IB=198.8A, IC=0A
|  | 29.01.19 | 5:01 | 29.01.19 | 5:19 | 0:18 | 0 | 18 | [5 empty] | At Joda end:- B/U (O/C), Tripped Phase-A, IA=199.9A, IB=198.8A, IC=0A
|  | 03.02.19 | 536:53 | 03.02.19 | 537:50 | 0:58 | 0 | 57 | [5 empty] | At Joda end:- B/U (O/C), Tripped Phase-A, IA=201.3A, IB=200.1A, IC=0A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
265 | 132kVJoda -Barbil |  |  |  |  | 0.0125 | 18 | 4 | [7 empty] | 9.82 | 8760 | 99.79% | 177.4147 | 86023.2
|  | 07.04.18 | 17:58 | 07.04.18 | 18:16 | 0:18 | 0 | 18 | [5 empty] | At Joda-'R'ph. to E/F
|  | 02.05.18 | 17:47 | 02.05.18 | 18:04 | 0:17 | 0 | 17 | [5 empty] | At Joda-D/P, Zn.-I
|  | 17.05.18 | 6:42 | 17.05.18 | 11:40 | 4:58 | 4 | 58
|  | 15.03.19 | 19:15 | 15.03.19 | 19:46 | 0:31 | 0 | 31 | [5 empty] | At Barbil end:-D.P relay.Zone-1 ,Distance-6.67 km ,Fault current:-R-ph=451.2 amp,Y ph= 195.6 amp B-ph=337.0 amp At Joda end:-Zone-1.Distance 6:06 Km Km,Fault current:-R-ph=4.919 kA.Y -ph=200 Amp,B-ph=331 amp neutral current=4.399 kA [Heavy rainfall and thundersome during the intrupption priod.]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
266 | 132kVJoda-FAP |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.03 | 8760 | 100% | 0 | 9022.8
267 | 132kVJoda-Kenduposi |  |  |  |  | 1900-01-13 04:05 | 14 | 17 | [7 empty] | 49.92 | 8760 | 99.84% | 713.024 | 437299.2
|  | 27.02.19 | 1:38 | 27.02.19 | 15:55 | 14.17 | 14 | 17 | [5 empty] | fdr tripped only at Joda end. At Joda end:- D.P, Dist = 26.131Km, Zone-1, L1-N, IL1=1633.22A, IL2=41.38A, IL3=46.19A, IN=1591.58A A big tree has fallen over R-Ph conductor between Loc-214 & 215.
|  | 15.03.19 | 13:55 | 15.03.19 | 14:52 | 0:57 | 0 | 57 | [5 empty] | D/P relay,Distance55.68 Km L2-N. Il1=313.33 amp,Il2=179910 Amp.Il3=223.56 AmpIn=127.89 amp
|  | 28.03.19 | 9:18 | 28.03.19 | 9:40 | 0:22 | 0 | 22 | [5 empty] | At JODA end-B/U Relay, Dir. O/C Trip, IL1=0.44 KA, IL2=0.56 KA, IL3=0.58ka At Kenduposi end= O/C tripped, R-Y Phase.
268 | 132kVJoda-Palasponga |  |  |  |  | 0.28181 | 14 | 44 | [7 empty] | 42 | 8760 | 99.83% | 618.8 | 367920
|  | 20.09.18 | 10:04 | 20.09.18 | 14:18 | 4:14 | 0 | 21 | [5 empty] | At Joda-D/P, Dist.-6.2493 k.m. ['R' ph. Jumper snapped at Loc. No.-15]At 10:25 hrs. Polasponga availed P/S from Karanjia end.
|  | 04.10.18 | 13:27 | 04.10.18 | 13:29 | 0:02 | 0 | 5 | [5 empty] | O/C, Ia= 416.9A, Ib= 338.3A, Ic=335.5A, In= 0.04A, Ig=2.83A
|  | 26.10.18 | 10:59 | 26.10.18 | 11:02 | 00:03 | 0 | 3 | [5 empty] | At Palasponga-O/C, Ia= 421.2A, Ib= 326.6A, Ic=329.7A, In= 0.02A, Ig=2.94A
|  | 06.12.18 | 18:09 | 06.12.18 | 18:11 | 0:02 | 0 | 2 | [5 empty] | TRIPPED FROM JODA END WITH E/F
|  | 12.12.18 | 13:35 | 12.12.18 | 13:37 | 0:02 | 0 | 2 | [5 empty] | O/C, Ia= 407.8A, Ib= 318.5A, Ic=321.7A, In= 0.04A, Ig= 1.65A
|  | 17.12.18 | 17:00 | 17.12.18 | 17:03 | 0:03 | 0 | 3 | [5 empty] | O/C,E/F Ia= 338.2A, Ib= 381.5A, Ic=1340.4A, In= 0.09A, Ig= 981.08A
|  | 03.11.18 | 0.74583 | 03.11.18 | 17:58 | 0:04 | 0 | 4 | [5 empty] | At Palasponga-Tripped on O/C
|  | 03.11.18 | 17:54 | 03.11.18 | 17:58 | 0:04 | 0 | 4 | [5 empty] | At Palaspanga-O/C, Ia= 413.5A, Ib= 349.6A, Ic=276.0A, In= 6A, Ig=5.06A
|  | 09.11.18 | 10:48 | 09.11.18 | 10:50 | 0:02 | 0 | 2 | [5 empty] | At Palasponga-Tripped on O/C
|  | 10.11.18 | 8:32 | 10.11.18 | 8:34 | 0:02 | 0 | 2 | [5 empty] | At Palasponga-Tripped on O/C, Ia= 413.5A, Ib= 349.6A, Ic=276.0A, In= 6A, Ig=5.06A
|  | 16.11.18 | 20:31 | 16.11.18 | 20:35 | 0:04 | 0 | 4 | [5 empty] | At Palasponga-Tripped on O/C, Ia= 413.5A, Ib= 349.6A, Ic=276.0A, In= 6A, Ig=5.06A
|  | 19.11.18 | 20:24 | 19.11.18 | 20:28 | 0:04 | 0 | 4 | [5 empty] | At Palasponga-Tripped on O/C
|  | 25.11.18 | 7:15 | 25.11.18 | 7:21 | 0:06 | 0 | 6 | [5 empty] | At Palasponga-Tripped on O/C
|  | 06.12.18 | 18:09 | 06.12.18 | 18:11 | 0:02 | 0 | 2 | [5 empty] | At Joda-Tripped on E/F
|  | 12.12.18 | 13:35 | 12.12.18 | 13:37 | 0.02 | 0 | 2 | [5 empty] | At Joda-Tripped on O/C, Ia= 407.8A, Ib= 318.5A, Ic=321.7A, In= 0.04A, Ig= 1.65A
|  | 17.12.18 | 17:00 | 17.12.18 | 17:03 | 0:03 | 0 | 3 | [5 empty] | O/C,E/F Ia= 338.2A, Ib= 381.5A, Ic=1340.4A, In= 0.09A, Ig= 981.08A
|  | 22.12.18 | 11:54 | 22.12.18 | 11:58 | 0:04 | 0 | 4 | [5 empty] | At Palasponga-Tripped on O/C
|  | 25.12.18 | 7:45 | 25.12.18 | 7:49 | 0:04 | 0 | 4 | [5 empty] | At Palasponga-Tripped on O/C
|  | 10.01.19 | 7:59 | 10.01.19 | 8:01 | 0:02 | 0 | 2 | [5 empty] | Tripped on O/C
|  | 30.01.19 | 19:27 | 30.01.19 | 19:29 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 15.02.19 | 18:39 | 15.02.19 | 18:43 | 0:04 | 0 | 4 | [5 empty] | At Joda-Tripped on O/C
|  | 16.02.19 | 1:58 | 16.02.19 | 2:04 | 0:06 | 0 | 6 | [5 empty] | At Joda-Tripped on O/C
|  | 16.02.19 | 2:01 | 16.02.19 | 2:19 | 0:18 | 0 | 18 | [5 empty] | source failure
|  | 18.02.19 | 11:08 | 18.02.19 | 11:13 | 0:05 | 0 | 5 | [5 empty] | At Joda-Tripped on O/C
|  | 26.02.19 | 15:21 | 26.02.19 | 15:33 | 0:12 | 0 | 12 | [5 empty] | At Joda-Tripped
|  | 27.02.19 | 1:34 | 27.02.19 | 1:47 | 0:13 | 0 | 13 | [5 empty] | At Joda-Tripped
|  | 27.02.19 | 1:34 | 27.02.19 | 1:47 | 0:13 | 0 | 13 | [5 empty] | At Joda-Tripped
|  | 08.03.19 | 13:15 | 08.03.19 | 13:27 | 00:12 | 0 | 12 | [5 empty] | O/C (B PH), Ia= 205.2A, Ib= 312.8A, Ic=1024.5A, In= 0.14A, Ig= 748.56A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
269 | 132kV Kamakhya Nagar -Kalarangi-Duburi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 74.84 | 8760 | 100% | 0 | 655598.4
270 | 132kV Kantabanji- Kantabanji Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4 | 8760 | 100% | 0 | 35040
271 | 132kV Karanjia-Palasponga |  |  |  |  | 0.0027778 | 0 | 4 | [7 empty] | 84 | 8760 | 100% | 5.6 | 735840
|  | 17.12.18 | 17:00 | 17.12.18 | 17:04 | 0:04 | 0 | 4 | [5 empty] | E/F WITH DP ZONE -1
272 | 132kV Karanjia-Dhenkikote |  |  |  |  | 0.29167 | 14 | 19 | [7 empty] | 41.902 | 8760 | 99.84% | 599.897 | 367061.52
|  | 11.01.19 | 8:00 | 11.01.19 | 15:00 | 7:00 | 0 | 7 | [5 empty] | At Karanjia -Tripped
|  | 11.02.19 | 10:31 | 11.02.19 | 10:39 | 0:08 | 0 | 8 | [5 empty] | At Kuchei-ICT tripped At Karanjia-Tripped
|  | 31.03.19 | 21:28 | 31.03.19 | 23:32 | 2:04 | 2 | 4 | [5 empty] | At Karanjia-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
273 | 132kV Katapalli-Sambalpur |  |  |  |  | 0.0041667 | 0 | 21 | [7 empty] | 22.25 | 8760 | 100% | 7.7875 | 194910
|  | 28.11.18 | 17:27 | 28.11.18 | 17:33 | 0:06 | 0 | 6 | [5 empty] | At Katapali-Tripped
|  | 29.12.18 | 17:23 | 29.12.18 | 17:38 | 0:15 | 0 | 15 | [5 empty] | At Katapalli-Tripped on E/F
274 | 132kV Sambalpur-Rairakhol |  |  |  |  | 0.042361 | 1 | 1 | [7 empty] | 63.46 | 8760 | 99.99% | 64.5177 | 555909.6
|  | 26.02.19 | 19:08 | 26.02.19 | 19:10 | 0:02 | 0 | 2 | [5 empty] | At Rairakhol-Tripped On E/F
|  | 17.03.19 | 16:39 | 17.03.19 | 17:38 | 0:59 | 0 | 59 | [5 empty] | Tripped on 'Y' phase, B N, Zone-I Distance Protection operated, Fault distance = 39.07Km, IA= 13.51A, IB=848.3A, IC= 14.21A, [Due to heavy wind]
275 | 132kV Kendrapada-Marshaghai ckt-I |  |  |  |  | 0.11319 | 14 | 43 | [7 empty] | 16.6 | 8760 | 99.83% | 244.2967 | 145416
|  | 19.10.18 | 12:42 | 19.10.18 | 13:32 | 0:50 | 0 | 50 | [5 empty] | At Kendrapada-Tripped BUS insulator punture at paradeep end .
|  | 12.11.18 | 18:40 | 12.11.18 | 18:57 | 0:17 | 0 | 17 | [5 empty] | At Kendrapara-DP RELAY,E/F WITH M/R
|  | 13.01.19 | 13:12 | 13.01.19 | 13:45 | 0:33 | 0 | 33 | [5 empty] | Trip On E/F With M/R
|  | 25.01.19 | 10:48 | 25.01.19 | 11:13 | 0:25 | 0 | 25 | [5 empty] | At Paradeep-220KV MAIN BUS-I B-PH BUS CONDUCTOR(SECTION) AFTER(ESSAR-II&50MVA) SNAPPED DUE TO PUNCTURE OF INSULATOR & PULL OUT THE WHOLE SYSTEM At Kendrapara-Trip On E/F With M/R
|  | 17.03.19 | 19:19 | 17.03.19 | 19:34 | 0:15 | 0 | 15 | [5 empty] | TRIP ON E/F With M/R
|  | 26.03.19 | 20:31 | 26.03.19 | 20:54 | 0:23 | 0 | 23
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
276 | 132kV Marshaghai-Paradeep ckt-I |  |  |  |  | 0.13681 | 14 | 40 | [7 empty] | 20.01 | 8760 | 99.83% | 293.48 | 175287.6
|  | 16.01.19 | 16:43 | 16.01.19 | 16:46 | 0:03 | 0 | 3 | [5 empty] | At Paradeep-Tripped
|  | 22.01.19 | 3:04 | 22.01.19 | 3:10 | 0:06 | 0 | 6 | [5 empty] | At New Duburi-DP Relay Operated At Both Ends ,Zone-II,B Ph -E/F,Fault Current-2.03 Ka.Distance-99.7 Km. At Paradeep-TRIPPED ON E/F,C-N,D-14.8KM,Z-1 (DUE TO SEVERE FOG) At Kendrapara-Trip On E/F With M/R
|  | 22.01.19 | 19:04 | 22.01.19 | 19:19 | 0:15 | 0 | 15 | [5 empty] | At Paradeep-Tripped
|  | 25.01.19 | 10:48 | 25.01.19 | 11:13 | 0:25 | 0 | 25 | [5 empty] | At Paradeep-220KV MAIN BUS-I B-PH BUS CONDUCTOR(SECTION) AFTER(ESSAR-II&50MVA) SNAPPED DUE TO PUNCTURE OF INSULATOR & PULL OUT THE WHOLE SYSTEM At Kendrapara-Trip On E/F With M/R
|  | 02.02.19 | 14:13 | 02.02.19 | 14:21 | 0:08 | 0 | 0 | [5 empty] | At Paradeep-Tripped
|  | 07.02.19 | 7:57 | 07.02.19 | 8:02 | 0:05 | 0 | 5 | [5 empty] | At Paradeep-Tripped
|  | 17.02.19 | 19:10 | 17.02.19 | 19:14 | 0:04 | 0 | 4 | [5 empty] | At Paradeep-Tripped
|  | 20.02.19 | 6:55 | 20.02.19 | 7:10 | 0:15 | 0 | 15 | [5 empty] | At Paradeep-Tripped
|  | 20.02.19 | 19:12 | 20.02.19 | 19:17 | 0:05 | 0 | 5 | [5 empty] | At Paradeep-Tripped
|  | 20.02.19 | 19:18 | 20.02.19 | 19:28 | 0:10 | [7 empty] | At Paradeep-Tripped
|  | 27.02.19 | 1:43 | 27.02.19 | 1:51 | 0:08 | 0 | 21 | [5 empty] | At Paradeep-Tripped
|  | 27.02.19 | 1:56 | 27.02.19 | 2:08 | 0:12
|  | 27.02.19 | 2:20 | 27.02.19 | 2:40 | 0:20
|  | 17.03.19 | 19:19 | 17.03.19 | 19:34 | 0:15 | 0 | 15 | [5 empty] | TRIP ON E/F With M/R
|  | 26.03.19 | 20:31 | 26.03.19 | 20:54 | 0:23 | 0 | 23 | [5 empty] | H/T at Paradeep end
|  | 26.03.19 | 20:31 | 26.03.19 | 20:54 | 0:23 | 0 | 23
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
277 | 132kV Kendrapada-Paradeep Ckt-II |  |  |  |  | 0.14028 | 15 | 17 | [7 empty] | 34.774 | 8760 | 99.83% | 531.4626 | 304620.24
|  | 19.10.18 | 12:42 | 19.10.18 | 13:31 | 0:49 | 0 | 49 | [5 empty] | At Kendrapada-Tripped BUS insulator punture at paradeep end .
|  | 12.11.18 | 18:40 | 12.11.18 | 18:55 | 0:15 | 0 | 15 | [5 empty] | At Kendrapara-DP RELAY,E/F WITH M/R
|  | 13.01.19 | 13:12 | 13.01.19 | 13:50 | 0:38 | 0 | 38 | [5 empty] | Trip On E/F With M/R
|  | 22.01.19 | 3:04 | 22.01.19 | 3:10 | 0:06 | 0 | 6 | [5 empty] | At New Duburi-DP Relay Operated At Both Ends ,Zone-II,B Ph -E/F,Fault Current-2.03 Ka.Distance-99.7 Km. At Paradeep-TRIPPED ON E/F,C-N,D-14.8KM,Z-1 (DUE TO SEVERE FOG) At Kendrapara-Trip On E/F With M/R
|  | 25.01.19 | 10:48 | 25.01.19 | 11:13 | 0:25 | 0 | 24 | [5 empty] | At Paradeep-220KV MAIN BUS-I B-PH BUS CONDUCTOR(SECTION) AFTER(ESSAR-II&50MVA) SNAPPED DUE TO PUNCTURE OF INSULATOR & PULL OUT THE WHOLE SYSTEM At Kendrapara-Trip On E/F With M/R
|  | 27.02.19 | 1:44 | 27.02.19 | 1:51 | 0:07 | 0 | 21 | [5 empty] | At Paradeep-Tripped
|  | 27.02.19 | 1:56 | 27.02.19 | 2:08 | 0:12
|  | 27.02.19 | 2:34 | 27.02.19 | 2:40 | 0:06
|  | 17.03.19 | 19:19 | 17.03.19 | 19:34 | 0:15 | 0 | 15 | [5 empty] | TRIP ON E/F With M/R
|  | 26.03.19 | 20:31 | 26.03.19 | 20:54 | 0:23 | 0 | 23 | [5 empty] | At Paradeep-H/T
|  | 31.03.19 | 23:00 | 31.03.19 | 23:06 | 0:06 | 0 | 6 | [5 empty] | TRIP ON M/R at Kendrapara
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
278 | 132kV Kendrapada-Pattamundai |  |  |  |  | 0.026389 | 15 | 4 | [7 empty] | 19.5 | 8760 | 99.83% | 293.8 | 170820
|  | 19.10.18 | 12:42 | 19.10.18 | 13:20 | 0:38 | 0 | 38 | [5 empty] | At Kendrapada-Tripped BUS insulator punture at paradeep end .
|  | 25.10.18 | 14:50 | 25.10.18 | 15:10 | 0:20 | 0 | 20 | [5 empty] | At Pattamundai-E/F (B- phase ) & M/R due to bursting of insulator string in 132 KV Main Bus(B/C section )
|  | 26.10.18 | 14:50 | 26.10.18 | 15:10 | 0:20 | 0 | 20 | [5 empty] | E/F (B-Phase ) & M/R (bursting of B- pase Insulator String of Main Bus Section -II(bus- coupler section ))
|  | 18.01.19 | 4:27 | 18.01.19 | 4:35 | 0:08 | 0 | 8 | [5 empty] | At Pattamundai- E/F (Hi Set - Y Phase ) & M/R
|  | 18.01.19 | 4:55 | 18.01.19 | 4:57 | 0:02 | 0 | 2
|  | 18.01.19 | 5:08 | 18.01.19 | 5:12 | 0:04 | 0 | 4
|  | 18.01.19 | 5:45 |  | 5:49 | 0:04 | 0 | 4
|  | 21.01.19 | 1:28 | 21.01.19 | 1:31 | 0:03 | 0 | 3 | [5 empty] | At Pattamundai- E/F ( Y Phase ) & M/R
|  | 22.01.19 | 3:04 | 22.01.19 | 3:12 | 0:08 | 0 | 8 | [5 empty] | At New Duburi-DP Relay Operated At Both Ends ,Zone-II,B Ph -E/F,Fault Current-2.03 Ka.Distance-99.7 Km. At Paradeep-TRIPPED ON E/F,C-N,D-14.8KM,Z-1 (DUE TO SEVERE FOG) At Kendrapara-Trip On E/F With M/R
|  | 24.01.19 | 15:56 | 24.01.19 | 16:06 | 0:10 | 0 | 10 | [5 empty] | At Pattamundai- E/F ( Y Phase ) & M/R
|  | 27.02.19 | 1:44 | 27.02.19 | 1:51 | 0:07 | 0 | 21 | [5 empty] | TRIP ON E/F With M/R
|  | 27.02.19 | 1:52 | 27.02.19 | 2:12 | 0:20 | [7 empty] | TRIP ON E/F With M/R
|  | 27.02.19 | 2:12 | 27.02.19 | 2:44 | 0:32 | [7 empty] | TRIP ON E/F With M/R
|  | 17.03.19 | 19:19 | 17.03.19 | 19:52 | 0:33 | 0 | 33 | [5 empty] | TRIP ON E/F With M/R
|  | 26.03.19 | 21:54 | 26.03.19 | 21:56 | 0:02 | 0 | 7 | [5 empty] | TRIP ON E/F,O/C With M/R
|  | 17.03.19 | 22:09 | 17.03.19 | 22:16 | 0:07
|  | 28.03.19 | 23:25 | 28.03.19 | 23:29 | 0:04 | 0 | 4 | [5 empty] | Tripped at Pattamundai-On E/F & M/R.Distance Protection and M/ R opertaed in 132 KV PMI - Olaver Ckt - I (5.4 Km) ,D/P, E/F & M/R operated in 132 KV Kendrapara Incomer
|  | 30.03.19 | 21:35 | 30.03.19 | 21:37 | 0:02 | 0 | 2 | [5 empty] | E/F & M/R operated in 132 KV Kendrapara Incomer
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
279(a) | 132kV Kesinga-Bhawanipatna |  |  |  |  | 0.16875 | 16 | 3 | [7 empty] | 40.61 | 8760 | 99.82% | 651.7905 | 355743.6
|  | 02.10.18 | 15:03 | 02.10.18 | 15:07 | 0:04 | 0 | 4 | [5 empty] | MASTER RELAY TRIPPED AT KESINGA GRID
|  | 03.10.18 | 18:42 | 03.10.18 | 18:52 | 0:10 | 0 | 10 | [5 empty] | At Therubali-Tripped on over load.
|  | 04.10.18 | 19:10 | 04.10.18 | 19:17 | 0:07 | 0 | 7 | [5 empty] | At Therubali-Tripped on over load.
|  | 06.10.18 | 17:55 | 06.10.18 | 18:05 | 0:10 | 0 | 10 | [5 empty] | At Therubali-Tripped on over load.
|  | 07.10.18 | 8:25 | 07.10.18 | 8:38 | 0:13 | 0 | 13 | [5 empty] | At Bolangir-Tripped on over load
|  | 07.10.18 | 9:55 | 07.10.18 | 10:05 | 0:10 | 0 | 10 | [5 empty] | At Bolangir-Tripped on over load
|  | 11.10.18 | 7:20 | 11.10.18 | 8:11 | 0:51 | 0 | 51 | [5 empty] | At Theruvali-Tripped on D/P( due to tree falls on rphase conductor betwwen loc 45 and 46 during cyclone titli)
|  | 12.10.18 | 17:30 | 12.10.18 | 17:50 | 0:20 | 0 | 20 | [5 empty] | At-Bhawanipatna Tripped
|  | 26.10.18 | 18:20 | 26.10.18 | 18:28 | 0:08 | 0 | 8 | [5 empty] | At Theruvali-Tripped
|  | 07.01.19 | 10:51 | 07.01.19 | 11:17 | 0:26 | 0 | 26 | [5 empty] | At Kesinga-Tripped
|  | 30.01.19 | 18:21 | 30.01.19 | 18:31 | 0:10 | 0 | 10 | [5 empty] | From Kesinga End
|  | 24.01.19 | 21:07 | 24.01.19 | 21:17 | 0:10 | 0 | 10 | [5 empty] | From Kesinga End
|  | 03.02.19 | 16:00 | 03.02.19 | 16:17 | 0:17 | 0 | 17 | [5 empty] | At Kesinga-Tripped
|  | 04.02.19 | 6:55 | 04.02.19 | 7:00 | 0:05 | 0 | 5 | [5 empty] | At Kesinga-Tripped
|  | 13.03.19 | 5:20 | 13.03.19 | 5:30 | 0:10 | 0 | 10 | [5 empty] | At Theruvali-Tripped
|  | 14.03.19 | 20:52 | 14.03.19 | 21:05 | 0:13 | 0 | 13 | [5 empty] | At Kesinga-Tripped
|  | 31.03.19 | 16:08 | 31.03.19 | 16:26 | 0:19 | 0 | 19 | [5 empty] | At Kesinga-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
279(b) | 132kV Kesinga-Khariar |  |  |  |  | 0.0020833 | 14 | 42 | [7 empty] | 58.5 | 8760 | 99.83% | 859.95 | 512460
|  | 04.10.18 | 12:58 | 04.10.18 | 13:01 | 0:03 | 0 | 8 | [5 empty] | At Saintala-H/T (Due to maintenance work at Sadeipali Grid)
|  | 04.10.18 | 12:58 | 04.10.18 | 13:01 | 0:03 | 0 | 3 | [5 empty] | At Kesinga-H/T(Change Over after completetion of work)
|  | 07.10.18 | 8:19 | 07.10.18 | 8:33 | 0:14 | 0 | 14 | [5 empty] | Tripped from Balangir end.
|  | 07.10.18 | 9:55 | 07.10.18 | 10:02 | 0:07 | 0 | 7 | [5 empty] | At Bolangir-Tripped on over load
|  | 10.10.18 | 10:50 | 10.10.18 | 10:55 | 0:05 | 0 | 5 | [5 empty] | At Saintala-H/T (132KV Breaker Erection at Sadeipali grid resumed from kesinga.)
|  | 10.10.18 | 13:39 | 10.10.18 | 13:43 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-H/T(Change Over after completetion of work)
|  | 11.10.18 | 8:08 | 11.10.18 | 8:11 | 0:03 | 0 | 3 | [5 empty] | At Saintala-H/T
|  | 16.10.18 | 9:56 | 16.10.18 | 10:09 | 0:13 | 0 | 13 | [5 empty] | Tripped from Balangir end.
|  | 23.10.18 | 12:36 | 23.10.18 | 12:46 | 0:10 | 0 | 10 | [5 empty] | At Bolangir-Tripped on Y-Phase E/F
|  | 24.10.18 | 0:28 | 24.10.18 | 0:38 | 0:10 | 0 | 10 | [5 empty] | At saintala-Tripped on B-phase E/F
|  | 25.10.18 | 13:24 | 25.10.18 | 13:28 | 0:04 | 0 | 4 | [5 empty] | At Kesinga-H/T(Change Over after completetion of work)
|  | 27.10.18 | 0:07 | 27.10.18 | 0:13 | 0:06 | 0 | 6 | [5 empty] | At Kesing-Tripped on E/F
|  | 29.12.18 | 9:05 | 29.12.18 | 11:26 | 2:21 | 0 | 21 | [5 empty] | At Kesinga-Tripped (Khariar O/G Feeder Wavetrap(B-Phase) Brust. )
|  | 12.01.19 | 18:06 | 12.01.19 | 18:13 | 0:07 | 0 | 7 | [5 empty] | Overcurrent Y Phase
|  | 30.01.19 | 18:27 | 30.01.19 | 18:29 | 0:02 | 0 | 2 | [5 empty] | Overcurrent B-Phase
|  | 03.02.19 | 6:59 | 03.02.19 | 7:01 | 0:02 | 0 | 2 | [5 empty] | At Saintala-Tripped on O/L
|  | 03.02.19 | 7:39 | 03.02.19 | 7:41 | 0:02 | 0 | 2
|  | 06.02.19 | 19:44 | 06.02.19 | 19:47 | 19:47 | 0 | 3 | [5 empty] | At Saintala-Tripped on O/L
|  | 08.02.19 | 20:30 | 08.02.19 | 20:35 | 0:05 | 0 | 5 | [5 empty] | Tripped On overloading
|  | 14.02.19 | 8:21 | 14.02.19 | 8:27 | 0:06 | 0 | 6 | [5 empty] | At Saintala-Tripped on over load
|  | 20.02.19 | 17:06 | 20.02.19 | 17:11 | 0:05 | 0 | 5 | [5 empty] | At Saintala-Tripped on O/L
|  | 20.02.19 | 17:18 | 20.02.19 | 17:20 | 0:02 | 0 | 2
|  | 20.02.19 | 21:31 | 20.02.19 | 21:34 | 0:03 | 0 | 3 | [5 empty] | At Saintala-Tripped on O/L
|  | 19.02.19 | 16:59 | 19.02.19 | 17:08 | 0:09 | 0 | 9 | [5 empty] | At Sadeipali-Tripped on O/L
|  | 19.02.19 | 17:11 | 19.02.19 | 17:19 | 0:08 | 0 | 8
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
280 | 132kV Kesinga-Kesinga RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.952 | 7392 | 100% | 0 | 36605.184
281 | 132kV Kesinga-Kesinga Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.48 | 7392 | 100% | 0 | 84860.16
282 | 132kV Kesinga-Powmex |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.532 | 8760 | 100% | 0 | 127300.32
283 | 132kV Kesinga-Saintala |  |  |  |  | 0.0055556 | 13 | 49 | [7 empty] | 33.2 | 8760 | 99.84% | 458.7133 | 290832
|  | 04.10.18 | 11:46 | 04.10.18 | 11:54 | 0:08 | 0 | 8 | [5 empty] | At Saintala-H/T (Due to maintenance work at Sadeipali Grid)
|  | 07.10.18 | 8:19 | 07.10.18 | 8:33 | 0:14 | 0 | 14 | [5 empty] | Tripped from Balangir end.
|  | 07.10.18 | 9:55 | 07.10.18 | 10:02 | 0:07 | 0 | 7 | [5 empty] | At Bolangir-Tripped on over load
|  | 10.10.18 | 10:50 | 10.10.18 | 10:55 | 0:05 | 0 | 5 | [5 empty] | At Saintala-H/T (132KV Breaker Erection at Sadeipali grid resumed from kesinga.)
|  | 24.10.18 | 0:28 | 24.10.18 | 0:38 | 0:10 | 0 | 10 | [5 empty] | At saintala-Tripped on B-phase E/F
|  | 27.10.18 | 0:07 | 27.10.18 | 0:13 | 0:06 | 0 | 6 | [5 empty] | At saintala-Tripped on E/F
|  | 04.11.18 | 5:35 | 04.11.18 | 5:42 | 0:07 | 0 | 7 | [5 empty] | At Saintala-Tripped on Earth fault from saintala.
|  | 28.11.18 | 17:57 | 28.11.18 | 18:02 | 0:05 | 0 | 5 | [5 empty] | Tripped on Earth fault from saintala.
|  | 29.11.18 | 13:28 | 29.11.18 | 13:29 | 0:01 | 0 | 1 | [5 empty] | Tripped on B-ph over current fault from saintala.
|  | 29.11.18 | 20:34 | 29.11.18 | 20:42 | 0:08 | 0 | 8 | [5 empty] | Tripped on Earth fault from saintala.
|  | 27.12.18 | 9:12 | 27.12.18 | 9:13 | 0:01 | 0 | 1 | [5 empty] | Tripped from Saintala
|  | 18.12.18 | 20:41 | 18.12.18 | 20:44 | 0:03 | 0 | 3 | [5 empty] | Tripped from Saintala (Pullout of 132KV Kesinga O/G at GSS Saintala)
|  | 12.01.19 | 18:06 | 12.01.19 | 18:13 | 0:07 | 0 | 7 | [5 empty] | At Saintala-Overcurrent B-Phase
|  | 23.01.19 | 18:12 | 23.01.19 | 18:21 | 0:09 | 0 | 9 | [5 empty] | At Saintala-Overcurrent B-Phase
|  | 30.01.19 | 18:27 | 30.01.19 | 18:29 | 0:02 | 0 | 2 | [5 empty] | At Saintala-Overcurrent B-Phase
|  | 10.03.19 | 19:18 | 10.03.19 | 19:25 | 0:07 | 0 | 7 | [5 empty] | Tripped from Saintala-On O/L
|  | 11.03.19 | 14:25 | 11.03.19 | 14:29 | 0:04 | 0 | 4 | [5 empty] | Tripped from Saintala-On O/L
|  | 15.03.19 | 19:17 | 15.03.19 | 19:22 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala-On O/L
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
284 | 132kV Kharagprasad-Kharagprasad (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.17 | 8760 | 100% | 0 | 10249.2
285 | 132kV Kharagprasad-MGM Ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.14 | 8760 | 100% | 0 | 62546.4
286 | 132kV Kharagprasad-Nabhabharat Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.577 | 8760 | 100% | 0 | 5054.52
287 | 132kV Kharagprasad-Nabhabharat Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.577 | 8760 | 100% | 0 | 5054.52
288 | 132kV Kharagprasad-Samal Metallic |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.03 | 8760 | 100% | 0 | 9022.8
289 | 132 kV Khariar - Kantabanji |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33 | 8760 | 100% | 0 | 289080
290
291 | 132 kV Khariar - Nuapara |  |  |  |  | 0.16458 | 19 | 15 | [7 empty] | 77.232 | 8760 | 99.78% | 1486.716 | 676552.32
|  | 11.04.18 | 10:18 | 11.04.18 | 14:15 | 3:57 | 3 | 57 | [5 empty] | At Khariar, D/P, Zn.-I, Dist.-57.59 k.m. [Tree fell on line between Loc No.-192 & 193]
|  | 07.10.18 | 8:19 | 07.10.18 | 8:33 | 0:14 | 0 | 14 | [5 empty] | Tripped from Balangir end.
|  | 07.10.18 | 9:55 | 07.10.18 | 10:02 | 0:07 | 0 | 7 | [5 empty] | At Bolangir-Tripped on over load
|  | 10.10.18 | 10:49 | 10.10.18 | 10:54 | 0:05 | 0 | 5 | [5 empty] | At Saintala-H/T (132KV Breaker Erection at Sadeipali grid resumed from kesinga.)
|  | 11.10.18 | 8:08 | 11.10.18 | 8:11 | 0:03 | 0 | 3 | [5 empty] | At Saintala-H/T
|  | 16.10.18 | 9:56 | 16.10.18 | 10:09 | 0:13 | 0 | 13 | [5 empty] | Tripped from Balangir end.
|  | 23.10.18 | 12:36 | 23.10.18 | 12:46 | 0:10 | 0 | 10 | [5 empty] | At Bolangir-Tripped on Y-Phase E/F
|  | 24.10.18 | 0:28 | 24.10.18 | 0:38 | 0:10 | 0 | 10 | [5 empty] | At saintala-Tripped on B-phase E/F
|  | 27.10.18 | 0:07 | 27.10.18 | 0:12 | 0:05 | 0 | 5 | [5 empty] | At Kesing-Tripped on E/F
|  | 12.01.19 | 18:06 | 12.01.19 | 18:13 | 0:07 | 0 | 7 | [5 empty] | At Nuapda-Overcurrent Y Phase
|  | 23.01.19 | 18:12 | 23.01.19 | 18:21 | 0:09 | 0 | 9 | [5 empty] | At Nuapada-Overcurrent R-Phase
|  | 30.01.19 | 18:27 | 30.01.19 | 18:29 | 0:02 | 0 | 2 | [5 empty] | At Nuapda-Overcurrent B-Phase
|  | 03.02.19 | 6:59 | 03.02.19 | 7:01 | 0:02 | 0 | 2 | [5 empty] | At Saintala-Tripped on O/L
|  | 03.02.19 | 7:39 | 03.02.19 | 7:41 | 0:02 | 0 | 2
|  | 06.02.19 | 19:44 | 06.02.19 | 19:47 | 0:03 | 0 | 3 | [5 empty] | At Saintala-Tripped on O/L
|  | 08.02.19 | 20:30 | 08.02.19 | 20:35 | 0:05 | 0 | 5 | [5 empty] | Tripped from Tushra
|  | 14.02.19 | 8:21 | 14.02.19 | 8:27 | 0:06 | 0 | 6 | [5 empty] | At Saintala-Tripped on over load.
|  | 19.02.19 | 16:59 | 19.02.19 | 17:08 | 0:09 | 0 | 9 | [5 empty] | At Sadeipali-Tripped on O/L
|  | 19.02.19 | 17:11 | 19.02.19 | 17:19 | 0:08 | 0 | 8
|  | 20.02.19 | 17:06 | 20.02.19 | 17:11 | 0:05 | 0 | 5 | [5 empty] | At Sadeipali-Tripped on O/L
|  | 20.02.19 | 17:18 | 20.02.19 | 17:20 | 0:02 | 0 | 2
|  | 20.02.19 | 21:31 | 20.02.19 | 21:34 | 0:03 | 0 | 3 | [5 empty] | At Sadeipali-Tripped on O/L
|  | 05.03.19 | 18:46 | 05.03.19 | 18:55 | 0:09 | 0 | 9 | [5 empty] | Tripped Due to Over current on R-Ph
|  | 10.03.19 | 19:18 | 10.03.19 | 19:25 | 0:07 | 0 | 7 | [5 empty] | Tripped Due to Over current on Y-Ph
|  | 11.03.19 | 13:19 | 11.03.19 | 13:35 | 0:16 | 0 | 16 | [5 empty] | Tripped on E/F at Bolangir
|  | 14.03.19 | 21:04 | 14.03.19 | 21:07 | 0:03 | 0 | 3 | [5 empty] | At Khariar-Tripped on O/L
|  | 15.03.19 | 19:17 | 15.03.19 | 19:22 | 0:05 | 0 | 5 | [5 empty] | Tripped from Saintala-On O/L
|  | 31.03.19 | 16:09 | 31.03.19 | 16:35 | 0:28 | 0 | 28 | [5 empty] | Tripped from Sadeipali [Due to Distance protection fault at ACME and Tushra Line.]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
292 | 132kV Khurda-Argul-Shamuka |  |  |  |  | 0.0097222 | 0 | 6 | [7 empty] | 54.742 | 8760 | 100% | 5.4742 | 479539.92
|  | 09.02.19 | 2:51 | 09.02.19 | 3:05 | 0:14 | 0 | 6 | [5 empty] | Tripped only at khurda end.DP realay displayed a distance of 48.48KM from khurda end
|  | 31.03.19 | 16:56 | 31.03.19 | 19:23 | 2:27 | 0 | 7 | [5 empty] | At Shamuka-Distance Protection.Shamuka availed from Puri side
293 | 132kV Khurda-Kaipadar (T) |  |  |  |  | 0.0041667 | 0 | 6 | [7 empty] | 11.259 | 8760 | 100% | 1.1259 | 98628.84
|  | 09.02.19 | 2:51 | 09.02.19 | 2:57 | 0:06 | 0 | 6 | [5 empty] | O/C B-ᶲ,E/F,Earth wire snap near chhatipur,informed by staffs of traction
294 | 132kV Kuchei PG- Bangiriposhi |  |  |  |  | 0.62569 | 18 | 40 | [7 empty] | 31.526 | 8760 | 99.79% | 588.4853 | 276167.76
|  | 09.04.18 | 14:28 | 09.04.18 | 14:35 | 0:07 | 0 | 7 | [5 empty] | At Bangriposi-'B' ph to E/F, Zn-I, Dist-5.5 km
|  | 23.05.18 | 3:23 | 23.05.18 | 12:15 | 8:52 | 1 | 59 | [5 empty] | At Bangriposi- , Zn.-I, Ý' ph, to E/F, Dist.-12.5 k.m.At 05:22 hrs. Karanjia, Bangriposi availed P/S from Polasponga
|  | 06.06.18 | 7:45 | 06.06.18 | 8:29 | 0:44 | 0 | 44 | [5 empty] | At Baripada PG-Zn.-II, Dist.-16.83 k.m.
|  | 19.06.18 | 20:20 | 20.06.18 | 15:13 | 18:53 | 0 | 12 | [5 empty] | At Rairangpur-Tripped.['R' ph. CT burst at Rairangpur].At 20:32 hrs. Rairangpur availed P/S from Joda end
|  | 04.10.18 | 18:30 | 04.10.18 | 22:08 | 3:38 | 3 | 38 | [5 empty] | ICT Failure at PGCIL end
|  | 11.02.19 | 9:31 | 11.02.19 | 10:20 | 0:49 |  |  | 0 | 49 |  |  |  | Tripping of ICT at PGCIL Kuchei
|  | 11.02.19 | 10:32 | 11.02.19 | 10:51 | 0:19 |  |  | 0 | 19 |  |  |  | Tripping of ICT at PGCIL Kuchei
|  | 11.02.19 | 10:32 | 11.02.19 | 11:04 | 0:32 |  |  | 0 | 32 |  |  |  | At Kuchei-ICT tripped At Karanjia-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
295 | 132kV Bangiriposhi- Rairangapur |  |  |  |  | 0.62569 | 18 | 40 | [7 empty] | 34.602 | 8760 | 99.79% | 645.904 | 303113.52
|  | 09.04.18 | 14:28 | 09.04.18 | 14:35 | 0:07 | 0 | 7 | [5 empty] | At Bangriposi-'B' ph to E/F, Zn-I, Dist-5.5 km
|  | 23.05.18 | 3:23 | 23.05.18 | 12:15 | 8:52 | 1 | 59 | [5 empty] | At Bangriposi- , Zn.-I, Ý' ph, to E/F, Dist.-12.5 k.m.At 05:22 hrs. Karanjia, Bangriposi availed P/S from Polasponga
|  | 06.06.18 | 7:45 | 06.06.18 | 8:29 | 0:44 | 0 | 44 | [5 empty] | At Baripada PG-Zn.-II, Dist.-16.83 k.m.
|  | 19.06.18 | 20:20 | 20.06.18 | 15:13 | 18:53 | 0 | 12 | [5 empty] | At Rairangpur-Tripped.['R' ph. CT burst at Rairangpur].At 20:32 hrs. Rairangpur availed P/S from Joda end
|  | 04.10.18 | 18:30 | 04.10.18 | 22:08 | 3:38 | 3 | 38 | [5 empty] | ICT Failure at PGCIL end
|  | 11.02.19 | 9:31 | 11.02.19 | 10:20 | 0:49 |  |  | 0 | 49 |  |  |  | Tripping of ICT at PGCIL Kuchei
|  | 11.02.19 | 10:32 | 11.02.19 | 10:51 | 0:19 |  |  | 0 | 19 |  |  |  | Tripping of ICT at PGCIL Kuchei
|  | 11.02.19 | 10:32 | 11.02.19 | 11:04 | 0:32 |  |  | 0 | 32 |  |  |  | At Kuchei-ICT tripped At Karanjia-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
296 | 132kV Kuchei PG- Jaleswar ckt - I |  |  |  |  | 1899-12-31 00:02 | 25 | 11 | [7 empty] | 79.282 | 8760 | 99.71% | 1996.585 | 694510.32
|  | 22.05.18 | 19:49 | 22.05.18 | 21:26 | 1:37 | 0 | 4 | [5 empty] | At Jaleswar-D/P, Zn.-I,Dist.-94.1 k.m. At 19:53 hrs. Jaleswar availed P/S from Bhograi end
|  | 05.07.18 | 13:12 | 05.07.18 | 14:10 | 0:58 | 0 | 19 | [5 empty] | At Jaleswar-O/C, E/F, D/P At Baripada PG-D/P At 13:31 hrs. Jaleswar availed P/S from Basta end
|  | 04.10.18 | 18:28 | 05.01.18 | 5:23 | 10:55 | 10 | 55
|  | 07.02.19 | 14:28 | 07.02.19 | 16:12 | 1:44 | 0 | 0 | [5 empty] | At Jaleswar : Z1 , Y-PH to ground ,Distance - 25.2 KM ,fault current - R-362.5A , B-199.9A , Y- 838.1A At Kuchei: Z1 , Y-PH to ground ,Distance - 45.3 KM,fault current - R-362.8A , B-186.2A , Y- 1.890KA
|  | 11.02.19 | 9:31 | 11.02.19 | 10:10 | 0:39 |  |  | 0 | 39 |  |  |  | Tripping of ICT at PGCIL Kuchei
|  | 11.02.19 | 10:33 | 11.02.19 | 20:40 | 10:07 |  |  | 0 | 36 |  |  |  | At Kuchei-ICT tripped At Karanjia-Tripped
|  | 26.02.19 | 12:00 | 26.02.19 | 17:04 | 5:04 |  |  | 0 | 27 |  |  |  | At Kuchei end- Z1 , B-ph/E , dist.- 28KM , Fault Current B-Ph - 2KA .D/P Optd.,B-Ph Ground(Kuchei End),26.0Km. (Tripped due to stormy weather )
|  | 15.03.19 | 5:08 | 15.03.19 | 6:16 | 1:08 | 0 | 0 | [5 empty] | At Jaleswar end:- DP realy indication :- Distance-13.1KM , Y-phase to ground , foult current- 1091.6 A , Zone -1 At Kuchei end:- DP realy indication :- Distance -62.2KM , Yphase to ground , Foult current - 1.546KA
|  | 16.03.19 | 5:09 | 16.03.19 | 6:16 | 1:07 | 1 | 7 | [5 empty] | At Jaleswar-DP realy indication :- Distance-13.1KM , Y-phase to ground , foult current- 1091.6 A , Zone -1 At Kuchei-DP realy indication :- Distance -62.2KM , Yphase to ground , Foult current - 1.546KA
|  | 17.03.19 | 18:25 | 17.03.19 | 20:03 | 1:38 | 0 | 46 | [5 empty] | At Kuchei end DP realy indication :- Distance -37.6 KM , B-phase to ground , Foult current - 1.824KA , zone-1 .No power supply at Jaleswar grid due to at the same time 132KV Kuchei-Bhogarai fdr also tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
297 | 132kV Kuchei PG- Bhogarai |  |  |  |  | 0.018056 | 0 | 0 | [7 empty] | 101.907 | 8760 | 100% | 0 | 892705.32
|  | 11.02.19 | 9:30 | 11.02.19 | 9:56 | 0:26 |  |  | 0 | 26 |  |  |  | Tripping of ICT at PGCIL Kuchei
|  | 11.02.19 | 9:31 | 11.02.19 | 10:11 | 0:40 |  |  | 0 | 40 |  |  |  | Tripping of ICT at PGCIL Kuchei
|  | 11.02.19 | 10:32 | 11.02.19 | 11:08 | 0:36 |  |  | 0 | 36 |  |  |  | Tripping of ICT at PGCIL Kuchei
|  | 11.02.19 | 10:33 | 11.02.19 | 20:38 | 10:05 |  |  | 0 | 36 |  |  |  | Tripping of ICT at PGCIL Kuchei
|  | 26.02.19 | 12:00 | 26.02.19 | 16:13 | 4:13 | 0 | 0 | [5 empty] | At Kuchei end- Z1 , B-ph/E , dist.- 28KM , Fault Current B-Ph - 2KA .D/P Optd.,B-Ph Ground(Kuchei End),26.0Km. (Tripped due to stormy weather )
|  | 17.03.19 | 18:25 | 17.03.19 | 20:12 | 1:47 | 0 | 46 | [5 empty] | DP OPTD.,R-PH TO B-PH TO GROUND,ZN-1(50.5KM),IR-639.8A,IB-120.4A,IY-149.2A
298 | Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
299 | 132kV Kuchinda-Bamara(T)-Rajgangpur |  |  |  |  | 0.19236 | 16 | 31 | [7 empty] | 118.4 | 8760 | 99.81% | 1955.5733 | 1037184
|  | 10.10.18 | 10:59 | 10.10.18 | 11:10 | 0:11 | 0 | 11 | [5 empty] | AT BUDHIPADAR END -Tripped on D/P,ZONE 2, RYB- PHASE TRIP , L1-243A,L2-1117A,L3-276A, L2N LOOP. AT RAJGANGPUR -132KV RAILWAY -II FEEDER EARTH WIRE AND Y-PHASE CONDUCTOR SNAPING AT LOC. NO- 06
|  | 20.10.18 | 18:02 | 20.10.18 | 21:30 | 3:28 | 3 | 28 | [5 empty] | At Rajgangpur -Tripped,BGT,Z1, LOC 319.10KM, Ia-0 A, Ib=251A,Ic- 113A, In-255A, Ig=286A. (CT-JUMPER OF R-PHASE SNAPPED)
|  | 22.10.18 | 21:50 | 22.10.18 | 22:00 | 0:10 | 0 | 10 | [5 empty] | At Rajgangpur-Tripped on D/P,AGT, ZONE-1, LOC.NO- 64.22KM, Ia- 1418A, Ib-124A, Ig-1237A. At Kuchinda-Tripped on D/P,R-PHASE, DISTANCE-14.89 FAULT CURRENT-Ir-346.5A.
|  | 04.11.18 | 3:38 | 04.11.18 | 3:47 | 0:09 | 0 | 9 | [5 empty] | At-Kuchinda- Tripped on AGT , ZONE -I, IA-1459A IG-1258A N-1257A LOC NO-63.46KM
|  | 05.11.18 | 3:38 | 05.11.18 | 3:57 | 0:19 | 0 | 19 | [5 empty] | Trip ph A, Diastance trip Z 1, Fault duration 10:01ms
|  | 16.01.19 | 4:37 | 16.01.19 | 4:51 | 0:14 | 0 | 14 | [5 empty] | At Rajgangpur-Cgt Loc No-64.08 Ic-1478 In-1246 Ig-1246 Amps Zone-I At Kuchinda-D/P Zone-I Ioc No-18 B-Phase
|  | 15.02.19 | 12:59 | 15.02.19 | 13:05 | 0:06 | 0 | 0 | [5 empty] | Tripped On E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
300 | 132kV Lapanga - Rengali RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.308 | 8760 | 100% | 0 | 107818.08
301 | 132kV Machkund PH-Jaynagar |  |  |  |  | 0.84653 | 12 | 0 | [7 empty] | 43 | 8760 | 99.86% | 516 | 376680
|  | 17.04.18 | 2:28 | 17.04.18 | 7:37 | 5:09 |  |  | 5 | 9 |  |  |  | Failed due to tripping of all unit
|  | 11.05.18 | 20:00 | 11.05.18 | 20:52 | 0:52 |  |  | 0 | 52 |  |  |  | At Machhkund-H/T due to thunderstorm
|  | 26.05.18 | 13:22 | 26.05.18 | 19:56 | 6:34 |  |  | 0 | 34 |  |  |  | At Machhkund-Tripped
|  | 09.06.18 | 0:45 | 09.06.18 | 5:25 | 4:40 |  |  | 0 | 18 |  |  |  | Ht/T at Machhkund. 01:03 hrs. Rayagada availed P/S from Theruvali
|  | 16.06.18 | 11:30 | 16.06.18 | 12:55 | 1:25 |  |  | 0 | 15 |  |  |  | At Machhkund-H/T. At 11:45 hrs. Akhusing and Paralakhemundi availed P/S from Berhampur end
|  | 10.07.18 | 11:53 | 11.07.18 | 2:37 | 15:02 |  |  | 0 | 12 |  |  |  | At Machhkund-H/T. At 11:47 hrs. Akhusing availed P/S from Mohana end
|  | 11.07.18 | 1:35 | 11.07.18 | 1:45 | 0:10 |  |  | 0 | 10 |  |  |  | At Machhkund-H/T
|  | 10.02.19 | 5:08 | 10.02.19 | 5:42 | 0:34 | 0 | 0 | [5 empty] | Tripped at Machkund end.
|  | 13.02.19 | 5:00 | 13.02.19 | 5:22 | 0:22 | 0 | 0 | [5 empty] | At Machkund-Tripped
|  | 21.02.19 | 5:33 | 21.02.19 | 6:06 | 0:33 | 0 | 0 | [5 empty] | At Machkund-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
302 | 132kV Machkund -Jaynagar (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 108 | 8760 | 100% | 0 | 946080
303 | 132kV Mendhasal-Chandpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35 | 8760 | 100% | 0 | 306600
304 | 132kV Mendhasal-Khurda |  |  |  |  | 0.38542 | 12 | 31 | [7 empty] | 18 | 8760 | 99.86% | 225.3 | 157680
|  | 13.05.18 | 3:48 | 13.05.18 | 4:39 | 0:51 | 0 | 31 | [5 empty] | At Mendhasal-Dist.-17 k.m.
|  | 21.02.19 | 3:41 | 21.02.19 | 11:53 | 8:12 | 0 | 2 | [5 empty] | Tripped on DP at Khurda
|  | 31.03.19 | 16:56 | 31.03.19 | 17:08 | 0:12 | 0 | 7 | [5 empty] | Tripped at Mendhasal end .Shamuka availed from Puri side
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
305 | 132kV Meramundali-BRG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.55 | 8760 | 100% | 0 | 31098
306 | 132kV Meramundali-Chainpal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.728 | 8760 | 100% | 0 | 15137.28
307 | 132kV Meramundali-Chainpal Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.728 | 8760 | 100% | 0 | 15137.28
308 | 132kV Meramundali-Dhenkanal S/s |  |  |  |  | 0.0083333 | 14 | 19 | [7 empty] | 51.916 | 8760 | 99.84% | 743.2641 | 454784.16
|  | 31.12.18 | 15:25 | 31.12.18 | 15:37 | 0:12 | 0 | 12 | [5 empty] | At Meramundali-Fault type-C-N, Z-1, 08.108KM, Ic=2.073kA, CB.
|  | 18.02.19 | 20:01 | 18.02.19 | 20:41 | 0:40 | 0 | 40 | [5 empty] | At Khajuriakata-Tripped On E/F At Nuapatna-Tripped on D/P,Y Phase Pick Up,With Y Phase To Earth Fault.Zone-4,Dist- 122.604%
|  | 31.03.19 | 12:02 | 31.03.19 | 13:29 | 1:27 | 1 | 27 | [5 empty] | E/F,Fault type-R-N, Z-2, 35.75KM, Ia-1.7 Kamp
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
309 | 132kV Meramundali-Kharagprasad Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.517 | 8760 | 100% | 0 | 48328.92
310 | 132kV Meramundali-Kharagprasad Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.517 | 8760 | 100% | 0 | 48328.92
311 | 132kV Meramundali-M.L. Rungta |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.468 | 8760 | 100% | 0 | 65419.68
312 | 132kV Meramundali-Khajuriakata |  |  |  |  | 0.035417 | 0 | 51 | [7 empty] | 33.5 | 8760 | 99.99% | 28.475 | 293460
|  | 18.02.19 | 19:58 | 18.02.19 | 20:35 | 0:37 | 0 | 37 | [5 empty] | At Khajuriakata-Tripped On E/F At Nuapatna-Tripped on D/P,Y Phase Pick Up,With Y Phase To Earth Fault.Zone-4,Dist- 122.604%
|  | 27.02.19 | 15:18 | 27.02.19 | 15:32 | 0:14 | 0 | 14 | [5 empty] | Tripped On E/F
313 | 132kV Khajuriakata-Nuapatna |  |  |  |  | 0.011111 | 0 | 16 | [7 empty] | 84.79 | 8760 | 100% | 22.6107 | 742760.4
|  | 03.03.19 | 16:58 | 03.03.19 | 17:14 | 0:16 | 0 | 16 | [5 empty] | A-G fault (Zone-1), 47.3 Kms
314 | 132kV Nuapatna-Arati Steel |  |  |  |  | 0.011111 | 0 | 0 | [7 empty] | 67.7 | 8760 | 100% | 0 | 593052
|  | 12.03.19 | 16:58 | 12.03.19 | 17:14 | 0:16 | 0 | 0 | [5 empty] | A-G fault (Zone-1), 47.3 Kms
315 | 132kV Mohana-Digpahandi |  |  |  |  | 0.029861 | 15 | 28 | [7 empty] | 29.882 | 8760 | 99.82% | 462.1749 | 261766.32
|  | 10.10.18 | 14:56 | 10.10.18 | 15:39 | 0:43 | 0 | 43 | [5 empty] | At Mohana-Tripped
|  | 10.10.18 | 15:04 | 10.10.18 | 15:22 | 0:18 | 0 | 18 | [5 empty] | Tripped on E/F
|  | 10.10.18 | 16:02 | 10.10.18 | 16:35 | 0:33 | 0 | 33 | [5 empty] | Tripped on E/F
|  | 10.10.18 | 16:36 | 10.10.18 | 17:42 | 1:06 | 1 | 6 | [5 empty] | Tripped on E/F
|  | 11.10.18 | 20:39 | 11.10.18 | 21:06 | 0:27 |  |  |  |  | 0 | 27 |  | Tripped on E/F
|  | 12.10.18 | 17:26 | 12.10.18 | 17:41 | 0:15 |  |  |  |  | 0 | 15 |  | Tripped on E/F
|  | 13.10.18 | 19:17 | 13.10.18 | 19:29 | 0:12 |  |  |  |  | 0 | 12 |  | Tripped on E/F
|  | 15.02.19 | 13:15 | 15.02.19 | 13:42 | 0:27 | 0 | 27 | [5 empty] | At Rayagada-Tripped on E/F
|  | 31.03.19 | 17:59 | 31.03.19 | 18:20 | 0:21 | 0 | 21 | [5 empty] | Zone-1 fault
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
316 | 132kV Muniguda-Muniguda RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.85 | 8760 | 100% | 0 | 121326
317 | 132kV Nalda-Beekay Steel |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.4 | 8760 | 100% | 0 | 47304
318 | 132kV Narendrapur-Berhampur Ckt -I |  |  |  |  | 0 | 12 | 2 | [7 empty] | 10.91 | 8760 | 99.86% | 131.2837 | 95571.6
|  | 11.10.18 | 2:42 | 11.10.18 | 2:53 | 0:11 |  |  |  |  | 0 | 11 |  | At Berhampur:- Tripped on earth fault and master relay tripped in zone-1 (Due to Cyclonic strom Titli.)
|  | 11.10.18 | 3:20 | 11.10.18 | 12:42 | 9:22 |  |  |  |  | 9 | 22 |  | At Berhampur:- Tripped on earth fault and master relay tripped in zone-1 (Due to Cyclonic strom Titli.)
|  | 21.02.19 | 18:29 | 21.02.19 | 18:31 | 0:02 | 0 | 2 | [5 empty] | Tripped due to M/R relay operated.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
319 | 132kV Narendrapur-Berhampur Ckt - II |  |  |  |  | 0 | 12 | 2 | [7 empty] | 10.91 | 8760 | 99.86% | 131.2837 | 95571.6
|  | 11.10.18 | 2:42 | 11.10.18 | 2:53 | 0:11 |  |  |  |  | 0 | 11 |  | At Berhampur:- Tripped on earth fault and master relay tripped in zone-1 (Due to Cyclonic strom Titli.)
|  | 11.10.18 | 3:20 | 11.10.18 | 12:35 | 9:15 |  |  |  |  | 9 | 15 |  | At Berhampur:- Tripped on earth fault and master relay tripped in zone-1 (Due to Cyclonic strom Titli.)
|  | 21.02.19 | 18:29 | 21.02.19 | 18:31 | 0:02 | 0 | 2 | [5 empty] | Tripped due to M/R relay operated.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
320 | 132kV Narendrapur-Chatrapur-I |  |  |  |  | 0.15694 | 12 | 48 | [7 empty] | 13.282 | 8760 | 99.85% | 170.0096 | 116350.32
|  | 15.11.18 | 2:44 | 15.11.18 | 2:56 | 0:12 | 0 | 12 | [5 empty] | R-phase-G with with M/R at Narendrapur end.
|  | 15.11.18 | 11:06 | 15.11.18 | 14:31 | 3:25 | 0 | 27 | [5 empty] | Y-phase to G, Zone-I, Dist-8.85KM along with M/R relay operated.
|  | 01.12.18 | 2:00 | 01.12.18 | 2:09 | 0:09 | 0 | 9 | [5 empty] | At Balugaon-Tripped on o/c (R-Y-B)ph., zone-1,fault distance- 8.01k.m, fault loop- L2-N,Yph-G fault and Zone-1 Indication(Loc-40.26 KM). At Narendrapur-Tripped with DP relay & M/R operated. DP relay showing Y-phase to E/F, Zone-I, Dist-30.22KM.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
321 | 132kV Narendrapur-Chatrapur-II |  |  |  |  | 0.015278 | 0 | 16 | [7 empty] | 13.282 | 8760 | 100% | 3.5419 | 116350.32
|  | 01.12.18 | 2:00 | 01.12.18 | 2:16 | 0:16 | 0 | 16 | [5 empty] | At Balugaon-Tripped on o/c (R-Y-B)ph., zone-1,fault distance- 8.01k.m, fault loop- L2-N,Yph-G fault and Zone-1 Indication(Loc-40.26 KM). At Narendrapur-Tripped with DP relay & M/R operated. DP relay showing Y-phase to E/F, Zone-I, Dist-30.22KM.
|  | 18.02.19 | 16:23 | 18.02.19 | 16:29 | 0:06 | 0 | 6 | [5 empty] | Tripped due to DP & directrional /C & E/F relay operated. DP relay showing Zone-I, Y-phase to E, Dist-27.79KM. No tripping at Chatrapur end.
322 | 132kV Narendrapur-Narendrapur(T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.51 | 8760 | 100% | 0 | 4467.6
323 | 132kV NBVL-Hind Metals |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1 | 8760 | 100% | 0 | 8760
324 | 132kV Nimapara-Konark |  |  |  |  | 0.023611 | 0 | 34 | [7 empty] | 20.31 | 8760 | 99.99% | 11.509 | 177915.6
|  | 31.03.19 | 20:20 | 31.03.19 | 20:54 | 0:34 | 0 | 34 | [5 empty] | Distance protection, FD- 8.1 KM
325 | 132kV Nimapara-Puri Ckt-II |  |  |  |  | 0.0069444 | 0 | 10 | [7 empty] | 30 | 8760 | 100% | 5 | 262800
|  | 23.03.19 | 11:04 | 23.03.19 | 11:14 | 0:10 | 0 | 10 | [5 empty] | At Nimapara -D/P operated. Dist- 22.16 At Puri-Tripped on O/CKM
326 | 132kV Nimapara-Samagara |  |  |  |  | 0.023611 | 0 | 28 | [7 empty] | 27.995 | 8760 | 99.99% | 13.0643 | 245236.2
|  | 11.01.19 | 8:43 | 11.01.19 | 9:17 | 0:34 | 0 | 28 | [5 empty] | Lbb Protection Optd
327 | 132kV Nuapara-Nuapara RTSS |  |  |  |  | 0.023611 | 0 | 28 | [7 empty] | 4.528 | 960 | 99.95% | 2.1131 | 4346.88
|  | 11.01.19 | 8:43 | 11.01.19 | 9:17 | 0:34 | 0 | 28 | [5 empty] | Lbb Protection Optd
328 | 132kV OCL-Salipur |  |  |  |  | 0.072222 | 0 | 51 | [7 empty] | 38.81 | 8760 | 99.99% | 32.9885 | 339975.6
|  | 06.12.18 | 15:27 | 06.12.18 | 17:11 | 1:44 | 0 | 38
|  | 08.12.18 | 12:33 | 10.12.18 | 7:00 | 42:27 | 0 | 13 | [5 empty] | Failure From Sources (132 KV Kendrapada-Salipur Feeder charged at 12:46 hrs) 132 KV Kendrapada-Salipur Feeder charged at 12:46 hrs on Dt. 08.12.2018
329 | 132kV OPCL-Kamakshyanagar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 55 | 8760 | 100% | 0 | 481800
330 | 132kV Paradeep-Trtol |  |  |  |  | 0.29722 | 14 | 38 | [7 empty] | 38.833 | 8760 | 99.83% | 568.2562 | 340177.08
|  | 14.05.18 | 13:01 | 14.05.18 | 15:57 | 2:56 | 0 | 4 | [5 empty] | At Paradeep-D/P,Dist.-3.3 k.m. At 13:05 hrs. Jagatsingpur availed P/S from Cuttack end
|  | 19.10.18 | 12:41 | 19.10.18 | 13:22 | 0:35 | 0 | 11 | [5 empty] | 220 KV P/S FAILED FROM DUBURI END.AVAILED ALTERNATE POWER SUPPLY FROM CUTTACK GRID AT 12:52 HRS
|  | 19.10.18 | 12:41 | 19.10.18 | 13:22 | 0:35 | 0 | 35
|  | 26.10.18 | 15:19 | 26.10.18 | 15:24 | 0:09 | 0 | 9 | [5 empty] | At Duburi-Tripped
|  | 11.11.18 | 2:51 | 11.11.18 | 3:01 | 0:10 | 0 | 10 | [5 empty] | RELAY INDICATION AT PARADEEP 3PH-E FAULT
|  | 02.12.18 | 3:32 | 02.12.18 | 3:44 | 0:12 | 0 | 12 | [5 empty] | At- Paraddep-Tripped on D/P, 9.4KM ,R Ph-Ground.,ZONE-1
|  | 25.01.19 | 10:48 | 25.01.19 | 10:52 | 0:04 | 0 | 4 | [5 empty] | At Paradeep-220KV MAIN BUS-I B-PH BUS CONDUCTOR(SECTION) AFTER(ESSAR-II&50MVA) SNAPPED DUE TO PUNCTURE OF INSULATOR & PULL OUT THE WHOLE SYSTEM At Kendrapara-Trip On E/F With M/R
|  | 03.02.19 | 14:12 | 03.02.19 | 14:21 | 0:09 | 0 | 9 | [5 empty] | At Paradeep-Tripped At Duburi-Tripped
|  | 27.02.19 | 1:43 | 27.02.19 | 2:21 | 0:38 | 0 | 21 | [5 empty] | 132 KV I/C P/S failed from Paradeep Grid end as I/C to paradeep failed from duburi.
|  | 27.02.19 | 1:42 | 27.02.19 | 1:51 | 0:09 | 0 | 27 | [5 empty] | Tripped
|  | 27.02.19 | 1:56 | 27.02.19 | 2:08 | 0:12
|  | 27.02.19 | 2:23 | 27.02.19 | 2:29 | 0:06
|  | 02.03.19 | 13:09 | 02.03.19 | 13:17 | 0:09 | 0 | 9 | [5 empty] | At Paradeep-Tripped, Zone-2,B phase,o/c
|  | 26.03.19 | 20:31 | 26.03.19 | 21:35 | 1:04 | 0 | 7 | [5 empty] | failed from Paradeep Grid end with no relay indication at JSPur end.Jumper of Auto TRf-1 Snapped .2 No of Auto TRf have pulled Out.Availed Alternate Power supply from Cuttack End at 20:38 Hrs.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
331 | 132kV Tirtol- Jagatsinghpur |  |  |  |  | 0.013194 | 0 | 19 | [7 empty] | 29.66 | 8760 | 100% | 9.3923 | 259821.6
|  | 20.03.19 | 17:42 | 20.03.19 | 18:01 | 0:19 | 0 | 19 | [5 empty] | At Jagatsinghapur-no relay indication At Paradeep-O/C(Y-Phase),E/F,DP relay Indication 40 km,Zone-1.
332 | 132kV Paradeep- IFFCO - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.171 | 8760 | 100% | 0 | 62817.96
333 | 132kV Paradeep- IFFCO - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.171 | 8760 | 100% | 0 | 62817.96
334 | 132kV Paradeep-PPL-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.2 | 8760 | 100% | 0 | 54312
335 | 132kV Paradeep-PPL-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.2 | 8760 | 100% | 0 | 54312
336 | 132kV Paradeep-PPT-I |  |  |  |  | 0.040972 | 0 | 59 | [7 empty] | 7.65 | 8760 | 99.99% | 7.5225 | 67014
|  | 19.10.18 | 12:41 | 19.10.18 | 13:28 | 0:47 | 0 | 47 | [5 empty] | TRIPPED ON O/C,E/F
|  | 22.01.19 | 3:04 | 22.01.19 | 3:16 | 0:12 | 0 | 12 | [5 empty] | At New Duburi-DP Relay Operated At Both Ends ,Zone-II,B Ph -E/F,Fault Current-2.03 Ka.Distance-99.7 Km. At Paradeep-TRIPPED ON E/F,C-N,D-14.8KM,Z-1 (DUE TO SEVERE FOG) At Kendrapara-Trip On E/F With M/R
337 | 132kV Paradeep-PPT-II |  |  |  |  | 0.072222 | 0 | 59 | [7 empty] | 7.65 | 8760 | 99.99% | 7.5225 | 67014
|  | 19.10.18 | 12:41 | 19.10.18 | 14:25 | 1:44 | 0 | 47 | [5 empty] | TRIPPED ON O/C,E/F
|  | 22.01.19 | 3:04 | 22.01.19 | 3:16 | 0:12 | 0 | 12 | [5 empty] | At New Duburi-DP Relay Operated At Both Ends ,Zone-II,B Ph -E/F,Fault Current-2.03 Ka.Distance-99.7 Km. At Paradeep-TRIPPED ON E/F,C-N,D-14.8KM,Z-1 (DUE TO SEVERE FOG) At Kendrapara-Trip On E/F With M/R
338 | 132kV Patnagarh-Padampur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 44.636 | 8760 | 100% | 0 | 391011.36
339 | 132kV Padampur-Padampur Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.7 | 8760 | 100% | 0 | 84972
340 | 132kV Pattamundai-Olavar Ckt - I |  |  |  |  | 0.0027778 | 0 | 4 | [7 empty] | 24.338 | 8760 | 100% | 1.6225 | 213200.88
|  | 28.03.19 | 23:25 | 28.03.19 | 23:29 | 0:04 | 0 | 4 | [5 empty] | Tripped at Pattamundai-On E/F & M/R.Distance Protection and M/ R opertaed in 132 KV PMI - Olaver Ckt - I (5.4 Km) ,D/P, E/F & M/R operated in 132 KV Kendrapara Incomer
341 | 132kV Pattamundai-Olavar Ckt -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.338 | 8760 | 100% | 0 | 213200.88
342 | 132kV Olavar - Chandabali Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.498 | 960 | 100% | 0 | 11998.08
343 | 132kV Olavar - Chandabali Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.498 | 960 | 100% | 0 | 11998.08
344 | 132kV Polasponga- Keonjhargarh (T) |  |  |  |  | 0.0013889 | 14 | 1 | [7 empty] | 19.433 | 8760 | 99.84% | 272.3859 | 170233.08
|  | 10.11.18 | 8:32 | 10.11.18 | 8:34 | 0:02 | 0 | 2 | [5 empty] | At Palasponga-Tripped on O/C, Ia= 413.5A, Ib= 349.6A, Ic=276.0A, In= 6A, Ig=5.06A
|  | 17.11.18 | 5:31 | 17.11.18 | 5:34 | 0:03 | 0 | 3 | [5 empty] | At Palasponga-Tripped on O/C, Ia= 219.7A, Ib= 169.3A, Ic=60.82A, In= 6.724A, IN DERIVED= 6.874A
|  | 31.03.19 | 21:04 | 31.03.19 | 21:20 | 00:16 | 1 | 56 | [5 empty] | E/F WITH DP Z-1, Ia= 43.5A, Ib= 21.72A, Ic=2.3KA,
|  | 31.03.19 | 21:20 | 31.03.19 | 23:00 | 01:40 | [7 empty] | E/F WITH DP Z-1, Ia= 12.63A, Ib= 18.91A, Ic=2.395KA,
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
345 | 132 kV Purusottampur-Chatrapur |  |  |  |  | 0.01875 | 0 | 27 | [7 empty] | 15.45 | 8760 | 99.99% | 6.9525 | 135342
|  | 15.11.18 | 11:07 | 15.11.18 | 11:34 | 0:27 | 0 | 27 | [5 empty] | Tripped due to Chatrapur Grid reserve bus Y- phase disc insulator brust. At Purushottampur-Distance Relay indication,Distance Loop-L1-2,Distance-17.1Km
|  | 31.03.19 | 16:35 | 31.03.19 | 17:32 | 0:57 | 0 | 0 | [5 empty] | Tripped on L3-N M/R,RYB zone-1,fault distance-35.31km.
346 | 132kV Rairakhole- Rairakhole RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.5 | 8760 | 100% | 0 | 30660
347 | 132kV Rairangapur- Karanjia |  |  |  |  | 0 | 0 | 0 | [7 empty] | 71.54 | 8760 | 100% | 0 | 626690.4
348 | 132kV Rajgangapur-OCL |  |  |  |  | 0.015278 | 16 | 6 | [7 empty] | 0.5 | 8760 | 99.82% | 8.05 | 4380
|  | 22.10.18 | 17:42 | 22.10.18 | 18:04 | 0:22 | 0 | 22 | [5 empty] | At Rajgangpur-Tripped on E/F, MASTER TRIP OPERATED, FAULT CURRENT Ia-205A,Ib-187A, Ic-203A
|  | 17.12.18 | 19:26 | 17.12.18 | 21:10 | 1:44 | 1 | 44 | [5 empty] | At Budhipadar-E/F 86
|  | 17.12.18 | 21:16 | 17.12.18 | 22:30 | 1:14 | 1 | 14 | [5 empty] | At Budhipadar-E/F 86 IC=1.535KA,L3N, L3-893 A, Ln-914 A, (Heavy Lightening).
|  | 25.02.19 | 1:04 | 25.02.19 | 1:50 | 0:46 | 0 | 46 | [5 empty] | E/F, O/C- BPHASE, FAULT CURRENT, Ib= 1.785KA, In- 1.388KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
349 | 132kV Rajgangapur-Rajgangapur (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.2 | 8760 | 100% | 0 | 36792
350 | 132kV Rajgangpur-Rourkela |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.5 | 8760 | 100% | 0 | 240900
351 | 132kV Ranasinghpur-Badagada |  |  |  |  | 0.025 | 12 | 36 | [7 empty] | 34.63 | 8760 | 99.86% | 436.338 | 303358.8
|  | 11.01.19 | 8:44 | 11.01.19 | 9:07 | 0:23 | 0 | 23 | [5 empty] | At Samangara Grid End
|  | 11.01.19 | 9:10 | 11.01.19 | 9:15 | 0:05 | 0 | 5 | [5 empty] | 133 Kv P/S Failed From Samangara Grid End
|  | 28.02.19 | 15:54 | 28.02.19 | 16:02 | 0:08 | 0 | 8 | [5 empty] | Earth Fault(Earth Wire Was Broken)
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
352 | 132kV RAWMET-Choudwar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23 | 8760 | 100% | 0 | 201480
353 | 132kV RAWMET-Arati Steel |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17.678 | 8760 | 100% | 0 | 154859.28
354 | 132kV Rayagada-Akhusingh |  |  |  |  | 0 | 15 | 9 | [7 empty] | 50 | 8760 | 99.83% | 757.5 | 438000
|  | 11.10.18 | 9:16 | 12.10.18 | 16:42 | 31:26 |  |  |  |  | 31 | 26 |  | AT Rayagada-Tripped on E/F (Due to Cyclonic strom Titli.)
|  | 11.12.18 | 4:58 | 11.12.18 | 5:15 | 0:17 | 0 | 17 | [5 empty] | At Raygada- Tripped
|  | 26.12.18 | 5:38 | 26.12.18 | 5:51 | 0:13 | 0 | 13 | [5 empty] | At Rayagada-Tripped
|  | 14.02.19 | 5:02 | 14.02.19 | 5:23 | 0:21 | 0 | 21 | [5 empty] | At Akhusingh-Tripped
|  | 11.02.19 | 5:08 | 11.02.19 | 5:42 | 0:34 | 0 | 34 | [5 empty] | At Akhusingh-Tripped
|  | 15.02.19 | 13:15 | 15.02.19 | 13:43 | 0:28 | 0 | 28 | [5 empty] | At Rayagada-Tripped on E/F
|  | 16.02.19 | 16:50 | 16.02.19 | 16:52 | 0:02 | 0 | 2 | [5 empty] | At Rayagada-Tripped
|  | 17.02.19 | 16:20 | 17.02.19 | 16:27 | 0:07 | 0 | 7 | [5 empty] | At Rayagada-Tripped
|  | 18.02.19 | 11:50 | 18.02.19 | 12:01 | 0:11 | 0 | 11 | [5 empty] | At Rayagada-Tripped
|  | 18.02.19 | 18:29 | 18.02.19 | 18:34 | 0:05 | 0 | 5 | [5 empty] | At Akhusingh-Tripped
|  | 20.02.19 | 8:46 | 20.02.19 | 8:52 | 0:06 | 0 | 6 | [5 empty] | At Akhusingh-Tripped
|  | 20.02.19 | 10:47 | 20.02.19 | 10:52 | 0:05 | 0 | 5 | [5 empty] | At Akhusingh-Tripped
|  | 21.02.19 | 11:53 | 21.02.19 | 11:57 | 0:04 | 0 | 4 | [5 empty] | At Akhusingh-Tripped
|  | 21.02.19 | 14:09 | 21.02.19 | 14:18 | 0:09 | 0 | 9 | [5 empty] | At Akhusingh-Tripped
|  | 21.02.19 | 16:28 | 21.02.19 | 16:30 | 0:02 | 0 | 2 | [5 empty] | At Akhusingh-Tripped
|  | 21.02.19 | 18:27 | 21.02.19 | 18:28 | 0:01 | 0 | 1 | [5 empty] | At Akhusingh-Tripped
|  | 21.02.19 | 23:48 | 21.02.19 | 23:51 | 0:03 | 0 | 3 | [5 empty] | At Akhusingh-Tripped
|  | 22.02.19 | 14:56 | 22.02.19 | 14:59 | 0:03 | 0 | 3 | [5 empty] | At Akhusingh-Tripped
|  | 22.02.19 | 16:52 | 22.02.19 | 16:55 | 0:03 | 0 | 3 | [5 empty] | At Akhusingh-Tripped
|  | 26.02.19 | 18:27 | 26.02.19 | 18:30 | 0:03 | 0 | 3 | [5 empty] | At Akhusingh-Tripped
|  | 26.02.19 | 19:55 | 26.02.19 | 19:57 | 0:02 | 0 | 2 | [5 empty] | At Akhusingh-Tripped
|  | 28.02.19 | 9:17 | 28.02.19 | 9:24 | 0:07 | 0 | 7 | [5 empty] | At Akhusingh-Tripped
|  | 28.02.19 | 18:00 | 28.02.19 | 18:03 | 0:03 | 0 | 3 | [5 empty] | At Akhusingh-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
355 | 132kV Rayagada-Rayagada Traction |  |  |  |  | 0.13264 | 0 | 0 | [7 empty] | 2.646 | 8760 | 100% | 0 | 23178.96
|  | 11.10.18 | 8:52 | 11.10.18 | 12:03 | 3:11 |  |  |  |  | 3 | 11 |  | AT Rayagada-Tripped on E/F (Due to Cyclonic strom Titli.)
356 | 132kV Rayagada-VBC Ferro |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.3 | 8760 | 100% | 0 | 2628
357
358 | 132kV Rourkela-Bhalulata |  |  |  |  | 0.49514 | 18 | 54 | [7 empty] | 24.29 | 8760 | 99.78% | 459.081 | 212780.4
|  | 27.04.18 | 22:08 | 28.04.18 | 11:41 | 11:53 | 0 | 24 | [5 empty] | At Rourkela-D/P, Dist.-7.2 k.m, ['B' ph. insulator damaged at Loc No.-24] At 22:32 hrs. B.K. Steel availed P/S from Joda
|  | 16.05.18 | 16:29 | 17.05.18 | 10:59 | 18:30 | 18 | 30 | [5 empty] | At Rourkela-Dist.-33.82 k.m, 'R'ph, Ý'ph, E/F
359 | 132kV Saintala-ACME-Tusura-Bolangir |  |  |  |  | 0.0090278 | 16 | 56 | [7 empty] | 68.018 | 8760 | 99.81% | 1151.7715 | 595837.68
|  | 16.10.18 | 9:56 | 16.10.18 | 10:09 | 0:13 | 0 | 13 | [5 empty] | At Sadeipali-Tripped on over current on RYB-ph and Earth fault.
|  | 23.10.18 | 12:36 | 23.10.18 | 12:46 | 0:10 | 0 | 10 | [5 empty] | At Bolangir-Tripped on Y-Phase E/F
|  | 03.11.18 | 17:35 | 03.11.18 | 17:52 | 0:17 | 0 | 17 | [5 empty] | At-Bolangir-Tripped due to LA Burst
|  | 08.12.18 | 14:58 | 08.12.18 | 15:01 | 0:03 | 0 | 3 | [5 empty] | At Bolangir- Tripped
|  | 08.12.18 | 15:57 | 08.12.18 | 15:59 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 10.12.18 | 16:44 | 10.12.18 | 16:46 | 0:02 | 0 | 2 | [5 empty] | Tripped from Bolangir
|  | 10.12.18 | 17:28 | 10.12.18 | 17:29 | 0:01 | 0 | 1 | [5 empty] | Tripped from Bolangir
|  | 17.12.18 | 4:01 | 17.12.18 | 4:22 | 0:21 | 0 | 21 | [5 empty] | At Bolangir- Tripped on O/C
|  | 17.12.18 | 4:23 | 17.12.18 | 4:56 | 0:33 | 0 | 21 | [5 empty] | Tripped from Tushra
|  | 17.12.18 | 17:55 | 17.12.18 | 18:34 | 0:39 | 0 | 39 | [5 empty] | Tripped from Tushra
|  | 21.12.18 | 16:06 | 21.12.18 | 16:20 | 0:14 | 0 | 14 | [5 empty] | Tripped from Tushra
|  | 24.12.18 | 16:29 | 24.12.18 | 16:43 | 0:14 | 0 | 14 | [5 empty] | Tripped from Bolangir
|  | 24.12.18 | 16:22 | 24.12.18 | 16:27 | 0:05 | 0 | 5 | [5 empty] | Tripped from Tushra
|  | 24.12.18 | 16:29 | 24.12.18 | 16:43 | 0:14 | 0 | 14 | [5 empty] | Tripped from Bolangir
|  | 24.12.18 | 16:35 | 24.12.18 | 16:45 | 0:10 | 0 | 10 | [5 empty] | At Bolangir-Tripped on E/F
|  | 19.02.19 | 16:54 | 19.02.19 | 17:07 | 0:13 | 0 | 17 | [5 empty] | 132kV Saintala-Tusura
|  | 19.02.19 | 17:11 | 19.02.19 | 17:20 | 0:09
|  | 20.02.19 | 17:05 | 20.02.19 | 17:11 | 0:06 | 0 | 6 | [5 empty] | At Sadeipali-Tripped on O/L
|  | 20.02.19 | 17:17 | 20.02.19 | 17:19 | 0:02 | 0 | 2 | [5 empty] | At Sadeipali-Tripped on O/L
|  | 20.02.19 | 21:33 | 20.02.19 | 21:37 | 0:04 | 0 | 4 | [5 empty] | At Sadeipali-Tripped on O/L
|  | 05.03.19 | 18:46 | 05.03.19 | 18:55 | 0:09 | 0 | 9 | [5 empty] | Tripped from Saintala-On O/L
|  | 11.03.19 | 13:19 | 11.03.19 | 13:35 | 0:16 | 0 | 16 | [5 empty] | Tripped from Saintala-On O/L
|  | 11.03.19 | 13:24 | 11.03.19 | 13:35 | 0:11 | 0 | 17 | [5 empty] | At Bolangir-Tripped on E/F
|  | 11.03.2019 | 13:36 | 11.03.2019 | 13:42 | 0:06 | [7 empty] | E/F
|  | 31.03.19 | 16:14 | 31.03.19 | 16:25 | 0:11 | 0 | 11 | [5 empty] | E/F
|  | 31.03.19 | 16:09 | 31.03.19 | 16:35 | 0:28 | 0 | 28 | [5 empty] | Tripped from Sadeipali [Due to Distance protection fault at ACME and Tushra Line.]
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
360 | 132kV Salipur-Kendrapara |  |  |  |  | 0.0069444 | 0 | 5 | [7 empty] | 34.4 | 8760 | 100% | 2.8667 | 301344
|  | 16.01.19 | 16:43 | 16.01.19 | 16:48 | 0:05 | 0 | 5 | [5 empty] | At Kendrapara-Tripped
|  | 27.02.19 | 0:19 | 27.02.19 | 0:24 | 0:05 | 0 | 0 | [5 empty] | TRIP ON DP WITH M/R
361 | 132kV Samagara-Puri |  |  |  |  | 0.013194 | 0 | 19 | [7 empty] | 3.99 | 8760 | 100% | 1.2635 | 34952.4
|  | 11.01.19 | 8:43 | 11.01.19 | 9:02 | 0:19 | 0 | 19 | [5 empty] | Lbb Protection Optd
362 | 132kV Sambalpur-Shyam Dri |  |  |  |  | 0 | 0 | 0 | [7 empty] | 26.589 | 8760 | 100% | 0 | 232919.64
363 | 132kV Shamuka-Puri |  |  |  |  | 0.0034722 | 0 | 5 | [7 empty] | 17.3 | 8760 | 100% | 1.4417 | 151548
|  | 07.02.19 | 10:50 | 07.02.19 | 10:55 | 0:05 | 0 | 5 | [5 empty] | E/F
|  | 21.02.19 | 3:36 | 21.02.19 | 3:38 | 0:02 | 0 | 2 | [5 empty] | E/F at Khurda
|  | 23.02.19 | 13:44 | 23.02.19 | 13:48 | 0:04 | 0 | 4 | [5 empty] | O/C Fault
|  | 31.03.19 | 20:15 | 31.03.19 | 20:53 | 0:38 | 0 | 38 | [5 empty] | At Shamuka-Tripped on D/P
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
364 | 132kV Shyam DRI-Lapanga-Aryan Ispat |  |  |  |  | 0.74861 | 17 | 58 | [7 empty] | 9.98 | 8760 | 99.79% | 179.3073 | 87424.8
|  | 15.02.19 | 23:32 | 16.02.19 | 17:30 | 17:58 | 17 | 58 | [5 empty] | At Lapanga-Tripped,ZONE 2, B PHASE,L3E,PU TIME =426 ms,TRIP TIME=349 ms,DISTANCE-4.2 KM,DISTANCE(%)-106.6 % IL3=7.07KA,B/U- O/C,E/F IN B PHASE, PU TIME -468 ms,TRIP TIME-426 ms,IL3=3.84 KA. (Heavy Sparking And Humming Sound Coming From B Phase Ct At Lapanga End)
365 | 132kV SMC Power-Aryan Ispat |  |  |  |  | 0.0041667 | 0 | 6 | [7 empty] | 7.95 | 8760 | 100% | 0.795 | 69642
|  | 16.11.18 | 17:17 | 16.11.18 | 17:23 | 0:06 | 0 | 6 | [5 empty] | LBB
366 | 132kV SMC Power-Kuchinda |  |  |  |  | 0.0069444 | 0 | 10 | [7 empty] | 53.33 | 8760 | 100% | 8.8883 | 467170.8
|  | 16.11.18 | 17:17 | 16.11.18 | 17:27 | 0:10 | 0 | 10 | [5 empty] | LBB
367 | 132 kV Sonepur - Boudh |  |  |  |  | 0.12361 | 14 | 58 | [7 empty] | 51.05 | 8760 | 99.83% | 764.0483 | 447198
|  | 05.01.19 | 10:50 | 05.01.19 | 11:10 | 0:20 | 0 | 20 | [5 empty] | Tripped From Boudh End.
|  | 31.01.19 | 14:58 | 31.01.19 | 15:07 | 0:09 | 0 | 9 | [5 empty] | Tripped At Sonepur End.
|  | 06.03.19 | 4:40 | 06.03.19 | 5:13 | 0:33 | 0 | 33 | [5 empty] | Tripped on E/F at Boudh
|  | 24.03.19 | 13:28 | 24.03.19 | 14:10 | 0:42 | 1 | 56 | [5 empty] | At Sonepur-Tripped
|  | 24.03.19 | 16:42 | 24.03.19 | 17:56 | 1:14 | [7 empty] | Supply failed from sonepur
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
368 | 132kV Soro-Bhadrak |  |  |  |  | 0 | 0 | 0 | [7 empty] | 46.215 | 8760 | 100% | 0 | 404843.4
369 | 132kV Sunabeda-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13 | 8760 | 100% | 0 | 113880
370 | 132kV Sunabeda-HAL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.7 | 8760 | 100% | 0 | 6132
371 | 132kV Sunabeda-Pottangi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.4 | 8760 | 100% | 0 | 292584
372 | 132kV Tarkera-Kalunga |  |  |  |  | 0.13194 | 0 | 0 | [7 empty] | 15.88 | 8760 | 100% | 0 | 139108.8
|  | 19.02.19 | 16:49 | 19.02.19 | 19:59 | 3:10 | 0 | 0 | [5 empty] | At Tarkera-Tripped on E/F
373 | 132kV Tarkera-Budhipadar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 110 | 8760 | 100% | 0 | 963600
374 | 132kV Tarkera-Chhend-I |  |  |  |  | 0.022222 | 0 | 54 | [7 empty] | 6.165 | 8760 | 99.99% | 5.5485 | 54005.4
|  | 06.04.18 | 13:41 | 06.04.18 | 14:13 | 0:32 | 0 | 32 | [5 empty] | At Tarkera-'R'ph. E/F
|  | 22.10.18 | 17:28 | 22.10.18 | 17:58 | 0:22 | 0 | 22 | [5 empty] | At Tarkera-Tripped AT Chhend-Tripped
375 | 132kV Tarkera-Chhend-II |  |  |  |  | 0.022917 | 0 | 54 | [7 empty] | 6.165 | 8760 | 99.99% | 5.5485 | 54005.4
|  | 06.04.18 | 13:41 | 06.04.18 | 14:14 | 0:33 | 0 | 32 | [5 empty] | At Tarkera-'R'ph. E/F
|  | 22.10.18 | 17:28 | 22.10.18 | 17:58 | 0:22 | 0 | 22 | [5 empty] | At Tarkera-Tripped AT Chhend-Tripped
376 | 132kV Tarkera-Rajgangapur-I |  |  |  |  | 0.11806 | 13 | 31 | [7 empty] | 24.5 | 8760 | 99.85% | 331.1583 | 214620
|  | 06.04.18 | 17:41 | 06.04.18 | 19:08 | 1:27 | 0 | 25 | [5 empty] | At Tarkera-D/P, 'R'ph. to E/F, Dist.-29.178 k.m.
|  | 10.10.18 | 10:59 | 10.10.18 | 11:12 | 0:13 | 0 | 13 | [5 empty] | AT BUDHIPADAR END -Tripped on D/P,ZONE 2, RYB- PHASE TRIP , L1-243A,L2-1117A,L3-276A, L2N LOOP. AT RAJGANGPUR -132KV RAILWAY -II FEEDER EARTH WIRE AND Y-PHASE CONDUCTOR SNAPING AT LOC. NO- 07
|  | 17.12.18 | 19:26 | 17.12.18 | 19:37 | 0:11 | 0 | 11 | [5 empty] | At Rajgangpur-Tripped on E/F
|  | 17.12.18 | 21:16 | 17.12.18 | 21:27 | 0:11 | 0 | 11 | [5 empty] | At Rajgangpur-Tripped on E/F
|  | 19.02.19 | 16:50 | 19.02.19 | 17:07 | 0:17 | 0 | 0 | [5 empty] | At Tarkera-Tripped on E/F
|  | 25.02.19 | 1:04 | 25.02.19 | 1:35 | 0:31 | 0 | 31 | [5 empty] | Tripped On E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
377 | 132kV Tarkera-Rajgangapur-II |  |  |  |  | 0.059722 | 12 | 41 | [7 empty] | 24.5 | 8760 | 99.86% | 310.7417 | 214620
|  | 06.04.18 | 17:41 | 06.04.18 | 18:06 | 0:25 | 0 | 25 | [5 empty] | At Tarkera-D/P, 'R'ph. to Ý'ph.
|  | 06.04.18 | 18:17 | 06.04.18 | 19:02 | 0:45
|  | 10.10.18 | 10:59 | 10.10.18 | 11:15 | 0:16 | 0 | 16 | [5 empty] | AT BUDHIPADAR END -Tripped on D/P,ZONE 2, RYB- PHASE TRIP , L1-243A,L2-1117A,L3-276A, L2N LOOP. AT RAJGANGPUR -132KV RAILWAY -II FEEDER EARTH WIRE AND Y-PHASE CONDUCTOR SNAPING AT LOC. NO- 08
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
378 | 132kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
379 | 132kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
380 | 132kV Tarkera-Rourkela-I |  |  |  |  | 0.020139 | 0 | 29 | [7 empty] | 3 | 8760 | 99.99% | 1.45 | 26280
|  | 10.07.18 | 18:26 | 10.07.18 | 18:55 | 0:29 | 0 | 29 | [5 empty] | At Tarkera-Tripped
381 | 132kV Tarkera-Rourkela-II |  |  |  |  | 0.034028 | 0 | 29 | [7 empty] | 3 | 8760 | 99.99% | 1.45 | 26280
|  | 10.07.18 | 18:26 | 10.07.18 | 19:15 | 0:49 | 0 | 29 | [5 empty] | At Tarkera-TrippedAfter 29 minutes power flow resumed through ckt-I
382 | 132kV Tarkera-Rourkela-III |  |  |  |  | 0.022222 | 0 | 29 | [7 empty] | 3 | 8760 | 99.99% | 1.45 | 26280
|  | 10.07.18 | 18:26 | 10.07.18 | 18:58 | 0:32 | 0 | 29 | [5 empty] | At Tarkera-TrippedAfter 29 minutes power flow resumed through ckt-I
383 | 132kV Tentulikhunti-Dabugaon ckt |  |  |  |  | 0.0069444 | 0 | 10 | [7 empty] | 43.2 | 8760 | 100% | 7.2 | 378432
|  | 16.02.19 | 16:13 | 16.02.19 | 16:23 | 0:10 | 0 | 10 | [5 empty] | At Jayanagar-Tripped
|  | 23.02.19 | 16:49 | 23.02.19 | 16:59 | 0:10 | 0 | 10 | [5 empty] | At Jayanagar-Tripped
|  | 26.02.19 | 12:07 | 26.02.19 | 12:29 | 0:22 | 0 | 22 | [5 empty] | At Jayanagar-Tripped
|  | 26.02.19 | 17:30 | 26.02.19 | 17:50 | 0:20 | 0 | 20 | [5 empty] | At Jayanagar-Tripped
|  | 28.02.19 | 9:50 | 28.02.19 | 10:09 | 0:19 | 0 | 19 | [5 empty] | At Jayanagar-Tripped
|  | 28.02.19 | 17:33 | 28.02.19 | 17:45 | 0:12 | 0 | 12 | [5 empty] | At Jayanagar-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
384 | 132kV Tentulikhunti-Vento Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.192 | 8760 | 100% | 0 | 36721.92
385 | 132kV Therubali-IMFAL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2 | 8760 | 100% | 0 | 17520
386 | 132kV Therubali-JK Pur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.68 | 8760 | 100% | 0 | 84796.8
387 | 132kV Therubali-Rayagada |  |  |  |  | 0.0041667 | 12 | 21 | [7 empty] | 20 | 8760 | 99.86% | 247 | 175200
|  | 03.11.18 | 13:41 | 03.11.18 | 13:47 | 0:06 | 0 | 6 | [5 empty] | BGT
|  | 16.11.18 | 17:34 | 16.11.18 | 17:44 | 0:10 | 0 | 10 | [5 empty] | ABC Over Current
|  | 16.11.18 | 19:23 | 16.11.18 | 19:28 | 0:05 | 0 | 5 | [5 empty] | C- Phase Over Current trip
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
388 | 132kV Therubali-Muniguda-Vedant Alumina |  |  |  |  | 1900-01-01 00:02 | 13 | 14 | [7 empty] | 76.951 | 8760 | 99.85% | 1018.3182 | 674090.76
|  | 03.10.18 | 18:42 | 03.10.18 | 18:52 | 0:10 | 0 | 10 | [5 empty] | At Therubali-Tripped on over load.
|  | 04.10.18 |  | 04.10.18 | 19:17 | 19:17 | 0 | 7 | [5 empty] | At Therubali-Tripped on over load.
|  | 11.10.18 | 7:20 | 11.10.18 | 16:30 | 9:10 |  |  |  |  | 9 | 10 |  | At Theruvali-Tripped on D/P( due to tree falls on rphase conductor betwwen loc 45 and 46 during cyclone titli)
|  | 26.10.18 | 18:20 | 26.10.18 | 18:28 | 18:28 |  |  |  |  | 18 | 28 |  | At Theruvali-Tripped
|  | 29.12.18 | 9:03 | 29.12.18 | 9:24 | 0:21 | 0 | 21 | [5 empty] | At Kesinga-Tripped (due to heavy spark on 132kv WT of 132kv khariar bay)
|  | 13.03.19 | 5:20 | 13.03.19 | 5:30 | 0:10 | 0 | 10 | [5 empty] | At Theruvali-Tripped
|  | 14.03.19 | 20:52 | 14.03.19 | 20:59 | 0:07 | 0 | 7 | [5 empty] | At Therubali-Tripped on O/C
|  | 31.03.19 | 16:08 | 31.03.19 | 16:26 | 0:19 | 0 | 19 | [5 empty] | At Therubali-Tripped on O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
389 | 132kV TTPS-Angul |  |  |  |  | 0 | 0 | 0 | [7 empty] | 16 | 8760 | 100% | 0 | 140160
390 | 132kV TTPS-Chainpal-I |  |  |  |  | 0.49583 | 2 | 37 | [7 empty] | 3 | 8760 | 99.97% | 7.85 | 26280
|  | 16.04.18 | 18:36 | 16.04.18 | 20:09 | 1:33 | 1 | 20 | [5 empty] | At Chainpal-Tripped
|  | 26.02.19 | 8:10 | 26.02.19 | 18:31 | 10:21 | 1 | 17 | [5 empty] | Tripped on E/F,O/C-B ph ,Bursting of CT
391 | 132kV TTPS-Chainpal-II |  |  |  |  | 0.49514 | 2 | 37 | [7 empty] | 3 | 8760 | 99.97% | 7.85 | 26280
|  | 16.04.18 | 18:36 | 16.04.18 | 20:08 | 1:32 | 1 | 20 | [5 empty] | At Chainpal-Tripped
|  | 26.02.19 | 8:10 | 26.02.19 | 18:31 | 10:21 | 1 | 17 | [5 empty] | Tripped on E/F,O/C-B ph ,Bursting of CT
392 | 132kV TTPS-Chainpal-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
393 | 132kV TTPS-Jabamayee FAlloys |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.276 | 8760 | 100% | 0 | 668177.76
394 | 132kV TTPS-OPCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31 | 8760 | 100% | 0 | 271560
395 | 132kV Tusura-Vento Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.8 | 8760 | 100% | 0 | 129648
396 | 132kV Vedant Alumina-Kesinga |  |  |  |  | 0.81736 | 12 | 27 | [7 empty] | 58.077 | 8760 | 99.86% | 723.0586 | 508754.52
|  | 03.10.18 | 18:42 | 03.10.18 | 18:52 | 0:10 | 0 | 10 | [5 empty] | At Therubali-Tripped on over load.
|  | 04.10.18 |  | 04.10.18 | 19:17 | 19:17 | 0 | 7 | [5 empty] | At Therubali-Tripped on over load.
|  | 30.01.19 | 18:20 | 30.01.19 | 18:30 | 0:10 | 0 | 10 | [5 empty] | Tripped From Lanjigarh Due To Over Current
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
(17): 7000.557; (20): 60559.3332; (21): 131946874.32 | 0.00045897 | 99.9541
ICTs / AUTOS
1 | Duburi 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | #REF! | 0 | 6898500
2 | Duburi 315MVA ICT – II |  |  |  |  | 0.0048611 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
|  | 03.02.19 | 14:15 | 03.02.19 | 14:22 | 0:07 | 0 | 0 | [5 empty] | At 220KV side :- Directional O/C Trip, Fault current - Ir - 0.72KA, Iy - 0.72 KA, Ib - 0.69 KA . Power flow resumed through ICT-I At 400KV side:- Master trip operated.
3 | Lapanga 315MVA ICT – I |  |  |  |  | 0.14375 | 3 | 27 | [6 empty] | 315 |  | 5856 | #REF! | #REF! | 4611600
|  | 15.03.19 | 11:59 | 15.03.19 | 15:26 | 3:27 | 3 | 27
4 | Meramundali 315MVA ICT – I |  |  |  |  | 0.049306 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
|  | 26.02.19 | 17:25 | 26.02.19 | 18:36 | 1:11 | 0 | 0 | [5 empty] | At Meramundali-Tripped on DT (distance trip)signal from Mendhasal end. (Associated tie breaker(402 Dia) at Meramundali S/S didn’t trip due to mechanical problem in R-ph limb. Hence LBB of tie breaker (402 dia) operated). Power flow resumed through ICT-II (LBB of Mendhasal feeder main beaker at Meramundali end operated) At New Duburi -R,Y, B ph pick up, DT received, M/T.
5 | Meramundali 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
6 | Mendhasal 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
7 | Mendhasal 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
8 | Atri 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
9 | Atri 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
10 | Balasore 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
11 | Balasore 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
12 | Balasore 160MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 4368 | 100% | 0 | 1747200
13 | Baragarh New 100MVA Auto – I |  |  |  |  | 0.015278 | 0 | 22 | [6 empty] | 100 |  | 8760 | 100% | 91.6667 | 2190000
|  | 05.01.19 | 10:52 | 05.01.19 | 11:14 | 0:22 | 0 | 22 | [5 empty] | REF,Differential protection,Bus bar Relay 96,Master trip 86 A 86 B
14 | Baragarh New 100MVA Auto – II |  |  |  |  | 0.015278 | 0 | 15 | [6 empty] | 100 |  | 8760 | 100% | 62.5 | 2190000
|  | 05.01.19 | 10:52 | 05.01.19 | 11:07 | 0:22 | 0 | 15 | [5 empty] | REF,Differential protection,Bus bar Relay 96,Master trip 86 A 86 B
15 | Bidanasi 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
16 | Bidanasi 100MVA Auto - II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
17 | Bidanasi 160MVA Auto - III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
18 | Bhadrak 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
19 | Bhadrak 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
20 | Bhadrak 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
21 | Bhadrak 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
22 | Bolangir 160MVA Auto I |  |  |  |  | 0 | 0 | 7 | [6 empty] | 160 |  | 8760 | 100% | 46.6667 | 3504000
|  | 23.10.18 | 12:36 | 23.10.18 | 12:46 | 0:10 | 0 | 7 | [5 empty] | At Sadeipali-Tripped on Back up o/c & e/f protection operated and transformer running over 90% load indication
23 | Bolangir 160 MVA Auto II |  |  |  |  | 0.0048611 | 0 | 7 | [6 empty] | 160 |  | 8760 | 100% | 46.6667 | 3504000
|  | 23.10.18 | 12:35 | 23.10.18 | 12:42 | 0:07 | 0 | 7 | [5 empty] | At Sadeipali-Tripped on Back up o/c & e/f protection operated and transformer running over 90% load indication
24 | Bhanjanagar 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
25 | Bhanjanagar 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
26 | Budhipadar 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
27 | Budhipadar 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
28 | Chandaka 100MVA Auto – I |  |  |  |  | 0.040972 | 0 | 56 | [6 empty] | 100 |  | 8760 | 99.99% | 233.3333 | 2190000
|  | 13.05.18 | 3:36 | 13.05.18 | 4:10 | 0:34 | 0 | 31 | [5 empty] | On 220 kV side-Tripped, Bus bar protection. Power flow resumed through Auto-II&IV after 31 minutes.
|  | 21.02.19 | 13:29 | 21.02.19 | 13:54 | 0:25 | 0 | 25 | [5 empty] | At Chandaka-Tripped on only master trip .
29 | Chandaka 160MVA Auto – II |  |  |  |  | 0.038194 | 0 | 55 | [6 empty] | 160 |  | 8760 | 99.99% | 366.6667 | 3504000
|  | 13.05.18 | 3:36 | 13.05.18 | 4:07 | 0:31 | 0 | 31 | [5 empty] | On 220 kV side-O/C, Bus bar protection
|  | 21.02.19 | 13:29 | 21.02.19 | 13:53 | 0:24 | 0 | 24 | [5 empty] | At Chandaka-Tripped on Dir. O/C , E/F trip, ,IL1=0.59 kA, ,IL2= 2.32 kA, ,IL3=1.86 kA.
30 | Chandaka 100MVA Auto – III |  |  |  |  | 0.034722 | 0 | 47 | [6 empty] | 100 |  | 8760 | 99.99% | 129.1667 | 2190000
|  | 13.05.18 | 3:36 | 13.05.18 | 4:10 | 0:34 | 0 | 31 | [5 empty] | On 220 kV side-O/C, Bus bar protection. Power flow resumed through Auto-II&IV after 31 minutes.
|  | 21.02.19 | 13:29 | 21.02.19 | 13:45 | 0:16 | 0 | 16 | [5 empty] | At Chandaka-Tripped on Dir O/C , E/F trip, master trip
31 | Chandaka 160MVA Auto – IV |  |  |  |  | 0.057639 | 1 | 23 | [6 empty] | 160 |  | 8760 | 99.98% | 553.3333 | 3504000
|  | 13.05.18 | 3:36 | 13.05.18 | 4:07 | 0:31 | 0 | 31 | [5 empty] | On 220 kV side-O/C, Bus bar protection.
|  | 21.02.19 | 13:29 | 21.02.19 | 14:21 | 0:52 | 0 | 52 | [5 empty] | At Chandaka-Tripped
32 | Chandaka-B 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
33 | Chandaka-B 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
34 | Cuttack 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
35 | Duburi 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
36 | Duburi 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
37 | Duburi 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
38 | Jayanagar 160MVA Auto – I |  |  |  |  | 0.04375 | 1 | 0 | [6 empty] | 160 |  | 8760 | 99.99% | 400 | 3504000
|  | 01.05.18 | 6:44 | 01.05.18 | 7:47 | 1:03 | 1 | 0 | [5 empty] | On 132 kV side-'B' ph. O/C Weather condition was rainy and windy with lightening and thunder
|  | 25.05.18 | 16:30 | 25.05.18 | 17:04 | 0:34 | 0 | 0 | [5 empty] | Hand tripped. Power flow tresumed through Auto-II
39 | Jayanagar 160MVA Auto – II |  |  |  |  | 0.041667 | 1 | 0 | [6 empty] | 160 |  | 8760 | 99.99% | 400 | 3504000
|  | 01.05.18 | 6:44 | 01.05.18 | 7:44 | 1:00 | 1 | 0 | [5 empty] | On 132 kV side-'B' ph. O/C
40 | Joda 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
41 | Joda 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
42 | Joda 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
43 | Katapalli 100MVA Auto – I |  |  |  |  | 0.011806 | 0 | 17 | [6 empty] | 100 |  | 8760 | 100% | 70.8333 | 2190000
|  | 07.01.19 | 15:55 | 07.01.19 | 16:12 | 0:17 | 0 | 17 | [5 empty] | H/T
44 | Katapalli 100MVA Auto – II |  |  |  |  | 0.011806 | 0 | 17 | [6 empty] | 100 |  | 8760 | 100% | 70.8333 | 2190000
|  | 07.01.19 | 15:55 | 07.01.19 | 16:12 | 0:17 | 0 | 17 | [5 empty] | H/T
45 | Katapalli 160MVA Auto – III |  |  |  |  | 0.011806 | 0 | 17 | [6 empty] | 160 |  | 8760 | 100% | 113.3333 | 3504000
|  | 07.01.19 | 15:55 | 07.01.19 | 16:12 | 0:17 | 0 | 17 | [5 empty] | H/T
46 | Lapanga 160MVA Auto – I |  |  |  |  | 0.0069444 | 0 | 10 | [6 empty] | 160 |  | 8760 | 100% | 66.6667 | 3504000
|  | 15.02.2019 | 23:32 | 15.02.2019 | 23:42 | 0:10 | 0 | 10 | [5 empty] | B/U- O/C,E/F IN B PHASE IL1-0.74KA,IL2- 0.64KA,IL3-3.85KA,PU TIME=165 ms,TRIP TIME=66ms
47 | Lapanga 160MVA Auto – II |  |  |  |  | 0.053472 | 1 | 17 | [6 empty] | 160 |  | 8760 | 99.99% | 513.3333 | 3504000
|  | 15.02.2019 | 23:32 | 15.02.2019 | 16.02.19 00:49 | 1:17 | 1 | 17 | [5 empty] | PU TIME -225 ms
48 | Lapanga 160MVA Auto – III |  |  |  |  | 0.0625 | 1 | 30 | [6 empty] | 160 |  | 8760 | 99.98% | 600 | 3504000
|  | 15.02.2019 | 23:32 | 15.02.2019 | 16.02.19 00:58 | 1:30 | 1 | 30 | [5 empty] | 87 T1 ,R PHASE ,PU TIME = 453 ms ,TRIP TIME = 308 ms,87 T2, PU TIME =454 ms,TRIP TIME = 309 ms
49 | Mendhasal 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
50 | Mendhasal 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
51 | Meramundali 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
52 | Meramundali 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
53 | Meramundali 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
54 | Narendrapur 160MVA Auto – I |  |  |  |  | 0.35556 | 0 | 12 | [6 empty] | 160 |  | 8760 | 99.99% | 206.6667 | 3504000
|  | 11.10.18 | 3:21 | 11.10.18 | 11:53 | 8:32 |  |  |  |  | 8 | 32 |  | At Narendrapur-Tripped with on 220KV side with REF protection M/R operated and 132KV side M/R operated.and no tripping at 220KV side.(Due to Cyclonic strom Titli.)
|  | 16.10.18 | 5:50 | 16.10.18 | 6:02 | 0:12 | 0 | 12 | [5 empty] | Tripped with E/F operated in 132KV side
55 | Narendrapur 160MVA Auto – II |  |  |  |  | 0 | 0 | 31 | [6 empty] | 160 |  | 8760 | 99.99% | 206.6667 | 3504000
|  | 11.10.18 | 2:40 | 12.10.18 | 12:20 | 33:40 |  |  |  |  | 33 | 40 |  | At Narendrapur-Tripped with on 220KV side with REF protection M/R operated and 132KV side M/R operated.and no tripping at 220KV side.(Due to Cyclonic strom Titli.)
|  | 16.10.18 | 5:50 | 16.10.18 | 6:21 | 0:31 | 0 | 31 | [5 empty] | Tripped with E/F operated in 132KV side
56 | Narendrapur 100MVA Auto – III |  |  |  |  | 0.44236 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
|  | 11.10.18 | 3:21 | 11.10.18 | 13:58 | 10:37 |  |  |  |  | 10 | 37 |  | At Narendrapur-Tripped with on 220KV side with REF protection M/R operated and 132KV side M/R operated.and no tripping at 220KV side.(Due to Cyclonic strom Titli.)
|  | 11.10.18 | 5:50 | 11.10.18 | 6:03 | 0:13 |  |  |  |  | 0 | 13 |  | Tripped with E/F operated in 132KV side
|  | 11.10.18 | 6:16 | 11.10.18 | 6:20 | 0:04 |  |  |  |  | 0 | 4 |  | Tripped with E/F operated in 132KV side
57 | Paradeep 100MVA Auto – I |  |  |  |  | 0.10764 | 2 | 21 | [6 empty] | 100 |  | 8760 | 99.97% | 587.5 | 2190000
|  | 20.09.18 | 10:23 | 20.09.18 | 12:58 | 2:35 | 2 | 21 | [5 empty] | On 220 kV side-O/C.Weather condition was rainy and windy
|  | 26.03.19 | 20:31 | 26.03.19 | 20:52 | 0:21 | 0 | 21 | [5 empty] | Tripped on M/R (Due to snapping of CT jumpers at 132 kV side of AT-2)
58 | Paradeep 160 MVA Auto – II |  |  |  |  | 0.12153 | 2 | 42 | [6 empty] | 160 |  | 8760 | 99.97% | 940 | 3504000
|  | 20.09.18 | 10:23 | 20.09.18 | 12:57 | 2:34 | 2 | 21 | [5 empty] | On 220 kV side-O/C.Weather condition was rainy and windy
|  | 26.03.19 | 20:31 | 26.03.19 | 20:52 | 0:21 | 0 | 21 | [5 empty] | Tripped on M/R (Due to snapping of CT jumpers at 132 kV side of AT-2)
59 | Paradeep 50MVA Auto – III |  |  |  |  | 0.097917 | 2 | 21 | [6 empty] | 50 |  | 8760 | 100% | 293.75 | 1095000
|  | 20.09.18 | 10:23 | 20.09.18 | 12:44 | 2:21 | 2 | 21 | [5 empty] | On 220 kV side-O/C.Weather condition was rainy and windy
60 | Samagara 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
61 | Samagara 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
62 | Tarkera 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
63 | Tarkera 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
64 | Tarkera 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
65 | Tarkera 100MVA Auto – IV |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
66 | Therubali 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
67 | Therubali 100MVA Auto – II |  |  |  |  | 0.031944 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
68 | Therubali 160MVA Auto –I II |  |  |  |  | 0.031944 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
|  | 08.02.19 | 14:53 | 08.02.19 | 15:39 | 0:46 | 0 | 0 | [5 empty] | B-N, 86A, 86B, 86C. Power supply resumed through Auto-I & II
(16): Sub-total (ICTs / Autos); (20): 5999.5833; (21): 196438200 | 3.0542e-05 | 99.9969
[15 empty] | TOTAL (Lines, ICTs & Autos) |  |  |  | 66558.9165 | 328385074.32
[11 empty] | NAFY |  | [ Σ ( OH l x Cktkm l x NSC l ) + Σ ( OH t x MVA t x 2.5 )] [THY x { Σ (Cktkm l x NSC l ) +Σ (MVA t x 2.5 ) } ] | [5 empty] | 0.00020269
[13 empty] | 100 - (100 X NAFY) | [5 empty] | 99.9797
Note on R10: Charged on 05.11.2018
Note on R12: Charged on 05.11.2018
Note on B67: Newly Added
Note on B73: Newly Added
Note on B90: Added newly
Note on B92: Added newly
Note on B94: Added newly
Note on B100: Added newly
Note on Q131: Confrimed from CP Branch
Note on Q133: Confrimed from CP Branch
Note on B143: Earlier it was Bidanasi- Chandaka
Note on Q150: OPTCL: Chandaka-B LILO charged on 28.03.2017
Note on Q156: OPTCL: Chandaka-B LILO charged on 28.03.2017
Note on B229: Part of 400kV Meramundali Mendhasala Ckt - II
Note on Q229: Data confirmed from Sri DPJena
Note on Q248: Atri LILO ckt is added.
Note on Q250: Atri LILO ckt is added.
Note on Q252: Atri LILO ckt is added.
Note on Q255: Atri LILO ckt is added.
Note on Q258: Atri LILO ckt is added.
Note on R448: charged on 28.8.2018
Note on Q554: commissioned on 30.07.2017
Note on Q557: Bhubaneswar Power on LILO charged on 17.02.2016
Note on Q614: Kalunga LILO is charged on 07.09.2015
Note on H726: Multified by factor 2
Note on H728: Multified by factor 2
Note on Q749: GRID STEEL on LILO charged on 24.12.2015
Note on R877: commissioned on 28.02.2018
Note on Q1211: distance between Narendrapur-Balugaon and Balugaon- Khurda added.
Note on Q1304: =1.33+17.43+15.87 km
Note on Q1386: Lapanga LILO charged on 25.11.2015
Note on Q1408: Kalunga LILO is charged on 07.09.2015
Note on R1502: charged on 10.8.2018
Note on R1537: commissioned on 24.09.2017
Note on B1629: Charged on 24.06.2012