## ANNEXURE IV
99.9771 |  | TRANSMISSION SYSTEM OUTAGE DATA
PERIOD : 2019-20
Sl. No. | Name of the Transmission Element | OUTAGE |  | RESTORATION |  | OUTAGE PERIOD | DURATION OF OUTAGE ATTRIBUTABLE TO | [5 empty] | Deemed Availability | Reason of Outage | MVA capacity for ICTs / Autos | Ckm and number of Sub-Conductor for lines | Time considered for availability (hrs) (365 X 24) | Element wise availbility (C19 - C7 - C8/60) / C19 | ( OH l x Cktkm l x NSC l ) ( OH t x MVA t x 2.5 ) | (THY x Ckt KM X NSC) (THY X MVA x 2.5)
|  | DATE | TIME | DATE | TIME |  | UTILITY ITSELF |  | OTHERS |  | System Constraints/Natural Calamities
|  | dd/mm/yy | hh:mm | dd/mm/yy | hh:mm | hh:mm | Hrs | Min | Hrs | Min | Hrs | Min
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
400KV LINES
1 | 400 kV Indravati - Indravati PG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.97 | 8760 | 100% | 0 | 69554.4
2 | 400kV Lapanga -IBTPS Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.491 | 8760 | 100% | 0 | 429082.32
3 | 400kV Lapanga -IBTPS Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.491 | 8760 | 100% | 0 | 429082.32
4 | 400kV Meramundali -New Duburi Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 96.6 | 8760 | 100% | 0 | 1692432
5 | 400kV Meramundali -New Duburi Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 96.6 | 8760 | 100% | 0 | 1692432
6 | 400kV Meramundali -Lapanga-Vedant Ckt- I (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 216.25 | 8760 | 100% | 0 | 3788700
7 | 400kV Meramundali -Lapanga-Vedant Ckt- II (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 216.25 | 8760 | 100% | 0 | 3788700
8 | 400kV Meramundali -Mendhasal Ckt- I |  |  |  |  | 1900-01-03 13:48 | 0 | 0 | [7 empty] | 100.451 | 8760 | 100% | 0 | 1759901.52
|  | 03.05.19 | 10:29 | 03.05.19 | 21:48 | 1900-01-03 13:48 |  |  |  |  | 109 | 48 |  | Tripped (Due to Cyclone Fani)
9 | 400kV Meramundali -Mendhasal Ckt- II |  |  |  |  | 1900-01-03 13:48 | 0 | 0 | [7 empty] | 100.451 | 8760 | 100% | 0 | 1759901.52
|  | 03.05.19 | 10:29 | 03.05.19 | 21:48 | 1900-01-03 13:48 |  |  |  |  | 109 | 48 |  | Tripped (Due to Cyclone Fani)
10 | 400 kV Meramundali - JSPL Ckt- I |  |  |  |  | 0.46528 | 9 | 37 | [7 empty] | 37.916 | 8760 | 99.89% | 729.2511 | 664288.32
|  | 05.06.19 | 19:29 | 06.06.19 | 6:35 | 0.4625 | 9 | 35 | [5 empty] | At MRDL end: DP, Zone-1, FC-17.5 KA Dist.-3.5 k.m.
|  | 24.08.19 | 15:31 | 24.08.19 | 15:35 | 0.0027778 | 0 | 2 | [5 empty] | At Meramundali end:-R-E,IR=30.42KA, At JSPL end:- R-E , Distance=28.29Km, Zone-1,IR=4.498KA
11 | 400 kV Meramundali - JSPL Ckt- II |  |  |  |  | 0.40069 | 9 | 37 | [7 empty] | 37.916 | 8760 | 99.89% | 729.2511 | 664288.32
|  | 05.06.19 | 19:29 | 06.06.19 | 5:04 | 0.39931 | 9 | 35 | [5 empty] | At MRDL end: DP, Zone-1, R, Y O-E/F, FC-31.45 KA
|  | 24.08.19 | 15:35 | 24.08.19 | 15:37 | 0.0013889 | 0 | 2 | [5 empty] | At Meramundali end:- R-E,4.7KM,IR=25.44KA, At JSPL end:- R-E , Distance=43.51Km, Zone-2,IR=2.329KA
12 | 400kV Rengali - Kuchei PG-Kolaghat |  |  |  |  | 0 | 0 | 0 | [7 empty] | 241.5 | 8760 | 100% | 0 | 4231080
1196.886
220KV LINES
12 | 220kV Atri-Pandiabil Ckt-I |  |  |  |  | 0.020139 | 0 | 0 | [7 empty] | 25.2 | 8760 | 100% | 0 | 220752
|  | 03.05.19 | 7:56 | 03.05.19 | 8:25 | 0.020139 |  |  |  |  | 0 | 29 |  | Tripped (Due to Cyclone Fani)
13 | 220kV Pandiabil-Samagara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 47.4 | 8760 | 100% | 0 | 415224
|  | 03.05.19 | 8:59 | Under Breakdown | [9 empty] | Tripped (Due to Cyclone Fani)-Tower Collapse ( still under Break down)
14 | 220kV Atri-Pandiabil Ckt-II |  |  |  |  | 0.74583 | 0 | 0 | [7 empty] | 25.2 | 8760 | 100% | 0 | 220752
|  | 03.05.19 | 7:56 | 04.05.19 | 1:50 | 0.74583 |  |  |  |  | 17 | 54 |  | Tripped (Due to Cyclone Fani)
15 | 220kV Pandiabil-Samagara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 47.4 | 8760 | 100% | 0 | 415224
|  | 03.05.19 | 8:59 | Under Breakdown | [9 empty] | Tripped (Due to Cyclone Fani)-Tower Collapse ( still under Break down)
16 | 220kV Balasore- Bhadrak |  |  |  |  | 0.023611 | 0 | 0 | [7 empty] | 67.95 | 8760 | 100% | 0 | 595242
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
17 | 220kV Balimela-Jayanagar-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 92.072 | 8760 | 100% | 0 | 806550.72
18 | 220kV Balimela-Jayanagar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 92.072 | 8760 | 100% | 0 | 806550.72
19 | 220kV Balimela-Jayanagar-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 93.46 | 8760 | 100% | 0 | 818709.6
20 | 220kV Balimela-Malkangiri Ckt - I |  |  |  |  | 0.020139 | 12 | 35 | [7 empty] | 22.41 | 1428 | 99.12% | 281.9925 | 32001.48
|  | 15.03.20 | 18:41 | 15.03.20 | 18:52 | 0.0076389 | 0 | 11 | [5 empty] | Tripped at Balimela(OHPC) end
|  | 02.03.20 | 13:23 | 02.03.20 | 13:29 | 0.0041667 | 0 | 6 | [5 empty] | Tripped at Balimela(OHPC) end
|  | 01.02.20 | 11:35 | 01.02.20 | 11:41 | 0.0041667 | 0 | 12 | [5 empty] | Tripped at Balimela end
|  | 31.01.20 | 16:37 | 31.01.20 | 16:43 | 0.0041667 | 0 | 6 | [5 empty] | Tripped at Balimela(OHPC) end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
21 | 220kV Balimela-Malkangiri Ckt - II |  |  |  |  | 0.020139 | 12 | 29 | [7 empty] | 22.41 | 1428 | 99.13% | 279.7515 | 32001.48
|  | 15.03.20 | 18:41 | 15.03.20 | 18:52 | 0.0076389 | 0 | 11 | [5 empty] | Tripped at Balimela(OHPC) end
|  | 02.03.20 | 13:23 | 02.03.20 | 13:29 | 0.0041667 | 0 | 6 | [5 empty] | Tripped at Balimela(OHPC) end
|  | 01.02.20 | 11:35 | 01.02.20 | 11:41 | 0.0041667 | 0 | 6 | [5 empty] | Tripped at Balimela end
|  | 31.01.20 | 16:37 | 31.01.20 | 16:43 | 0.0041667 | 0 | 6 | [5 empty] | Tripped at Balimela(OHPC) end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
22 | 220kV Balimela PH -Balimela |  |  |  |  | 0.063194 | 15 | 2 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 0.2 | 8760 | 99.83% | 3.0067 | 1752
|  | 15.03.20 | 18:41 | 15.03.20 | 18:52 | 0.0076389 | 0 | 22 | [5 empty] | Tripped at Balimela(OHPC) end
|  | 02.03.20 | 13:23 | 02.03.20 | 13:29 | 0.0041667 | 0 | 12 | [5 empty] | Tripped at Balimela(OHPC) end
|  | 31.01.20 | 16:37 | 31.01.20 | 16:43 | 0.0041667 | 0 | 12 | [5 empty] | Tripped at Balimela(OHPC) end
|  | 03.11.19 | 9:42 | 03.11.19 | 10:50 | 0.047222 | 2 | 16 | [5 empty] | Tripped at Balimela(OHPC) end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
23 | 220kV Balimela PH -Upper Sileru |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.76 | 8760 | 100% | 0 | 216897.6
24 | 220kV Barkote-Bonai |  |  |  |  | 0 | 0 | 0 | [7 empty] | 55.807 | 8760 | 100% | 0 | 488869.32
25 | 220kV Bonai-Tarkera |  |  |  |  | 0 | 0 | 0 | [7 empty] | 47.467 | 8760 | 100% | 0 | 415810.92
26 | 220kV Bhanjanagar-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 134.14 | 8760 | 100% | 0 | 1175066.4
27 | 220kV Bhanjanagar-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 134.14 | 8760 | 100% | 0 | 1175066.4
28 | 220kV Bhanjanagar-Mendhasal ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 136.47 | 8760 | 100% | 0 | 1195477.2
29 | 220kV Bhanjanagar-Nayagarh ckt |  |  |  |  | 0.025 | 0 | 15 | [7 empty] | 63 | 8760 | 100% | 15.75 | 551880
|  | 19.08.19 | 12:47 | 19.08.19 | 13:02 | 0.010417 | 0 | 15 | [5 empty] | At Bhanjangar end: Zone-I, Dist.-26 k.m, FC-1.8 KA,L3 TO E/F, Tripped at Nayagarh end : Z-1,D=60.6KM
|  | 03.05.19 | 11:12 | 03.05.19 | 11:33 | 0.014583 |  |  |  |  | 0 | 21 |  | Tripped during extreme severe cyclone 'FANI
30 | 220kV Bidanasi -Mendhasal Ckt-I |  |  |  |  | 0.0034722 | 0 | 5 | [7 empty] | 15 | 8760 | 100% | 1.25 | 131400
|  | 25.10.19 | 7:25 | 25.10.19 | 7:28 | 0.0020833 | 0 | 3 | [5 empty] | At Meramundali end-Tripped
|  | 14.09.19 | 13:27 | 14.09.19 | 13:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped from Mendhasal end
31 | 220kV Bidanasi -Mendhasal Ckt-II |  |  |  |  | 1899-12-31 11:15 | 0 | 18 | [7 empty] | 15 | 8760 | 100% | 4.5 | 131400
|  | 23.02.20 | 5:20 | 24.02.20 | 16:35 | 1899-12-31 11:15 | 0 | 18 | [5 empty] | At Mendhasala End: Zone-I, R-Phase,7.47KA, 4 KM ( Due to jumper snapping at Loc.No.74 & bend the cross arm of Loc.No.73). Cuttack, Phulnakhara P/S availed from Bidanasi end
32 | 220kV Bidanasi -Cuttack Ckt-I |  |  |  |  | 1899-12-31 21:52 | 13 | 17 | [7 empty] | 9.3 | 8760 | 99.85% | 123.535 | 81468
|  | 23.02.20 | 5:20 | 24.02.20 | 16:35 | 1899-12-31 11:15 | 0 | 18 | [5 empty] | At Mendhasala End: Zone-I, R-Phase,7.47KA, 4 KM ( Due to jumper snapping at Loc.No.74 & bend the cross arm of Loc.No.73). Cuttack, Phulnakhara P/S availed from Bidanasi end
|  | 22.02.20 | 5:20 | 22.02.20 | 5:27 | 0.0048611 | 0 | 7 | [5 empty] | At Bidanasi end: Tripped
|  | 03.12.19 | 17:15 | 03.12.19 | 17:16 | 00:01 | 0 | 1 | [5 empty] | Bidanasi end-Tripped
|  | 02.12.19 | 21:03 | 02.12.19 | 21:10 | 0.0048611 | 0 | 6 | [5 empty] | Bidanasi end-Tripped
|  | 02.12.19 | 9:14 | 02.12.19 | 9:25 | 0.0076389 | 0 | 8 | [5 empty] | Bidanasi end-Tripped
|  | 26.10.19 | 1:12 | 26.10.19 | 1:17 | 0.0034722 | 0 | 5 | [5 empty] | At Bidanasi end-Tripped
|  | 10.10.19 | 13:14 | 10.10.19 | 13:17 | 0.0020833 | 0 | 3 | [5 empty] | At Bidanasi end-Tripped
|  | 25.10.19 | 7:25 | 25.10.19 | 7:28 | 0.0020833 | 0 | 3 | [5 empty] | At Meramundali end-Tripped
|  | 30.09.19 | 17:31 | 30.09.19 | 17:36 | 0.0034722 | 0 | 5 | [5 empty] | Power supply failure from Bidanasi end
|  | 29.09.19 | 7:07 | 29.09.19 | 7:12 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on E/F at Bidanasi end
|  | 31.05.19 | 8:06 | 31.05.19 | 13:44 | 0.23472 | 0 | 5 | [5 empty] | At Bidanasi- Zone-1,Y & B-ph to Ground, Fault current-10.29kamps , Fault Location 2.9 Km.Y-ph insulator burst at location no-14
|  | 25.05.19 | 12:33 | 25.05.19 | 16:44 | 0.17431 | 0 | 9 | [5 empty] | At Bidanasi- Zone-1,r-ph to Ground, Ir-769.5A , Fault Location 14.01 Km.Tree falling over the conductor. Availed alternate supply from 220 kv mendhasal feeder.
|  | 03.05.19 | 12:29 | 05.05.19 | 7:40 | 43:11 |  |  |  |  | 43 | 11 |  | Tripped at Meramundali end during extreme severe cyclone 'FANI
|  | 14.09.19 | 13:27 | 14.09.19 | 13:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped from Mendhasal end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
33 | 220kV Bidanasi -Cuttack Ckt-II |  |  |  |  | 1899-12-31 21:34 | 13 | 17 | [7 empty] | 9.3 | 8760 | 99.85% | 123.535 | 81468
|  | 23.02.20 | 5:20 | 24.02.20 | 16:35 | 1899-12-31 11:15 | 0 | 18 | [5 empty] | At Mendhasala End: Zone-I, R-Phase,7.47KA, 4 KM ( Due to jumper snapping at Loc.No.74 & bend the cross arm of Loc.No.73). Cuttack, Phulnakhara P/S availed from Bidanasi end
|  | 22.02.20 | 5:20 | 22.02.20 | 5:27 | 0.0048611 | 0 | 7 | [5 empty] | At Bidanasi end: Tripped
|  | 03.12.19 | 17:15 | 03.12.19 | 17:16 | 00:01 | 0 | 1 | [5 empty] | Bidanasi end-Tripped
|  | 02.12.19 | 21:04 | 02.12.19 | 21:10 | 00:06 | 0 | 6 | [5 empty] | Bidanasi end-Tripped
|  | 02.12.19 | 9:15 | 02.12.19 | 9:23 | 00:08 | 0 | 8 | [5 empty] | Bidanasi end-Tripped
|  | 26.10.19 | 1:12 | 26.10.19 | 1:17 | 0.0034722 | 0 | 5 | [5 empty] | At Bidanasi end-Tripped
|  | 10.10.19 | 13:14 | 10.10.19 | 13:17 | 0.0020833 | 0 | 3 | [5 empty] | At Bidanasi end-Tripped
|  | 25.10.19 | 7:25 | 25.10.19 | 7:28 | 0.0020833 | 0 | 3 | [5 empty] | At Meramundali end-Tripped
|  | 30.09.19 | 17:31 | 30.09.19 | 17:36 | 0.0034722 | 0 | 5 | [5 empty] | Power supply failure from Bidanasi end
|  | 29.09.19 | 7:07 | 29.09.19 | 7:12 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on E/F at Bidanasi end
|  | 31.05.19 | 8:06 | 31.05.19 | 13:44 | 0.23472 | 0 | 5 | [5 empty] | At Bidanasi- Zone-1,Y & B-ph to Ground, Fault current-10.29kamps , Fault Location 2.9 Km.Y-ph insulator burst at location no-14
|  | 25.05.19 | 12:33 | 25.05.19 | 16:44 | 0.17431 | 0 | 9 | [5 empty] | At Bidanasi- Zone-1,r-ph to Ground, Ir-769.5A , Fault Location 14.01 Km.Tree falling over the conductor. Availed alternate supply from 220 kv mendhasal feeder.
|  | 03.05.19 | 12:29 | 05.05.19 | 7:40 | 43:11 |  |  |  |  | 43 | 11 |  | Tripped at Meramundali end during extreme severe cyclone 'FANI
|  | 14.09.19 | 13:27 | 14.09.19 | 13:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped from Mendhasal end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
34 | 220kV Bisra-Tarkera-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.335 | 8760 | 100% | 0 | 134334.6
35 | 220kV Budhipadar-Aditya Aluminium Ckt.-I |  |  |  |  | 0.040972 | 0 | 50 | [7 empty] | 20.507 | 8760 | 99.99% | 17.0892 | 179641.32
|  | 12.06.19 | 0:37 | 13.06.19 | 1:36 | 0.040972 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
36 | 220kV Budhipadar-Aditya Aluminium Ckt.-II |  |  |  |  | 0.040972 | 0 | 50 | [7 empty] | 20.507 | 8760 | 99.99% | 17.0892 | 179641.32
|  | 12.06.19 | 0:37 | 13.06.19 | 1:36 | 0.040972 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
37 | 220kV Budhipadar-Basundhara Ckt-I |  |  |  |  | 0.051389 | 0 | 50 | [7 empty] | 35.29 | 8760 | 99.99% | 29.4083 | 309140.4
|  | 12.06.19 | 0:37 | 13.06.19 | 1:51 | 0.051389 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
38 | 220kV Budhipadar-Basundhara Ckt-II |  |  |  |  | 0.0625 | 1 | 6 | [7 empty] | 35.29 | 8760 | 99.99% | 38.819 | 309140.4
|  | 12.06.19 | 0:37 | 13.06.19 | 1:51 | 0.051389 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
|  | 17.09.19 | 13:03 | 17.09.19 | 13:19 | 0.011111 | 0 | 16 | [5 empty] | Tripped at Budhipadar end on E/F , B-ph
39 | 220kV Budhipadar-IbTPS -I |  |  |  |  | 0.034722 | 1 | 40 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 99.98% | 43.3333 | 227760
|  | 12.06.19 | 0:37 | 13.06.19 | 1:27 | 0.034722 | 1 | 40 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
40 | 220kV Budhipadar-IbTPS -II |  |  |  |  | 0.036111 | 1 | 40 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 99.98% | 43.3333 | 227760
|  | 12.06.19 | 0:37 | 13.06.19 | 1:29 | 0.036111 | 1 | 40 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
41 | 220kV Budhipadar-IbTPS -III |  |  |  |  | 1900-01-23 00:41 | 3 | 12 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 99.96% | 81.216 | 222328.8
|  | 02.06.19 | 14:35 | 26.06.19 | 12:22 | 1900-01-22 21:47 | 1 | 16 | [5 empty] | At-Budhipadar end: L2E, Zone-1, IL2-23.87 kA Distance-3.1 k.m. (Cross arm of tower at Loc.-13 bent and earth wire broken at Loc.-16 of DC Tower.)
|  | 19.03.20 | 15:30 | 19.03.20 | 18:24 | 0.12083 | 1 | 56 | [5 empty] | At Budhipadar End B-Phase Trip, Zone-I, FD= 1.75Kms, FL= L3-N, IL3=29.8 KA At IBTPS End: Zone-I & II operated, Bphase-E/F
42 | 220kV Budhipadar-IbTPS -IV |  |  |  |  | 1900-01-22 21:50 | 1 | 16 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 99.99% | 32.148 | 222328.8
|  | 02.06.19 | 14:35 | 26.06.19 | 12:25 | 1900-01-22 21:50 | 1 | 16 | [5 empty] | At-Budhipadar end: L2E, Zone-1, IL2-23.87 kA Distance-3.1 k.m. (Cross arm of tower at Loc.-13 bent and earth wire broken at Loc.-16 of DC Tower.)
43 | 220kV Budhipadar-Raigarh-I |  |  |  |  | 0.073611 | 0 | 50 | [7 empty] | 60 | 8760 | 99.99% | 50 | 525600
|  | 12.06.19 | 0:37 | 13.06.19 | 2:23 | 0.073611 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
44 | 220kV Budhipadar-Korba-II |  |  |  |  | 0.063194 | 0 | 50 | [7 empty] | 60 | 8760 | 99.99% | 50 | 525600
|  | 12.06.19 | 0:37 | 13.06.19 | 2:08 | 0.063194 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
45 | 220kV Budhipadar-Lapanga-I |  |  |  |  | 0.054167 | 0 | 50 | [7 empty] | 20 | 8760 | 99.99% | 16.6667 | 175200
|  | 12.06.19 | 0:37 | 13.06.19 | 1:55 | 0.054167 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
46 | 220kV Budhipadar-Lapanga-II |  |  |  |  | 0.094444 | 0 | 50 | [7 empty] | 20 | 8760 | 99.99% | 16.6667 | 175200
|  | 12.06.19 | 0:37 | 13.06.19 | 2:53 | 0.094444 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
47 | 220kV Budhipadar-SPS Feeder-I |  |  |  |  | 0.051389 | 0 | 50 | [7 empty] | 13.424 | 8760 | 99.99% | 11.1867 | 117594.24
|  | 12.06.19 | 0:37 | 13.06.19 | 1:51 | 0.051389 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
48 | 220kV Budhipadar-SPS Feeder-II |  |  |  |  | 0.051389 | 0 | 50 | [7 empty] | 13.424 | 8760 | 99.99% | 11.1867 | 117594.24
|  | 12.06.19 | 0:37 | 13.06.19 | 1:51 | 0.051389 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
49 | 220kV Budhipadar-Bhusan Ckt-I |  |  |  |  | 0.051389 | 0 | 50 | [7 empty] | 14.92 | 8760 | 99.99% | 12.4333 | 130699.2
|  | 12.06.19 | 0:37 | 13.06.19 | 1:51 | 0.051389 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
50 | 220kV Budhipadar-Bhusan Ckt II |  |  |  |  | 0.051389 | 0 | 50 | [7 empty] | 14.92 | 8760 | 99.99% | 12.4333 | 130699.2
|  | 12.06.19 | 0:37 | 13.06.19 | 1:51 | 0.051389 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
51 | 220kV Chandaka -Mendhasal Ckt-I |  |  |  |  | 365:41 | 0 | 0 | [7 empty] | 19 | 8760 | 100% | 0 | 166440
|  | 03.05.19 | 8:20 | 18.05.19 | 13:41 | 365:41 |  |  |  |  | 365 | 41 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'
52 | 220kV Chandaka- Mendhasal ckt II |  |  |  |  | 106:45 | 0 | 0 | [7 empty] | 19.9 | 8760 | 100% | 0 | 174324
|  | 03.05.19 | 11:05 | 07.05.19 | 21:50 | 106:45 |  |  |  |  | 106 | 45 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'
53 | 220kV Chandaka- Mendhasal ckt III |  |  |  |  | 365:41 | 0 | 0 | [7 empty] | 19.9 | 8760 | 100% | 0 | 174324
|  | 03.05.19 | 8:20 | 18.05.19 | 13:41 | 365:41 |  |  |  |  | 365 | 41 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'
54 | 220kV Chandaka- Chandaka-B |  |  |  |  | 126:46 | 0 | 0 | [7 empty] | 0.1 | 8760 | 100% | 0 | 876
|  | 03.05.19 | 10:23 | 03.05.19 | 14:46 | 126:46 |  |  |  |  | 126 | 46 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'
55 | 220kV Chandaka-B-Mendhasal ckt IV |  |  |  |  | 126:46 | 0 | 0 | [7 empty] | 18.96 | 8760 | 100% | 0 | 166089.6
|  | 03.05.19 | 10:23 | 03.05.19 | 14:46 | 126:46 |  |  |  |  | 126 | 46 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'
56 | 220kV Duburi-Duburi (New) Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.38 | 8760 | 100% | 0 | 55888.8
57 | 220kV Duburi-Duburi (New) Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.38 | 8760 | 100% | 0 | 55888.8
58 | 220kV Duburi-NINL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6 | 8760 | 100% | 0 | 52560
59 | 220kV Indravati PH-Therubali-I (TVL) |  |  |  |  | 0.079861 | 2 | 2 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 99.98% | 175.2733 | 755112
|  | 20.06.19 | 19:08 | 20.06.19 | 20:14 | 0.045833 | 0 | 42 | [5 empty] | #2, #3 running Units of Indravati PH tripped
|  | 27.05.19 | 17:50 | 27.05.19 | 18:39 | 0.034028 | 1 | 20 | [5 empty] | AGT due to Grid Disturbance at Therubali end
60 | 220kV Indravati PH-Therubali-II |  |  |  |  | 0.59236 | 2 | 2 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 99.98% | 175.2733 | 755112
|  | 20.06.19 | 19:08 | 21.06.19 | 9:21 | 0.59236 | 0 | 42 | [5 empty] | #2, #3 running Units of Indravati PH tripped
|  | 27.05.19 | 17:50 | 27.05.19 | 19:32 | 01:42 | 1 | 20 | [5 empty] | AGT due to Grid Disturbance at Therubali end
61 | 220kV Indravati PH-Therubali-III |  |  |  |  | 0.061806 | 2 | 2 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 91 | 8760 | 99.98% | 185.0333 | 797160
|  | 20.06.19 | 19:08 | 20.06.19 | 20:37 | 0.061806 | 0 | 42 | [5 empty] | #2, #3 running Units of Indravati PH tripped
|  | 27.05.19 | 17:50 | 27.05.19 | 19:11 | 01:31 | 1 | 20 | [5 empty] | Grid Disturbance at Therubali end but Circuit was not tripped at Therubali end.
62 | 220kV Indravati PH-Jayapatna-Kasipur-Therubali-IV |  |  |  |  | 0.043056 | 2 | 2 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 91 | 8760 | 99.98% | 185.0333 | 797160
|  | 20.06.19 | 19:08 | 20.06.19 | 20:10 | 0.043056 | 0 | 42 | [5 empty] | #2, #3 running Units of Indravati PH tripped
|  | 27.05.19 | 17:50 | 27.05.19 | 6:35 | 12:45 | 1 | 20 | [5 empty] | Grid Disturbance at Therubali end. Back up protection operated.
63 | 220kV Jayanagar-Jeypore PG-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
64 | 220kV Jayanagar-Jeypore PG-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
65 | 220kV Jayanagar-Jeypore PG-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 1764 | 100% | 0 | 13635.72
66 | 220kV Jayanagar-Jeypore PG-IV |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 1764 | 100% | 0 | 13635.72
67 | 220kV Jayanagar-Laxmipur ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65 | 8760 | 100% | 0 | 569400
68 | 220kV Jayanagar-Laxmipur ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65 | 8760 | 100% | 0 | 569400
69 | 220kV Jindal-Jamsedpur DVC |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.8 | 8760 | 100% | 0 | 182208
70 | 220kV Joda-RCPur |  |  |  |  | 0.080556 | 13 | 49 | [7 empty] | 15.5 | 8760 | 99.84% | 214.1583 | 135780
|  | 28.05.19 | 14.33 | 28.05.19 | 15.02 | 0.020139 | 0 | 22 | [5 empty] | Fdr tripped at both end. At JODA end- DP Relay, Dist= 44.358Km, Fault loop= L2-L3, IL1=521.17A, IL2=1015.17A, IL3=1524.47A, IN=13.51A At RCPUR end- DP Relay, Dist= 77.26Km, Zone-1, Fault loop= L2-L3,IL1=518.7A, IL2=3.187KA, IL3=2.727KA
|  | 28.05.19 | 12:09 | 28.05.19 | 12:31 | 0.015278 | 0 | 22 | [5 empty] | Fdr tripped at both end. At JODA end- B/U relay-(E/F) (1)Dir. O/C tripped, (2)E/F relay (3)IL1=0.04 KA, IL2=1.38 KA, IL3=0.04KA At RCPUR end-B/U relay-(E/F) (1) O/C tripped, (2)E/F relay (3)DP relay -: IL1=409.0A, IL2=1.740 KA, IL3=336.8KA,dist=75.12km,zone-1.
|  | 07.05.19 | 17:36 | 07.05.19 | 18.41 | 0.045139 | 1 | 5 | [5 empty] | Tripped at TTPS end due to 220 kV incomer bus-1 pull out.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
71 | 220kV Joda-Jindal |  |  |  |  | 0.090972 | 2 | 0 | [7 empty] | 21 | 8760 | 99.98% | 42 | 183960
|  | 28.05.19 | 14.35 | 28.05.19 | 15.12 | 0.025694 | 0 | 37 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 07.05.19 | 17.43 | 07.05.19 | 19.17 | 0.065278 | 1 | 23 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end due to 220 kV Bus-01 pull out.
72 | 220kV Joda-TSIL Ckt. |  |  |  |  | 0.084028 | 2 | 1 | [7 empty] | 7.3 | 8760 | 99.98% | 14.7217 | 63948
|  | 28.05.19 | 14.35 | 28.05.19 | 15.13 | 0.026389 | 0 | 38 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 07.05.19 | 17:37 | 07.05.19 | 19:00 | 0.057639 | 1 | 23 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end due to 220 kV Bus-01 pull out.
73 | 220kV Katapalli- HINDALCO Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
74 | 220kV Katapalli- HINDALCO Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
75 | 220kV Katapalli- Bargarh New Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 52.035 | 8760 | 99.98% | 0 | 455826.6
76 | 220kV Bargarh New- New Bolangir Ckt-I |  |  |  |  | 0.13472 | 14 | 53 | [7 empty] | 65.885 | 8760 | 100% | 980.5884 | 577152.6
|  | 13.01.20 | 6:46 | 13.01.20 | 7:13 | 0.01875 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 24.09.19 | 17:49 | 24.09.19 | 19:00 | 0.049306 | 1 | 11 | [5 empty] | At New Bolangir end: DP, Zone-I, R ph.-E/F, Dist.-19.75 k.m, FC-7.33 KA (R-Phase insulator string bursted at Loc no-292 & 293.)
|  | 23.09.19 | 18:42 | 23.09.19 | 19:26 | 0.030556 | 0 | 30 | [5 empty] | Tripped at 220KV GSS Bargarh(New) end with back up relay pick up at New Bolangir end.
|  | 13.08.19 | 5:53 | 13.08.19 | 6:33 | 0.027778 | 0 | 40 | [5 empty] | Tripped at Bolangir New end. P/s availed from Kesinga.
|  | 12.08.19 | 5:07 | 12.08.19 | 5:19 | 0.0083333 | 0 | 12 | [5 empty] | Tripped on O/C at Bolangir New end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
77 | 220kV Katapalli- Bolangir PG |  |  |  |  | 0.015278 | 0 | 20 | [7 empty] | 118.45 | 8760 | 100% | 39.4833 | 1037622
|  | 13.08.19 | 5:53 | 13.08.19 | 6:15 | 0.015278 | 0 | 20 | [5 empty] | Tripped at Bolangir New end
78 | 220kV Keonjhar PG - Keonjhar Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
79 | 220kV Keonjhar PG - Keonjhar Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
80 | 220kV Bolangir PG- New Bolangir Ckt-II |  |  |  |  | 0.15833 | 13 | 36 | [7 empty] | 3 | 8760 | 99.84% | 40.8 | 26280
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 23.09.19 | 18:42 | 23.09.19 | 19:06 | 0.016667 | 0 | 24 | [5 empty] | At New Bolangir end-Tripped on distance protection showing fault in Zone-I and fault location-126.5mtr. (Due to 220KV R-Phase conductor snapped between dead end tower to gantry.)
|  | 17.09.19 | 19:12 | 17.09.19 | 20:29 | 0.053472 |  |  | 0 | 21 |  |  |  | At Bolangir New end:- Tripped on Dir O/C, E/F (Due to snapping of conductor at PGCIL end)
|  | 13.08.19 | 5:19 | 13.08.19 | 6:10 | 0.035417 | 0 | 40 | [5 empty] | Tripped at Bolangir New end. P/s availed from Kesinga.
|  | 12.08.19 | 5:07 | 12.08.19 | 6:03 | 0.038889 | 0 | 12 | [5 empty] | Tripped at Bolangir PG end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
81 | 220kV Kuchei PG-Balasore Ckt I |  |  |  |  | 0.023611 | 0 | 0 | [7 empty] | 76.859 | 8760 | 100% | 0 | 673284.84
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
82 | 220kV Kuchei PG-Balasore Ckt-II |  |  |  |  | 0.023611 | 0 | 0 | [7 empty] | 76.859 | 8760 | 100% | 0 | 673284.84
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
83 | 220kV Lapanga-Katapali-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 49.72 | 8760 | 100% | 0 | 435547.2
84 | 220kV Lapanga-Katapali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 49.72 | 8760 | 100% | 0 | 435547.2
85 | 220kV Laxmipur - Therubali ckt-I |  |  |  |  | 0.027778 | 13 | 19 | [7 empty] | 56 | 8760 | 99.85% | 745.7333 | 490560
|  | 20.06.19 | 19:08 | 20.06.19 | 19:30 | 0.015278 | 0 | 21 | [5 empty] | #2, #3 running Units of Indravati PH tripped
|  | 10.08.19 | 20:11 | 10.08.19 | 20:29 | 0.0125 | 0 | 18 | [5 empty] | Back up relay operated at Therubali end
|  | 27.05.19 | 17:50 | 28.05.19 | 15:22 | 21:32 | 0 | 40 | [5 empty] | R-N,Zone-3,Dist.-106KM at Laxmipur end. Circuit was not tripped at Therubali end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
86 | 220kV Laxmipur - Therubali ckt-II |  |  |  |  | 0.042361 | 13 | 1 | [7 empty] | 56 | 8760 | 99.85% | 728.9333 | 490560
|  | 20.06.19 | 19:08 | 20.06.19 | 19:29 | 0.014583 | 0 | 21 | [5 empty] | #2, #3 running Units of Indravati PH tripped
|  | 10.08.19 | 20:11 | 10.08.19 | 20:29 | 0.0125 | 0 | 18 | [5 empty] | Back up relay operated at Therubali end
|  | 27.05.19 | 17:50 | 27.05.19 | 18:12 | 0.015278 | 0 | 22 | [5 empty] | R phase to N line fault
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
87 | 220kV Laxmipur - Utkal Alumina ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.04 | 8760 | 100% | 0 | 271910.4
88 | 220kV Laxmipur - Utkal Alumina ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.04 | 8760 | 100% | 0 | 271910.4
89 | 220kV Laxmipur - NALCO ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 36.99 | 7356 | 100% | 0 | 272098.44
90 | 220kV Laxmipur - NALCO ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 36.99 | 7356 | 100% | 0 | 272098.44
91 | 220kV Mendhasala-Godi Sahi-Bidanasi-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 32.991 | 8760 | 100% | 0 | 289001.16
92 | 220kV Meramundali-Godi sahi-Bidanasi-II |  |  |  |  | 1899-12-31 23:22 | 0 | 14 | [7 empty] | 90.942 | 8760 | 100% | 21.2198 | 796651.92
|  | 31.05.19 | 8:06 | 31.05.19 | 13:44 | 0.23472 | 0 | 5 | [5 empty] | At Bidanasi- Zone-1,Y & B-ph to Ground, Fault current-10.29kamps , Fault Location 2.9 Km.Y-ph insulator burst at location no-14
|  | 25.05.19 | 12:33 | 25.05.19 | 16:44 | 0.17431 | 0 | 9 | [5 empty] | At Bidanasi- Zone-1,r-ph to Ground, Ir-769.5A , Fault Location 14.01 Km.Tree falling over the conductor. Availed alternate supply from 220 kv mendhasal feeder.
|  | 03.05.19 | 12:29 | 05.05.19 | 7:40 | 1899-12-31 19:11 |  |  |  |  | 43 | 11 |  | Tripped at Meramundali end during extreme severe cyclone 'FANI
93 | 220kV Meramundali-Bhusan Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
94 | 220kV Meramundali-Bhusan Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
95 | 220kV Meramundali-Duburi-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 95.556 | 8760 | 100% | 0 | 837070.56
96 | 220kV Meramundali-Duburi-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 95.556 | 8760 | 100% | 0 | 837070.56
97 | 220kV NALCO-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
98 | 220kV NALCO-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
99 | 220kV Nayagarh-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 68.58 | 8760 | 100% | 0 | 600760.8
100 | 220kV Narendrapur-Atri Ckt-I |  |  |  |  | 1900-01-27 01:03 | 0 | 9 | [7 empty] | 150.35 | 8760 | 100% | 22.5525 | 1317066
|  | 18.09.19 | 12:00 | 18.09.19 | 22:22 | 0.43194 | 0 | 9 | [5 empty] | At Narendrapur end;-DP, ZONE-3, IR=443.6 A, IY=1.359kA, IB=998.8 A,VAN=126.9 KV, VBN=118.8 KV, VCN= 119.9KV,Distance=204.9 km (Problem in line CVT)
|  | 03.05.19 | 0:39 | 30.05.19 | 15:27 | 1900-01-26 14:41 |  |  |  |  | 662 | 41 |  | Tripped (Due to Cyclone Fani)
101 | 220kV Atri-Mendhasal Ckt-I |  |  |  |  | 1899-12-31 23:04 | 0 | 0 | [7 empty] | 24.85 | 8760 | 100% | 0 | 217686
|  | 03.05.19 | 8:36 | 05.05.19 | 7:40 | 1899-12-31 23:04 |  |  |  |  | 47 | 4 |  | Tripped (Due to Cyclone Fani)
102 | 220kV Narendrapur-Atri Ckt-II |  |  |  |  | 1900-01-27 00:27 | 0 | 14 | [7 empty] | 150.35 | 8760 | 100% | 35.0817 | 1317066
|  | 18.09.19 | 12:01 | 18.09.19 | 14:16 | 0.09375 | 0 | 14 | [5 empty] | At Narendrapur end:- Zone-1, R ph. -N, IR = 2.063 kA, VAN = 106.6 kV Dist = 64.30 km
|  | 03.05.19 | 7:18 | 03.05.19 | 15:29 | 0.31181 |  |  |  |  | 7 | 29 |  | Tripped (Due to Cyclone Fani)
|  | 03.05.19 | 0:39 | 30.05.19 | 15:29 | 1900-01-26 14:43 |  |  |  |  | 662 | 43 |  | Tripped (Due to Cyclone Fani)
103 | 220kV Atri-Infocity-II Ckt-II |  |  |  |  | 0.55903 | 0 | 0 | [7 empty] | 21.3 | 8760 | 100% | 0 | 186588
|  | 03.05.19 | 7:56 | 03.05.19 | 21:21 | 0.55903 |  |  |  |  | 13 | 25 |  | Tripped (Due to Cyclone Fani)
104 | 220kV Infocity-II-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.47 | 8760 | 100% | 0 | 47917.2
105 | 220kV New Duburi -Balasore |  |  |  |  | 0 | 0 | 0 | [7 empty] | 140.97 | 8760 | 100% | 0 | 1234897.2
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
106 | 220kV New Duburi -Bhadrakh |  |  |  |  | 0 | 0 | 0 | [7 empty] | 73.798 | 8760 | 100% | 0 | 646470.48
107 | 220kV New Duburi-Paradeep Ckt-I |  |  |  |  | 0.065278 | 13 | 34 | [7 empty] | 113.433 | 8760 | 99.85% | 1538.9077 | 993673.08
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 19.09.19 | 3:48 | 19.09.19 | 5:02 | 0.051389 | 1 | 14 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-2, Dist.-119.2 k.m.
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At New Duburi end:- DP, Zone-I, Y ph-E/F, Dist.-27 k.m, FC-6.54 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
108 | 220kV New Duburi-Paradeep Ckt-II |  |  |  |  | 0.12153 | 0 | 55 | [7 empty] | 113.433 | 8760 | 99.99% | 103.9802 | 993673.08
|  | 22.01.20 | 15:07 | 22.01.20 | 16:50 | 0.071528 | 0 | 10 | [5 empty] | At Paradeep end: Tripped on A-G Z1,D-13.3KM
|  | 19.09.19 | 3:48 | 19.09.19 | 5:00 | 0.05 | 0 | 45 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-II Dist.-112 k.m, FC-7.83 kA.At 04:33-Kendrapara availed P/S from Jajpur Road end .
109 | 220kV Paradeep - IOCL Ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6 | 8760 | 100% | 0 | 52560
110 | 220kV Paradeep - ESSAR Steel Ckt -I |  |  |  |  | 0.024306 | 0 | 35 | [7 empty] | 8.868 | 8760 | 99.99% | 5.173 | 77683.68
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 17.01.20 | 17:06 | 0.017361 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F
111 | 220kV Paradeep - ESSAR Steel Ckt -II |  |  |  |  | 0.024306 | 0 | 35 | [7 empty] | 8.868 | 8760 | 99.99% | 5.173 | 77683.68
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 17.01.20 | 17:06 | 0.017361 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F
112 | 220kV Rengali PH-Nalco-TTPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 71.337 | 8760 | 100% | 0 | 624912.12
113 | 220kV Rengali GD-Rengali PG -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.4 | 8760 | 100% | 0 | 3504
114 | 220kV Rengali GD-Rengali PG -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.4 | 8760 | 100% | 0 | 3504
115 | 220kV Rengali GD-Chandiposh (T)-Tarkera |  |  |  |  | 0 | 0 | 0 | [7 empty] | 162.08 | 8760 | 100% | 0 | 1419820.8
116 | 220kV Rengali GD-Barkote |  |  |  |  | 0 | 0 | 0 | [7 empty] | 48.776 | 8760 | 100% | 0 | 427277.76
117 | 220kV Rengali PH-Rengali GD -I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
118 | 220kV Rengali PH-Rengali GD -II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
119 | 220kV Rengali PH -STPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 29.5 | 8760 | 100% | 0 | 258420
120 | 220kV STPS (Kaniha)-TTPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 34.5 | 8760 | 100% | 0 | 302220
121 | 220kV STPS-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
122 | 220kV STPS-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
123 | 220kV Tarkera-Budhipadar-I |  |  |  |  | 1899-12-31 16:35 | 0 | 50 | [7 empty] | 109 | 8760 | 99.99% | 90.8333 | 954840
|  | 12.06.19 | 0:37 | 13.06.19 | 17:12 | 1899-12-31 16:35 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
124 | 220kV Tarkera-Budhipadar-II |  |  |  |  | 0.034722 | 0 | 50 | [7 empty] | 109 | 8760 | 99.99% | 90.8333 | 954840
|  | 12.06.19 | 0:37 | 13.06.19 | 1:27 | 0.034722 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
125 | 220kV Tarkera-RSP-I |  |  |  |  | 0.16736 | 4 | 1 | [7 empty] | 10 | 8760 | 99.95% | 40.1667 | 87600
|  | 02.09.19 | 15:23 | 02.09.19 | 19:24 | 0.16736 | 4 | 1 | [5 empty] | At Tarkera end:- Dist.-19.3 k.m, FC-8.32 KA (Snapping of earth wire)
126 | 220kV Tarkera-RSP-II |  |  |  |  | 0.23472 | 4 | 1 | [7 empty] | 10 | 8760 | 99.95% | 40.1667 | 87600
|  | 02.09.19 | 15:23 | 02.09.19 | 21:01 | 0.23472 | 4 | 1 | [5 empty] | Tripped at Tarkera end due to breaker problem
127 | 220kV Therubali-Narendrapur-I |  |  |  |  | 0.088889 | 13 | 18 | [7 empty] | 196 | 8760 | 99.85% | 2606.8 | 1716960
|  | 20.06.19 | 19:08 | 20.06.19 | 19:40 | 0.022222 | 0 | 21 | [5 empty] | #2, #3 running Units of Indravati PH tripped
|  | 18.09.19 | 12:00 | 18.09.19 | 12:17 | 0.011806 | 0 | 17 | [5 empty] | At Narendrapur end: Zone-I, R ph.-E/F, Dist.-76.25 k.m.
|  | 27.05.19 | 17:50 | 27.05.19 | 19:09 | 0.054861 | 0 | 40 | [5 empty] | Grid disturbance at Therubali S/s But circuit was not tripped at Therubali end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
128 | 220kV Therubali-Narendrapur-II |  |  |  |  | 0.14306 | 13 | 18 | [7 empty] | 196 | 8760 | 99.85% | 2606.8 | 1716960
|  | 20.06.19 | 19:08 | 20.06.19 | 20:44 | 0.066667 | 0 | 21 | [5 empty] | #2, #3 running Units of Indravati PH tripped
|  | 18.09.19 | 12:00 | 18.09.19 | 12:17 | 0.011806 | 0 | 17 | [5 empty] | At Narendrapur end-Tripped on E/F
|  | 27.05.19 | 17:50 | 27.05.19 | 19:23 | 0.064583 | 0 | 40 | [5 empty] | Grid disturbance at Therubali S/s But circuit was not tripped at Therubali end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
129 | 220kV Therubali-Bhanjanagar-I |  |  |  |  | 0.027083 | 0 | 21 | [7 empty] | 171.46 | 8760 | 100% | 60.011 | 1501989.6
|  | 20.06.19 | 19:08 | 20.06.19 | 19:47 | 0.027083 | 0 | 21 | [5 empty] | #2, #3 running Units of Indravati PH tripped
130 | 220kV Therubali-Bhanjanagar-II |  |  |  |  | 0.01875 | 0 | 21 | [7 empty] | 171.46 | 8760 | 100% | 60.011 | 1501989.6
|  | 20.06.19 | 19:08 | 20.06.19 | 19:35 | 0.01875 | 0 | 21 | [5 empty] | #2, #3 running Units of Indravati PH tripped
131 | 220kV Bhanjanagar- Aska New - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.6 | 7644 | 100% | 0 | 218618.4
132 | 220kV Bhanjanagar- Aska New - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.6 | 7644 | 100% | 0 | 218618.4
133 | 220kV TTPS-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
134 | 220kV TTPS-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
135 | 220kV TTPS-Joda-I |  |  |  |  | 0.097222 | 3 | 30 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 154 | 8760 | 99.96% | 539 | 1349040
|  | 28.05.19 | 14:10 | 28.05.19 | 15.09 | 0.040972 | 0 | 44 | [5 empty] | Fdr tripped at both end. At JODA end- DP Relay, Dist= 45.69Km,Zone-1, Fault loop= L3-N, IL1=161.98A, IL2=557.98A, IL3=2092.60A, IN=2638.94A At TTPS end- DP Relay, Dist= 95Km, Zone-1, Y-ph tripped,IL1=23.7A, IL2=562.95A, IL3=2.045KA
|  | 07.05.19 | 17:36 | 07.05.19 | 18.57 | 0.05625 | 2 | 46 | [5 empty] | Tripped at TTPS end due to 220 kv incomer bus-1 tripping at Joda.
136 | 220kV TTPS-Joda-II |  |  |  |  | 0.06875 | 3 | 22 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 154 | 8760 | 99.96% | 518.4667 | 1349040
|  | 28.05.19 | 14.35 | 28.05.19 | 15.53 | 0.0125 | 0 | 36 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.220 KV JODA-TTPS Ckt-2 idle charged from JODA end upto loc no.-463.
|  | 07.05.19 | 17:36 | 07.05.19 | 18.57 | 0.05625 | 2 | 46 | [5 empty] | Tripped at TTPS end due to 220 kv incomer bus-1 tripping at Joda.
137 | 220kV U. Kolab-Jayanagar-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
138 | 220kV U. Kolab-Jayanagar-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
139 | 220kV U. Kolab-Jayanagar-Therubali Ckt-III |  |  |  |  | 0.064583 | 1 | 34 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 128 | 8760 | 99.98% | 200.5333 | 1121280
|  | 10.08.19 | 20:11 | 10.08.19 | 20:18 | 0.0048611 | 0 | 14 | [5 empty] | At Therubali end: DP, Y-ph, E/F, Dist.-18.39 k.m.
|  | 27.05.19 | 17:50 | 27.05.19 | 19:16 | 0.059722 | 1 | 20 | [5 empty] | Grid disturbance at Therubali S/s But circuit was not tripped at Therubali end.
6265.171
132 KV
140 | 132kV Akhusing-Mohana |  |  |  |  | 0.48333 | 0 | 34 | [7 empty] | 70 | 8760 | 99.99% | 39.6667 | 613200
|  | 25.07.19 | 17:25 | 25.07.19 | 17:59 | 0.023611 | 0 | 34 | [5 empty] | At Jayanagar end: Z-I, Dist.-27.25 k.m. R,Y,B ph.-E/F
|  | 16.07.19 | 15:47 | 16.07.19 | 23:02 | 0.30208 |  |  | 0 | 9 |  |  |  | Tripped at Machhkund end.Akhusingh GS/S availed P/S from Digapahandi end at 15:56 Hrs.15:55-Rayagada load C.O to TVL Auto.
|  | 17.07.19 | 17:10 | 17.07.19 | 20:57 | 0.15764 |  |  | 0 | 29 |  |  |  | Tripped at Machhkund end: At 17:39 - Akhusingh, Paralakhemundi availed P/S from Digapahandi end.Rayagada Load C/O to TVL Load at 17:46 Hrs.
141 | 132kV Akhusing-Parlakhemundi |  |  |  |  | 0.48333 | 0 | 34 | [7 empty] | 76.9 | 8760 | 99.99% | 43.5767 | 673644
|  | 25.07.19 | 17:25 | 25.07.19 | 17:59 | 0.023611 | 0 | 34 | [5 empty] | At Jayanagar end: Z-I, Dist.-27.25 k.m. R,Y,B ph.-E/F
|  | 16.07.19 | 15:47 | 16.07.19 | 23:02 | 0.30208 |  |  | 0 | 9 |  |  |  | Tripped at Machhkund end.Akhusingh GS/S availed P/S from Digapahandi end at 15:56 Hrs.15:55-Rayagada load C.O to TVL Auto.
|  | 17.07.19 | 17:10 | 17.07.19 | 20:57 | 0.15764 |  |  | 0 | 29 |  |  |  | Tripped at Machhkund end: At 17:39 - Akhusingh, Paralakhemundi availed P/S from Digapahandi end.Rayagada Load C/O to TVL Load at 17:46 Hrs.
142 | 132kV Angul-Boinda |  |  |  |  | 0.01875 | 0 | 27 | [7 empty] | 38.5 | 8760 | 99.99% | 17.325 | 337260
|  | 23.02.20 | 19:28 | 23.02.20 | 19:36 | 0.0055556 | 0 | 8 | [5 empty] | At Angul end: Tripped on O/C (Y -PH)
|  | 22.02.20 | 8:50 | 22.02.20 | 9:09 | 0.013194 | 0 | 19 | [5 empty] | At Angul end: Tripped on O/C R PH
143 | 132kV Angul-Nandira (MCL)- I |  |  |  |  | 0.34028 | 16 | 17 | [7 empty] | 10.826 | 8760 | 99.81% | 176.2834 | 94835.76
|  | 27.04.19 | 17:31 | 27.04.19 | 22:34 | 0.21042 | 1 | 10 | [5 empty] | At Chainpal- O/C -R ph ,Y ph, B ph , E/F,M/T
|  | 23.04.19 | 15:35 | 23.04.19 | 15:49 | 0.0097222 | 0 | 14 | [5 empty] | At Chainpal-O/C -Y ph , E/F.
|  | 22.04.19 | 16:16 | 22.04.19 | 16:34 | 0.0125 | 0 | 18 | [5 empty] | At Chainpal-O/C - B ph , E/F.
|  | 21.04.19 | 13:10 | 21.04.19 | 13:27 | 0.011111 | 0 | 16 | [5 empty] | Tripped with DP relay (Fault Abs Dist 3.125 KM , Fault Loop L2-N)
|  | 14.04.19 | 11:09 | 14.04.19 | 11:18 | 0.00625 | 0 | 9 | [5 empty] | At Chainpal-O/C -Y ph, B ph , E/F.
|  | 13.04.19 | 19:29 | 13.04.19 | 19:46 | 0.011806 | 0 | 17 | [5 empty] | At Chainpal-O/C -R ph ,Y ph, B ph , E/F.
|  | 13.04.19 | 13:30 | 13.04.19 | 14:18 | 0.033333 | 0 | 48 | [5 empty] | At Chainpal-O/C -R ph , Y ph, E/F.
|  | 13.04.19 | 14:19 | 13.04.19 | 15:24 | 0.045139 | 1 | 5 | [5 empty] | At Chainpal-O/C -R ph , E/F.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
145 | 132kV Angul-Nandira (MCL)- II |  |  |  |  | 0.38056 | 17 | 14 | [7 empty] | 10.826 | 8760 | 99.81% | 186.5681 | 94835.76
|  | 31.05.19 | 19:33 | 31.05.19 | 20:31 | 0.040278 | 0 | 57 | [5 empty] | E/F at Angul end.
|  | 27.04.19 | 17:31 | 27.04.19 | 22:34 | 0.21042 | 1 | 10 | [5 empty] | At Chainpal- O/C -R ph ,Y ph, B ph , E/F,M/T
|  | 23.04.19 | 15:35 | 23.04.19 | 15:49 | 0.0097222 | 0 | 14 | [5 empty] | At Chainpal-O/C -Y ph , E/F.
|  | 22.04.19 | 16:16 | 22.04.19 | 16:34 | 0.0125 | 0 | 18 | [5 empty] | At Chainpal-O/C - B ph , E/F.
|  | 21.04.19 | 13:10 | 21.04.19 | 13:27 | 0.011111 | 0 | 16 | [5 empty] | Tripped with DP relay (Fault Abs Dist 3.125 KM , Fault Loop L2-N)
|  | 14.04.19 | 11:09 | 14.04.19 | 11:18 | 0.00625 | 0 | 9 | [5 empty] | At Chainpal-O/C -Y ph, B ph , E/F.
|  | 13.04.19 | 19:29 | 13.04.19 | 19:46 | 0.011806 | 0 | 17 | [5 empty] | At Chainpal-O/C -R ph ,Y ph, B ph , E/F.
|  | 13.04.19 | 13:30 | 13.04.19 | 14:18 | 0.033333 | 0 | 48 | [5 empty] | At Chainpal-O/C -R ph , Y ph, E/F.
|  | 13.04.19 | 14:19 | 13.04.19 | 15:24 | 0.045139 | 1 | 5 | [5 empty] | At Chainpal-O/C -R ph , E/F.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
146 | 132kV Arya Iron & Steel- BRPL |  |  |  |  | 1900-01-03 03:39 | 20 | 52 | [7 empty] | 9.008 | 8760 | 99.76% | 187.9669 | 78910.08
|  | 24.02.20 | 21:24 | 24.02.20 | 21:55 | 0.021528 | 0 | 31 | [5 empty] | At Nalda RTSS : Tripped
|  | 15.01.20 | 9:09 | 15.01.20 | 9:45 | 0.025 | 0 | 36 | [5 empty] | At Joda end-Tripped
|  | 15.11.19 | 9:49 | 15.11.19 | 10:52 | 0.04375 | 1 | 3 | [5 empty] | At Barbil end; Tripped on E/F
|  | 15.11.19 | 15:29 | 15.11.19 | 15:55 | 0.018056 | 0 | 26 | [5 empty] | At Barbil end; Tripped on E/F
|  | 15.06.19 | 18:32 | 16.06.19 | 16:42 | 0.92361 | 0 | 47 | [5 empty] | At 19:19 Hrs. Barbil availed P/S from Rourkela end.
|  | 07.10.19 | 16:50 | 07.10.19 | 17:08 | 0.0125 | 0 | 18 | [5 empty] | At Barbil end: D/P relay opreated , Distance- 62.66km; Fault current:- IA- 1437A; IB-16A; IC-45A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:04 | 0.020833 | 0 | 30 | [5 empty] | At Barbil end: Tripped on E/F ,FC:- IA- 461.9A; IB- 290.3A; IC-685.8A; IN-9485.7A
|  | 02.09.19 | 18:46 | 02.09.19 | 18:57 | 0.0076389 | 0 | 11 | [5 empty] | Tripped as D/P relay operated at Both Barbil & Joda Grid end with following indications at Barbil Grid: Zone-I; 6.227km(C-N); Ic=551.8A
|  | 19.07.19 | 19:25 | 19.07.19 | 23:03 | 0.15139 | 0 | 9 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.
|  | 28.05.19 | 14.35 | 28.05.19 | 16.04 | 0.061806 | 0 | 34 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.132 KV barbil Fdr is idle charged from JODA end & availed p/s from Rourkela end.
|  | 07.05.19 | 17:37 | 07.05.19 | 19:00 | 0.057639 | 0 | 15 | [5 empty] | Fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.132KV Barbil S/S availed Extended P/S from RKl end till restoration of power at Joda end.
|  | 03.05.19 | 10.54 | 03.05.19 | 12.22 | 1899-12-31 06:43 | 1 | 28 | [5 empty] | S/D of 132KV main Bus availed at Joda end for replacement of B-ph damaged sec-1 isolator clamp of 132 KV main Bus.
|  | 02.05.19 | 16.02 | 02.05.19 | 17.54 | 1899-12-31 12:29 | 1 | 52 | [5 empty] | Fdr tripped only at JODA end. At JODA end- DP Relay, Zone-1, Dist= -3.43Km, Fault loop= BG T, IA=269A, IB=7427A,IC=120A, IG=7125A
|  | 02.05.19 | 8:21 | 02.05.19 | 8:33 | 0.0083333 | 0 | 12 | [5 empty] | Fdr tripped only at JODA end. At JODA end- DP Relay, Zone-1, Dist= -3.03Km, Fault loop= BG T, IA=262A, IB=6778A,IC=143A, IG=6490A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
147 | 132kV Barbil - Bolani |  |  |  |  | 1900-01-03 03:39 | 20 | 52 | [7 empty] | 7.8 | 8760 | 99.76% | 162.76 | 68328
|  | 24.02.20 | 21:24 | 24.02.20 | 21:55 | 0.021528 | 0 | 31 | [5 empty] | At Nalda RTSS : Tripped
|  | 15.01.20 | 9:09 | 15.01.20 | 9:45 | 0.025 | 0 | 36 | [5 empty] | At Joda end-Tripped
|  | 15.11.19 | 9:49 | 15.11.19 | 10:52 | 0.04375 | 1 | 3 | [5 empty] | At Barbil end; Tripped on E/F
|  | 15.11.19 | 15:29 | 15.11.19 | 15:55 | 0.018056 | 0 | 26 | [5 empty] | At Barbil end; Tripped on E/F
|  | 15.06.19 | 18:32 | 16.06.19 | 16:42 | 0.92361 | 0 | 47 | [5 empty] | At 19:19 Hrs. Barbil availed P/S from Rourkela end.
|  | 07.10.19 | 16:50 | 07.10.19 | 17:08 | 0.0125 | 0 | 18 | [5 empty] | At Barbil end: D/P relay opreated , Distance- 62.66km; Fault current:- IA- 1437A; IB-16A; IC-45A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:04 | 0.020833 | 0 | 30 | [5 empty] | At Barbil end: Tripped on E/F ,FC:- IA- 461.9A; IB- 290.3A; IC-685.8A; IN-9485.7A
|  | 02.09.19 | 18:46 | 02.09.19 | 18:57 | 0.0076389 | 0 | 11 | [5 empty] | Tripped as D/P relay operated at Both Barbil & Joda Grid end with following indications at Barbil Grid: Zone-I; 6.227km(C-N); Ic=551.8A
|  | 19.07.19 | 19:25 | 19.07.19 | 23:03 | 0.15139 | 0 | 9 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.
|  | 28.05.19 | 14.35 | 28.05.19 | 16.04 | 0.061806 | 0 | 34 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.132 KV barbil Fdr is idle charged from JODA end & availed p/s from Rourkela end.
|  | 07.05.19 | 17:37 | 07.05.19 | 19:00 | 0.057639 | 0 | 15 | [5 empty] | Fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.132KV Barbil S/S availed Extended P/S from RKl end till restoration of power at Joda end.
|  | 03.05.19 | 10.54 | 03.05.19 | 12.22 | 1899-12-31 06:43 | 1 | 28 | [5 empty] | S/D of 132KV main Bus availed at Joda end for replacement of B-ph damaged sec-1 isolator clamp of 132 KV main Bus.
|  | 02.05.19 | 16.02 | 02.05.19 | 17.54 | 1899-12-31 12:29 | 1 | 52 | [5 empty] | Fdr tripped only at JODA end. At JODA end- DP Relay, Zone-1, Dist= -3.43Km, Fault loop= BG T, IA=269A, IB=7427A,IC=120A, IG=7125A
|  | 02.05.19 | 8:21 | 02.05.19 | 8:33 | 0.0083333 | 0 | 12 | [5 empty] | Fdr tripped only at JODA end. At JODA end- DP Relay, Zone-1, Dist= -3.03Km, Fault loop= BG T, IA=262A, IB=6778A,IC=143A, IG=6490A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
148 | 132 kV Aska-Aska New -Chatrapur-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 56.25 | 8760 | 100% | 0 | 492750
149 | 132 kV Aska-Purusottampur |  |  |  |  | 0.00625 | 0 | 9 | [7 empty] | 28.61 | 8760 | 100% | 4.2915 | 250623.6
|  | 14.12.19 | 4:45 | 14.12.19 | 4:54 | 0.00625 | 0 | 9 | [5 empty] | Ar Bhanjanagar end-Tripped on: BGT,Z=1,D-18.23KM
150 | 132kV Atri - Argul Ckt-I |  |  |  |  | 1899-12-31 15:48 | 0 | 37 | [7 empty] | 19.4 | 8760 | 99.99% | 11.9633 | 169944
|  | 05.06.19 | 20:58 | 05.06.19 | 21:35 | 0.025694 | 0 | 37 | [5 empty] | At Atri end: D/P, RYB-E/F, Dist.-11.7 k.m.
|  | 03.05.19 | 9:04 | 05.05.19 | 0:15 | 1899-12-31 15:11 |  |  |  |  | 39 | 11 |  | Tripped (Due to Cyclone Fani)
151 | 132kV Atri - Argul Ckt-II |  |  |  |  | 0.0048611 | 0 | 7 | [7 empty] | 19.4 | 8760 | 100% | 2.2633 | 169944
|  | 04.07.19 | 14:28 | 04.07.19 | 14:35 | 0.0048611 | 0 | 7 | [5 empty] | DP relay operated at Atri end.
152 | 132kV Atri - Banki |  |  |  |  | 1899-12-31 14:26 | 0 | 0 | [7 empty] | 20.9 | 8760 | 100% | 0 | 183084
|  | 03.05.19 | 9:48 | 05.05.19 | 0:14 | 1899-12-31 14:26 |  |  |  |  | 38 | 26 |  | Tripped (Due to Cyclone Fani)
153 | 132 kV Badagada-Nimapara |  |  |  |  | 1900-01-03 11:20 | 0 | 35 | [7 empty] | 36.87 | 8760 | 99.99% | 21.5075 | 322981.2
|  | 11.12.19 | 3:27 | 11.12.19 | 4:02 | 0.024306 | 0 | 35 | [5 empty] | Chandaka end-Tripped
|  | 03.05.19 | 11:05 | 07.05.19 | 21:50 | 1900-01-03 10:45 |  |  |  |  | 106 | 45 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'. 132 kV Choudwar supply extended to Chandaka Grid by means of special arrangement through 132 kV Bidanasi -BPPL ckt
154 | 132 kV Balasore-Udala |  |  |  |  | 0.57222 | 18 | 32 | [7 empty] | 71.76 | 8760 | 99.79% | 1329.952 | 628617.6
|  | 23.09.19 | 5:15 | 25.09.19 | 16:02 | 58:47 | 1 | 10 | [5 empty] | At Balasore end:-Tripped on distance protection, Distance-35.3KM,Zone 1. Availed P/S from Baripada end.
|  | 02.09.19 | 13:56 | 03.09.19 | 17:13 | 27:17 | 3 | 7 | [5 empty] | At Udala-Tripped on distance protection, Distance-23.2KM,Zone 1.
|  | 05.08.19 | 16:55 | 05.08.19 | 17:42 | 0.032639 | 0 | 47 | [5 empty] | At Udala end:- Tripped on Y-Phase Fault. Zone-I, Distance 11.7km
|  | 31.05.19 | 19:13 | 31.05.19 | 07:05 | 0.49444 | 0 | 57 | [5 empty] | Balasore End : Y-N , Zone- I, L1=154Amp,L2= 1826Amp,L3=134Amp Fault Distance=47.3Km Udala End : Y-N , Zone- I, L1=0.16KAmp,L2=0. 17KAmp,L3=0.15KAmp Fault Distance=12.00Km Grid s/s Betnoti & Udala availed P/S from Grid S/S Baripada at 20.10 Hrs
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
|  | 15.05.19 | 16:10 | 15.05.19 | 16:41 | 0.021528 | 0 | 31 | [5 empty] | Udala End Tripping Details y- Phase to Ground, Zone-I Fault Distance=25.90Km KM, Later charged from Balasore.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
155 | 132 kV Udala-Betanati |  |  |  |  | 0.69236 | 17 | 42 | [7 empty] | 50.69 | 8760 | 99.8% | 897.213 | 444044.4
|  | 03.02.20 | 7:38 | 03.02.20 | 7:50 | 0.0083333 | 0 | 12 | [5 empty] | At Baripada end: Tripped on E/F
|  | 18.11.19 | 12:48 | 18.11.19 | 13:04 | 0.011111 | 0 | 16 | [5 empty] | At Udala end: Zone-1,Yph-G, Ia-0.06KA, Ib-1.49KA, Ic-0.01KA
|  | 23.09.19 | 5:13 | 23.09.19 | 6:23 | 0.048611 | 1 | 10 | [5 empty] | At Baripada end:-ZONE-I, General Trip,B-G, Distance-35.3 Km,IL1-0.14Kamp,IL2-0.10Kamp, IL3-0.7Kamp,
|  | 02.09.19 | 13:57 | 02.09.19 | 17:04 | 0.12986 | 3 | 7 | [5 empty] | At Baripada end :-ZONE-I, General Trip,B-G, Distance-23.2 Km,IL1-0.12Kamp,IL2-0.15Kamp, IL3-0.18Kamp.Availed P/S from Balasore end.
|  | 31.05.19 | 19:13 | 31.05.19 | 07:05 | 0.49444 | 0 | 57 | [5 empty] | Balasore End : Y-N , Zone- I, L1=154Amp,L2= 1826Amp,L3=134Amp Fault Distance=47.3Km Udala End : Y-N , Zone- I, L1=0.16KAmp,L2=0. 17KAmp,L3=0.15KAmp Fault Distance=12.00Km Grid s/s Betnoti & Udala availed P/S from Grid S/S Baripada at 20.10 Hrs
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
156 | 132 kV Betanati-Baripada |  |  |  |  | 0.73542 | 18 | 44 | [7 empty] | 24.83 | 8760 | 99.79% | 465.1487 | 217510.8
|  | 03.02.20 | 7:38 | 03.02.20 | 7:50 | 0.0083333 | 0 | 12 | [5 empty] | At Baripada end: Tripped on E/F
|  | 18.11.19 | 12:48 | 18.11.19 | 13:04 | 0.011111 | 0 | 16 | [5 empty] | At Baripada end: Zone -1, Y-Ph ,E/F, Distance -1.2 KM,Ia-0.06KA,Ib-1.41KA,Ic-0.01KA
|  | 23.09.19 | 5:13 | 23.09.19 | 6:23 | 0.048611 | 1 | 10 | [5 empty] | At Baripada end:-ZONE-I, General Trip,B-G, Distance-35.3 Km,IL1-0.14Kamp,IL2-0.10Kamp, IL3-0.7Kamp,
|  | 02.09.19 | 13:57 | 02.09.19 | 17:04 | 0.12986 | 3 | 7 | [5 empty] | At Baripada end :-ZONE-I, General Trip,B-G, Distance-23.2 Km,IL1-0.12Kamp,IL2-0.15Kamp, IL3-0.18Kamp.Availed P/S from Balasore end.
|  | 12.07.19 | 16:23 | 12.07.19 | 17:25 | 0.043056 | 1 | 2 | [5 empty] | Tripped on L1-G Fault. Zone-I, Distance 39.2km at Baripada end.
|  | 31.05.19 | 19:13 | 31.05.19 | 7:05 | 0.49444 | 0 | 57 | [5 empty] | Balasore End : Y-N , Zone- I, L1=154Amp,L2= 1826Amp,L3=134Amp Fault Distance=47.3Km Udala End : Y-N , Zone- I, L1=0.16KAmp,L2=0. 17KAmp,L3=0.15KAmp Fault Distance=12.00Km Grid s/s Betnoti & Udala availed P/S from Grid S/S Baripada at 20.10 Hrs
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
157 | 132 kV Balasore-Basta |  |  |  |  | 1899-12-31 04:22 | 13 | 1 | [7 empty] | 32.91 | 8760 | 99.85% | 428.3785 | 288291.6
|  | 22.03.20 | 0:29 | 22.03.20 | 0:49 | 0.013889 | 0 | 20 | [5 empty] | At Balasore end: Zone-1, IA=4.877KA, Dist-: 11.95KM At Basta end: Zone-1, Dist - 15.06 kM
|  | 05.02.20 | 12:37 | 05.02.20 | 21:23 | 0.36528 | 0 | 16 | [5 empty] | At Basta end: B-G (R,Y,B ph), FC:- 181A Dist -: 13.09KM ( Insulator string failure at Loc -59 )
|  | 14.06.19 | 18:17 | 14.06.19 | 14.06.19 | 0.77917 | 0 | 25 | [5 empty] | At Balasore end: 'R' Ø -E/F, Dist.-13.27 k.m, FC-4.57 KA At Basta-Tripped on distance protection relay 21M1 and 21M2 , zone -1 fault current IA- 169.8A, IB-162.0A, IC-178.0A Fault distance 22.35 Km
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
158 | 132 kV Balasore- Balasore Alloy |  |  |  |  | 0.042361 | 0 | 27 | [7 empty] | 6.45 | 8760 | 99.99% | 2.9025 | 56502
|  | 22.03.20 | 16:03 | 22.03.20 | 16:30 | 0.01875 | 0 | 27 | [5 empty] | At Balasore end: E/F, IA= 1.398KA, IB= 1.999KA,IC= 95.67A
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
159 | 132 kV Balasore-Birla Tyre |  |  |  |  | 0.023611 | 0 | 0 | [7 empty] | 2.598 | 8760 | 100% | 0 | 22758.48
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
160 | 132 kV Balasore-Soro |  |  |  |  | 0.47292 | 1 | 3 | [7 empty] | 29.995 | 8760 | 99.99% | 31.4948 | 262756.2
|  | 05.03.20 | 2:04 | 05.03.20 | 12:51 | 0.44931 | 1 | 3 | [5 empty] | At Balasore end: Zone-2, Bph-N, IB=2.573KA , Dist - 38.12kM At Soro end: Tripped on E/F, 2.10Km, Z-I ( Insulator failure at Loc- 02)
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
161 | 132 kV Balasore-Somnathpur |  |  |  |  | 0.023611 | 0 | 0 | [7 empty] | 4 | 8760 | 100% | 0 | 35040
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
162 | 132 kV Somnathpur-Stork |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.1 | 8760 | 100% | 0 | 876
163 | 132 kV Somnathpur-EMAMI |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6 | 8760 | 100% | 0 | 52560
164 | 132kV Balugaon-Chandpur |  |  |  |  | 0.1125 | 12 | 30 | [7 empty] | 43.52 | 8760 | 99.86% | 544 | 381235.2
|  | 15.09.19 | 19:59 | 15.09.19 | 20:12 | 0.0090278 | 0 | 2 | [5 empty] | At Chhatrapur-Tripped on O/C B-G with M/R.
|  | 24.09.19 | 2:12 | 24.09.19 | 2:26 | 0.0097222 | 0 | 14 | [5 empty] | At Chhatrapur end: Tripped on Y-G with M/R,Dist-4.29km
|  | 18.09.19 | 12:01 | 18.09.19 | 14:16 | 0.09375 | 0 | 14 | [5 empty] | At Narendrapur end:- Zone-1, R ph. -N, IR = 2.063 kA, VAN = 106.6 kV Dist = 64.30 km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
165 | 132 kv Balugaon-Solari(T) |  |  |  |  | 0.1125 | 12 | 30 | [7 empty] | 14.5 | 8760 | 99.86% | 181.25 | 127020
|  | 15.09.19 | 19:59 | 15.09.19 | 20:12 | 0.0090278 | 0 | 2 | [5 empty] | At Chhatrapur-Tripped on O/C B-G with M/R.
|  | 24.09.19 | 2:12 | 24.09.19 | 2:26 | 0.0097222 | 0 | 14 | [5 empty] | At Chhatrapur end: Tripped on Y-G with M/R,Dist-4.29km
|  | 18.09.19 | 12:01 | 18.09.19 | 14:16 | 0.09375 | 0 | 14 | [5 empty] | At Narendrapur end:- Zone-1, R ph. -N, IR = 2.063 kA, VAN = 106.6 kV Dist = 64.30 km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
166 | 132 kv Banki-Nuapatna |  |  |  |  | 1900-01-01 14:49 | 0 | 13 | [7 empty] | 21.014 | 8760 | 100% | 4.553 | 184082.64
|  | 19.03.20 | 18:39 | 19.03.20 | 19:01 | 0.015278 | 0 | 13 | [5 empty] | At Banki end: Tripped on Zone-3
|  | 04.05.19 | 0.96319 | 07.05.19 | 0.56528 | 1900-01-01 14:27 |  |  |  |  | 1 | 7 |  | R phase O/C,E/F,LBB (DP relay operated,SURGE ARRESTOR OF R phase bursted subsequently damaged.) due to severe cyclonic storm FANI
167 | 132 kV Bargarh-Barpalli |  |  |  |  | 0.00625 | 0 | 9 | [7 empty] | 20 | 8760 | 100% | 3 | 175200
|  | 29.04.19 | 12:28 | 29.04.19 | 12:32 | 0.0027778 | 0 | 4 | [5 empty] | Tripped at Barpali end.
|  | 16.04.19 | 1:18 | 16.04.19 | 1:23 | 0.0034722 | 0 | 5 | [5 empty] | SOURCE FAILURE
168 | 132 kV Bargarh-ACC Ckt I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.87 | 8760 | 100% | 0 | 25141.2
169 | 132 kV Bargarh-ACC Ckt II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.87 | 8760 | 100% | 0 | 25141.2
170 | 132 kV Bargarh-Katapalli |  |  |  |  | 0.0090278 | 0 | 13 | [7 empty] | 32.32 | 8760 | 100% | 7.0027 | 283123.2
|  | 05.04.19 | 16:18 | 05.04.19 | 16:31 | 0.0090278 | 0 | 13 | [5 empty] | FAILURE FROM SOURCE
171 | 132 kV Bargarh New-Ghens Ckt -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.53 | 8760 | 100% | 0 | 258682.8
172 | 132 kV Bargarh New-Ghens Ckt -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.53 | 8760 | 100% | 0 | 258682.8
173 | 132kV Baripada-Kuchei PG |  |  |  |  | 1899-12-31 03:23 | 13 | 1 | [7 empty] | 3.1 | 8760 | 99.85% | 40.3517 | 27156
|  | 30.01.20 | 11:10 | 30.01.20 | 11:54 | 0.030556 |  |  | 0 | 44 |  |  |  | At Baripada PG end: Master Trip, E/F & O/C in L1,L2& L3
|  | 18.01.20 | 16:26 | 19.01.20 | 12:48 | 0.84861 | 0 | 20 | [5 empty] | At Baripada PG end: B-Phase,E/F,Zone-I, Fault Distance=1.542Km At Baripada end: Master Trip , Zone-I, Ia-152 Amp,Ib-292Amp,Ic=200A. At 16:46 Hrs, P/S availed from Betnoti end.
|  | 16.11.19 | 22:01 | 17.11.19 | 03:11 | 0.21528 |  |  | 0 | 13 |  |  |  | Tripped at both ends due to R-phase LA of 132KV Baripada- PGCIL line burst at PGCIL end. P/S availed from Betonati Grid end.
|  | 13.11.19 | 8:39 | 13.11.19 | 8:55 | 0.011111 |  |  | 0 | 16 |  |  |  | PGCIL I/C breaker Tripped at Baripada Grid due to LA of 132KV Bangiriposi – PGCIL line burst at PGCIL end. Relay Indication Master Trip ,Zone -1, Distance -22.53 KM,Ia-122A,Ib-294A,Ic-190A(causing tripping of all the transformers)
|  | 06.10.19 | 12:06 | 06.10.19 | 12:16 | 0.0069444 | 0 | 10 | [5 empty] | At Baripada end: O/C & E/F , Zone-I, DISTANCE -O.5 Km,IL-E,IL1=2.92KAmp, IL2=0.22 Kamp,IL3=O.34KAmp
|  | 02.04.19 | 0:07 | 02.04.19 | 0:48 | 0.028472 | 0 | 31 | [5 empty] | 132 KV Baripada - PGCIL Line I/C Tripped at PGCIL end .O/C B – Phase ,Fault Current – 7.825 KA, Fault Distance – 4.09 Km. Power supply Restored by charging 132Kv Baripada – Udala Line From Udala Grid end at 00:38 Hr Dated 02.04.19
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
174 | 132 kV Barpalli- New Bolangir |  |  |  |  | 0.17361 | 15 | 28 | [7 empty] | 60 | 8760 | 99.82% | 928 | 525600
|  | 28.01.20 | 12:04 | 28.01.20 | 12:11 | 0.0048611 | 0 | 7 | [5 empty] | At New Bolangir-Tripped on distance protection.
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | P/S failure at Bolangir New S/S due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 01.10.19 | 7:13 | 01.10.19 | 7:26 | 0.0090278 | 0 | 13 | [5 empty] | Tripped at Bolangir New end ( Jumper snapped at GSS Sadeipali)
|  | 24.09.19 | 17:48 | 24.09.19 | 19:00 | 0.05 | 0 | 30 | [5 empty] | At Sadeipalli end: Tripped on distance protection showing fault in B-Phase.
|  | 23.09.19 | 18:43 | 23.09.19 | 19:11 | 0.019444 | 0 | 28 | [5 empty] | Bolangir New end-Hand Tripped
|  | 17.09.19 | 19:12 | 17.09.19 | 19:45 | 0.022917 | 0 | 33 | [5 empty] | At Bolangir New end:-Hand Tripped. Supply availed from Bargarh end
|  | 27.05.19 | 0.52986 | 27.05.19 | 12:58 | 0.010417 | 0 | 15 | [5 empty] | SOURCE FAILURE
|  | 16.05.19 | 0.7 | 16.05.19 | 17:07 | 0.013194 | 0 | 19 | [5 empty] | SOURCE FAILURE
|  | 12.05.19 | 16:00 | 12.05.19 | 16:32 | 0.022222 | 0 | 32 | [5 empty] | SOURCE FAILURE
|  | 29.04.19 | 12:28 | 29.04.19 | 12:32 | 0.0027778 | 0 | 4 | [5 empty] | Tripped at Barpali end.
|  | 16.04.19 | 1:18 | 16.04.19 | 1:23 | 0.0034722 | 0 | 5 | [5 empty] | SOURCE FAILURE
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
175 | 132 kV Barpalli-Dunguripalli RTSS |  |  |  |  | 0.0034722 | 0 | 5 | [7 empty] | 13.6 | 8760 | 100% | 1.1333 | 119136
|  | 16.04.19 | 1:18 | 16.04.19 | 1:23 | 0.0034722 | 0 | 5 | [5 empty] | SOURCE FAILURE
176 | 132 kV Basta-Jaleswar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23.81 | 8760 | 100% | 0 | 208575.6
177 | 132kV BCMohanty-Bamnipal(Tisco) |  |  |  |  | 0.18819 | 4 | 31 | [7 empty] | 10 | 8760 | 99.95% | 45.1667 | 87600
|  | 12.06.19 | 20:17 | 12.06.19 | 21:03 | 0.031944 | 0 | 46
|  | 13.07.19 | 14:09 | 13.07.19 | 17:54 | 0.15625 | 3 | 45 | [5 empty] | R' Phase LA failure at B.C. Mohanty Swithing Station. Tripped at both ends.
178 | 132kV BCMohanty-Tomka (T) |  |  |  |  | 0.2 | 4 | 48 | [7 empty] | 11.86 | 8760 | 99.95% | 56.928 | 103893.6
|  | 12.06.19 | 20:04 | 12.06.19 | 21:07 | 0.04375 | 1 | 3
|  | 13.07.19 | 14:09 | 13.07.19 | 17:54 | 0.15625 | 3 | 45 | [5 empty] | R' Phase LA failure at B.C. Mohanty Swithing Station. Tripped at both ends.
179 | 132kV Beekay Steel - Bhalulata |  |  |  |  | 0.74722 | 17 | 56 | [7 empty] | 27.4 | 8760 | 99.8% | 491.3733 | 240024
|  | 19.09.19 | 3:45 | 19.09.19 | 21:41 | 0.74722 | 17 | 56 | [5 empty] | At Rourkela end:- B ph.-E/F, FC-1.64 KA, Dist.-57.8 k.m.
180 | 132kV Berhampur-Aska New |  |  |  |  | 0 | 0 | 0 | [7 empty] | 40.4 | 7284 | 100% | 0 | 294273.6
181 | 132kV Aska New- Aska |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.98 | 7284 | 100% | 0 | 50842.32
182 | 132kV Berhampur-Digapahandi |  |  |  |  | 0.011806 | 0 | 17 | [7 empty] | 31.882 | 8760 | 100% | 9.0332 | 279286.32
|  | 18.09.19 | 12:00 | 18.09.19 | 12:17 | 0.011806 | 0 | 17 | [5 empty] | At Narendrapur end: Zone-I, R ph.-E/F, Dist.-76.25 k.m.
183 | 132kV Bhadrak-FACOR |  |  |  |  | 0.38958 | 9 | 21 | [7 empty] | 4.564 | 8760 | 99.89% | 42.6734 | 39980.64
|  | 24.10.19 | 4:32 | 24.10.19 | 6:28 | 0.080556 | 1 | 56 | [5 empty] | Tripped at Bhadrak end; on zone 1,distance protection optd.(B ph. LA failure)
|  | 25.08.19 | 5:29 | 25.08.19 | 12:54 | 0.30903 | 7 | 25 | [5 empty] | At Bhadrak end:- E/F, Y ph. LA failure
184 | 132kV Bhadrak-Dhamara Ckt-I |  |  |  |  | 0.83125 | 31 | 57 | [7 empty] | 64.7 | 8760 | 99.64% | 2067.165 | 566772
|  | 27.03.20 | 12:25 | 27.03.20 | 12:48 | 0.015972 | 0 | 23 | [5 empty] | At Bhadrak end: zone-I,R-Ph.fault distance=30.94km,IA=2.114KA,IB=135.1A,IC=229.1A
|  | 13.03.20 | 12:47 | 13.03.20 | 13:11 | 0.016667 | 0 | 24 | [5 empty] | At Bhadrak end: Zone I,RPh.IA=2.02KA,IB=138.1A,IC=195.2A,Dist - 32.18 kM
|  | 10.11.19 | 10:38 | 10.11.19 | 13:28 | 0.11806 | 2 | 50 | [5 empty] | At Bhadrak end: Tripped on back up protection optd.,Dir.IDMTL E/F optd.86 A relay
|  | 11.11.19 | 9:05 | 11.11.19 | 13:40 | 0.19097 | 4 | 35 | [5 empty] | At Bhadrak end; Tripped on back up protection optd.,Dir.IDMTL E/F optd.86 A relay
|  | 09.11.19 | 3:22 | 09.11.19 | 14:23 | 0.45903 | 11 | 1 | [5 empty] | At Bhadrak end: Tripped on back up protection optd.,Dir.IDMTL E/F optd.86 A relay
|  | 10.10.19 | 0:23 | 10.10.19 | 0:43 | 0.013889 | 0 | 20 | [5 empty] | At Bhadrak end;- Tripped on DP Relay.O/C & E/F with master trip relay 86 A,ZONE 1,Fault distance=27.97 KM, Ia=2.39 KA,Ib=190.2 A,Ic=277.0A
|  | 06.10.19 | 11:30 | 06.10.19 | 11:54 | 0.016667 | 0 | 24 | [5 empty] | At Bhadrak end:- Tripped on o/c (R Ph)&E/F with master trip relay 86 A, Zone 1,fault distance=30.16km,Ia=2.25KA, Ib=170.3A,iC=251.6A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
185 | 132kV Bhadrak-Dhamara Ckt-II |  |  |  |  | 0.084722 | 14 | 2 | [7 empty] | 35.7 | 8760 | 99.84% | 500.99 | 312732
|  | 19.03.20 | 19:38 | 19.03.20 | 20:01 | 0.015972 | 0 | 23 | [5 empty] | At Bhadrak end: E/F,86A,IA=1.62KA,IB=243.7A,IC=322.7A,
|  | 30.01.20 | 7:31 | 30.01.20 | 8:32 | 0.042361 | 1 | 1 | [5 empty] | At Bhadrak end: Tripped on E/F, 86 A & 86 B
|  | 08.11.19 | 20:43 | 08.11.19 | 20:50 | 0.0048611 | 0 | 7 | [5 empty] | At Bhadrak end: Tripped on back up protection optd.,Dir.IDMTL E/F optd.86 A relay
|  | 08.11.19 | 21:46 | 08.11.19 | 22:08 | 0.015278 | 0 | 22 | [5 empty] | At Bhadrak end: Tripped on back up protection optd.,Dir.IDMTL E/F optd.86 A relay
|  | 04.11.19 | 10:27 | 04.11.19 | 10:36 | 0.00625 | 0 | 9 | [5 empty] | Tripped on instantaneous over current B ph. 86 A back up protn. Optd.,Dir.IDMTL E/F at Bhadrak end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
186 | 132kV Bhadrak-Bhdrak Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.086 | 8760 | 100% | 0 | 70833.36
187 | 132kV Bhadrak-Jajpur Town |  |  |  |  | 0.14931 | 2 | 0 | [7 empty] | 40.519 | 8760 | 99.98% | 81.038 | 354946.44
|  | 27.06.19 | 17:43 | 27.06.19 | 19:15 | 0.063889 | 1 | 32 | [5 empty] | At 17:45 Hrs, Jajpur Rd-Jajpur Town Fdr. Tripped from Jajpur Rd. end and declared faulty.(From Idle charge condition)
|  | 21.08.19 | 14:26 | 21.08.19 | 16:29 | 0.085417 | 0 | 28 | [5 empty] | At Bhadrak end:- Tripped on E/F, O/C R ph.
188 | 132kV Bhanjanagar-Aska-I |  |  |  |  | 0.0125 | 0 | 9 | [7 empty] | 33.72 | 8760 | 100% | 5.058 | 295387.2
|  | 14.12.19 | 4:45 | 14.12.19 | 4:54 | 0.00625 | 0 | 9 | [5 empty] | Ar Bhanjanagar end-Tripped on: BGT,Z=1,D-18.23KM
189 | 132kV Bhanjanagar-Aska-II |  |  |  |  | 0.00625 | 0 | 9 | [7 empty] | 33.72 | 8760 | 100% | 5.058 | 295387.2
|  | 14.12.19 | 4:45 | 14.12.19 | 4:54 | 0.00625 | 0 | 9 | [5 empty] | At Bhanjanagar end-Tripped on: Y-ph E/F
190 | 132KV Bhanjanagar-Phulbani |  |  |  |  | 0.30417 | 19 | 10 | [7 empty] | 86.5 | 8760 | 99.78% | 1657.9167 | 757740
|  | 26.03.20 | 12:00 | 26.03.20 | 12:22 | 0.015278 | 0 | 22 | [5 empty] | At Bhanjanagar end: CN.Z-1.D=52.34KM
|  | 05.03.20 | 16:54 | 05.03.20 | 18:01 | 0.046528 | 1 | 7 | [5 empty] | At Bhanjanagar end: BCN,Z-1,D=54.2KM
|  | 17.02.20 | 8:40 | 17.02.20 | 10:56 | 0.094444 | 2 | 16 | [5 empty] | At Bhanjanagar end: Tripped on BCN,Z=1,D=42.73KM
|  | 10.10.19 | 15:40 | 10.10.19 | 16:05 | 0.017361 | 0 | 17 | [5 empty] | Tripped at Bhanjanagar end
|  | 09.10.19 | 3:39 | 09.10.19 | 3:50 | 0.0076389 | 0 | 11 | [5 empty] | Tripped at Phulbani end
|  | 01.10.19 | 12:12 | 01.10.19 | 12:21 | 0.00625 | 0 | 9 | [5 empty] | Tripped at Bhanjanagar end
|  | 31.08.19 | 15:38 | 31.08.19 | 16:04 | 0.018056 | 0 | 26 | [5 empty] | At Bhanjanagr end-Tripped on O/C ,E/F
|  | 12.08.19 | 7:15 | 12.08.19 | 7:40 | 0.017361 | 0 | 25 | [5 empty] | At Bhanjanagr end-Tripped on O/C in R&B PH,Z-2 D:-84.13KM
|  | 20.06.19 | 18:34 | 20.06.19 | 19:24 | 0.034722 | 0 | 50 | [5 empty] | Tripped at Bhanjanagar end.
|  | 02.06.19 | 14:03 | 02.06.19 | 14:39 | 0.025 | 0 | 36 | [5 empty] | At-Bhanjanagar end-'R' ph.-E/F, Dist.-59.4 k.m, If-1.366 KA
|  | 31.05.19 | 14:06 | 31.05.19 | 14:12 | 0.0041667 | 0 | 6 | [5 empty] | CGT,ZONE=1,Dist.=63.17KM
|  | 23.05.19 | 15:28 | 23.05.19 | 15:44 | 0.011111 | 0 | 16 | [5 empty] | DP operated, ABCT,Z=1,D=43.66Km.
|  | 16.04.19 | 15:13 | 16.04.19 | 15:22 | 0.00625 | 0 | 9 | [5 empty] | Tripped due to E/F at Bhanjanagar.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
191 | 132kV Bhawanipatna-Junagarh |  |  |  |  | 1899-12-31 09:20 | 45 | 30 | [7 empty] | 25.158 | 8760 | 99.48% | 1144.689 | 220384.08
|  | 04.03.20 | 16:01 | 04.03.20 | 16:13 | 00:12 | 0 | 12 | [5 empty] | At Therubali end: Zone-2, B-N, 27.99KM ,Ib=3.6 kA
|  | 29.03.20 | 15:57 | 29.03.20 | 16:17 | 0.013889 | 0 | 20 | [5 empty] | At Kesinga end: Tripped
|  | 20.03.20 | 12:40 | 20.03.20 | 12:47 | 0.0048611 | 0 | 7 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 21:05 | 19.03.20 | 21:09 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 21:21 | 19.03.20 | 21:38 | 0.011806 | 0 | 17 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 22:08 | 19.03.20 | 22:17 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 23:48 | 19.03.20 | 23:56 | 0.0055556 | 0 | 8 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 17:43 | 19.03.20 | 17:47 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 17:28 | 19.03.20 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 16:29 | 19.03.20 | 17:00 | 0.021528 | 0 | 31 | [5 empty] | At Kesinga end: Tripped
|  | 08.03.20 | 16:49 | 08.03.20 | 17:06 | 0.011806 | 0 | 17 | [5 empty] | At Kesinga end: Tripped
|  | 08.03.20 | 17:44 | 08.03.20 | 17:47 | 0.0020833 | 0 | 3 | [5 empty] | At Kesinga end: Tripped
|  | 25.02.20 | 22:23 | 25.02.20 | 22:42 | 0.013194 | 0 | 19 | [5 empty] | At Therubali end: Zone-2,ABT, 31.84Km, Ia= 3.3kA, Ib= 3.1kA
|  | 13.02.20 | 16:37 | 13.02.20 | 16:41 | 0.0027778 | 0 | 4 | [5 empty] | At Therubali end: Tripped on O/ C
|  | 13.01.20 | 14:38 | 13.01.20 | 15:11 | 0.022917 | 0 | 33 | [5 empty] | At Therubali end: Tripped on O/C, D/P Zone-2,B-N, 28.23Km
|  | 02.01.20 | 11:53 | 02.01.20 | 12:12 | 0.013194 | 0 | 19 | [5 empty] | At Therubali end: Tripped on O/C.
|  | 13.01.20 | 14:29 | 13.01.20 | 14:33 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end-Tripped
|  | 17.12.19 | 11:32 | 17.12.19 | 11:33 | 0.00069444 | 0 | 1 | [5 empty] | Kesinga end-Tripped
|  | 17.12.19 | 15:11 | 17.12.19 | 15:12 | 0.00069444 | 0 | 1 | [5 empty] | Kesinga end-Tripped
|  | 07.12.19 | 15:18 | 07.12.19 | 15:31 | 0.0090278 | 0 | 13 | [5 empty] | Kesinga end-Tripped
|  | 07.12.19 | 8:19 | 07.12.19 | 8:21 | 0.0013889 | 0 | 2 | [5 empty] | Kesinga end-Tripped on E/F
|  | 07.12.19 | 8:22 | 07.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | Kesinga end-Tripped on E/F
|  | 23.11.19 | 16:10 | 23.11.19 | 16:20 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped on O/C
|  | 21.07.19 | 21:33 | 21.07.19 | 21:40 | 0.0048611 | 0 | 7 | [5 empty] | At Lanjigarh-Tripped
|  | 09.07.19 | 16:31 | 09.07.19 | 16:55 | 0.016667 | 0 | 24 | [5 empty] | At Kesinga-Tripped on distance relay
|  | 19.06.19 | 23:33 | 20.06.19 | 9:23 | 0.40972 | 9 | 50 | [5 empty] | At Kesinga -Tripped on D/P ( JUMPER SNAPPED AT LOC-1 OF 132 KV KESINGA-BPT-JUNAGARH LILO LINE)
|  | 10.06.19 | 17:26 | 10.06.19 | 17:33 | 0.0048611 | 0 | 7 | [5 empty] | At Theruvali-Tripped on O/C
|  | 05.06.19 | 21:55 | 05.06.19 | 22:02 | 0.0048611 | 0 | 7 | [5 empty] | At Theruvali-Tripped on O/C
|  | 08.06.19 | 20:56 | 08.06.19 | 20:59 | 0.0020833 | 0 | 3 | [5 empty] | At Theruvali-Tripped on O/C
|  | 03.06.19 | 10:15 | 03.06.19 | 10:44 | 0.020139 | 0 | 29 | [5 empty] | At Theruvali-Tripped (Distance relay indication at Lanjigarh end)
|  | 02.06.19 | 20:40 | 02.06.19 | 20:54 | 0.0097222 | 0 | 14 | [5 empty] | At Theruvali-Tripped
|  | 20.06.19 | 23:33 | 20.06.19 | 9:23 | 0.40972 | 9 | 50 | [5 empty] | DP operated: Zn.-I, Dist.-4.5 km, B-N, FC-1.17 KA
|  | 20.06.19 | 18:20 | 20.06.19 | 18:54 | 0.023611 | 0 | 34
|  | 02.10.19 | 16:48 | 02.10.19 | 16:59 | 0.0076389 | 0 | 11 | [5 empty] | At Therubali end: A-N,Z-1, 18.3KM
|  | 30.09.19 | 17:05 | 30.09.19 | 17:20 | 0.010417 | 0 | 15 | [5 empty] | At Theruvali-Tripped
|  | 29.05.19 | 21:11 | 29.05.19 | 21:55 | 0.030556 | 0 | 44 | [5 empty] | 132 KV P/S FAIL DUE TO DISTURBANCE AT KESINGA END. INCOMING SUPPLY WAS AVAILED FROM BOLANGIR
|  | 27.05.19 | 19:26 | 27.05.19 | 19:31 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped
|  | 27.05.19 | 17:50 | 27.05.19 | 18:32 | 0.029167 | 0 | 40 | [5 empty] | Grid disturbance at Therubali S/s but circuit was not tripped at Therubali end.
|  | 29.04.19 | 2:34 | 29.04.19 | 2:39 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped on over load.
|  | 29.05.19 | 22:52 | 29.05.19 | 23:08 | 0.011111 | 0 | 16 | [5 empty] | Tripped at Kesinga.
|  | 27.05.19 | 18:13 | 27.05.19 | 18:30 | 0.011806 | 0 | 17 | [5 empty] | 132 KV P/S FAIL; TRIPPED FROM THERUVALLI END SUPPLY AVAILED FROM BOLANGIR
|  | 27.05.19 | 19:26 | 27.05.19 | 19:31 | 0.0034722 | 0 | 5 | [5 empty] | 132 KV P/S FAIL; INCOMING SUPPLY CHANGED OVER TO THERUVALLI
|  | 20.05.19 | 6:31 | 20.05.19 | 6:47 | 0.011111 | 0 | 16 | [5 empty] | 132 KV P/S FAIL
|  | 11.05.19 | 4:56 | 11.05.19 | 5:03 | 0.0048611 | 0 | 7 | [5 empty] | 132 KV P/S FAIL
|  | 03.05.19 | 20:49 | 03.05.19 | 21:00 | 0.0076389 | 0 | 11 | [5 empty] | 132 KV P/S FAIL
|  | 30.04.19 | 5:14 | 30.04.19 | 5:24 | 0.0069444 | 0 | 10 | [5 empty] | 132 KV P/S FAIL
|  | 30.04.19 | 15:42 | 30.04.19 | 15:48 | 0.0041667 | 0 | 6 | [5 empty] | 132 KV P/S FAIL
|  | 25.04.19 | 6:50 | 25.04.19 | 6:55 | 0.0034722 | 0 | 5 | [5 empty] | 132 KV P/S FAIL
|  | 29.04.19 | 11:10 | 29.04.19 | 11:20 | 0.0069444 | 0 | 10 | [5 empty] | 132 KV P/S FAIL
|  | 24.04.19 | 16:00 | 24.04.19 | 16:14 | 0.0097222 | 0 | 14 | [5 empty] | 132 KV P/S FAIL
|  | 24.04.19 | 21:39 | 24.04.19 | 21:45 | 0.0041667 | 0 | 6 | [5 empty] | 132 KV P/S FAIL
|  | 17.04.19 | 1:01 | 17.04.19 | 1:08 | 0.0048611 | 0 | 7 | [5 empty] | 132 KV P/S FAIL
|  | 06.04.19 | 7:02 | 06.04.19 | 10:25 | 0.14097 | 3 | 23 | [5 empty] | 132 KV P/S FAIL
|  | 04.04.19 | 13:13 | 04.04.19 | 13:22 | 0.00625 | 0 | 9 | [5 empty] | 132 KV P/S FAIL
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
192 | 132kV Bhubaneswar-Phulnakhara |  |  |  |  | 1900-01-11 21:32 | 0 | 0 | [7 empty] | 23.14 | 8760 | 100% | 0 | 202706.4
|  | 03.05.19 | 12:30 | 11.05.19 | 18:47 | 1900-01-07 10:47 |  |  |  |  | 202 | 47 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI
|  | 03.05.19 | 11:05 | 07.05.19 | 21:50 | 1900-01-03 10:45 |  |  |  |  | 106 | 45 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'. 132 kV Choudwar supply extended to Chandaka Grid by means of special arrangement through 132 kV Bidanasi -BPPL ckt
193 | 132kV Chandaka-Mancheswar-B UG Cable |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.2 | 780 | 100% | 0 | 8736
194 | 132kV Bidanasi-Bhubaneswar Power-Chandaka |  |  |  |  | 1900-01-25 09:40 | 0 | 0 | [7 empty] | 35.34 | 8760 | 100% | 0 | 309578.4
|  | 03.05.19 | 12:30 | 29.05.19 | 22:10 | 1900-01-25 09:40 |  |  |  |  | 633 | 40 |  | H/T due to severe Cyclone FANI
195 | 132kV Boinda-Rairakhol |  |  |  |  | 0.027083 | 0 | 38 | [7 empty] | 60 | 8760 | 99.99% | 38 | 525600
|  | 22.02.20 | 8:49 | 22.02.20 | 9:09 | 0.013889 | 0 | 19 | [5 empty] | At Rairakhole end : Tripped
|  | 25.07.19 | 15:54 | 25.07.19 | 16:13 | 0.013194 | 0 | 19 | [5 empty] | O/C, E/F at Rairakhol end. Availed supply from Samabalpur end.
196 | 132kV Bolani - Arya Iron & Steel |  |  |  |  | 1900-01-03 03:39 | 20 | 52 | [7 empty] | 3.17 | 8760 | 99.76% | 66.1473 | 27769.2
|  | 24.02.20 | 21:24 | 24.02.20 | 21:55 | 0.021528 | 0 | 31 | [5 empty] | At Nalda RTSS : Tripped
|  | 15.01.20 | 9:09 | 15.01.20 | 9:45 | 0.025 | 0 | 36 | [5 empty] | At Joda end-Tripped
|  | 15.11.19 | 9:49 | 15.11.19 | 10:52 | 0.04375 | 1 | 3 | [5 empty] | At Barbil end; Tripped on E/F
|  | 15.11.19 | 15:29 | 15.11.19 | 15:55 | 0.018056 | 0 | 26 | [5 empty] | At Barbil end; Tripped on E/F
|  | 15.06.19 | 18:32 | 16.06.19 | 16:42 | 0.92361 | 0 | 47 | [5 empty] | At 19:19 Hrs. Barbil availed P/S from Rourkela end.
|  | 07.10.19 | 16:50 | 07.10.19 | 17:08 | 0.0125 | 0 | 18 | [5 empty] | At Barbil end: D/P relay opreated , Distance- 62.66km; Fault current:- IA- 1437A; IB-16A; IC-45A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:04 | 0.020833 | 0 | 30 | [5 empty] | At Barbil end: Tripped on E/F ,FC:- IA- 461.9A; IB- 290.3A; IC-685.8A; IN-9485.7A
|  | 02.09.19 | 18:46 | 02.09.19 | 18:57 | 0.0076389 | 0 | 11 | [5 empty] | Tripped as D/P relay operated at Both Barbil & Joda Grid end with following indications at Barbil Grid: Zone-I; 6.227km(C-N); Ic=551.8A
|  | 19.07.19 | 19:25 | 19.07.19 | 23:03 | 0.15139 | 0 | 9 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.
|  | 28.05.19 | 14.35 | 28.05.19 | 16.04 | 0.061806 | 0 | 34 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.132 KV barbil Fdr is idle charged from JODA end & availed p/s from Rourkela end.
|  | 07.05.19 | 17:37 | 07.05.19 | 19:00 | 0.057639 | 0 | 15 | [5 empty] | Fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.132KV Barbil S/S availed Extended P/S from RKl end till restoration of power at Joda end.
|  | 03.05.19 | 10.54 | 03.05.19 | 12.22 | 1899-12-31 06:43 | 1 | 28 | [5 empty] | S/D of 132KV main Bus availed at Joda end for replacement of B-ph damaged sec-1 isolator clamp of 132 KV main Bus.
|  | 02.05.19 | 16.02 | 02.05.19 | 17.54 | 1899-12-31 12:29 | 1 | 52 | [5 empty] | Fdr tripped only at JODA end. At JODA end- DP Relay, Zone-1, Dist= -3.43Km, Fault loop= BG T, IA=269A, IB=7427A,IC=120A, IG=7125A
|  | 02.05.19 | 8:21 | 02.05.19 | 8:33 | 0.0083333 | 0 | 12 | [5 empty] | Fdr tripped only at JODA end. At JODA end- DP Relay, Zone-1, Dist= -3.03Km, Fault loop= BG T, IA=262A, IB=6778A,IC=143A, IG=6490A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
197 | 132kV Bolangir-Sonepur |  |  |  |  | 0.80972 | 31 | 26 | [7 empty] | 53.845 | 8760 | 99.64% | 1692.5278 | 471682.2
|  | 28.03.20 | 10:48 | 28.03.20 | 10:51 | 0.0020833 | 0 | 3 | [5 empty] | At Bolangir end: Tripped
|  | 20.03.20 | 4:38 | 20.03.20 | 4:41 | 0.0020833 | 0 | 3 | [5 empty] | At Bolangir end: Tripped
|  | 17.03.20 | 17:36 | 17.03.20 | 17:46 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir end: Tripped
|  | 04.03.20 | 16:48 | 04.03.20 | 16:52 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir end: Tripped
|  | 16.02.20 | 8:03 | 16.02.20 | 8:31 | 0.019444 | 0 | 28 | [5 empty] | At Bolangir end: Tripped
|  | 13.02.20 | 16:40 | 13.02.20 | 17:05 | 0.017361 | 0 | 25 | [5 empty] | At Bolangir end: Tripped
|  | 13.02.20 | 17:51 | 13.02.20 | 17:58 | 0.0048611 | 0 | 7 | [5 empty] | At Bolangir end: Tripped
|  | 13.02.20 | 8:03 | 13.02.20 | 8:17 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:34 | 12.02.20 | 17:46 | 0.0083333 | 0 | 12 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 16:15 | 12.02.20 | 16:36 | 0.014583 | 0 | 21 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:05 | 12.02.20 | 17:10 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 8:12 | 12.02.20 | 8:33 | 0.014583 | 0 | 21 | [5 empty] | At Bolangir end: Tripped
|  | 03.02.20 | 14:52 | 03.02.20 | 15:04 | 0.0083333 | 0 | 12 | [5 empty] | At Bolangir end: Tripped
|  | 30.01.20 | 10:50 | 30.01.20 | 11:01 | 0.0076389 | 0 | 11 | [5 empty] | At Bolangir end-Tripped
|  | 30.01.20 | 16:22 | 30.01.20 | 16:27 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir end-Tripped
|  | 28.01.20 | 12:53 | 28.01.20 | 13:25 | 0.022222 | 0 | 32 | [5 empty] | At Bolangir end-Tripped
|  | 28.01.20 | 12:53 | 28.01.20 | 13:22 | 0.020139 | 0 | 29 | [5 empty] | At Sadeipali-Tripped on distance protection as well as on directional o/c and e/f.
|  | 27.01.20 | 18:00 | 27.01.20 | 18:30 | 0.020833 | 0 | 30 | [5 empty] | At Bolangir end-Tripped
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 30.12.19 | 13:36 | 30.12.19 | 13:45 | 0.00625 | 0 | 9 | [5 empty] | At Bolangir end-Tripped
|  | 29.10.19 | 10:20 | 29.10.19 | 10:25 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on O/C at Bolangir end
|  | 26.10.19 | 11:06 | 26.10.19 | 11:18 | 0.0083333 | 0 | 12 | [5 empty] | Source failure
|  | 26.10.19 | 13:53 | 26.10.19 | 13:57 | 0.0027778 | 0 | 4 | [5 empty] | Source failure
|  | 25.10.19 | 4:44 | 25.10.19 | 5:38 | 0.0375 | 0 | 54 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 24.10.19 | 4:46 | 24.10.19 | 5:38 | 0.036111 | 0 | 52 | [5 empty] | Source failure
|  | 23.10.19 | 13:06 | 23.10.19 | 13:11 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at Sonepur end
|  | 23.10.19 | 11:07 | 23.10.19 | 11:20 | 0.0090278 | 0 | 13 | [5 empty] | Tripped at Sonepur end
|  | 22.10.19 | 14:34 | 22.10.19 | 15:20 | 0.031944 | 0 | 46 | [5 empty] | P/S failure from Bolangir New end
|  | 16.10.19 | 8:00 | 16.10.19 | 8:30 | 0.020833 | 0 | 30 | [5 empty] | P/S failure from Bolangir New end
|  | 14.10.19 | 10:28 | 14.10.19 | 10:49 | 0.014583 | 0 | 21 | [5 empty] | P/S failure at Bolangir New S/S due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:44 | 0.15278 | 3 | 40 | [5 empty] | Tripped at Bolangir New end ( Jumper snapped at GSS Sadeipali)
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:39 | 0.020139 | 0 | 29 | [5 empty] | Tripped at New Bolangir end.
|  | 25.09.19 | 23:09 | 25.09.19 | 23:26 | 0.011806 | 0 | 17 | [5 empty] | At Sonepur end-Tripped
|  | 25.09.19 | 23:40 | 26.09.19 | 0:10 | 0.020833 | 0 | 30 | [5 empty] | At Sonepur end-Tripped
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 17.09.19 | 19:12 | 17.09.19 | 21:00 | 0.075 | 1 | 48 | [5 empty] | P/S Failure from Bolangir New end
|  | 13.08.19 | 5:53 | 13.08.19 | 6:33 | 0.027778 | 0 | 40 | [5 empty] | Tripped at Bolangir New end. P/s availed from Kesinga.
|  | 21.08.19 | 18:58 | 21.08.19 | 19:07 | 0.00625 | 0 | 9 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:19 | 0.0083333 | 0 | 12 | [5 empty] | 160 MVA Auto TRF-02 tripped
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 31.05.19 | 18:57 | 31.05.19 | 19:10 | 0.0090278 | 0 | 13 | [5 empty] | AC Supply failed from Bolangir
|  | 30.05.19 | 19:00 | 30.05.19 | 19:06 | 0.0041667 | 0 | 6 | [5 empty] | AC Supply failed from Bolangir
|  | 29.04.19 | 12:29 | 29.04.19 | 12:32 | 0.0020833 | 0 | 3 | [5 empty] | Tripped
|  | 27.04.19 | 20:01 | 27.04.19 | 20:06 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on directional o/c.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 12.04.19 | 14:15 | 12.04.19 | 14:29 | 0.0097222 | 0 | 14 | [5 empty] | Tripped on directional o/c and e/f.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
198 | 132 kV New Bolangir 'T' (on 132 kV Bolangir - Sonepur Line) |  |  |  |  | 0.020139 | 0 | 29 | [7 empty] | 2.011 | 1548 | 99.97% | 0.97198 | 3113.028
|  | 28.01.20 | 12:53 | 28.01.20 | 13:22 | 0.020139 | 0 | 29 | [5 empty] | At Sadeipali-Tripped on distance protection as well as on directional o/c and e/f.
199 | 132 kV New Bolangir - Bolangir Ckt - I |  |  |  |  | 0.57917 | 22 | 11 | [7 empty] | 3.78 | 8760 | 99.75% | 83.853 | 33112.8
|  | 12.02.20 | 17:35 | 12.02.20 | 17:40 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir New end: Tripped on O/C
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 25.10.19 | 4:44 | 25.10.19 | 5:40 | 0.038889 | 0 | 56 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 19:30 | 22.10.19 | 19:42 | 0.0083333 | 0 | 12 | [5 empty] | P/S failure from Bolangir New end
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | At Bolangir New S/S -Tripped due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:43 | 0.15208 | 0 | 49 | [5 empty] | Tripped at Bolangir New end( Jumper snapped at GSS Sadeipali). Availed P/S at 07:53 Hrs from Kesinga end
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:36 | 0.018056 | 0 | 26 | [5 empty] | Tripped at New Bolangir end.
|  | 26.09.19 | 0:10 | 26.09.19 | 0:30 | 0.013889 | 0 | 20 | [5 empty] | P/S Failure from Bolangir New end
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 23.09.19 | 18:42 | 23.09.19 | 19:12 | 0.020833 | 0 | 30 | [5 empty] | Tripped on overload at New Bolangir end.
|  | 23.09.19 | 15:53 | 23.09.19 | 16:00 | 0.0048611 | 0 | 7 | [5 empty] | Tripped at New Bolangir end.
|  | 17.09.19 | 19:13 | 17.09.19 | 20:56 | 0.071528 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 10.09.19 | 19:45 | 10.09.19 | 20:27 | 0.029167 | 0 | 42 | [5 empty] | At Bolangir New end-Tripped on directional O/C and E/F.
|  | 21.08.19 | 18:58 | 21.08.19 | 19:06 | 0.0055556 | 0 | 8 | [5 empty] | At Bolangir New-Tripped due to 132KV LA failure
|  | 21.08.19 | 18:32 | 21.08.19 | 18:46 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 13.08.19 | 5:53 | 13.08.19 | 6:09 | 0.011111 | 0 | 16 | [5 empty] | P/S failure from New Bolangir end
|  | 12.08.19 | 5:07 | 12.08.19 | 5:19 | 0.0083333 | 0 | 12 | [5 empty] | 160 MVA Auto TRF-02 tripped
|  | 21.08.19 | 18:32 | 21.08.19 | 18:42 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:30 | 0.015972 | 0 | 23 | [5 empty] | P/S failure from Bolangir New due to over loading
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 29.04.19 | 12:29 | 29.04.19 | 12:32 | 0.0020833 | 0 | 3 | [5 empty] | Tripped
|  | 27.04.19 | 20:01 | 27.04.19 | 20:06 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on directional o/c.
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 01.05.19 | 16:28 | 01.05.19 | 16:30 | 0.0013889 | 0 | 2 | [5 empty] | Due to ckt overloading ; Tripped from New Bolangir
|  | 29.04.19 | 17:28 | 29.04.19 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 29.04.19 | 16:45 | 29.04.19 | 16:48 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 12.04.19 | 21:37 | 12.04.19 | 21:50 | 0.0090278 | 0 | 13 | [5 empty] | Source Failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
200 | 132 kV New Bolangir - Bolangir Ckt - II |  |  |  |  | 0.54306 | 24 | 6 | [7 empty] | 3.008 | 8760 | 99.72% | 72.4928 | 26350.08
|  | 12.02.20 | 17:34 | 12.02.20 | 17:46 | 0.0083333 | 0 | 12 | [5 empty] | At Bolangir end: Tripped
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 25.10.19 | 4:44 | 25.10.19 | 5:38 | 0.0375 | 0 | 54 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 14:34 | 22.10.19 | 15:20 | 0.031944 | 0 | 46 | [5 empty] | P/S failure from Bolangir New end
|  | 16.10.19 | 8:00 | 16.10.19 | 8:30 | 0.020833 | 0 | 30 | [5 empty] | P/S failure from Bolangir New end
|  | 14.10.19 | 10:28 | 14.10.19 | 10:49 | 0.014583 | 0 | 21 | [5 empty] | P/S failure at Bolangir New S/S due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:44 | 0.15278 | 3 | 40 | [5 empty] | Tripped at Bolangir New end ( Jumper snapped at GSS Sadeipali)
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:39 | 0.020139 | 0 | 29 | [5 empty] | Tripped at New Bolangir end.
|  | 25.09.19 | 23:09 | 25.09.19 | 23:26 | 0.011806 | 0 | 17 | [5 empty] | At Sonepur end-Tripped
|  | 25.09.19 | 23:40 | 26.09.19 | 0:10 | 0.020833 | 0 | 30 | [5 empty] | At Sonepur end-Tripped
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 17.09.19 | 19:13 | 17.09.19 | 20:59 | 0.073611 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 13.08.19 | 5:53 | 13.08.19 | 6:33 | 0.027778 | 0 | 40 | [5 empty] | Tripped at Bolangir New end. P/s availed from Kesinga.
|  | 21.08.19 | 18:58 | 21.08.19 | 19:07 | 0.00625 | 0 | 9 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:19 | 0.0083333 | 0 | 12 | [5 empty] | 160 MVA Auto TRF-02 tripped
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 29.04.19 | 12:29 | 29.04.19 | 12:32 | 0.0020833 | 0 | 3 | [5 empty] | Tripped
|  | 27.04.19 | 20:01 | 27.04.19 | 20:06 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on directional o/c.
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 12.04.19 | 14:15 | 12.04.19 | 14:29 | 0.0097222 | 0 | 14 | [5 empty] | Tripped on directional o/c and e/f.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
201 | 132kV Bolangir New-Patnagarh Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 39.805 | 8760 | 100% | 0 | 348691.8
202 | 132kV Bolangir New-Patnagarh Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 39.805 | 8760 | 100% | 0 | 348691.8
203 | 132kV Arya Iron & Steel-Nalda (T) |  |  |  |  | 1900-01-03 03:39 | 20 | 52 | [7 empty] | 14.38 | 8760 | 99.76% | 300.0627 | 125968.8
|  | 24.02.20 | 21:24 | 24.02.20 | 21:55 | 0.021528 | 0 | 31 | [5 empty] | At Nalda RTSS : Tripped
|  | 15.01.20 | 9:09 | 15.01.20 | 9:45 | 0.025 | 0 | 36 | [5 empty] | At Joda end-Tripped
|  | 15.11.19 | 9:49 | 15.11.19 | 10:52 | 0.04375 | 1 | 3 | [5 empty] | At Barbil end; Tripped on E/F
|  | 15.11.19 | 15:29 | 15.11.19 | 15:55 | 0.018056 | 0 | 26 | [5 empty] | At Barbil end; Tripped on E/F
|  | 15.06.19 | 18:32 | 16.06.19 | 16:42 | 0.92361 | 0 | 47 | [5 empty] | At 19:19 Hrs. Barbil availed P/S from Rourkela end.
|  | 07.10.19 | 16:50 | 07.10.19 | 17:08 | 0.0125 | 0 | 18 | [5 empty] | At Barbil end: D/P relay opreated , Distance- 62.66km; Fault current:- IA- 1437A; IB-16A; IC-45A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:04 | 0.020833 | 0 | 30 | [5 empty] | At Barbil end: Tripped on E/F ,FC:- IA- 461.9A; IB- 290.3A; IC-685.8A; IN-9485.7A
|  | 02.09.19 | 18:46 | 02.09.19 | 18:57 | 0.0076389 | 0 | 11 | [5 empty] | Tripped as D/P relay operated at Both Barbil & Joda Grid end with following indications at Barbil Grid: Zone-I; 6.227km(C-N); Ic=551.8A
|  | 19.07.19 | 19:25 | 19.07.19 | 23:03 | 0.15139 | 0 | 9 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.
|  | 28.05.19 | 14.35 | 28.05.19 | 16.04 | 0.061806 | 0 | 34 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.132 KV barbil Fdr is idle charged from JODA end & availed p/s from Rourkela end.
|  | 07.05.19 | 17:37 | 07.05.19 | 19:00 | 0.057639 | 0 | 15 | [5 empty] | Fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.132KV Barbil S/S availed Extended P/S from RKl end till restoration of power at Joda end.
|  | 03.05.19 | 10.54 | 03.05.19 | 12.22 | 1899-12-31 06:43 | 1 | 28 | [5 empty] | S/D of 132KV main Bus availed at Joda end for replacement of B-ph damaged sec-1 isolator clamp of 132 KV main Bus.
|  | 02.05.19 | 16.02 | 02.05.19 | 17.54 | 1899-12-31 12:29 | 1 | 52 | [5 empty] | Fdr tripped only at JODA end. At JODA end- DP Relay, Zone-1, Dist= -3.43Km, Fault loop= BG T, IA=269A, IB=7427A,IC=120A, IG=7125A
|  | 02.05.19 | 8:21 | 02.05.19 | 8:33 | 0.0083333 | 0 | 12 | [5 empty] | Fdr tripped only at JODA end. At JODA end- DP Relay, Zone-1, Dist= -3.03Km, Fault loop= BG T, IA=262A, IB=6778A,IC=143A, IG=6490A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
204 | 132kV Duburi- BRPL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.632 | 8760 | 100% | 0 | 66856.32
205 | 132kV BRPL-Mesco |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.436 | 8760 | 100% | 0 | 38859.36
206 | 132kV Lapanga-Jharsuguda Ckt-I |  |  |  |  | 0.17847 | 15 | 18 | [7 empty] | 10 | 8760 | 99.83% | 153 | 87600
|  | 07.12.19 | 15:15 | 07.12.19 | 16:22 | 0.046528 | 1 | 2 | [5 empty] | At Jharsuguda end-Tripped on E/F
|  | 19.03.20 | 15:30 | 19.03.20 | 17:22 | 0.077778 | 0 | 58 | [5 empty] | At Budhipadar End D/P ( ABB RAZOA), zone-II, Dir E/F Trip, IL2=10.67 KA At Jharsuguda End D/P operated in Zone-I, FD=2.3 Kms, FL =L2-E, IL2=8KA
|  | 02.06.19 | 14:45 | 02.06.19 | 15:09 | 0.016667 | 0 | 24 | [5 empty] | At Jharsuguda-Tripped on o/c B-phase
|  | 20.08.19 | 19:46 | 20.08.19 | 20:40 | 0.0375 | 0 | 54 | [5 empty] | Tripped at Lapanga end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
207 | 132kV Budhipadar-Jharsuguda Ckt-II |  |  |  |  | 0.12917 | 14 | 12 | [7 empty] | 4.5 | 8760 | 99.84% | 63.9 | 39420
|  | 19.03.20 | 15:30 | 19.03.20 | 17:22 | 0.077778 | 0 | 58 | [5 empty] | At Budhipadar End D/P ( ABB RAZOA), zone-II, Dir E/F Trip, IL2=10.67 KA At Jharsuguda End D/P operated in Zone-I, FD=2.3 Kms, FL =L2-E, IL2=8KA
|  | 20.08.19 | 19:46 | 20.08.19 | 20:40 | 0.0375 | 0 | 54 | [5 empty] | Tripped at Lapanga end
|  | 02.06.19 | 14:35 | 02.06.19 | 14:55 | 0.013889 | 0 | 20 | [5 empty] | At Budhipadar end-Tripped on: Dir E/F Trip, Dir O/C ,IL3=2.02KAmp
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
208 | 132kV Budhipadar-Jharsuguda Ckt-I |  |  |  |  | 0.052083 | 13 | 15 | [7 empty] | 7 | 8760 | 99.85% | 92.75 | 61320
|  | 07.12.19 | 15:15 | 07.12.19 | 15:25 | 0.0069444 | 0 | 10 | [5 empty] | At Budhipadar end-Tripped on: Dir E/F Trip, Dir O/C ,IL3=2.02KAmp
|  | 02.06.19 | 14:35 | 02.06.19 | 14:55 | 0.013889 | 0 | 20 | [5 empty] | At Budhipadar end-Tripped on: Dir E/F Trip, Dir O/C ,IL3=2.02KAmp
|  | 19.03.20 | 15:33 | 19.03.20 | 16:18 | 0.03125 | 0 | 45 | [5 empty] | At Jharsuguda-Tripped on Y-ph O/C, At Budhipadar end - Zone-2, Master Trip
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
209 | 132kV Budhipadar-Rajgangpur ckt-II |  |  |  |  | 0.10278 | 13 | 17 | [7 empty] | 80 | 8760 | 99.85% | 1062.6667 | 700800
|  | 19.03.20 | 15:30 | 19.03.20 | 17:08 | 0.068056 | 0 | 58 | [5 empty] | At Rajagangpur end: Tripped on E/F. At Budhipadar End: D/P( ABB REL 670), R,Y & B-Phase Trip Zone-I, FD= 14 Kms, FL=L2-N, IL2= 4.997 KA
|  | 22.09.19 | 17:25 | 22.09.19 | 18:09 | 0.030556 | 0 | 13 | [5 empty] | At Rajgangpur end:-AGT,LOC-65.03KM ZONE-II IA=1063A IG=1080A , At Budhipadar end:- L1N LOOP LOC-19.272KM ZONE-1 L1=3.22KA,
|  | 25.04.19 | 12:55 | 25.04.19 | 13:01 | 0.0041667 | 0 | 6 | [5 empty] | DP OPERATED, FAULT- L1 TO L2, FAULT CURRENT- L1-1.529kA, L2-1.396kA, LOC- 99.176, ZONE-2
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
210 | 132kV Budhipadar-Sundargarh-I |  |  |  |  | 1899-12-31 06:58 | 17 | 50 | [7 empty] | 31.61 | 8760 | 99.8% | 563.7117 | 276903.6
|  | 19.03.20 | 15:30 | 19.03.20 | 16:35 | 0.045139 | 0 | 58 | [5 empty] | At-Sundargarh, E/F , IL1=0.06 KA,IL2-0.07 KA,IL3=0.06KA
|  | 12.06.19 | 0:37 | 13.06.19 | 1:27 | 0.034722 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
|  | 24.07.19 | 17:40 | 24.07.19 | 18:12 | 0.022222 | 0 | 32 | [5 empty] | At Budhipadar End- B/U(MICOM P14DB) Trip,O/C+E/F(R-Phase),IL1= 1.777 KA, In=1.423 KA . At Sundargarh End-O/C+E/F(R-Phase
|  | 28.10.19 | 14:24 | 28.10.19 | 12:56 | 0.93889 | 0 | 31 | [5 empty] | At-Sundargarh,O/C,E/F,B-phase,DP: CGT,Loc-2.04,Zone-1,A-188,B-246,C-2415,N-2846/ ( B-phase LA failure)
|  | 12.09.19 | 5:55 | 12.09.19 | 11:54 | 0.24931 | 2 | 59 | [5 empty] | At Sundargarh end;- E/F, R-phase At Budhipadar end;- DP,Zone-1, 2.7 KM,R-ph-9.33 kA,Y-ph-8.33 kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
211 | 132kV Budhipadar-Sundargarh-II |  |  |  |  | 0.20347 | 16 | 52 | [7 empty] | 31.61 | 8760 | 99.81% | 533.1553 | 276903.6
|  | 12.06.19 | 0:37 | 13.06.19 | 1:27 | 0.034722 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
|  | 24.07.19 | 17:40 | 24.07.19 | 18:13 | 0.022917 | 0 | 32 | [5 empty] | At Budhipadar End- B/U(MICOM P14DB) Trip,O/C+E/F(R-Phase),IL1= 1.777 KA, In=1.423 KA . At Sundargarh End-O/C+E/F(R-Phase
|  | 28.10.19 | 14:24 | 28.10.19 | 14:55 | 0.021528 | 0 | 31 | [5 empty] | At-Sundargarh,E/F,B-phase,R-phase-0.18 kA,Y-phase-0.26 kA,B-phase-0.17 KA
|  | 12.09.19 | 5:55 | 12.09.19 | 8:54 | 0.12431 | 2 | 59 | [5 empty] | At-Sundargarh end:- Tripped on E/F, R-phase At-Budhipadar,DP,Zone-1,3.72 Km,R-phase-6.95 KA,Y-phase-6.99 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
212 | 132kV Budhipadar-MCL(Jorbaga)-I |  |  |  |  | 0.034722 | 0 | 50 | [7 empty] | 23 | 8760 | 99.99% | 19.1667 | 201480
|  | 12.06.19 | 0:37 | 13.06.19 | 1:27 | 0.034722 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
213 | 132kV Budhipadar-MCL(Jorbaga)-II |  |  |  |  | 0.034722 | 0 | 50 | [7 empty] | 23 | 8760 | 99.99% | 19.1667 | 201480
|  | 12.06.19 | 0:37 | 13.06.19 | 1:27 | 0.034722 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
214 | 132kV Budhipadar-MSP |  |  |  |  | 0.034722 | 0 | 50 | [7 empty] | 0.592 | 8760 | 99.99% | 0.49333 | 5185.92
|  | 12.06.19 | 0:37 | 13.06.19 | 1:27 | 0.034722 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
215 | 132kV Budhipadar-Brajrajnagar (Remja) |  |  |  |  | 0.38958 | 18 | 55 | [7 empty] | 11.745 | 8760 | 99.78% | 222.1763 | 102886.2
|  | 22.03.20 | 12:05 | 22.03.20 | 14:23 | 0.095833 | 2 | 18 | [5 empty] | At Budhipadar end: Tripped
|  | 21.03.20 | 13:09 | 21.03.20 | 14:08 | 0.040972 | 0 | 59 | [5 empty] | At Budhipadar end: Tripped
|  | 12.06.19 | 0:37 | 13.06.19 | 1:27 | 0.034722 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
|  | 02.06.19 | 14:35 | 02.06.19 | 15:13 | 0.026389 | 0 | 38 | [5 empty] | At-Budhipadar end: R, Y, 'B' ph.-E/F, Zone-I
|  | 24.09.19 | 14:33 | 24.09.19 | 14:47 | 0.0097222 | 0 | 14 | [5 empty] | Tripped at Budhipadar end on Zone-1,FL = C-N,FD= 4.47 Kms, Ic= 10.54 KA
|  | 22.05.19 | 19:46 | 22.05.19 | 20:30 | 0.030556 | 0 | 44 | [5 empty] | Failure from Source.
|  | 20.05.19 | 6:14 | 20.05.19 | 9:43 | 0.14514 | 1 | 3 | [5 empty] | Failure from Source.
|  | 21.04.19 | 12:22 | 21.04.19 | 12.31 | 0.00625 | 0 | 9 | [5 empty] | Failure from Source.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
216 | 132kV Budhipadar - Kalunga-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 100 | 8760 | 100% | 0 | 876000
217 | 132kV Burla-Chipilima Ckt-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 19.9 | 8760 | 100% | 0 | 174324
218 | 132kV Burla-Hindalco-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 9 | 8760 | 100% | 0 | 78840
219 | 132kV Burla-Hindalco-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 9 | 8760 | 100% | 0 | 78840
220 | 132kV Burla-Katapali-Chipilima Ckt-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 22.66 | 8760 | 100% | 0 | 198501.6
221 | 132kV Burla-Katapalli |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 7 | 8760 | 100% | 0 | 61320
222 | 132kV Burla-Lapanga-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 44 | 8760 | 100% | 0 | 385440
223 | 132kV Burla-Lapanga-II |  |  |  |  | 0.0375 | 1 | 48 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 44 | 8760 | 99.98% | 79.2 | 385440
|  | 20.08.19 | 19:46 | 20.08.19 | 20:40 | 0.0375 | 1 | 48 | [5 empty] | At Lapanga end:- Tripped on E/F due to snapping of cross bus conductor
224 | 132kV Lapanga-Budhipadar Ckt-II |  |  |  |  | 0.04375 | 1 | 2 | [7 empty] | 16 | 8760 | 99.99% | 16.5333 | 140160
|  | 07.12.19 | 15:15 | 07.12.19 | 16:18 | 0.04375 | 1 | 2 | [5 empty] | At Budhipadar end-Tripped on: Dir E/F Trip IL3=2.95KAmp
225 | 132kV Burla-Sambalpur |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 19.9 | 8760 | 100% | 0 | 174324
226 | 132kV Chainpal-Angul |  |  |  |  | 0.32917 | 16 | 1 | [7 empty] | 14.931 | 8760 | 99.82% | 239.1448 | 130795.56
|  | 27.04.19 | 17:31 | 27.04.19 | 22:34 | 0.21042 | 1 | 10 | [5 empty] | At Chainpal- O/C -R ph ,Y ph, B ph , E/F,M/T
|  | 23.04.19 | 15:35 | 23.04.19 | 15:49 | 0.0097222 | 0 | 14 | [5 empty] | At Chainpal-O/C -Y ph , E/F.
|  | 22.04.19 | 16:16 | 22.04.19 | 16:34 | 0.0125 | 0 | 18 | [5 empty] | At Chainpal-O/C - B ph , E/F.
|  | 14.04.19 | 11:09 | 14.04.19 | 11:18 | 0.00625 | 0 | 9 | [5 empty] | At Chainpal-O/C -Y ph, B ph , E/F.
|  | 13.04.19 | 19:29 | 13.04.19 | 19:46 | 0.011806 | 0 | 17 | [5 empty] | At Chainpal-O/C -R ph ,Y ph, B ph , E/F.
|  | 13.04.19 | 13:30 | 13.04.19 | 14:18 | 0.033333 | 0 | 48 | [5 empty] | At Chainpal-O/C -R ph , Y ph, E/F.
|  | 13.04.19 | 14:19 | 13.04.19 | 15:24 | 0.045139 | 1 | 5 | [5 empty] | At Chainpal-O/C -R ph , E/F.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
227 | 132kV Chainpal-FCI-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7 | 8760 | 100% | 0 | 61320
228 | 132kV Chainpal-FCI-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7 | 8760 | 100% | 0 | 61320
229 | 132kV Chainpal-Talcher Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.448 | 8760 | 100% | 0 | 3924.48
230 | 132kV Chandaka-Bhubaneswar-I |  |  |  |  | 1900-01-03 11:07 | 0 | 16 | [7 empty] | 5.5 | 8760 | 100% | 1.4667 | 48180
|  | 26.08.19 | 3:44 | 26.08.19 | 4:06 | 0.015278 | 0 | 16 | [5 empty] | At Bhubaneswar end:- Tripped on E/F ,O/C due to 33 kV fault in Switchyard
|  | 03.05.19 | 11:05 | 07.05.19 | 21:50 | 1900-01-03 10:45 |  |  |  |  | 106 | 45 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'. 132 kV Choudwar supply extended to Chandaka Grid by means of special arrangement through 132 kV Bidanasi -BPPL ckt
231 | 132kV Chandaka-Bhubaneswar-II |  |  |  |  | 0.011111 | 0 | 16 | [7 empty] | 5.5 | 8760 | 100% | 1.4667 | 48180
|  | 26.08.19 | 3:44 | 26.08.19 | 4:00 | 0.011111 | 0 | 16 | [5 empty] | At Bhubaneswar end:- Tripped on E/F ,O/C
|  | 03.05.19 | 11:05 | 07.05.19 | 21:50 | 106:45 |  |  |  |  | 106 | 45 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'. 132 kV Choudwar supply extended to Chandaka Grid by means of special arrangement through 132 kV Bidanasi -BPPL ckt
232 | 132kV Chandaka-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 18.5 | 8760 | 100% | 0 | 162060
233 | 132kV Chandaka-Nimapara |  |  |  |  | 1900-01-10 01:31 | 12 | 34 | [7 empty] | 65.8 | 8760 | 99.86% | 826.8867 | 576408
|  | 11.12.19 | 3:27 | 11.12.19 | 3:50 | 0.015972 | 0 | 23 | [5 empty] | At Chandaka end-Tripped on: DP operated
|  | 29.03.20 | 18:55 | 29.03.20 | 19:01 | 0.0041667 | 0 | 6 | [5 empty] | At Chandaka end: Distance=17.95Km, Zone1, B-Ph
|  | 03.05.19 | 11:00 | 14.05.19 | 22:53 | 1900-01-10 00:53 |  |  |  |  | 264 | 43 |  | Tripped (Due to Cyclone Fani) (Tower Collapsed)
|  | 11.04.19 | 19:09 | 11.04.19 | 19:18 | 0.00625 | 0 | 5 | [5 empty] | Tripped due to tripping at Samangara-DIST.PROTECTION operated.due to 2/3 MULTIPHASE FAULT
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
234 | 132kV Chandaka-Ransingpur |  |  |  |  | 0.070833 | 13 | 19 | [7 empty] | 28.25 | 8760 | 99.85% | 376.1958 | 247470
|  | 11.12.19 | 3:27 | 11.12.19 | 4:02 | 0.024306 | 0 | 35 | [5 empty] | Chandaka end-Tripped
|  | 05.08.19 | 5:15 | 05.08.19 | 5:32 | 0.011806 | 0 | 17 | [5 empty] | Distance relay operated at Ransinghpur end
|  | 05.08.19 | 5:35 | 05.08.19 | 6:03 | 0.019444 | 0 | 5 | [5 empty] | Tripped at Chandaka end. At 05:40 Hrs P/S availed from Kesura end.
|  | 07.03.20 | 6:12 | 07.03.20 | 6:22 | 0.0069444 | 0 | 10 | [5 empty] | At Chandaka end: Tripped
|  | 19.11.19 | 12:07 | 19.11.19 | 12:19 | 0.0083333 | 0 | 12 | [5 empty] | DP relay operated at Ransinghpur end
|  | 03.05.19 | 11:05 | 07.05.19 | 21:50 | 106:45 |  |  |  |  | 106 | 45 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'. 132 kV Choudwar supply extended to Chandaka Grid by means of special arrangement through 132 kV Bidanasi -BPPL ckt
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
235 | 132kV Chandaka- Mancheswar-B Ckt -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.2 | 780 | 100% | 0 | 8736
236 | 132kV Chandaka B-Unit-8 |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.4 | 8760 | 100% | 0 | 99864
237 | 132kV Chandpur - Khurda |  |  |  |  | 1900-01-02 07:35 | 0 | 0 | [7 empty] | 35.93 | 8760 | 100% | 0 | 314746.8
|  | 03.05.19 | 8:55 | 06.05.19 | 15:35 | 1900-01-02 07:35 |  |  |  |  | 79 | 35 |  | Tripped (Due to Cyclone Fani)
238 | 132kV Chandikhol-Kendrapada |  |  |  |  | 1899-12-31 09:56 | 15 | 38 | [7 empty] | 31.6 | 8760 | 99.82% | 494.0133 | 276816
|  | 19.03.20 | 12:02 | 19.03.20 | 12:35 | 0.022917 | 0 | 33 | [5 empty] | At Kendrapara end: Tripped
|  | 21.01.20 | 15:07 | 21.01.20 | 16:28 | 0.05625 | 0 | 10 | [5 empty] | Tripped at Kendrapara end. At 15:17 Hrs P/S availed from Jajapur Road end
|  | 17.01.20 | 16:41 | 17.01.20 | 17:34 | 0.036806 | 0 | 4 | [5 empty] | Tripped at Kendrapara end. At 16:45 Hrs , P/S availed from Jajapur Road end.
|  | 17.01.20 | 17:42 | 17.01.20 | 18:10 | 0.019444 | 0 | 28 | [5 empty] | At Paradeep end: Tripped on A-G Z1,Dist-23.33KM
|  | 17.01.20 | 16:41 | 18.01.20 | 13:21 | 0.85417 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F,O/C RYB PH,Differential R-Y operated ( 132 kV B-ph LA failure)
|  | 13.12.19 | 13:02 | 13.12.19 | 13:14 | 0.0083333 | 0 | 12 | [5 empty] | At Kendrapara end-Tripped on back up E/F
|  | 13.12.19 | 14:10 | 13.12.19 | 14:35 | 0.017361 | 0 | 25 | [5 empty] | At Kendrapara end-Tripped on back up E/F
|  | 07.12.19 | 6:32 | 07.12.19 | 6:45 | 0.0090278 | 0 | 13 | [5 empty] | At Kendrapara-Tripped
|  | 09.11.19 | 4:37 | 09.11.19 | 12:06 | 0.31181 | 0 | 29 | [5 empty] | At Paradeep end-Tripped. Availed I/C P/S From Jajpur Road end at 05:06Hrs.
|  | 08.11.19 | 22:09 | 08.11.19 | 22:17 | 0.0055556 | 0 | 8 | [5 empty] | At Paradeep end-Tripped
|  | 23.10.19 | 10:34 | 23.10.19 | 10:40 | 0.0041667 | 0 | 6 | [5 empty] | At Kendrapara-TRIPPED ON BACK UP E/F & At Chandikhole end: E/F operated
|  | 01.10.19 | 11:54 | 01.10.19 | 13:18 | 0.058333 | 0 | 11 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1 At Marshaghai-TRIPPED ON O/C & E/F Availed P/S at 12:02 Hrs from Jajpur road end
|  | 01.10.19 | 11:09 | 01.10.19 | 11:13 | 0.0027778 | 0 | 4 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep-Tripped on TRIPPED ON Y-PH O/C,E/F,Z-1,D-86.6KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
239 | 132kV Chatrapur-Balugaon |  |  |  |  | 0.1125 | 12 | 30 | [7 empty] | 54.19 | 8760 | 99.86% | 677.375 | 474704.4
|  | 15.09.19 | 19:59 | 15.09.19 | 20:12 | 0.0090278 | 0 | 2 | [5 empty] | At Chhatrapur-Tripped on O/C B-G with M/R.
|  | 24.09.19 | 2:12 | 24.09.19 | 2:26 | 0.0097222 | 0 | 14 | [5 empty] | At Chhatrapur end: Tripped on Y-G with M/R,Dist-4.29km
|  | 18.09.19 | 12:01 | 18.09.19 | 14:16 | 0.09375 | 0 | 14 | [5 empty] | At Narendrapur end:- Zone-1, R ph. -N, IR = 2.063 kA, VAN = 106.6 kV Dist = 64.30 km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
240 | 132kV Chatrapur-Ganjam |  |  |  |  | 1899-12-31 08:11 | 33 | 58 | [7 empty] | 12.6 | 8760 | 99.61% | 427.98 | 110376
|  | 31.03.20 | 15:19 | 31.03.20 | 15:31 | 0.0083333 | 0 | 12 | [5 empty] | At Chatrapur end-Tripped.
|  | 20.03.20 | 6:07 | 20.03.20 | 6:29 | 0.015278 | 0 | 22 | [5 empty] | At Chatrapur end-Tripped.
|  | 29.01.20 | 5:59 | 29.01.20 | 6:08 | 0.00625 | 0 | 9 | [5 empty] | At Chatrapur end-Tripped.
|  | 08.01.20 | 9:47 | 08.01.20 | 09:54 | 0.0048611 | 0 | 7 | [5 empty] | Power supply failure from Chatrapur end.
|  | 07.11.19 | 21:19 | 08.11.19 | 09:39 | 0.51389 | 12 | 20 | [5 empty] | Incoming Supply failure from Chatrapur-End(132KV Y-ph conductor at loc-26 of 132kv Chatrapur-Ganjam line was detached from longrod insulator).
|  | 02.11.19 | 2:26 | 02.11.19 | 02:35 | 0.00625 | 0 | 9 | [5 empty] | P/S failure from Chatrapur-End.
|  | 18.09.19 | 12:00 | 18.09.19 | 22:22 | 0.43194 | 0 | 9 | [5 empty] | At Narendrapur end;-DP, ZONE-3, IR=443.6 A, IY=1.359kA, IB=998.8 A,VAN=126.9 KV, VBN=118.8 KV, VCN= 119.9KV,Distance=204.9 km (Problem in line CVT)
|  | 10.08.19 | 21:32 | 10.08.19 | 21:40 | 0.0055556 | 0 | 8 | [5 empty] | P/S failed from Chhatrapur end
|  | 26.04.19 | 12:23 | 26.04.19 | 12:44 | 0.014583 | 0 | 21 | [5 empty] | 132KV Incoming supply failed from Chatrapur end.
|  | 05.04.19 | 11:47 | 05.04.19 | 19:48 | 0.33403 | 8 | 1 | [5 empty] | The Conductor at B-ph had detached from the longrod insulator at loc.No.24 of 132 KV Chatrapur Ganjam SC Line.The longrod insulator itself had got damaged.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
241 | 132kV Chatrapur-IRE-I |  |  |  |  | 0.43194 | 0 | 9 | [7 empty] | 5.8 | 8760 | 100% | 0.87 | 50808
|  | 18.09.19 | 12:00 | 18.09.19 | 22:22 | 0.43194 | 0 | 9 | [5 empty] | At Narendrapur end;-DP, ZONE-3, IR=443.6 A, IY=1.359kA, IB=998.8 A,VAN=126.9 KV, VBN=118.8 KV, VCN= 119.9KV,Distance=204.9 km (Problem in line CVT)
242 | 132kV Chatrapur-IRE-II |  |  |  |  | 0.43194 | 0 | 9 | [7 empty] | 5.8 | 8760 | 100% | 0.87 | 50808
|  | 18.09.19 | 12:00 | 18.09.19 | 22:22 | 0.43194 | 0 | 9 | [5 empty] | At Narendrapur end;-DP, ZONE-3, IR=443.6 A, IY=1.359kA, IB=998.8 A,VAN=126.9 KV, VBN=118.8 KV, VCN= 119.9KV,Distance=204.9 km (Problem in line CVT)
243 | 132kV Chatrapur-Rambha (T) |  |  |  |  | 0.43194 | 0 | 9 | [7 empty] | 28.904 | 8760 | 100% | 4.3356 | 253199.04
|  | 18.09.19 | 12:00 | 18.09.19 | 22:22 | 0.43194 | 0 | 9 | [5 empty] | At Narendrapur end;-DP, ZONE-3, IR=443.6 A, IY=1.359kA, IB=998.8 A,VAN=126.9 KV, VBN=118.8 KV, VCN= 119.9KV,Distance=204.9 km (Problem in line CVT)
244 | 132kV Chhend-Adhunik Metalics |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.44 | 8760 | 100% | 0 | 214094.4
245 | 132kV Chhend-Nuagaon(T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35 | 8760 | 100% | 0 | 306600
246 | 132kV Chipilima-Katapalli Ckt-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 100% | 0 | 110901.6
247 | 132kV Chipilima-Katapalli Ckt-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 100% | 0 | 110901.6
248 | 132kV Choudwar-Bidanasi |  |  |  |  | 1900-01-25 11:28 | 0 | 34 | [7 empty] | 15.414 | 8760 | 99.99% | 8.7346 | 135026.64
|  | 19.03.20 | 19:00 | 19.03.20 | 19:54 | 0.0375 | 0 | 14 | [5 empty] | At Biadanasi end: Tripped At Choudwr- Tripped on O/C
|  | 09.03.20 | 11:45 | 09.03.20 | 12:05 | 0.013889 | 0 | 20 | [5 empty] | At choudwar end-Tripped due to Yph L/A brust of CDR-TS Alloys
|  | 03.05.19 | 12:35 | 29.05.19 | 22:49 | 1900-01-25 10:14 |  |  |  |  | 634 | 14 |  | Due to Severe Cyclone FANI, Zone-1,Y-ph to Ground, Iy-3.97KA , Fault Location 7.69 Km.Tower was colapsed inside kathajodi river at location no-16
251 | 132kV Choudwar-Kendrapara Road Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.6 | 8760 | 100% | 0 | 40296
252 | 132kV Cuttack-Jagatsingpur |  |  |  |  | 0.031944 | 12 | 38 | [7 empty] | 35.112 | 8760 | 99.86% | 443.5816 | 307581.12
|  | 22.02.20 | 5:20 | 22.02.20 | 5:27 | 0.0048611 | 0 | 7 | [5 empty] | At Bidanasi end: Tripped
|  | 30.09.19 | 17:31 | 30.09.19 | 17:36 | 0.0034722 | 0 | 5 | [5 empty] | Power supply failure from Bidanasi end
|  | 29.09.19 | 6:58 | 29.09.19 | 7:06 | 0.0055556 |  |  | 0 | 8 |  |  |  | Tripped at Jagatsinghpur end on O/C
|  | 29.09.19 | 7:07 | 29.09.19 | 7:33 | 0.018056 | 0 | 26 | [5 empty] | P/S Failure from Cuttack end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
253 | 132kV Cuttack-Phulnakhara |  |  |  |  | 0.43194 | 13 | 20 | [7 empty] | 20.256 | 8760 | 99.85% | 270.08 | 177442.56
|  | 23.02.20 | 5:20 | 24.02.20 | 16:35 | 35:15 | 0 | 18 | [5 empty] | At Mendhasala End: Zone-I, R-Phase,7.47KA, 4 KM ( Due to jumper snapping at Loc.No.74 & bend the cross arm of Loc.No.73). Cuttack, Phulnakhara P/S availed from Bidanasi end
|  | 22.02.20 | 5:20 | 22.02.20 | 5:27 | 0.0048611 | 0 | 7 | [5 empty] | At Bidanasi end: Tripped
|  | 03.12.19 | 17:15 | 03.12.19 | 17:16 | 00:01 | 0 | 1 | [5 empty] | Bidanasi end-Tripped
|  | 04.12.19 | 19:07 | 04.12.19 | 19:15 | 0.0055556 | 0 | 8 | [5 empty] | Cuttack end-Tripped
|  | 02.12.19 | 21:04 | 02.12.19 | 21:10 | 00:06 | 0 | 6 | [5 empty] | Bidanasi end-Tripped
|  | 02.12.19 | 9:15 | 02.12.19 | 9:23 | 00:08 | 0 | 8 | [5 empty] | Bidanasi end-Tripped
|  | 26.10.19 | 1:12 | 26.10.19 | 1:22 | 0.0069444 | 0 | 10 | [5 empty] | At Bidanasi end-Tripped
|  | 10.10.19 | 21:12 | 10.10.19 | 21:14 | 0.0013889 | 0 | 2 | [5 empty] | At Cuttack end-Tripped
|  | 10.10.19 | 13:14 | 10.10.19 | 13:17 | 0.0020833 | 0 | 3 | [5 empty] | At Bidanasi end-Tripped
|  | 25.10.19 | 7:25 | 25.10.19 | 7:28 | 0.0020833 | 0 | 3 | [5 empty] | At Meramundali end-Tripped
|  | 31.05.19 | 8:06 | 31.05.19 | 13:44 | 0.23472 | 0 | 5 | [5 empty] | At Bidanasi- Zone-1,Y & B-ph to Ground, Fault current-10.29kamps , Fault Location 2.9 Km.Y-ph insulator burst at location no-14
|  | 25.05.19 | 12:33 | 25.05.19 | 16:44 | 0.17431 | 0 | 9 | [5 empty] | At Bidanasi- Zone-1,r-ph to Ground, Ir-769.5A , Fault Location 14.01 Km.Tree falling over the conductor. Availed alternate supply from 220 kv mendhasal feeder.
|  | 03.05.19 | 12:30 | 11.05.19 | 18:47 | 202:47 |  |  |  |  | 202 | 47 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI
|  | 03.05.19 | 11:09 | 10.05.19 | 1:42 | 182:33 |  |  |  |  | 182 | 33 |  | Tower no. 27 & 28 of 132KV Mancheswar-Phulnakhara-Cuttack LILO Line collapsed due to cyclone FANI. Power availed from Bhubaneswar grid after restoration work.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
254 | 132kV Dabugaon -Umerkote |  |  |  |  | 0.97431 | 35 | 23 | [7 empty] | 45.89 | 8760 | 99.6% | 1623.7412 | 401996.4
|  | 29.03.20 | 11:15 | 29.03.20 | 17:04 | 0.24236 | 5 | 49 | [5 empty] | At Jaynagar end: Tripped on B-ph E/F, Zone -1
|  | 23.03.20 | 21:12 | 23.03.20 | 21:17 | 0.0034722 | 0 | 5 | [5 empty] | At Jaynagar end: Tripped
|  | 29.02.20 | 14:04 | 29.02.20 | 14:15 | 0.0076389 | 0 | 11 | [5 empty] | At Jaynagar end: Tripped on E/F
|  | 25.02.20 | 18:21 | 25.02.20 | 18:39 | 0.0125 | 0 | 18 | [5 empty] | At Jayanagar end: Tripped
|  | 14.02.20 | 9:11 | 14.02.20 | 9:30 | 0.013194 | 0 | 19 | [5 empty] | At Jayanagar end: Tripped
|  | 12.02.20 | 12:08 | 12.02.20 | 12:17 | 0.00625 | 0 | 9 | [5 empty] | At Jayanagar end: Tripped
|  | 09.12.19 | 8:25 | 09.12.19 | 8:44 | 0.013194 | 0 | 19 | [5 empty] | Jayangar end-Tripped
|  | 09.12.19 | 15:08 | 09.12.19 | 15:21 | 0.0090278 | 0 | 13 | [5 empty] | Jayangar end-Tripped
|  | 21.04.19 | 1:00 | 21.04.2019 | 11:26 | 0.43472 | 10 | 26 | [5 empty] | Line fault at Tentulikhunti-Dabugaon 132 kV line
|  | 20.04.19 | 18:26 | 20.04.2019 | 24:00 | 0.23194 | 5 | 34 | [5 empty] | Line fault at Tentulikhunti-Dabugaon 132 kV line
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
255 | 132kV Dhenkanal-Khuntuni-Grid Steel -ICCL |  |  |  |  | 0.24931 | 4 | 31 | [7 empty] | 39.58 | 8760 | 99.95% | 178.7697 | 346720.8
|  | 18.03.20 | 11:20 | 18.03.20 | 12:58 | 0.068056 | 0 | 10 | [5 empty] | At Dhenkanal end: E/F B/U Relay operated
|  | 09.08.19 | 13:44 | 09.08.19 | 18:05 | 0.18125 | 4 | 21 | [5 empty] | Tripped at Dhenkanal end due to Bursting of LA in R-phase
256 | 132kV Dhenkanal-Joranda (T) |  |  |  |  | 0.83681 | 20 | 5 | [7 empty] | 19.345 | 8760 | 99.77% | 388.5121 | 169462.2
|  | 27.12.19 | 9:44 | 27.12.19 | 14:43 | 0.20764 | 4 | 59 | [5 empty] | Tripped on E/F (snapping of Earth wire )
|  | 05.06.19 | 20:14 | 06.06.19 | 11:20 | 0.62917 | 15 | 6 | [5 empty] | Tripped on E/F. Heavy spark observed at S/Y
|  | 24.10.19 | 15:40 | 24.10.19 | 19:16 | 0.15 |  |  | 3 | 36 |  |  |  | At Dhenkanal end; E/F (snapping of line conductor)
257 | 132kV Digapahandi-Chikiti ckt - I |  |  |  |  | 0.011806 | 0 | 17 | [7 empty] | 29.5 | 8760 | 100% | 8.3583 | 258420
|  | 18.09.19 | 12:00 | 18.09.19 | 12:17 | 0.011806 | 0 | 17 | [5 empty] | At Narendrapur end: Zone-I, R ph.-E/F, Dist.-76.25 k.m.
258 | 132kV Digapahandi-Chikiti ckt - II |  |  |  |  | 0.011806 | 0 | 17 | [7 empty] | 29.5 | 8760 | 100% | 8.3583 | 258420
|  | 18.09.19 | 12:00 | 18.09.19 | 12:17 | 0.011806 | 0 | 17 | [5 empty] | At Narendrapur end: Zone-I, R ph.-E/F, Dist.-76.25 k.m.
259 | 132kV Duburi-BC Mohanty |  |  |  |  | 0.15625 | 3 | 45 | [7 empty] | 10.974 | 8760 | 99.96% | 41.1525 | 96132.24
|  | 13.07.19 | 14:09 | 13.07.19 | 17:54 | 0.15625 | 3 | 45 | [5 empty] | R' Phase LA failure at B.C. Mohanty Swithing Station. Tripped at both ends.
260 | 132kV Duburi-BRPL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.43 | 8760 | 100% | 0 | 38806.8
261 | 132kV Duburi-Jajpur Road-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.2 | 8760 | 100% | 0 | 115632
262 | 132kV Duburi-Jajpur Road-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.2 | 8760 | 100% | 0 | 115632
263 | 132kV Duburi-Jakhapura (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.851 | 8760 | 100% | 0 | 112574.76
264 | 132kV JSWCL- Mesco |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.464 | 8760 | 100% | 0 | 47864.64
265 | 132kV Duburi-JSWCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.26 | 8760 | 100% | 0 | 81117.6
266 | 132kV ICCL-Choudwar |  |  |  |  | 0.0048611 | 0 | 0 | [7 empty] | 0.5 | 8760 | 100% | 0 | 4380
|  | 03.08.19 | 13:03 | 03.08.19 | 13:10 | 0.0048611 |  |  | 0 | 7 |  |  |  | P/S failed from ICCL end
267 | 132kV Jabamayee FAlloys-Duburi-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12 | 8760 | 100% | 0 | 105120
268 | 132kVJagatsinghpur-Gorakhnath (T) |  |  |  |  | 1899-12-31 03:15 | 13 | 58 | [7 empty] | 16.53 | 8760 | 99.84% | 230.869 | 144802.8
|  | 19.03.20 | 19:51 | 19.03.20 | 17:46 | 0.92014 | 0 | 14 | [5 empty] | At Paradeep end: Tripped (Earthwire snapped at Loc. No:190). At 20:05 Hrs P/S availed from Cuttack end.
|  | 22.01.20 | 15:07 | 22.01.20 | 15:13 | 0.0041667 | 0 | 6 | [5 empty] | P/S failure Paradeep end
|  | 29.01.20 | 3:02 | 29.01.20 | 3:10 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Paradeep end on E/F
|  | 17.01.20 | 16:41 | 17.01.20 | 17:06 | 0.017361 | 0 | 6 | [5 empty] | Tripped from Paradeep end on E/F
|  | 04.01.20 | 10:22 | 04.01.20 | 10:31 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Paradeep end
|  | 16.12.19 | 3:53 | 16.12.19 | 3:59 | 0.0041667 | 0 | 6 | [5 empty] | At Tirtol end-Tripped on E/F
|  | 17.12.19 | 4:47 | 17.12.19 | 4:53 | 0.0041667 | 0 | 6 | [5 empty] | At Tirtol end-Tripped on E/F
|  | 17.12.19 | 5:08 | 17.12.19 | 5:13 | 0.0034722 | 0 | 5 | [5 empty] | At Tirtol end-Tripped on E/F
|  | 27.11.19 | 5:23 | 27.11.19 | 5:30 | 0.0048611 | 0 | 2 | [5 empty] | P/S failure from Tirtol end. At 05:25 Hrs P/S availed from Cuttack end
|  | 25.11.19 | 4:54 | 25.11.19 | 5:13 | 0.013194 | 0 | 13 | [5 empty] | Tripped at Jagatsinghpur on O/C, E/F. At 05:09 Hrs P/S availed from Cuttack end
|  | 26.11.19 | 4:17 | 26.11.19 | 4:26 | 0.00625 | 0 | 1 | [5 empty] | P/S failure from Tirtol end. At 04:18 Hrs P/S availed from Cuttack end
|  | 08.11.19 | 22:09 | 08.11.19 | 22:18 | 0.00625 | 0 | 4 | [5 empty] | At Paradeep end-Tripped. At 22:13 Hrs P/S availed from Cuttack end
|  | 25.07.19 | 2:50 | 25.07.19 | 2:55 | 0.0034722 |  |  | 0 | 5 |  |  |  | O/C, E/F at Jagatsinghpur end
|  | 05.06.19 | 21:39 | 05.06.19 | 23:02 | 0.057639 | 0 | 5 | [5 empty] | At Paradeep end: B o - E/F, Zone-1, Dist.-43.4 k.m.. At 21:44 hrs. Jagatsingpur availed P/S from Cuttack end.
|  | 29.09.19 | 6:58 | 29.09.19 | 7:06 | 0.0055556 |  |  | 0 | 8 |  |  |  | Tripped at Jagatsinghpur end on O/C
|  | 29.09.19 | 7:07 | 29.09.19 | 7:33 | 0.018056 | 0 | 26 | [5 empty] | P/S Failure from Cuttack end
|  | 13.09.19 | 18:49 | 13.09.19 | 20:03 | 0.051389 | 0 | 4 | [5 empty] | Tripped from Paradeep end but at 18:53 hrs, P/S availed from Cuttack end.
|  | 06.09.19 | 13:26 | 06.09.19 | 13:31 | 0.0034722 | 0 | 3 | [5 empty] | Tripped from Paradeep end but P/S availed from Cuttack end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
269 | 132kVJajpur Road-Anandpur Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30 | 8760 | 100% | 0 | 262800
270 | 132kVJajpur Road-Anandpur Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30 | 8760 | 100% | 0 | 262800
271 | 132kV Bhadrak-Agarpada |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.47 | 5124 | 100% | 0 | 145880.28
272 | 132kV Agarpada-Anandpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 41.4 | 5124 | 100% | 0 | 212133.6
273 | 132kVJajpur Road-Chandikhol |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.71 | 8760 | 100% | 0 | 304059.6
274 | 132kVJajpur Road-Jajpur Town |  |  |  |  | 0.21458 | 5 | 9 | [7 empty] | 25.451 | 8760 | 99.94% | 131.0727 | 222950.76
|  | 01.09.19 | 12:19 | 01.09.19 | 17:28 | 0.21458 | 5 | 9 | [5 empty] | At Jajpur Road end:-DP Relay & Master trip Relay operated
275 | 132kVJajpur Road-Kendrapada Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 63.11 | 8760 | 100% | 0 | 552843.6
276 | 132kV Jaleswar-Bhogarai |  |  |  |  | 0.14722 | 13 | 23 | [7 empty] | 57.934 | 8760 | 99.85% | 775.35 | 507501.84
|  | 29.06.19 | 15:24 | 29.06.19 | 16:09 | 0.03125 | 0 | 26 | [5 empty] | P/s availed from Jaleswar end.
|  | 16.06.19 | 1:30 | 16.06.19 | 1:50 | 0.013889 | 0 | 14 | [5 empty] | Tripped at Bhograi end & P/s availed from Baripada (PG)
|  | 16.06.19 | 1:03 | 16.06.19 | 1:26 | 0.015972 | 0 | 19 | [5 empty] | Tripped at Bhograi end & P/s availed from Baripada (PG)
|  | 19.08.19 | 14:53 | 19.08.19 | 16:10 | 0.053472 | 0 | 12 | [5 empty] | Tripped at Baripada(PG) end but Supply availed from Basta end.
|  | 05.08.19 | 15:59 | 05.08.19 | 16:46 | 0.032639 | 0 | 12 | [5 empty] | At Jaleswar end:DP, Zone-I, Y ph. E/F, Dist.-80.3 k.m, FC-9.61 kA But At 16:11 Hrs Jaleswar & Bhograi Grid availed supply from Basta Grid.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
277 | 132kVJaleswar-Jaleswar (T) |  |  |  |  | 0.11736 | 12 | 33 | [7 empty] | 2.34 | 8760 | 99.86% | 29.367 | 20498.4
|  | 19.08.19 | 14:53 | 19.08.19 | 16:10 | 0.053472 | 0 | 12 | [5 empty] | At Jaleswar end: B ph.-E/F, Zone-I, Dist.-54.1 k.m. But Supply availed from Basta end.
|  | 05.08.19 | 15:59 | 05.08.19 | 16:46 | 0.032639 | 0 | 12 | [5 empty] | At Jaleswar end:DP, Zone-I, Y ph. E/F, Dist.-80.3 k.m, FC-9.61 kA But At 16:11 Hrs Jaleswar & Bhograi Grid availed supply from Basta Grid.
|  | 29.06.19 | 15:24 | 29.06.19 | 16:09 | 0.03125 | 0 | 9 | [5 empty] | P/s availed from Jaleswar end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
278 | 132kVJayanagar-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.272 | 8760 | 100% | 0 | 396582.72
279 | 132kVJayanagar-Jayanagar(T) |  |  |  |  | 0.04375 | 1 | 3 | [7 empty] | 40 | 8760 | 99.99% | 42 | 350400
|  | 10.08.19 | 20:12 | 10.08.19 | 21:15 | 0.04375 | 1 | 3 | [5 empty] | At Jayanagar end:- DP, E/F-R ph, Dist.- 40k.m, FC-1.8 KA
280 | 132kVJaynagar-Podagada-Rayagada |  |  |  |  | 0.48333 | 0 | 34 | [7 empty] | 112.236 | 8760 | 99.99% | 63.6004 | 983187.36
|  | 25.07.19 | 17:25 | 25.07.19 | 17:59 | 0.023611 | 0 | 34 | [5 empty] | At Jayanagar end: Z-I, Dist.-27.25 k.m. R,Y,B ph.-E/F
|  | 16.07.19 | 15:47 | 16.07.19 | 23:02 | 0.30208 |  |  | 0 | 9 |  |  |  | Tripped at Machhkund end.Akhusingh GS/S availed P/S from Digapahandi end at 15:56 Hrs.15:55-Rayagada load C.O to TVL Auto.
|  | 17.07.19 | 17:10 | 17.07.19 | 20:57 | 0.15764 |  |  | 0 | 29 |  |  |  | Tripped at Machhkund end: At 17:39 - Akhusingh, Paralakhemundi availed P/S from Digapahandi end.Rayagada Load C/O to TVL Load at 17:46 Hrs.
281 | 132kVJaynagar-Tentulikhunti |  |  |  |  | 0.30764 | 19 | 23 | [7 empty] | 56.4 | 8760 | 99.78% | 1093.22 | 494064
|  | 29.03.20 | 11:15 | 29.03.20 | 17:04 | 0.24236 | 5 | 49 | [5 empty] | At Jaynagar end: Tripped on B-ph E/F, Zone -1
|  | 23.03.20 | 21:12 | 23.03.20 | 21:17 | 0.0034722 | 0 | 5 | [5 empty] | At Jaynagar end: Tripped
|  | 29.02.20 | 14:04 | 29.02.20 | 14:15 | 0.0076389 | 0 | 11 | [5 empty] | At Jaynagar end: Tripped on E/F
|  | 25.02.20 | 18:21 | 25.02.20 | 18:39 | 0.0125 | 0 | 18 | [5 empty] | At Jayanagar end: Tripped
|  | 14.02.20 | 9:11 | 14.02.20 | 9:30 | 0.013194 | 0 | 19 | [5 empty] | At Jayanagar end: Tripped
|  | 12.02.20 | 12:08 | 12.02.20 | 12:17 | 0.00625 | 0 | 9 | [5 empty] | At Jayanagar end: Tripped
|  | 09.12.19 | 8:25 | 09.12.19 | 8:44 | 0.013194 | 0 | 19 | [5 empty] | Jayangar end-Tripped
|  | 09.12.19 | 15:08 | 09.12.19 | 15:21 | 0.0090278 | 0 | 13 | [5 empty] | Jayangar end-Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
282 | 132kVJharsuguda-Jharsuguda(T) |  |  |  |  | 0.010417 | 0 | 11 | [7 empty] | 0.15 | 8760 | 100% | 0.0275 | 1314
|  | 06.10.19 | 2:35 | 06.10.19 | 2:39 | 0.0027778 |  |  | 0 | 4 |  |  |  | Tripped due to O/C at Jharshuguda end.
|  | 02.06.19 | 14:45 | 02.06.19 | 14:56 | 0.0076389 | 0 | 11 | [5 empty] | At Jharsuguda-Tripped on O/C,E/F
283 | 132kVJharsuguda-Ultratech |  |  |  |  | 1900-01-03 13:39 | 25 | 50 | [7 empty] | 31.4 | 8760 | 99.71% | 811.1667 | 275064
|  | 23.02.20 | 21:21 | 23.02.20 | 10:09 | 0.56111 | 13 | 28 | [5 empty] | At Jharsuguda end: Tripped on E/F
|  | 15.02.20 | 13:32 | 15.02.20 | 13:43 | 1900-01-03 00:11 | 0 | 11 | [5 empty] | At Jharsuguda end: Tripped on E/F
|  | 02.06.19 | 14:45 | 02.06.19 | 14:56 | 0.0076389 | 0 | 11 | [5 empty] | At Jharsuguda-Tripped on O/C,E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
284 | 132kVJoda- Banaspani(T) |  |  |  |  | 1899-12-31 05:53 | 15 | 29 | [7 empty] | 2.99 | 8760 | 99.82% | 46.2952 | 26192.4
|  | 28.05.19 | 14.35 | 28.05.19 | 15.06 | 0.021528 | 0 | 31 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 07.05.19 | 17:37 | 07.05.19 | 19.03 | 0.059722 | 1 | 23 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end due to 220 kV Bus-01 pull out.
|  | 03.05.19 | 10.54 | 03.05.19 | 12.09 | 1899-12-31 03:36 | 1 | 15 | [5 empty] | S/D of 132KV main Bus availed at Joda end for replacement of B-ph damaged sec-1 isolator clamp of 132 KV main Bus.
|  | 29.04.19 | 9:30 | 29.04.19 | 9:35 | 0.0034722 | 0 | 5 | [5 empty] | Fdr tripped at Joda ends. At JODA end-B/U Relay,O/C tripped,Phase=A, Zone-1, IL1=201.1A, IL2=199.9A,IL3=0 .
|  | 25.04.19 | 2:15 | 25.04.19 | 2:24 | 0.00625 | 0 | 9 | [5 empty] | Fdr tripped only at Joda end. At JODA end- B/U (O/C) , IA=204.7A, IB=203.4A, IC=0
|  | 12.04.19 | 3:43 | 12.04.19 | 3:49 | 0.0041667 | 0 | 6 | [5 empty] | At Joda end- B/U Relay, O/C Trip, Tripped phase-A, IA=200.4A, IB=199.2A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
285 | 132kVJoda -Barbil |  |  |  |  | 1900-01-03 00:51 | 18 | 4 | [7 empty] | 9.82 | 8760 | 99.79% | 177.4147 | 86023.2
|  | 15.01.20 | 9:09 | 15.01.20 | 9:45 | 0.025 | 0 | 36 | [5 empty] | At Joda end-Tripped
|  | 15.06.19 | 18:32 | 16.06.19 | 16:42 | 0.92361 | 0 | 47 | [5 empty] | At 19:19 Hrs. Barbil availed P/S from Rourkela end.
|  | 02.09.19 | 18:46 | 02.09.19 | 18:57 | 0.0076389 | 0 | 11 | [5 empty] | Tripped as D/P relay operated at Both Barbil & Joda Grid end with following indications at Barbil Grid: Zone-I; 6.227km(C-N); Ic=551.8A
|  | 19.07.19 | 19:25 | 19.07.19 | 23:03 | 0.15139 | 0 | 9 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.
|  | 28.05.19 | 14.35 | 28.05.19 | 16.04 | 0.061806 | 0 | 34 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.132 KV barbil Fdr is idle charged from JODA end & availed p/s from Rourkela end.
|  | 07.05.19 | 17:37 | 07.05.19 | 19:00 | 0.057639 | 0 | 15 | [5 empty] | Fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.132KV Barbil S/S availed Extended P/S from RKl end till restoration of power at Joda end.
|  | 03.05.19 | 10.54 | 03.05.19 | 12.22 | 1899-12-31 06:43 | 1 | 28 | [5 empty] | S/D of 132KV main Bus availed at Joda end for replacement of B-ph damaged sec-1 isolator clamp of 132 KV main Bus.
|  | 02.05.19 | 16.02 | 02.05.19 | 17.54 | 1899-12-31 12:29 | 1 | 52 | [5 empty] | Fdr tripped only at JODA end. At JODA end- DP Relay, Zone-1, Dist= -3.43Km, Fault loop= BG T, IA=269A, IB=7427A,IC=120A, IG=7125A
|  | 02.05.19 | 8:21 | 02.05.19 | 8:33 | 0.0083333 | 0 | 12 | [5 empty] | Fdr tripped only at JODA end. At JODA end- DP Relay, Zone-1, Dist= -3.03Km, Fault loop= BG T, IA=262A, IB=6778A,IC=143A, IG=6490A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
286 | 132kVJoda-FAP |  |  |  |  | 1899-12-31 05:55 | 15 | 9 | [7 empty] | 1.03 | 8760 | 99.83% | 15.6045 | 9022.8
|  | 28.05.19 | 14.35 | 28.05.19 | 15.04 | 0.020139 | 0 | 29 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 07.05.19 | 17:37 | 07.05.19 | 18.58 | 0.05625 | 1 | 23 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end due to 220 kV Bus-01 pull out.
|  | 03.05.19 | 10.51 | 03.05.19 | 12.08 | 1899-12-31 04:05 | 1 | 17 | [5 empty] | S/D of 132KV main Bus availed at Joda end for replacement of B-ph damaged sec-1 isolator clamp of 132 KV main Bus.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
287 | 132kVJoda-Kenduposi |  |  |  |  | 0.15625 | 3 | 45 | [7 empty] | 49.92 | 8760 | 99.96% | 187.2 | 437299.2
|  | 28.05.19 | 14.35 | 28.05.19 | 18.2 | 0.15625 | 3 | 45 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
288 | 132kVJoda-Palasponga |  |  |  |  | 0.33264 | 17 | 36 | [7 empty] | 42 | 8760 | 99.8% | 739.2 | 367920
|  | 19.03.20 | 17:06 | 19.03.20 | 17:34 | 0.019444 | 0 | 28 | [5 empty] | At Polasponga end: E/F ZONE1 , Ia=264A, Ib=240A, Ic=152A, IG= 451A
|  | 12.03.20 | 12:42 | 12.03.20 | 12:55 | 0.0090278 | 0 | 13 | [5 empty] | At Polasponga end: E/F ZONE1 LOC 32.85KM, Ia=202.1A, Ib=203A, Ic=79A, IG= 427A
|  | 12.06.19 | 17:32 | 13.06.19 | 18:01 | 0.020139 | 0 | 29
|  | 16.10.19 | 1:27 | 16.10.19 | 1:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Palasponga end; O/C & E/F, Ia=341.3A, Ib=844.1A, Ic=148.9A, In =0.09A, Ig = 386.63A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:15 | 0.028472 | 0 | 41 | [5 empty] | Tripped at Joda end.
|  | 04.10.19 | 21:13 | 04.10.19 | 21:15 | 0.0013889 | 0 | 2 | [5 empty] | At Polasponga end: O/C R-ph, Ia=431.3A, Ib=363.6A, Ic=280.1A, In =0.04A
|  | 04.09.19 | 19:54 | 04.09.19 | 19:55 | 0.00069444 | 0 | 1 | [5 empty] | At Polasponga end:- O/C (R PH), Ia=432.0A, Ib=357.1A, Ic=291.8A, In =0.09A, Ig = 3.94A
|  | 15.09.19 | 18:42 | 15.09.19 | 18:46 | 0.0027778 | 0 | 4 | [5 empty] | At Polasponga end;- O/C (R PH), Ia=423.0A, Ib=341.2A, Ic=288.2A, In =0.01A, Ig = 2.91A
|  | 19.07.19 | 19:25 | 19.07.19 | 21:06 | 0.070139 | 0 | 23 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.Polasponga GSS availed P/S at 19:48 Hrs from Karanjia GSS.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 34 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end; E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 09.05.19 | 14.15 | 09.05.19 | 14.18 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Joda end; O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA ,IN=0.0A,IG=1.1
|  | 07.05.19 | 17:37 | 07.05.19 | 19.06 | 0.061806 | 0 | 30 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end; 132KV PPG S/S availed P/S from Karanjia end till restoration of power at Joda end.
|  | 21.04.19 | 15:18 | 21.04.19 | 15:28 | 0.0069444 | 0 | 10 | [5 empty] | Fdr tripped at both ends. At JODA end- DP Relay, zone-1,fault loop=L2_N,fault distance=2.27 km, IL1=161.90A, IL2=6868.97A, IL3=109.93A, IN=6763.22A. At PPG end- DP Relay, zone-1,fault loop=L2_N,fault distance=32.2 km, IL1=176A, IL2=293A, IL3=127A, IN=407A
|  | 19.04.19 | 1:25 | 19.04.19 | 1:43 | 0.0125 | 0 | 18 | [5 empty] | Fdr tripped only at Joda end. At JODA end- DP Relay, zone-1,fault loop=L2_N,fault distance=2.0437 km, IL1=247.75A, IL2=6817.47A, IL3=238.20A, IN=6895.73A
|  | 29.04.19 | 21:33 | 29.04.19 | 21:38 | 0.0034722 | 0 | 5 | [5 empty] | O/C (R PH), Ia= 405A, Ib= 340A, Ic= 242.8A, In= 0.1A, Ig= 4.66A
|  | 28.04.19 | 15:06 | 28.04.19 | 15:09 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R PH), Ia= 423.4A, Ib= 355.9A, Ic= 309.8A, In= 0.09A, Ig= 2.4A
|  | 25.04.19 | 7:58 | 25.04.19 | 8:06 | 0.0055556 | 0 | 8 | [5 empty] | O/C,E/F (Y PH), Ia= 221.5A, Ib= 654.1A, Ic=161.2A, In= 0.1A, Ig= 686.26A
|  | 25.04.19 | 23:41 | 25.04.19 | 23:46 | 0.0034722 | 0 | 5 | [5 empty] | O/C (R PH), Ia= 421A, Ib= 361A, Ic=277.7A, In= 0.03A, Ig= 3.12A
|  | 21.04.19 | 15.35 | 21.04.19 | 16:15 | 0.027778 | 0 | 40 | [5 empty] | SOURCE FAILURE but Restricted P/S availed from Karanjia GSS end.
|  | 13.04.19 | 5:25 | 13.04.19 | 5:34 | 0.00625 | 0 | 9 | [5 empty] | O/C (B PH), Ia=1532A, Ib= 1037A, Ic=366.2, In= 0.00A, Ig= 4.9A
|  | 12.04.19 | 16:38 | 12.04.19 | 16:40 | 0.0013889 | 0 | 2 | [5 empty] | E/F WITH DP Z, Ia=80.81A, Ib=1.019KA, Ic=55.05, In=1.052KA, Ig= 1.05KA
|  | 07.04.19 | 16:01 | 07.04.19 | 16:03 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R PH), Ia=396.4A, Ib= 376.04A, Ic=388.84A Ig=51.8A
|  | 02.04.19 | 0.275 | 02.04.19 | 6:39 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R PH), Ia=414.1A, Ib= 341.7A, Ic=285.9A, In= 0.09A, Ig= 5.73A
|  | 02.04.19 | 3:02 | 02.04.19 | 3:05 | 0.0020833 | 0 | 3 | [5 empty] | O/C (B PH), Ia= 435.38A, Ib= 355.4A, Ic=333.3A, In= 0.0A, Ig= 3.94A
|  | 01.04.19 | 20:53 | 01.04.19 | 20:55 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R PH), Ia= 421.5A, Ib= 364.0A, Ic= 388.0A, In= 0.05A, Ig= 5.56A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
289 | 132kV Kamakhya Nagar -Kalarangi-Duburi |  |  |  |  | 0.041667 | 1 | 18 | [7 empty] | 74.84 | 8760 | 99.99% | 97.292 | 655598.4
|  | 24.10.19 | 4:50 | 25.10.19 | 12:33 | 33:43 | 0 | 32 | [5 empty] | Tripped on E/F at Kamakhyanagar end (B-Phase LA burst at Kalarangi end)
|  | 23.09.19 | 3:50 | 23.09.19 | 4:50 | 0.041667 | 0 | 46 | [5 empty] | At Kamakhyanagar end;- Tripped on E/F
290 | 132kV Kamakhya Nagar - Kamakhya Nagar (T) |  |  |  |  | 0.041667 | 0 | 46 | [7 empty] | 4.94 | 276 | 99.72% | 3.7873 | 1363.44
|  | 23.09.19 | 3:50 | 23.09.19 | 4:50 | 0.041667 | 0 | 46 | [5 empty] | At Kamakhyanagar end;- Tripped on E/F
291 | 132kV Kantabanji- Kantabanji Traction |  |  |  |  | 1899-12-31 15:07 | 46 | 24 | [7 empty] | 4 | 8760 | 99.47% | 185.6 | 35040
|  | 24.03.20 | 19:00 | 24.03.20 | 19:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 25.03.20 | 16:17 | 25.03.20 | 16:31 | 0.0097222 | 0 | 14 | [5 empty] | At Saintala end: Tripped on O/C
|  | 22.03.20 | 7:38 | 22.03.20 | 7:51 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:04 | 19.03.20 | 21:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:23 | 19.03.20 | 21:39 | 0.011111 | 0 | 16 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 22:08 | 19.03.20 | 22:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 23:48 | 19.03.20 | 23:56 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:45 | 19.03.20 | 17:48 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:28 | 19.03.20 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 6:48 | 19.03.20 | 6:55 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 16.03.20 | 19:12 | 16.03.20 | 19:25 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 15.03.20 | 17:07 | 15.03.20 | 17:12 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 7:20 | 14.03.20 | 7:30 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 8:17 | 14.03.20 | 8:22 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 9:04 | 14.03.20 | 9:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.03.20 | 18:00 | 13.03.20 | 18:07 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 8:00 | 12.03.20 | 8:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 9:10 | 12.03.20 | 9:17 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 12:15 | 12.03.20 | 12:26 | 0.0076389 | 0 | 11 | [5 empty] | At Saintala end: Tripped on O/C
|  | 11.03.20 | 7:40 | 11.03.20 | 7:47 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:25 | 03.03.20 | 15:26 | 0.00069444 | 0 | 1 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:32 | 03.03.20 | 15:34 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:44 | 03.03.20 | 15:51 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 16:13 | 03.03.20 | 16:26 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 17:31 | 03.03.20 | 17:33 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 7:53 | 28.02.20 | 7:59 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 10:54 | 28.02.20 | 10:59 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 23.02.20 | 8:52 | 23.02.20 | 8:58 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped
|  | 19.02.20 | 15:49 | 19.02.20 | 15:52 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 16:44 | 19.02.20 | 16:57 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 18:06 | 19.02.20 | 18:13 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:08 | 20.02.20 | 7:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:29 | 20.02.20 | 7:36 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 18:36 | 20.02.20 | 18:39 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 21.02.20 | 8:21 | 21.02.20 | 8:27 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 4:59 | 19.02.20 | 5:02 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:35 | 12.02.20 | 17:40 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir New end: Tripped on O/C
|  | 12.02.20 | 16:12 | 12.02.20 | 17:18 | 0.045833 | 1 | 6 | [5 empty] | At Bolangir end: Tripped
|  | 20.01.20 | 5:54 | 20.01.20 | 5:56 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 11.01.20 | 5:27 | 11.01.20 | 5:31 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala on E/F
|  | 07.12.19 | 8:22 | 07.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | Kesinga end-Tripped on E/F
|  | 17.12.19 | 8:22 | 17.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end-Tripped on E/F
|  | 06.12.19 | 18:28 | 06.12.19 | 18:34 | 0.0041667 | 0 | 6 | [5 empty] | At Kesinga end-Tripped onover loadig and O/C
|  | 30.11.19 | 10:12 | 30.11.19 | 10:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped due to Bolangir-Solar Incomer Breaker Tripped.
|  | 23.11.19 | 16:37 | 23.11.19 | 16:50 | 0.0090278 | 0 | 13 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 23.11.19 | 16:11 | 23.11.19 | 16:20 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 20.11.19 | 11:02 | 20.11.19 | 11:11 | 0.00625 | 0 | 9 | [5 empty] | At Bolangir end :-Tripped (dropping conductor of wave trap b-ph at sadeipali)
|  | 15.11.19 | 2:51 | 15.11.19 | 3:06 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: Tripped on overloading
|  | 12.11.19 | 1:45 | 12.11.19 | 1:47 | 0.0013889 | 0 | 2 | [5 empty] | At Kesinga end :-Tripped on Over loading
|  | 07.11.19 | 3:22 | 07.11.19 | 3:24 | 0.0013889 | 0 | 2 | [5 empty] | At Kesinga end :-Tripped on E/F
|  | 02.11.19 | 9:10 | 02.11.19 | 9:14 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 01.11.19 | 6:37 | 01.11.19 | 6:47 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 28.10.19 | 4:21 | 28.10.19 | 4:23 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Saintala end
|  | 27.10.19 | 5:17 | 27.10.19 | 5:28 | 0.0076389 | 0 | 11 | [5 empty] | Tripped at Saintala end
|  | 26.10.19 | 10:49 | 26.10.19 | 10:52 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Saintala end
|  | 25.10.19 | 10:24 | 25.10.19 | 10:38 | 0.0097222 | 0 | 14 | [5 empty] | Tripped at Tushra end
|  | 25.10.19 | 4:44 | 25.10.19 | 5:40 | 0.038889 | 0 | 56 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 19:30 | 22.10.19 | 19:42 | 0.0083333 | 0 | 12 | [5 empty] | P/S failure from Bolangir New end
|  | 22.10.19 | 6:09 | 22.10.19 | 6:42 | 0.022917 | 0 | 33 | [5 empty] | Tripped at ACME end due to snapping of line conductor
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | At Bolangir New S/S -Tripped due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 13.10.19 | 5:07 | 13.10.19 | 5:28 | 0.014583 | 0 | 21 | [5 empty] | Trippead at Khariar end
|  | 13.10.19 | 3:11 | 13.10.19 | 3:17 | 0.0041667 | 0 | 6 | [5 empty] | Trippead at Saintala end
|  | 11.10.19 | 1:10 | 11.10.19 | 1:21 | 0.0076389 | 0 | 11 | [5 empty] | Trippead at Saintala end
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 11:07 | 01.10.19 | 11:12 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at ACME end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:43 | 0.15208 | 0 | 49 | [5 empty] | Tripped at Bolangir New end( Jumper snapped at GSS Sadeipali). Availed P/S at 07:53 Hrs from Kesinga end
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:36 | 0.018056 | 0 | 26 | [5 empty] | Tripped at New Bolangir end.
|  | 26.09.19 | 0:10 | 26.09.19 | 0:30 | 0.013889 | 0 | 20 | [5 empty] | P/S Failure from Bolangir New end
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 23.09.19 | 18:42 | 23.09.19 | 19:12 | 0.020833 | 0 | 30 | [5 empty] | Tripped on overload at New Bolangir end.
|  | 23.09.19 | 15:53 | 23.09.19 | 16:00 | 0.0048611 | 0 | 7 | [5 empty] | Tripped at New Bolangir end.
|  | 17.09.19 | 19:13 | 17.09.19 | 20:56 | 0.071528 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 27.09.19 | 4:03 | 27.09.19 | 4:11 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala-Tripped on E/F
|  | 27.09.19 | 7:56 | 27.09.19 | 8:01 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala-Tripped on Over load
|  | 27.09.19 | 21:41 | 27.09.19 | 21:50 | 0.00625 | 0 | 9 | [5 empty] | At Saintala-Tripped on Over load
|  | 19.09.19 | 12:47 | 19.09.19 | 12:57 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped and At Tusura end also DP operated.
|  | 10.09.19 | 19:45 | 10.09.19 | 21:27 | 0.070833 | 0 | 42 | [5 empty] | At Kesinga-Tripped on over load
|  | 05.09.19 | 17:23 | 05.09.19 | 17:34 | 0.0076389 | 0 | 11 | [5 empty] | At Kesinga-Tripped on over load
|  | 14.09.19 | 11:29 | 14.09.19 | 11:38 | 0.029167 | 0 | 42 | [5 empty] | At Khariar-Tripped on E/F
|  | 21.08.19 | 18:58 | 21.08.19 | 19:06 | 0.0055556 | 0 | 8 | [5 empty] | At Bolangir New-Tripped due to 132KV LA failure
|  | 21.08.19 | 18:32 | 21.08.19 | 18:46 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 13.08.19 | 6:28 | 13.08.19 | 6:32 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala end.
|  | 13.08.19 | 5:53 | 13.08.19 | 6:09 | 0.011111 | 0 | 16 | [5 empty] | P/S failure from New Bolangir end
|  | 21.08.19 | 18:32 | 21.08.19 | 18:42 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:30 | 0.015972 | 0 | 23 | [5 empty] | P/S failure from Bolangir New due to over loading
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 11.08.19 | 5:09 | 11.08.19 | 5:27 | 0.0125 | 0 | 18 | [5 empty] | Tripped on E/F at Bolangir end
|  | 22.07.19 | 3:28 | 22.07.19 | 3:55 | 0.01875 | 0 | 27 | [5 empty] | Tripped at Saintala end
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 05.07.19 | 15:06 | 05.07.19 | 15:56 | 0.034722 | 0 | 50 | [5 empty] | At Kesinga-Tripped on D/P relay
|  | 20.06.19 | 9:51 | 20.06.19 | 10:02 | 0.0076389 | 0 | 11 | [5 empty] | 132KV Tushra-Saintal line didn’t stand. Power supply resumed from kesinga
|  | 20.06.19 | 14:55 | 20.06.19 | 15:04 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.06.19 | 16:00 | 20.06.19 | 16:12 | 0.0083333 | 0 | 12 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 22.06.19 | 14:13 | 22.06.19 | 14:16 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 25.06.19 | 21:43 | 25.06.19 | 21:47 | 0.0027778 | 0 | 4 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 20:55 | 26.06.19 | 21:00 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:18 | 26.06.19 | 22:23 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:45 | 26.06.19 | 22:54 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 18.06.19 | 1:17 | 18.06.19 | 1:23 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 13.06.19 | 16:55 | 13.06.19 | 16:58 | 0.0020833 | 0 | 3 | [5 empty] | 132KV Saintala I/C pullout
|  | 11.06.19 | 15:29 | 11.06.19 | 15:36 | 0.0048611 | 0 | 7 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.06.19 | 15:55 | 09.06.19 | 16:23 | 0.019444 | 0 | 28 | [5 empty] | 132KV Y-phase CT brust at GSS Saintala
|  | 05.06.19 | 0.92708 | 05.06.19 | 22:18 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.06.19 | 18:00 | 05.06.19 | 18:06 | 0.0041667 | 0 | 6 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 03.06.19 | 6:58 | 03.06.19 | 7:08 | 0.0069444 | 0 | 10 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 02.06.19 | 23:03 | 02.06.19 | 23:26 | 0.015972 | 0 | 23 | [5 empty] | Earth fault located at bolangir
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder). Tripped from Saintala end.
|  | 29.04.19 | 2:34 | 29.04.19 | 2:39 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped on over load.
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 28.05.19 | 16:58 | 28.05.19 | 17:07 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Tusura; LBB Trip Supervision
|  | 17.05.19 | 16:06 | 17.05.19 | 16:12 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from ACME;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 29.05.19 | 21:10 | 29.05.19 | 23:12 | 0.084722 | 2 | 2 | [5 empty] | Tripped from Saintala;CT Brust on 132KV Khariar O/G Feeder at GSS Kesinga
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 21.05.19 | 0:23 | 21.05.19 | 0:31 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 17.05.19 | 22:20 | 17.05.19 | 22:25 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.05.19 | 0:03 | 20.05.19 | 0:09 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 12.05.19 | 16:55 | 12.05.19 | 17:04 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala; Y Phase, E/F on 132 KV Kesinga O/G Feeder
|  | 13.05.19 | 14:39 | 13.05.19 | 14:46 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 6:28 | 11.05.19 | 6:35 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 8:03 | 11.05.19 | 8:08 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.05.19 | 15:53 | 09.05.19 | 15:57 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 4:54 | 11.05.19 | 5:03 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 23:45 | 04.05.19 | 23:48 | 0.0020833 | 0 | 3 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.05.19 | 5:52 | 05.05.19 | 5:59 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 16:25 | 04.05.19 | 16:33 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 22:43 | 01.05.19 | 22:48 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 16:28 | 01.05.19 | 16:30 | 0.0013889 | 0 | 2 | [5 empty] | Due to ckt overloading ; Tripped from New Bolangir
|  | 20.04.19 | 20:12 | 20.04.19 | 20:16 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, Tushra 132KV I/C Pullout; Tripped from Tusura
|  | 30.04.19 | 3:43 | 30.04.19 | 7:00 | 0.13681 | 3 | 17 | [5 empty] | Y-Phase Jumper snapped on 132Kesinga-Khariar O/G Feeder at GSS Kesinga, Tripped from Saintala end.
|  | 30.04.19 | 22:32 | 30.04.19 | 22:38 | 0.0041667 | 0 | 6 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 28.04.19 | 16:27 | 28.04.19 | 17:48 | 0.05625 | 1 | 21 | [5 empty] | B-Phase Jumper snapped at Gantry point of 132 Saintala O/G Feeder, Tripped from Tusura end.
|  | 27.04.19 | 22:27 | 27.04.19 | 22:42 | 0.010417 | 0 | 15 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 24.04.19 | 21:22 | 24.04.19 | 21:26 | 0.0027778 | 0 | 4 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 23.04.19 | 22:20 | 23.04.19 | 22:27 | 0.0048611 | 0 | 7 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 21.04.19 | 8:24 | 21.04.19 | 8:40 | 0.011111 | 0 | 16 | [5 empty] | 132KV Saintala O/G Feeder Tripped on E/F, Tripped from Tusura end.
|  | 19.04.19 | 20:08 | 19.04.19 | 20:16 | 0.0055556 | 0 | 8 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 17.04.19 | 5:27 | 17.04.19 | 5:40 | 0.0090278 | 0 | 13 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 29.04.19 | 17:28 | 29.04.19 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 29.04.19 | 16:45 | 29.04.19 | 16:48 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 12.04.19 | 21:37 | 12.04.19 | 21:50 | 0.0090278 | 0 | 13 | [5 empty] | Source Failure
|  | 08.04.19 | 6:52 | 08.04.19 | 6:54 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 08.04.19 | 22:44 | 08.04.19 | 22:46 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:00 | 09.04.19 | 5:07 | 0.0048611 | 0 | 7 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:45 | 09.04.19 | 5:48 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 07.04.19 | 21:51 | 07.04.19 | 21:54 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 05.04.19 | 22:17 | 05.04.19 | 22:22 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 03.04.19 | 20:38 | 03.04.19 | 20:43 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 01.04.19 | 21:57 | 01.04.19 | 22:00 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
292 | 132kV Karanjia-Palasponga |  |  |  |  | 0.034722 | 0 | 50 | [7 empty] | 84 | 8760 | 99.99% | 70 | 735840
|  | 28.10.19 | 10:17 | 28.10.19 | 10:27 | 0.0069444 | 0 | 10 | [5 empty] | Tripped From Karanjia Grid s/s
|  | 21.04.19 | 15.35 | 21.04.19 | 16:15 | 0.027778 | 0 | 40 | [5 empty] | SOURCE FAILURE but Restricted P/S availed from Karanjia GSS end.
293 | 132kV Karanjia-Dhenkikote |  |  |  |  | 0.18958 | 3 | 38 | [7 empty] | 41.902 | 8760 | 99.96% | 152.2439 | 367061.52
|  | 13.11.19 | 8:39 | 13.11.19 | 9:34 | 0.038194 |  |  | 0 | 55 |  |  |  | Tripped at both ends due to B-phase LA of 132KV Bangiriposi- PGCIL line burst at PGCIL end. Rairangpur Grid avail P/ S from Karanjia Grid end and Bangiriposi avail P/S from Rairangpur.
|  | 21.04.19 | 15.35 | 21.04.19 | 16:15 | 0.027778 | 0 | 40 | [5 empty] | SOURCE FAILURE but Restricted P/S availed from Karanjia GSS end.
|  | 07.04.19 | 14:17 | 07.04.19 | 17:15 | 0.12361 | 2 | 58 | [5 empty] | O/C in B- phase Ib-8.59KA,Z1-405m. Then ICT was tripped at PGCIL end & Restricted P/S restored from Rairangpur end.
294 | 132kV Katapalli-Sambalpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 22.25 | 8760 | 100% | 0 | 194910
295 | 132kV Sambalpur-Rairakhol |  |  |  |  | 0 | 0 | 0 | [7 empty] | 63.46 | 8760 | 100% | 0 | 555909.6
296 | 132kV Kendrapada-Marshaghai ckt-I |  |  |  |  | 1899-12-31 16:06 | 15 | 11 | [7 empty] | 16.6 | 8760 | 99.83% | 252.0433 | 145416
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 18.01.20 | 13:21 | 0.85417 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F,O/C RYB PH,Differential R-Y operated ( 132 kV B-ph LA failure)
|  | 15.12.19 | 13:23 | 15.12.19 | 13:36 | 0.0090278 | 0 | 13 | [5 empty] | At Paradeep end-Tripped on C-N,Z-I D-3.33kM At Kendrapara-TRIPPED ON DP RELAY ZONE-1 SHOWS DISTANCE 23.73KM
|  | 09.11.19 | 4:38 | 09.11.19 | 8:30 | 0.16111 | 0 | 29 | [5 empty] | At Paradeep end-Tripped. Availed I/C P/S From Jajpur Road end at 05:06Hrs
|  | 08.11.19 | 22:09 | 08.11.19 | 22:17 | 0.0055556 | 0 | 8 | [5 empty] | At Paradeep end-Tripped
|  | 23.10.19 | 10:34 | 23.10.19 | 10:40 | 0.0041667 | 0 | 6 | [5 empty] | At Kendrapara-TRIPPED ON BACK UP E/F & At Chandikhole end: E/F operated
|  | 01.10.19 | 11:54 | 01.10.19 | 13:18 | 0.058333 | 0 | 11 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1 At Marshaghai-TRIPPED ON O/C & E/F Availed P/S at 12:02 Hrs from Jajpur road end
|  | 19.09.19 | 3:48 | 19.09.19 | 5:00 | 0.05 | 0 | 45 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-II Dist.-112 k.m, FC-7.83 kA.At 04:33-Kendrapara availed P/S from Jajpur Road end .
|  | 20.08.19 | 12:27 | 20.08.19 | 12:31 | 0.0027778 | 0 | 4 | [5 empty] | At Kendrapara:- TRIP ON DP RELAY B-PHASE WITH M/R, DISTANCE 5.96 KM
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep-Tripped on TRIPPED ON Y-PH O/C,E/F,Z-1,D-86.6KM
|  | 24.05.19 | 23:44 | 24.05.19 | 23:46 | 0.0013889 | 0 | 2 | [5 empty] | At Paradeep-Tripped on O/C
|  | 24.05.19 | 23:47 | 25.05.19 | 12:02 | 0.51042 | 0 | 28 | [5 empty] | At Paradeep-Tripped on O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
297 | 132kV Marshaghai-Paradeep ckt-I |  |  |  |  | 1899-12-31 13:16 | 14 | 20 | [7 empty] | 20.01 | 8760 | 99.84% | 286.81 | 175287.6
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 18.01.20 | 13:21 | 0.85417 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F,O/C RYB PH,Differential R-Y operated ( 132 kV B-ph LA failure)
|  | 15.12.19 | 13:23 | 15.12.19 | 13:36 | 0.0090278 | 0 | 13 | [5 empty] | At Paradeep end-Tripped on C-N,Z-I D-3.33kM At Kendrapara-TRIPPED ON DP RELAY ZONE-1 SHOWS DISTANCE 23.73KM
|  | 09.11.19 | 4:38 | 09.11.19 | 8:30 | 0.16111 | 0 | 29 | [5 empty] | At Paradeep end-Tripped. Availed I/C P/S From Jajpur Road end at 05:06Hrs
|  | 08.11.19 | 22:09 | 08.11.19 | 22:17 | 0.0055556 | 0 | 8 | [5 empty] | At Paradeep end-Tripped
|  | 19.09.19 | 3:48 | 19.09.19 | 5:00 | 0.05 | 0 | 45 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-II Dist.-112 k.m, FC-7.83 kA.At 04:33-Kendrapara availed P/S from Jajpur Road end .
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep-Tripped on TRIPPED ON Y-PH O/C,E/F,Z-1,D-86.6KM
|  | 03.05.19 | 13:50 | 03.05.19 | 19:16 | 0.22639 |  |  |  |  | 5 | 26 |  | Tripped at Paradeep end during extreme severe cyclone 'FANI
|  | 03.05.19 | 12:40 | 03.05.19 | 18:15 | 0.23264 |  |  |  |  | 5 | 35 |  | Tripped at Paradeep end during extreme severe cyclone 'FANI
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
298 | 132kV Kendrapada-Paradeep Ckt-II |  |  |  |  | 1900-01-01 21:04 | 14 | 56 | [7 empty] | 34.774 | 8760 | 99.83% | 519.2917 | 304620.24
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 18.01.20 | 13:21 | 0.85417 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F,O/C RYB PH,Differential R-Y operated ( 132 kV B-ph LA failure)
|  | 15.12.19 | 13:23 | 15.12.19 | 13:36 | 0.0090278 | 0 | 13 | [5 empty] | At Paradeep end-Tripped on C-N,Z-I D-3.33kM At Kendrapara-TRIPPED ON DP RELAY ZONE-1 SHOWS DISTANCE 23.73KM
|  | 09.11.19 | 4:38 | 09.11.19 | 8:30 | 0.16111 | 0 | 29 | [5 empty] | At Paradeep end-Tripped. Availed I/C P/S From Jajpur Road end at 05:06Hrs
|  | 08.11.19 | 22:09 | 08.11.19 | 22:17 | 0.0055556 | 0 | 8 | [5 empty] | At Paradeep end-Tripped
|  | 23.10.19 | 10:34 | 23.10.19 | 10:40 | 0.0041667 | 0 | 6 | [5 empty] | At Kendrapara-TRIPPED ON BACK UP E/F
|  | 01.10.19 | 11:09 | 01.10.19 | 11:13 | 0.0027778 | 0 | 4 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1
|  | 19.09.19 | 3:48 | 19.09.19 | 5:00 | 0.05 | 0 | 45 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-II Dist.-112 k.m, FC-7.83 kA.At 04:33-Kendrapara availed P/S from Jajpur Road end .
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep-Tripped on TRIPPED ON Y-PH O/C,E/F,Z-1,D-86.6KM
|  | 24.05.19 | 23:44 | 24.05.19 | 23:46 | 0.0013889 | 0 | 2 | [5 empty] | At Paradeep-Tripped on O/C
|  | 24.05.19 | 23:47 | 25.05.19 | 12:02 | 0.51042 | 0 | 24 | [5 empty] | At Paradeep-Tripped on O/C
|  | 03.05.19 | 12:40 | 04.05.19 | 43:02 | 1899-12-31 06:22 |  |  |  |  | 30 | 22 |  | Tripped at Paradeep end during extreme severe cyclone 'FANI
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
299 | 132kV Kendrapada-Pattamundai |  |  |  |  | 1899-12-31 16:33 | 15 | 38 | [7 empty] | 19.5 | 8760 | 99.82% | 304.85 | 170820
|  | 19.03.20 | 19:50 | 19.03.20 | 20:26 | 0.025 | 0 | 36 | [5 empty] | At Kendrapara end: DP relay operated (R-phase), Dist - 12.67 kM
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 18.01.20 | 13:21 | 0.85417 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F,O/C RYB PH,Differential R-Y operated ( 132 kV B-ph LA failure)
|  | 09.11.19 | 4:38 | 09.11.19 | 8:30 | 0.16111 | 0 | 29 | [5 empty] | At Paradeep end-Tripped. Availed I/C P/S From Jajpur Road end at 05:06Hrs
|  | 08.11.19 | 22:09 | 08.11.19 | 22:17 | 0.0055556 | 0 | 8 | [5 empty] | At Paradeep end-Tripped
|  | 23.10.19 | 10:34 | 23.10.19 | 10:40 | 0.0041667 | 0 | 6 | [5 empty] | At Kendrapara-TRIPPED ON BACK UP E/F & At Chandikhole end: E/F operated
|  | 01.10.19 | 11:54 | 01.10.19 | 13:18 | 0.058333 | 0 | 11 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1 At Marshaghai-TRIPPED ON O/C & E/F Availed P/S at 12:02 Hrs from Jajpur road end
|  | 01.10.19 | 11:09 | 01.10.19 | 11:13 | 0.0027778 | 0 | 4 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1
|  | 19.09.19 | 3:48 | 19.09.19 | 5:00 | 0.05 | 0 | 45 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-II Dist.-112 k.m, FC-7.83 kA.At 04:33-Kendrapara availed P/S from Jajpur Road end .
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Kendrapara:- Tripped on M/R
|  | 24.05.19 | 23:44 | 24.05.19 | 23:46 | 0.0013889 | 0 | 2 | [5 empty] | At Paradeep-Tripped on O/C
|  | 24.05.19 | 23:47 | 25.05.19 | 12:02 | 0.51042 | 0 | 28 | [5 empty] | At Paradeep-Tripped on O/C
|  | 17.08.19 | 20:31 | 17.08.19 | 20:35 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, R-phase at Pattamundai end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
300 | 132kV Kesinga-Bhawanipatna |  |  |  |  | 0.97917 | 35 | 40 | [7 empty] | 40.61 | 8760 | 99.59% | 1448.4233 | 355743.6
|  | 04.03.20 | 16:01 | 04.03.20 | 16:13 | 00:12 | 0 | 12 | [5 empty] | At Therubali end: Zone-2, B-N, 27.99KM ,Ib=3.6 kA
|  | 29.03.20 | 15:57 | 29.03.20 | 16:17 | 0.013889 | 0 | 20 | [5 empty] | At Kesinga end: Tripped
|  | 20.03.20 | 12:40 | 20.03.20 | 12:47 | 0.0048611 | 0 | 7 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 21:05 | 19.03.20 | 21:09 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 21:21 | 19.03.20 | 21:38 | 0.011806 | 0 | 17 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 22:08 | 19.03.20 | 22:17 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 23:48 | 19.03.20 | 23:56 | 0.0055556 | 0 | 8 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 17:43 | 19.03.20 | 17:47 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 17:28 | 19.03.20 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | At Kesinga end: Tripped
|  | 19.03.20 | 16:29 | 19.03.20 | 17:00 | 0.021528 | 0 | 31 | [5 empty] | At Kesinga end: Tripped
|  | 08.03.20 | 16:49 | 08.03.20 | 17:06 | 0.011806 | 0 | 17 | [5 empty] | At Kesinga end: Tripped
|  | 08.03.20 | 17:44 | 08.03.20 | 17:47 | 0.0020833 | 0 | 3 | [5 empty] | At Kesinga end: Tripped
|  | 25.02.20 | 22:23 | 25.02.20 | 22:42 | 0.013194 | 0 | 19 | [5 empty] | At Therubali end: Zone-2,ABT, 31.84Km, Ia= 3.3kA, Ib= 3.1kA
|  | 13.02.20 | 16:37 | 13.02.20 | 16:41 | 0.0027778 | 0 | 4 | [5 empty] | At Therubali end: Tripped on O/ C
|  | 13.01.20 | 14:38 | 13.01.20 | 15:11 | 0.022917 | 0 | 33 | [5 empty] | At Therubali end: Tripped on O/C, D/P Zone-2,B-N, 28.23Km
|  | 02.01.20 | 11:53 | 02.01.20 | 12:12 | 0.013194 | 0 | 19 | [5 empty] | At Therubali end: Tripped on O/C.
|  | 13.01.20 | 14:29 | 13.01.20 | 14:33 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end-Tripped
|  | 17.12.19 | 11:32 | 17.12.19 | 11:33 | 0.00069444 | 0 | 1 | [5 empty] | Kesinga end-Tripped
|  | 17.12.19 | 15:11 | 17.12.19 | 15:12 | 0.00069444 | 0 | 1 | [5 empty] | Kesinga end-Tripped
|  | 07.12.19 | 15:18 | 07.12.19 | 15:31 | 0.0090278 | 0 | 13 | [5 empty] | Kesinga end-Tripped
|  | 07.12.19 | 8:19 | 07.12.19 | 8:21 | 0.0013889 | 0 | 2 | [5 empty] | Kesinga end-Tripped on E/F
|  | 07.12.19 | 8:22 | 07.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | Kesinga end-Tripped on E/F
|  | 23.11.19 | 16:10 | 23.11.19 | 16:20 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped on O/C
|  | 21.07.19 | 21:33 | 21.07.19 | 21:40 | 0.0048611 | 0 | 7 | [5 empty] | At Lanjigarh-Tripped
|  | 09.07.19 | 16:31 | 09.07.19 | 16:55 | 0.016667 | 0 | 24 | [5 empty] | At Kesinga-Tripped on distance relay
|  | 19.06.19 | 23:33 | 20.06.19 | 9:23 | 0.40972 | 9 | 50 | [5 empty] | At Kesinga -Tripped on D/P ( JUMPER SNAPPED AT LOC-1 OF 132 KV KESINGA-BPT-JUNAGARH LILO LINE)
|  | 10.06.19 | 17:26 | 10.06.19 | 17:33 | 0.0048611 | 0 | 7 | [5 empty] | At Theruvali-Tripped on O/C
|  | 05.06.19 | 21:55 | 05.06.19 | 22:02 | 0.0048611 | 0 | 7 | [5 empty] | At Theruvali-Tripped on O/C
|  | 08.06.19 | 20:56 | 08.06.19 | 20:59 | 0.0020833 | 0 | 3 | [5 empty] | At Theruvali-Tripped on O/C
|  | 03.06.19 | 10:15 | 03.06.19 | 10:44 | 0.020139 | 0 | 29 | [5 empty] | At Theruvali-Tripped (Distance relay indication at Lanjigarh end)
|  | 02.06.19 | 20:40 | 02.06.19 | 20:54 | 0.0097222 | 0 | 14 | [5 empty] | At Theruvali-Tripped
|  | 20.06.19 | 18:20 | 20.06.19 | 18:54 | 0.023611 | 0 | 34
|  | 02.10.19 | 16:48 | 02.10.19 | 16:59 | 0.0076389 | 0 | 11 | [5 empty] | At Therubali end: A-N,Z-1, 18.3KM
|  | 30.09.19 | 17:05 | 30.09.19 | 17:20 | 0.010417 | 0 | 15 | [5 empty] | At Theruvali-Tripped
|  | 29.05.19 | 21:11 | 29.05.19 | 21:55 | 0.030556 | 0 | 44 | [5 empty] | 132 KV P/S FAIL DUE TO DISTURBANCE AT KESINGA END. INCOMING SUPPLY WAS AVAILED FROM BOLANGIR
|  | 27.05.19 | 19:26 | 27.05.19 | 19:31 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped
|  | 27.05.19 | 17:50 | 27.05.19 | 18:32 | 0.029167 | 0 | 40 | [5 empty] | Grid disturbance at Therubali S/s but circuit was not tripped at Therubali end.
|  | 29.04.19 | 2:34 | 29.04.19 | 2:39 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped on over load.
|  | 29.05.19 | 22:52 | 29.05.19 | 23:08 | 0.011111 | 0 | 16 | [5 empty] | Tripped at Kesinga.
|  | 27.05.19 | 18:13 | 27.05.19 | 18:30 | 0.011806 | 0 | 17 | [5 empty] | 132 KV P/S FAIL; TRIPPED FROM THERUVALLI END SUPPLY AVAILED FROM BOLANGIR
|  | 27.05.19 | 19:26 | 27.05.19 | 19:31 | 0.0034722 | 0 | 5 | [5 empty] | 132 KV P/S FAIL; INCOMING SUPPLY CHANGED OVER TO THERUVALLI
|  | 20.05.19 | 6:31 | 20.05.19 | 6:47 | 0.011111 | 0 | 16 | [5 empty] | 132 KV P/S FAIL
|  | 11.05.19 | 4:56 | 11.05.19 | 5:03 | 0.0048611 | 0 | 7 | [5 empty] | 132 KV P/S FAIL
|  | 03.05.19 | 20:49 | 03.05.19 | 21:00 | 0.0076389 | 0 | 11 | [5 empty] | 132 KV P/S FAIL
|  | 30.04.19 | 5:14 | 30.04.19 | 5:24 | 0.0069444 | 0 | 10 | [5 empty] | 132 KV P/S FAIL
|  | 30.04.19 | 15:42 | 30.04.19 | 15:48 | 0.0041667 | 0 | 6 | [5 empty] | 132 KV P/S FAIL
|  | 25.04.19 | 6:50 | 25.04.19 | 6:55 | 0.0034722 | 0 | 5 | [5 empty] | 132 KV P/S FAIL
|  | 29.04.19 | 11:10 | 29.04.19 | 11:20 | 0.0069444 | 0 | 10 | [5 empty] | 132 KV P/S FAIL
|  | 24.04.19 | 16:00 | 24.04.19 | 16:14 | 0.0097222 | 0 | 14 | [5 empty] | 132 KV P/S FAIL
|  | 24.04.19 | 21:39 | 24.04.19 | 21:45 | 0.0041667 | 0 | 6 | [5 empty] | 132 KV P/S FAIL
|  | 17.04.19 | 1:01 | 17.04.19 | 1:08 | 0.0048611 | 0 | 7 | [5 empty] | 132 KV P/S FAIL
|  | 06.04.19 | 7:02 | 06.04.19 | 10:25 | 0.14097 | 3 | 23 | [5 empty] | 132 KV P/S FAIL
|  | 04.04.19 | 13:13 | 04.04.19 | 13:22 | 0.00625 | 0 | 9 | [5 empty] | 132 KV P/S FAIL
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
301 | 132kV Kesinga-Khariar |  |  |  |  | 1899-12-31 14:04 | 45 | 21 | [7 empty] | 58.5 | 8760 | 99.48% | 2652.975 | 512460
|  | 24.03.20 | 19:00 | 24.03.20 | 19:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 25.03.20 | 16:17 | 25.03.20 | 16:31 | 0.0097222 | 0 | 14 | [5 empty] | At Saintala end: Tripped on O/C
|  | 22.03.20 | 7:38 | 22.03.20 | 7:51 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:04 | 19.03.20 | 21:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:23 | 19.03.20 | 21:39 | 0.011111 | 0 | 16 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 22:08 | 19.03.20 | 22:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 23:48 | 19.03.20 | 23:56 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:45 | 19.03.20 | 17:48 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:28 | 19.03.20 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 6:48 | 19.03.20 | 6:55 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 16.03.20 | 19:12 | 16.03.20 | 19:25 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 15.03.20 | 17:07 | 15.03.20 | 17:12 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 7:20 | 14.03.20 | 7:30 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 8:17 | 14.03.20 | 8:22 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 9:04 | 14.03.20 | 9:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.03.20 | 18:00 | 13.03.20 | 18:07 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 8:00 | 12.03.20 | 8:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 9:10 | 12.03.20 | 9:17 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 12:15 | 12.03.20 | 12:26 | 0.0076389 | 0 | 11 | [5 empty] | At Saintala end: Tripped on O/C
|  | 11.03.20 | 7:40 | 11.03.20 | 7:47 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:25 | 03.03.20 | 15:26 | 0.00069444 | 0 | 1 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:32 | 03.03.20 | 15:34 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:44 | 03.03.20 | 15:51 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 16:13 | 03.03.20 | 16:26 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 17:31 | 03.03.20 | 17:33 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 7:53 | 28.02.20 | 7:59 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 10:54 | 28.02.20 | 10:59 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 23.02.20 | 8:52 | 23.02.20 | 8:58 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped
|  | 19.02.20 | 15:49 | 19.02.20 | 15:52 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 16:44 | 19.02.20 | 16:57 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 18:06 | 19.02.20 | 18:13 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:08 | 20.02.20 | 7:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:29 | 20.02.20 | 7:36 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 18:36 | 20.02.20 | 18:39 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 21.02.20 | 8:21 | 21.02.20 | 8:27 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 4:59 | 19.02.20 | 5:02 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:35 | 12.02.20 | 17:40 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir New end: Tripped on O/C
|  | 12.02.20 | 16:12 | 12.02.20 | 17:18 | 0.045833 | 1 | 6 | [5 empty] | At Bolangir end: Tripped
|  | 20.01.20 | 5:54 | 20.01.20 | 5:56 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 11.01.20 | 5:27 | 11.01.20 | 5:31 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala on E/F
|  | 07.12.19 | 8:22 | 07.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | Kesinga end-Tripped on E/F
|  | 17.12.19 | 8:22 | 17.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end-Tripped on E/F
|  | 06.12.19 | 18:28 | 06.12.19 | 18:34 | 0.0041667 | 0 | 6 | [5 empty] | At Kesinga end-Tripped onover loadig and O/C
|  | 30.11.19 | 10:12 | 30.11.19 | 10:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped due to Bolangir-Solar Incomer Breaker Tripped.
|  | 23.11.19 | 16:37 | 23.11.19 | 16:50 | 0.0090278 | 0 | 13 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 23.11.19 | 16:11 | 23.11.19 | 16:20 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 20.11.19 | 11:02 | 20.11.19 | 11:11 | 0.00625 | 0 | 9 | [5 empty] | At Bolangir end :-Tripped (dropping conductor of wave trap b-ph at sadeipali)
|  | 15.11.19 | 2:51 | 15.11.19 | 3:06 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: Tripped on overloading
|  | 12.11.19 | 1:45 | 12.11.19 | 1:47 | 0.0013889 | 0 | 2 | [5 empty] | At Kesinga end :-Tripped on Over loading
|  | 07.11.19 | 3:22 | 07.11.19 | 3:24 | 0.0013889 | 0 | 2 | [5 empty] | At Kesinga end :-Tripped on E/F
|  | 02.11.19 | 9:10 | 02.11.19 | 9:14 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 01.11.19 | 6:37 | 01.11.19 | 6:47 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 28.10.19 | 4:21 | 28.10.19 | 4:23 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Saintala end
|  | 27.10.19 | 5:17 | 27.10.19 | 5:28 | 0.0076389 | 0 | 11 | [5 empty] | Tripped at Saintala end
|  | 26.10.19 | 10:49 | 26.10.19 | 10:52 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Saintala end
|  | 25.10.19 | 10:24 | 25.10.19 | 10:38 | 0.0097222 | 0 | 14 | [5 empty] | Tripped at Tushra end
|  | 25.10.19 | 4:44 | 25.10.19 | 5:40 | 0.038889 | 0 | 56 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 19:30 | 22.10.19 | 19:42 | 0.0083333 | 0 | 12 | [5 empty] | P/S failure from Bolangir New end
|  | 22.10.19 | 6:09 | 22.10.19 | 6:42 | 0.022917 | 0 | 33 | [5 empty] | Tripped at ACME end due to snapping of line conductor
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | At Bolangir New S/S -Tripped due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 13.10.19 | 3:11 | 13.10.19 | 3:17 | 0.0041667 | 0 | 6 | [5 empty] | Trippead at Saintala end
|  | 11.10.19 | 1:10 | 11.10.19 | 1:21 | 0.0076389 | 0 | 11 | [5 empty] | Trippead at Saintala end
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 11:07 | 01.10.19 | 11:12 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at ACME end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:43 | 0.15208 | 0 | 49 | [5 empty] | Tripped at Bolangir New end( Jumper snapped at GSS Sadeipali). Availed P/S at 07:53 Hrs from Kesinga end
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:36 | 0.018056 | 0 | 26 | [5 empty] | Tripped at New Bolangir end.
|  | 26.09.19 | 0:10 | 26.09.19 | 0:30 | 0.013889 | 0 | 20 | [5 empty] | P/S Failure from Bolangir New end
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 23.09.19 | 18:42 | 23.09.19 | 19:12 | 0.020833 | 0 | 30 | [5 empty] | Tripped on overload at New Bolangir end.
|  | 23.09.19 | 15:53 | 23.09.19 | 16:00 | 0.0048611 | 0 | 7 | [5 empty] | Tripped at New Bolangir end.
|  | 17.09.19 | 19:13 | 17.09.19 | 20:56 | 0.071528 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 27.09.19 | 4:03 | 27.09.19 | 4:11 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala-Tripped on E/F
|  | 27.09.19 | 7:56 | 27.09.19 | 8:01 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala-Tripped on Over load
|  | 27.09.19 | 21:41 | 27.09.19 | 21:50 | 0.00625 | 0 | 9 | [5 empty] | At Saintala-Tripped on Over load
|  | 19.09.19 | 12:47 | 19.09.19 | 12:57 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped and At Tusura end also DP operated.
|  | 10.09.19 | 19:45 | 10.09.19 | 21:27 | 0.070833 | 0 | 42 | [5 empty] | At Kesinga-Tripped on over load
|  | 05.09.19 | 17:23 | 05.09.19 | 17:34 | 0.0076389 | 0 | 11 | [5 empty] | At Kesinga-Tripped on over load
|  | 21.08.19 | 18:58 | 21.08.19 | 19:06 | 0.0055556 | 0 | 8 | [5 empty] | At Bolangir New-Tripped due to 132KV LA failure
|  | 21.08.19 | 18:32 | 21.08.19 | 18:46 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 13.08.19 | 6:28 | 13.08.19 | 6:32 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala end.
|  | 13.08.19 | 5:53 | 13.08.19 | 6:09 | 0.011111 | 0 | 16 | [5 empty] | P/S failure from New Bolangir end
|  | 21.08.19 | 18:32 | 21.08.19 | 18:42 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:30 | 0.015972 | 0 | 23 | [5 empty] | P/S failure from Bolangir New due to over loading
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 11.08.19 | 5:09 | 11.08.19 | 5:27 | 0.0125 | 0 | 18 | [5 empty] | Tripped on E/F at Bolangir end
|  | 22.07.19 | 3:28 | 22.07.19 | 3:55 | 0.01875 | 0 | 27 | [5 empty] | Tripped at Saintala end
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 05.07.19 | 15:06 | 05.07.19 | 15:56 | 0.034722 | 0 | 50 | [5 empty] | At Kesinga-Tripped on D/P relay
|  | 20.06.19 | 9:51 | 20.06.19 | 10:02 | 0.0076389 | 0 | 11 | [5 empty] | 132KV Tushra-Saintal line didn’t stand. Power supply resumed from kesinga
|  | 20.06.19 | 14:55 | 20.06.19 | 15:04 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.06.19 | 16:00 | 20.06.19 | 16:12 | 0.0083333 | 0 | 12 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 22.06.19 | 14:13 | 22.06.19 | 14:16 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 25.06.19 | 21:43 | 25.06.19 | 21:47 | 0.0027778 | 0 | 4 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 20:55 | 26.06.19 | 21:00 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:18 | 26.06.19 | 22:23 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:45 | 26.06.19 | 22:54 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 18.06.19 | 1:17 | 18.06.19 | 1:23 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 13.06.19 | 16:55 | 13.06.19 | 16:58 | 0.0020833 | 0 | 3 | [5 empty] | 132KV Saintala I/C pullout
|  | 11.06.19 | 15:29 | 11.06.19 | 15:36 | 0.0048611 | 0 | 7 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.06.19 | 15:55 | 09.06.19 | 16:23 | 0.019444 | 0 | 28 | [5 empty] | 132KV Y-phase CT brust at GSS Saintala
|  | 05.06.19 | 0.92708 | 05.06.19 | 22:18 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.06.19 | 18:00 | 05.06.19 | 18:06 | 0.0041667 | 0 | 6 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 03.06.19 | 6:58 | 03.06.19 | 7:08 | 0.0069444 | 0 | 10 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 02.06.19 | 23:03 | 02.06.19 | 23:26 | 0.015972 | 0 | 23 | [5 empty] | Earth fault located at bolangir
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder). Tripped from Saintala end.
|  | 29.04.19 | 2:34 | 29.04.19 | 2:39 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped on over load.
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 28.05.19 | 16:58 | 28.05.19 | 17:07 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Tusura; LBB Trip Supervision
|  | 17.05.19 | 16:06 | 17.05.19 | 16:12 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from ACME;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 29.05.19 | 21:10 | 29.05.19 | 23:12 | 0.084722 | 2 | 2 | [5 empty] | Tripped from Saintala;CT Brust on 132KV Khariar O/G Feeder at GSS Kesinga
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 21.05.19 | 0:23 | 21.05.19 | 0:31 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 17.05.19 | 22:20 | 17.05.19 | 22:25 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.05.19 | 0:03 | 20.05.19 | 0:09 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 12.05.19 | 16:55 | 12.05.19 | 17:04 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala; Y Phase, E/F on 132 KV Kesinga O/G Feeder
|  | 13.05.19 | 14:39 | 13.05.19 | 14:46 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 6:28 | 11.05.19 | 6:35 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 8:03 | 11.05.19 | 8:08 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.05.19 | 15:53 | 09.05.19 | 15:57 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 4:54 | 11.05.19 | 5:03 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 23:45 | 04.05.19 | 23:48 | 0.0020833 | 0 | 3 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.05.19 | 5:52 | 05.05.19 | 5:59 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 16:25 | 04.05.19 | 16:33 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 22:43 | 01.05.19 | 22:48 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 16:28 | 01.05.19 | 16:30 | 0.0013889 | 0 | 2 | [5 empty] | Due to ckt overloading ; Tripped from New Bolangir
|  | 20.04.19 | 20:12 | 20.04.19 | 20:16 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, Tushra 132KV I/C Pullout; Tripped from Tusura
|  | 30.04.19 | 3:43 | 30.04.19 | 7:00 | 0.13681 | 3 | 17 | [5 empty] | Y-Phase Jumper snapped on 132Kesinga-Khariar O/G Feeder at GSS Kesinga, Tripped from Saintala end.
|  | 30.04.19 | 22:32 | 30.04.19 | 22:38 | 0.0041667 | 0 | 6 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 28.04.19 | 16:27 | 28.04.19 | 17:48 | 0.05625 | 1 | 21 | [5 empty] | B-Phase Jumper snapped at Gantry point of 132 Saintala O/G Feeder, Tripped from Tusura end.
|  | 27.04.19 | 22:27 | 27.04.19 | 22:42 | 0.010417 | 0 | 15 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 24.04.19 | 21:22 | 24.04.19 | 21:26 | 0.0027778 | 0 | 4 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 23.04.19 | 22:20 | 23.04.19 | 22:27 | 0.0048611 | 0 | 7 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 21.04.19 | 8:24 | 21.04.19 | 8:40 | 0.011111 | 0 | 16 | [5 empty] | 132KV Saintala O/G Feeder Tripped on E/F, Tripped from Tusura end.
|  | 19.04.19 | 20:08 | 19.04.19 | 20:16 | 0.0055556 | 0 | 8 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 17.04.19 | 5:27 | 17.04.19 | 5:40 | 0.0090278 | 0 | 13 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 29.04.19 | 17:28 | 29.04.19 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 29.04.19 | 16:45 | 29.04.19 | 16:48 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 12.04.19 | 21:37 | 12.04.19 | 21:50 | 0.0090278 | 0 | 13 | [5 empty] | Source Failure
|  | 08.04.19 | 6:52 | 08.04.19 | 6:54 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 08.04.19 | 22:44 | 08.04.19 | 22:46 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:00 | 09.04.19 | 5:07 | 0.0048611 | 0 | 7 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:45 | 09.04.19 | 5:48 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 07.04.19 | 21:51 | 07.04.19 | 21:54 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 05.04.19 | 22:17 | 05.04.19 | 22:22 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 03.04.19 | 20:38 | 03.04.19 | 20:43 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 01.04.19 | 21:57 | 01.04.19 | 22:00 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
302 | 132kV Kesinga-Junagarh Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 53 | 2868 | 100% | 0 | 152004
303 | 132kV Kesinga-Kesinga RTSS |  |  |  |  | 0.067361 | 13 | 49 | [7 empty] | 4.952 | 8760 | 99.84% | 68.4201 | 43379.52
|  | 04.03.20 | 16:01 | 04.03.20 | 16:13 | 00:12 | 0 | 12 | [5 empty] | At Therubali end: Zone-2, B-N, 27.99KM ,Ib=3.6 kA
|  | 25.02.20 | 22:23 | 25.02.20 | 22:42 | 0.013194 | 0 | 19 | [5 empty] | At Therubali end: Zone-2,ABT, 31.84Km, Ia= 3.3kA, Ib= 3.1kA
|  | 13.02.20 | 16:37 | 13.02.20 | 16:41 | 0.0027778 | 0 | 4 | [5 empty] | At Therubali end: Tripped on O/ C
|  | 13.01.20 | 14:38 | 13.01.20 | 15:11 | 0.022917 | 0 | 33 | [5 empty] | At Therubali end: Tripped on O/C, D/P Zone-2,B-N, 28.23Km
|  | 02.01.20 | 11:52 | 02.01.20 | 12:12 | 0.013889 | 0 | 20 | [5 empty] | At Therubali end: Tripped on O/C.
|  | 23.11.19 | 16:10 | 23.11.19 | 16:20 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped on O/C
|  | 02.10.19 | 16:48 | 02.10.19 | 16:59 | 0.0076389 | 0 | 11 | [5 empty] | At Therubali end: A-N,Z-1, 18.3KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
304 | 132kV Kesinga-Kesinga Solar |  |  |  |  | 0.0069444 | 0 | 10 | [7 empty] | 11.48 | 8760 | 100% | 1.9133 | 100564.8
|  | 23.11.19 | 16:10 | 23.11.19 | 16:20 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped on O/C
305 | 132kV Kesinga-Powmex |  |  |  |  | 0.60347 | 16 | 54 | [7 empty] | 14.532 | 8760 | 99.81% | 245.5908 | 127300.32
|  | 04.03.20 | 16:01 | 04.03.20 | 16:13 | 00:12 | 0 | 12 | [5 empty] | At Therubali end: Zone-2, B-N, 27.99KM ,Ib=3.6 kA
|  | 25.02.20 | 22:23 | 25.02.20 | 22:42 | 0.013194 | 0 | 19 | [5 empty] | At Therubali end: Zone-2,ABT, 31.84Km, Ia= 3.3kA, Ib= 3.1kA
|  | 13.02.20 | 16:37 | 13.02.20 | 16:41 | 0.0027778 | 0 | 4 | [5 empty] | At Therubali end: Tripped on O/ C
|  | 13.01.20 | 14:38 | 13.01.20 | 15:11 | 0.022917 | 0 | 33 | [5 empty] | At Therubali end: Tripped on O/C, D/P Zone-2,B-N, 28.23Km
|  | 02.01.20 | 11:52 | 02.01.20 | 12:12 | 0.013889 | 0 | 20 | [5 empty] | At Therubali end: Tripped on O/C.
|  | 23.11.19 | 16:10 | 23.11.19 | 16:20 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped on O/C
|  | 19.06.19 | 23:33 | 20.06.19 | 9:23 | 0.40972 | 0 | 5 | [5 empty] | At Kesinga -Tripped on D/P ( JUMPER SNAPPED AT LOC-1 OF 132 KV KESINGA-BPT-JUNAGARH LILO LINE)
|  | 10.06.19 | 17:26 | 10.06.19 | 17:33 | 0.0048611 | 0 | 7 | [5 empty] | At Theruvali-Tripped on O/C
|  | 05.06.19 | 21:55 | 05.06.19 | 22:02 | 0.0048611 | 0 | 7 | [5 empty] | At Theruvali-Tripped on O/C
|  | 08.06.19 | 20:56 | 08.06.19 | 20:59 | 0.0020833 | 0 | 3 | [5 empty] | At Theruvali-Tripped on O/C
|  | 03.06.19 | 10:15 | 03.06.19 | 10:44 | 0.020139 | 0 | 29 | [5 empty] | At Theruvali-Tripped (Distance relay indication at Lanjigarh end)
|  | 02.06.19 | 20:40 | 02.06.19 | 20:54 | 0.0097222 | 0 | 14 | [5 empty] | At Theruvali-Tripped
|  | 20.06.19 | 18:20 | 20.06.19 | 18:54 | 0.023611 | 0 | 34
|  | 02.10.19 | 16:48 | 02.10.19 | 16:59 | 0.0076389 | 0 | 11 | [5 empty] | At Therubali end: A-N,Z-1, 18.3KM
|  | 30.09.19 | 17:05 | 30.09.19 | 17:20 | 0.010417 | 0 | 15 | [5 empty] | At Theruvali-Tripped
|  | 20.01.20 | 5:54 | 20.01.20 | 5:56 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 11.01.20 | 5:27 | 11.01.20 | 5:31 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala on E/F
|  | 27.05.19 | 19:26 | 27.05.19 | 19:31 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped
|  | 27.05.19 | 17:50 | 27.05.19 | 18:32 | 0.029167 | 0 | 40 | [5 empty] | Grid disturbance at Therubali S/s but circuit was not tripped at Therubali end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
306 | 132kV Kesinga-Saintala |  |  |  |  | 1899-12-31 12:17 | 44 | 32 | [7 empty] | 33.2 | 8760 | 99.49% | 1478.5067 | 290832
|  | 24.03.20 | 19:00 | 24.03.20 | 19:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 25.03.20 | 16:17 | 25.03.20 | 16:31 | 0.0097222 | 0 | 14 | [5 empty] | At Saintala end: Tripped on O/C
|  | 22.03.20 | 7:38 | 22.03.20 | 7:51 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:04 | 19.03.20 | 21:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:23 | 19.03.20 | 21:39 | 0.011111 | 0 | 16 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 22:08 | 19.03.20 | 22:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 23:48 | 19.03.20 | 23:56 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:45 | 19.03.20 | 17:48 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:28 | 19.03.20 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 6:48 | 19.03.20 | 6:55 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 16.03.20 | 19:12 | 16.03.20 | 19:25 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 15.03.20 | 17:07 | 15.03.20 | 17:12 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 7:20 | 14.03.20 | 7:30 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 8:17 | 14.03.20 | 8:22 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 9:04 | 14.03.20 | 9:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.03.20 | 18:00 | 13.03.20 | 18:07 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 8:00 | 12.03.20 | 8:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 9:10 | 12.03.20 | 9:17 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 12:15 | 12.03.20 | 12:26 | 0.0076389 | 0 | 11 | [5 empty] | At Saintala end: Tripped on O/C
|  | 11.03.20 | 7:40 | 11.03.20 | 7:47 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:25 | 03.03.20 | 15:26 | 0.00069444 | 0 | 1 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:32 | 03.03.20 | 15:34 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:44 | 03.03.20 | 15:51 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 16:13 | 03.03.20 | 16:26 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 17:31 | 03.03.20 | 17:33 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 7:53 | 28.02.20 | 7:59 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 10:54 | 28.02.20 | 10:59 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 23.02.20 | 8:52 | 23.02.20 | 8:58 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped
|  | 19.02.20 | 15:49 | 19.02.20 | 15:52 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 16:44 | 19.02.20 | 16:57 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 18:06 | 19.02.20 | 18:13 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:08 | 20.02.20 | 7:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:29 | 20.02.20 | 7:36 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 18:36 | 20.02.20 | 18:39 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 21.02.20 | 8:21 | 21.02.20 | 8:27 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 4:59 | 19.02.20 | 5:02 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:35 | 12.02.20 | 17:40 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir New end: Tripped on O/C
|  | 12.02.20 | 16:12 | 12.02.20 | 17:18 | 0.045833 | 1 | 6 | [5 empty] | At Bolangir end: Tripped
|  | 07.12.19 | 8:22 | 07.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | Kesinga end-Tripped on E/F
|  | 17.12.19 | 8:22 | 17.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end-Tripped on E/F
|  | 06.12.19 | 18:28 | 06.12.19 | 18:34 | 0.0041667 | 0 | 6 | [5 empty] | At Kesinga end-Tripped onover loadig and O/C
|  | 23.11.19 | 16:37 | 23.11.19 | 16:50 | 0.0090278 | 0 | 13 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 23.11.19 | 16:11 | 23.11.19 | 16:20 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 20.11.19 | 11:02 | 20.11.19 | 11:16 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end :-Tripped (dropping conductor of wave trap b-ph at sadeipali)
|  | 30.11.19 | 10:12 | 30.11.19 | 10:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped due to Bolangir-Solar Incomer Breaker Tripped.
|  | 01.11.19 | 6:37 | 01.11.19 | 6:47 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 28.10.19 | 4:21 | 28.10.19 | 4:23 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Saintala end
|  | 27.10.19 | 5:17 | 27.10.19 | 5:28 | 0.0076389 | 0 | 11 | [5 empty] | Tripped at Saintala end
|  | 26.10.19 | 10:49 | 26.10.19 | 10:52 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Saintala end
|  | 25.10.19 | 10:24 | 25.10.19 | 10:38 | 0.0097222 | 0 | 14 | [5 empty] | Tripped at Tushra end
|  | 25.10.19 | 4:44 | 25.10.19 | 5:40 | 0.038889 | 0 | 56 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 19:30 | 22.10.19 | 19:42 | 0.0083333 | 0 | 12 | [5 empty] | P/S failure from Bolangir New end
|  | 22.10.19 | 6:09 | 22.10.19 | 6:42 | 0.022917 | 0 | 33 | [5 empty] | Tripped at ACME end due to snapping of line conductor
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | At Bolangir New S/S -Tripped due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 13.10.19 | 3:11 | 13.10.19 | 3:17 | 0.0041667 | 0 | 6 | [5 empty] | Trippead at Saintala end
|  | 11.10.19 | 1:10 | 11.10.19 | 1:21 | 0.0076389 | 0 | 11 | [5 empty] | Trippead at Saintala end
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 11:07 | 01.10.19 | 11:12 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at ACME end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:43 | 0.15208 | 0 | 49 | [5 empty] | Tripped at Bolangir New end( Jumper snapped at GSS Sadeipali). Availed P/S at 07:53 Hrs from Kesinga end
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:36 | 0.018056 | 0 | 26 | [5 empty] | Tripped at New Bolangir end.
|  | 26.09.19 | 0:10 | 26.09.19 | 0:30 | 0.013889 | 0 | 20 | [5 empty] | P/S Failure from Bolangir New end
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 23.09.19 | 18:42 | 23.09.19 | 19:12 | 0.020833 | 0 | 30 | [5 empty] | Tripped on overload at New Bolangir end.
|  | 23.09.19 | 15:53 | 23.09.19 | 16:00 | 0.0048611 | 0 | 7 | [5 empty] | Tripped at New Bolangir end.
|  | 17.09.19 | 19:13 | 17.09.19 | 20:56 | 0.071528 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 27.09.19 | 4:03 | 27.09.19 | 4:11 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala-Tripped on E/F
|  | 27.09.19 | 7:56 | 27.09.19 | 8:01 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala-Tripped on Over load
|  | 27.09.19 | 21:41 | 27.09.19 | 21:50 | 0.00625 | 0 | 9 | [5 empty] | At Saintala-Tripped on Over load
|  | 19.09.19 | 12:47 | 19.09.19 | 12:57 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped and At Tusura end also DP operated.
|  | 10.09.19 | 19:45 | 10.09.19 | 20:29 | 0.030556 | 0 | 42 | [5 empty] | At Bolangir New end-Tripped on directional O/C and E/F.
|  | 05.09.19 | 17:23 | 05.09.19 | 17:34 | 0.0076389 | 0 | 11 | [5 empty] | At Kesinga-Tripped on over load
|  | 21.08.19 | 18:58 | 21.08.19 | 19:06 | 0.0055556 | 0 | 8 | [5 empty] | At Bolangir New-Tripped due to 132KV LA failure
|  | 21.08.19 | 18:32 | 21.08.19 | 18:46 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 13.08.19 | 6:28 | 13.08.19 | 6:32 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala end.
|  | 13.08.19 | 5:53 | 13.08.19 | 6:09 | 0.011111 | 0 | 16 | [5 empty] | P/S failure from New Bolangir end
|  | 21.08.19 | 18:32 | 21.08.19 | 18:42 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:30 | 0.015972 | 0 | 23 | [5 empty] | P/S failure from Bolangir New due to over loading
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 11.08.19 | 5:09 | 11.08.19 | 5:27 | 0.0125 | 0 | 18 | [5 empty] | Tripped on E/F at Bolangir end
|  | 22.07.19 | 3:28 | 22.07.19 | 3:55 | 0.01875 | 0 | 27 | [5 empty] | Tripped at Saintala end
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source at Bolangir.
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 05.07.19 | 15:06 | 05.07.19 | 15:56 | 0.034722 | 0 | 50 | [5 empty] | At Kesinga-Tripped on D/P relay
|  | 20.06.19 | 9:51 | 20.06.19 | 10:02 | 0.0076389 | 0 | 11 | [5 empty] | 132KV Tushra-Saintal line didn’t stand. Power supply resumed from kesinga
|  | 20.06.19 | 14:55 | 20.06.19 | 15:04 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.06.19 | 16:00 | 20.06.19 | 16:12 | 0.0083333 | 0 | 12 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 22.06.19 | 14:13 | 22.06.19 | 14:16 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 25.06.19 | 21:43 | 25.06.19 | 21:47 | 0.0027778 | 0 | 4 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 20:55 | 26.06.19 | 21:00 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:18 | 26.06.19 | 22:23 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:45 | 26.06.19 | 22:54 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 18.06.19 | 1:17 | 18.06.19 | 1:23 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 13.06.19 | 16:55 | 13.06.19 | 16:58 | 0.0020833 | 0 | 3 | [5 empty] | 132KV Saintala I/C pullout
|  | 11.06.19 | 15:29 | 11.06.19 | 15:36 | 0.0048611 | 0 | 7 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.06.19 | 15:55 | 09.06.19 | 16:23 | 0.019444 | 0 | 28 | [5 empty] | 132KV Y-phase CT brust at GSS Saintala
|  | 05.06.19 | 0.92708 | 05.06.19 | 22:18 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.06.19 | 18:00 | 05.06.19 | 18:06 | 0.0041667 | 0 | 6 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 03.06.19 | 6:58 | 03.06.19 | 7:08 | 0.0069444 | 0 | 10 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 02.06.19 | 23:03 | 02.06.19 | 23:26 | 0.015972 | 0 | 23 | [5 empty] | Earth fault located at bolangir
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder). Tripped from Saintala end.
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 28.05.19 | 16:58 | 28.05.19 | 17:07 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Tusura; LBB Trip Supervision
|  | 17.05.19 | 16:06 | 17.05.19 | 16:12 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from ACME;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 29.05.19 | 21:10 | 29.05.19 | 23:12 | 0.084722 | 2 | 2 | [5 empty] | Tripped from Saintala;CT Brust on 132KV Khariar O/G Feeder at GSS Kesinga
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 21.05.19 | 0:23 | 21.05.19 | 0:31 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 17.05.19 | 22:20 | 17.05.19 | 22:25 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.05.19 | 0:03 | 20.05.19 | 0:09 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 12.05.19 | 16:55 | 12.05.19 | 17:04 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala; Y Phase, E/F on 132 KV Kesinga O/G Feeder
|  | 13.05.19 | 14:39 | 13.05.19 | 14:46 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 6:28 | 11.05.19 | 6:35 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 8:03 | 11.05.19 | 8:08 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.05.19 | 15:53 | 09.05.19 | 15:57 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 4:54 | 11.05.19 | 5:03 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 23:45 | 04.05.19 | 23:48 | 0.0020833 | 0 | 3 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.05.19 | 5:52 | 05.05.19 | 5:59 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 16:25 | 04.05.19 | 16:33 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 22:43 | 01.05.19 | 22:48 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 16:28 | 01.05.19 | 16:30 | 0.0013889 | 0 | 2 | [5 empty] | Due to ckt overloading ; Tripped from New Bolangir
|  | 20.04.19 | 20:12 | 20.04.19 | 20:16 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, Tushra 132KV I/C Pullout; Tripped from Tusura
|  | 30.04.19 | 3:43 | 30.04.19 | 7:00 | 0.13681 | 3 | 17 | [5 empty] | Y-Phase Jumper snapped on 132Kesinga-Khariar O/G Feeder at GSS Kesinga, Tripped from Saintala end.
|  | 30.04.19 | 22:32 | 30.04.19 | 22:38 | 0.0041667 | 0 | 6 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 28.04.19 | 16:27 | 28.04.19 | 17:48 | 0.05625 | 1 | 21 | [5 empty] | B-Phase Jumper snapped at Gantry point of 132 Saintala O/G Feeder, Tripped from Tusura end.
|  | 27.04.19 | 22:27 | 27.04.19 | 22:42 | 0.010417 | 0 | 15 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 24.04.19 | 21:22 | 24.04.19 | 21:26 | 0.0027778 | 0 | 4 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 23.04.19 | 22:20 | 23.04.19 | 22:27 | 0.0048611 | 0 | 7 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 21.04.19 | 8:24 | 21.04.19 | 8:40 | 0.011111 | 0 | 16 | [5 empty] | 132KV Saintala O/G Feeder Tripped on E/F, Tripped from Tusura end.
|  | 19.04.19 | 20:08 | 19.04.19 | 20:16 | 0.0055556 | 0 | 8 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 17.04.19 | 5:27 | 17.04.19 | 5:40 | 0.0090278 | 0 | 13 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 29.04.19 | 17:28 | 29.04.19 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 29.04.19 | 16:45 | 29.04.19 | 16:48 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 12.04.19 | 21:37 | 12.04.19 | 21:50 | 0.0090278 | 0 | 13 | [5 empty] | Source Failure
|  | 08.04.19 | 6:52 | 08.04.19 | 6:54 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 08.04.19 | 22:44 | 08.04.19 | 22:46 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:00 | 09.04.19 | 5:07 | 0.0048611 | 0 | 7 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:45 | 09.04.19 | 5:48 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 07.04.19 | 21:51 | 07.04.19 | 21:54 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 05.04.19 | 22:17 | 05.04.19 | 22:22 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 03.04.19 | 20:38 | 03.04.19 | 20:43 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 01.04.19 | 21:57 | 01.04.19 | 22:00 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
307 | 132kV Kharagprasad-Kharagprasad (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.17 | 8760 | 100% | 0 | 10249.2
308 | 132kV Kharagprasad-MGM Ckt |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.14 | 8760 | 100% | 0 | 62546.4
309 | 132kV Kharagprasad-Nabhabharat Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.577 | 8760 | 100% | 0 | 5054.52
310 | 132kV Kharagprasad-Nabhabharat Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.577 | 8760 | 100% | 0 | 5054.52
311 | 132kV Kharagprasad-Samal Metallic |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.03 | 8760 | 100% | 0 | 9022.8
312 | 132 kV Khariar - Kantabanji |  |  |  |  | 1899-12-31 15:07 | 46 | 24 | [7 empty] | 33 | 8760 | 99.47% | 1531.2 | 289080
|  | 24.03.20 | 19:00 | 24.03.20 | 19:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 25.03.20 | 16:17 | 25.03.20 | 16:31 | 0.0097222 | 0 | 14 | [5 empty] | At Saintala end: Tripped on O/C
|  | 22.03.20 | 7:38 | 22.03.20 | 7:51 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:04 | 19.03.20 | 21:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:23 | 19.03.20 | 21:39 | 0.011111 | 0 | 16 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 22:08 | 19.03.20 | 22:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 23:48 | 19.03.20 | 23:56 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:45 | 19.03.20 | 17:48 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:28 | 19.03.20 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 6:48 | 19.03.20 | 6:55 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 16.03.20 | 19:12 | 16.03.20 | 19:25 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 15.03.20 | 17:07 | 15.03.20 | 17:12 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 7:20 | 14.03.20 | 7:30 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 8:17 | 14.03.20 | 8:22 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 9:04 | 14.03.20 | 9:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.03.20 | 18:00 | 13.03.20 | 18:07 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 8:00 | 12.03.20 | 8:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 9:10 | 12.03.20 | 9:17 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 12:15 | 12.03.20 | 12:26 | 0.0076389 | 0 | 11 | [5 empty] | At Saintala end: Tripped on O/C
|  | 11.03.20 | 7:40 | 11.03.20 | 7:47 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:25 | 03.03.20 | 15:26 | 0.00069444 | 0 | 1 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:32 | 03.03.20 | 15:34 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:44 | 03.03.20 | 15:51 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 16:13 | 03.03.20 | 16:26 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 17:31 | 03.03.20 | 17:33 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 7:53 | 28.02.20 | 7:59 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 10:54 | 28.02.20 | 10:59 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 23.02.20 | 8:52 | 23.02.20 | 8:58 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped
|  | 19.02.20 | 15:49 | 19.02.20 | 15:52 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 16:44 | 19.02.20 | 16:57 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 18:06 | 19.02.20 | 18:13 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:08 | 20.02.20 | 7:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:29 | 20.02.20 | 7:36 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 18:36 | 20.02.20 | 18:39 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 21.02.20 | 8:21 | 21.02.20 | 8:27 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 4:59 | 19.02.20 | 5:02 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:35 | 12.02.20 | 17:40 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir New end: Tripped on O/C
|  | 12.02.20 | 16:12 | 12.02.20 | 17:18 | 0.045833 | 1 | 6 | [5 empty] | At Bolangir end: Tripped
|  | 20.01.20 | 5:54 | 20.01.20 | 5:56 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 11.01.20 | 5:27 | 11.01.20 | 5:31 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala on E/F
|  | 07.12.19 | 8:22 | 07.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | Kesinga end-Tripped on E/F
|  | 17.12.19 | 8:22 | 17.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end-Tripped on E/F
|  | 06.12.19 | 18:28 | 06.12.19 | 18:34 | 0.0041667 | 0 | 6 | [5 empty] | At Kesinga end-Tripped onover loadig and O/C
|  | 30.11.19 | 10:12 | 30.11.19 | 10:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped due to Bolangir-Solar Incomer Breaker Tripped.
|  | 23.11.19 | 16:37 | 23.11.19 | 16:50 | 0.0090278 | 0 | 13 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 23.11.19 | 16:11 | 23.11.19 | 16:20 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 20.11.19 | 11:02 | 20.11.19 | 11:11 | 0.00625 | 0 | 9 | [5 empty] | At Bolangir end :-Tripped (dropping conductor of wave trap b-ph at sadeipali)
|  | 15.11.19 | 2:51 | 15.11.19 | 3:06 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: Tripped on overloading
|  | 12.11.19 | 1:45 | 12.11.19 | 1:47 | 0.0013889 | 0 | 2 | [5 empty] | At Kesinga end :-Tripped on Over loading
|  | 07.11.19 | 3:22 | 07.11.19 | 3:24 | 0.0013889 | 0 | 2 | [5 empty] | At Kesinga end :-Tripped on E/F
|  | 02.11.19 | 9:10 | 02.11.19 | 9:14 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 01.11.19 | 6:37 | 01.11.19 | 6:47 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 28.10.19 | 4:21 | 28.10.19 | 4:23 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Saintala end
|  | 27.10.19 | 5:17 | 27.10.19 | 5:28 | 0.0076389 | 0 | 11 | [5 empty] | Tripped at Saintala end
|  | 26.10.19 | 10:49 | 26.10.19 | 10:52 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Saintala end
|  | 25.10.19 | 10:24 | 25.10.19 | 10:38 | 0.0097222 | 0 | 14 | [5 empty] | Tripped at Tushra end
|  | 25.10.19 | 4:44 | 25.10.19 | 5:40 | 0.038889 | 0 | 56 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 19:30 | 22.10.19 | 19:42 | 0.0083333 | 0 | 12 | [5 empty] | P/S failure from Bolangir New end
|  | 22.10.19 | 6:09 | 22.10.19 | 6:42 | 0.022917 | 0 | 33 | [5 empty] | Tripped at ACME end due to snapping of line conductor
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | At Bolangir New S/S -Tripped due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 13.10.19 | 5:07 | 13.10.19 | 5:28 | 0.014583 | 0 | 21 | [5 empty] | Trippead at Khariar end
|  | 13.10.19 | 3:11 | 13.10.19 | 3:17 | 0.0041667 | 0 | 6 | [5 empty] | Trippead at Saintala end
|  | 11.10.19 | 1:10 | 11.10.19 | 1:21 | 0.0076389 | 0 | 11 | [5 empty] | Trippead at Saintala end
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 11:07 | 01.10.19 | 11:12 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at ACME end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:43 | 0.15208 | 0 | 49 | [5 empty] | Tripped at Bolangir New end( Jumper snapped at GSS Sadeipali). Availed P/S at 07:53 Hrs from Kesinga end
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:36 | 0.018056 | 0 | 26 | [5 empty] | Tripped at New Bolangir end.
|  | 26.09.19 | 0:10 | 26.09.19 | 0:30 | 0.013889 | 0 | 20 | [5 empty] | P/S Failure from Bolangir New end
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 23.09.19 | 18:42 | 23.09.19 | 19:12 | 0.020833 | 0 | 30 | [5 empty] | Tripped on overload at New Bolangir end.
|  | 23.09.19 | 15:53 | 23.09.19 | 16:00 | 0.0048611 | 0 | 7 | [5 empty] | Tripped at New Bolangir end.
|  | 17.09.19 | 19:13 | 17.09.19 | 20:56 | 0.071528 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 27.09.19 | 4:03 | 27.09.19 | 4:11 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala-Tripped on E/F
|  | 27.09.19 | 7:56 | 27.09.19 | 8:01 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala-Tripped on Over load
|  | 27.09.19 | 21:41 | 27.09.19 | 21:50 | 0.00625 | 0 | 9 | [5 empty] | At Saintala-Tripped on Over load
|  | 19.09.19 | 12:47 | 19.09.19 | 12:57 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped and At Tusura end also DP operated.
|  | 10.09.19 | 19:45 | 10.09.19 | 21:27 | 0.070833 | 0 | 42 | [5 empty] | At Kesinga-Tripped on over load
|  | 05.09.19 | 17:23 | 05.09.19 | 17:34 | 0.0076389 | 0 | 11 | [5 empty] | At Kesinga-Tripped on over load
|  | 14.09.19 | 11:29 | 14.09.19 | 11:38 | 0.029167 | 0 | 42 | [5 empty] | At Khariar-Tripped on E/F
|  | 21.08.19 | 18:58 | 21.08.19 | 19:06 | 0.0055556 | 0 | 8 | [5 empty] | At Bolangir New-Tripped due to 132KV LA failure
|  | 21.08.19 | 18:32 | 21.08.19 | 18:46 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 13.08.19 | 6:28 | 13.08.19 | 6:32 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala end.
|  | 13.08.19 | 5:53 | 13.08.19 | 6:09 | 0.011111 | 0 | 16 | [5 empty] | P/S failure from New Bolangir end
|  | 21.08.19 | 18:32 | 21.08.19 | 18:42 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:30 | 0.015972 | 0 | 23 | [5 empty] | P/S failure from Bolangir New due to over loading
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 11.08.19 | 5:09 | 11.08.19 | 5:27 | 0.0125 | 0 | 18 | [5 empty] | Tripped on E/F at Bolangir end
|  | 22.07.19 | 3:28 | 22.07.19 | 3:55 | 0.01875 | 0 | 27 | [5 empty] | Tripped at Saintala end
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 05.07.19 | 15:06 | 05.07.19 | 15:56 | 0.034722 | 0 | 50 | [5 empty] | At Kesinga-Tripped on D/P relay
|  | 20.06.19 | 9:51 | 20.06.19 | 10:02 | 0.0076389 | 0 | 11 | [5 empty] | 132KV Tushra-Saintal line didn’t stand. Power supply resumed from kesinga
|  | 20.06.19 | 14:55 | 20.06.19 | 15:04 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.06.19 | 16:00 | 20.06.19 | 16:12 | 0.0083333 | 0 | 12 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 22.06.19 | 14:13 | 22.06.19 | 14:16 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 25.06.19 | 21:43 | 25.06.19 | 21:47 | 0.0027778 | 0 | 4 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 20:55 | 26.06.19 | 21:00 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:18 | 26.06.19 | 22:23 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:45 | 26.06.19 | 22:54 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 18.06.19 | 1:17 | 18.06.19 | 1:23 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 13.06.19 | 16:55 | 13.06.19 | 16:58 | 0.0020833 | 0 | 3 | [5 empty] | 132KV Saintala I/C pullout
|  | 11.06.19 | 15:29 | 11.06.19 | 15:36 | 0.0048611 | 0 | 7 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.06.19 | 15:55 | 09.06.19 | 16:23 | 0.019444 | 0 | 28 | [5 empty] | 132KV Y-phase CT brust at GSS Saintala
|  | 05.06.19 | 0.92708 | 05.06.19 | 22:18 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.06.19 | 18:00 | 05.06.19 | 18:06 | 0.0041667 | 0 | 6 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 03.06.19 | 6:58 | 03.06.19 | 7:08 | 0.0069444 | 0 | 10 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 02.06.19 | 23:03 | 02.06.19 | 23:26 | 0.015972 | 0 | 23 | [5 empty] | Earth fault located at bolangir
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder). Tripped from Saintala end.
|  | 29.04.19 | 2:34 | 29.04.19 | 2:39 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped on over load.
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 28.05.19 | 16:58 | 28.05.19 | 17:07 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Tusura; LBB Trip Supervision
|  | 17.05.19 | 16:06 | 17.05.19 | 16:12 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from ACME;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 29.05.19 | 21:10 | 29.05.19 | 23:12 | 0.084722 | 2 | 2 | [5 empty] | Tripped from Saintala;CT Brust on 132KV Khariar O/G Feeder at GSS Kesinga
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 21.05.19 | 0:23 | 21.05.19 | 0:31 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 17.05.19 | 22:20 | 17.05.19 | 22:25 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.05.19 | 0:03 | 20.05.19 | 0:09 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 12.05.19 | 16:55 | 12.05.19 | 17:04 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala; Y Phase, E/F on 132 KV Kesinga O/G Feeder
|  | 13.05.19 | 14:39 | 13.05.19 | 14:46 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 6:28 | 11.05.19 | 6:35 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 8:03 | 11.05.19 | 8:08 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.05.19 | 15:53 | 09.05.19 | 15:57 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 4:54 | 11.05.19 | 5:03 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 23:45 | 04.05.19 | 23:48 | 0.0020833 | 0 | 3 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.05.19 | 5:52 | 05.05.19 | 5:59 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 16:25 | 04.05.19 | 16:33 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 22:43 | 01.05.19 | 22:48 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 16:28 | 01.05.19 | 16:30 | 0.0013889 | 0 | 2 | [5 empty] | Due to ckt overloading ; Tripped from New Bolangir
|  | 20.04.19 | 20:12 | 20.04.19 | 20:16 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, Tushra 132KV I/C Pullout; Tripped from Tusura
|  | 30.04.19 | 3:43 | 30.04.19 | 7:00 | 0.13681 | 3 | 17 | [5 empty] | Y-Phase Jumper snapped on 132Kesinga-Khariar O/G Feeder at GSS Kesinga, Tripped from Saintala end.
|  | 30.04.19 | 22:32 | 30.04.19 | 22:38 | 0.0041667 | 0 | 6 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 28.04.19 | 16:27 | 28.04.19 | 17:48 | 0.05625 | 1 | 21 | [5 empty] | B-Phase Jumper snapped at Gantry point of 132 Saintala O/G Feeder, Tripped from Tusura end.
|  | 27.04.19 | 22:27 | 27.04.19 | 22:42 | 0.010417 | 0 | 15 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 24.04.19 | 21:22 | 24.04.19 | 21:26 | 0.0027778 | 0 | 4 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 23.04.19 | 22:20 | 23.04.19 | 22:27 | 0.0048611 | 0 | 7 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 21.04.19 | 8:24 | 21.04.19 | 8:40 | 0.011111 | 0 | 16 | [5 empty] | 132KV Saintala O/G Feeder Tripped on E/F, Tripped from Tusura end.
|  | 19.04.19 | 20:08 | 19.04.19 | 20:16 | 0.0055556 | 0 | 8 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 17.04.19 | 5:27 | 17.04.19 | 5:40 | 0.0090278 | 0 | 13 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 29.04.19 | 17:28 | 29.04.19 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 29.04.19 | 16:45 | 29.04.19 | 16:48 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 12.04.19 | 21:37 | 12.04.19 | 21:50 | 0.0090278 | 0 | 13 | [5 empty] | Source Failure
|  | 08.04.19 | 6:52 | 08.04.19 | 6:54 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 08.04.19 | 22:44 | 08.04.19 | 22:46 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:00 | 09.04.19 | 5:07 | 0.0048611 | 0 | 7 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:45 | 09.04.19 | 5:48 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 07.04.19 | 21:51 | 07.04.19 | 21:54 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 05.04.19 | 22:17 | 05.04.19 | 22:22 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 03.04.19 | 20:38 | 03.04.19 | 20:43 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 01.04.19 | 21:57 | 01.04.19 | 22:00 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
313 | 132 kV Khariar - Nuapara |  |  |  |  | 1899-12-31 20:06 | 51 | 23 | [7 empty] | 77.232 | 8760 | 99.41% | 3968.4376 | 676552.32
|  | 24.03.20 | 19:00 | 24.03.20 | 19:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 25.03.20 | 16:17 | 25.03.20 | 16:31 | 0.0097222 | 0 | 14 | [5 empty] | At Saintala end: Tripped on O/C
|  | 22.03.20 | 7:38 | 22.03.20 | 7:51 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:04 | 19.03.20 | 21:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:23 | 19.03.20 | 21:39 | 0.011111 | 0 | 16 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 22:08 | 19.03.20 | 22:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 23:48 | 19.03.20 | 23:56 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:45 | 19.03.20 | 17:48 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:28 | 19.03.20 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 6:48 | 19.03.20 | 6:55 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 16.03.20 | 19:12 | 16.03.20 | 19:25 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 15.03.20 | 17:07 | 15.03.20 | 17:12 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 7:20 | 14.03.20 | 7:30 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 8:17 | 14.03.20 | 8:22 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 9:04 | 14.03.20 | 9:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.03.20 | 18:00 | 13.03.20 | 18:07 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 8:00 | 12.03.20 | 8:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 9:10 | 12.03.20 | 9:17 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 12:15 | 12.03.20 | 12:26 | 0.0076389 | 0 | 11 | [5 empty] | At Saintala end: Tripped on O/C
|  | 11.03.20 | 7:40 | 11.03.20 | 7:47 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:25 | 03.03.20 | 15:26 | 0.00069444 | 0 | 1 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:32 | 03.03.20 | 15:34 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:44 | 03.03.20 | 15:51 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 16:13 | 03.03.20 | 16:26 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 17:31 | 03.03.20 | 17:33 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 7:53 | 28.02.20 | 7:59 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 10:54 | 28.02.20 | 10:59 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 23.02.20 | 8:52 | 23.02.20 | 8:58 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped
|  | 19.02.20 | 15:49 | 19.02.20 | 15:52 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 16:44 | 19.02.20 | 16:57 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 18:06 | 19.02.20 | 18:13 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:08 | 20.02.20 | 7:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:29 | 20.02.20 | 7:36 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 18:36 | 20.02.20 | 18:39 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 21.02.20 | 8:21 | 21.02.20 | 8:27 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 4:59 | 19.02.20 | 5:02 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:35 | 12.02.20 | 17:40 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir New end: Tripped on O/C
|  | 12.02.20 | 16:12 | 12.02.20 | 17:18 | 0.045833 | 1 | 6 | [5 empty] | At Bolangir end: Tripped
|  | 20.01.20 | 5:54 | 20.01.20 | 5:56 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 11.01.20 | 5:27 | 11.01.20 | 5:31 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala on E/F
|  | 07.12.19 | 8:22 | 07.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | Kesinga end-Tripped on E/F
|  | 17.12.19 | 8:22 | 17.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end-Tripped on E/F
|  | 06.12.19 | 18:28 | 06.12.19 | 18:34 | 0.0041667 | 0 | 6 | [5 empty] | At Kesinga end-Tripped onover loadig and O/C
|  | 30.11.19 | 10:12 | 30.11.19 | 10:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped due to Bolangir-Solar Incomer Breaker Tripped.
|  | 23.11.19 | 16:37 | 23.11.19 | 16:50 | 0.0090278 | 0 | 13 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 23.11.19 | 16:11 | 23.11.19 | 16:20 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 20.11.19 | 11:02 | 20.11.19 | 11:11 | 0.00625 | 0 | 9 | [5 empty] | At Bolangir end :-Tripped (dropping conductor of wave trap b-ph at sadeipali)
|  | 15.11.19 | 2:51 | 15.11.19 | 3:06 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: Tripped on overloading
|  | 12.11.19 | 1:45 | 12.11.19 | 1:47 | 0.0013889 | 0 | 2 | [5 empty] | At Kesinga end :-Tripped on Over loading
|  | 07.11.19 | 3:22 | 07.11.19 | 3:24 | 0.0013889 | 0 | 2 | [5 empty] | At Kesinga end :-Tripped on E/F
|  | 02.11.19 | 9:10 | 02.11.19 | 9:14 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 01.11.19 | 6:37 | 01.11.19 | 6:47 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 28.10.19 | 4:21 | 28.10.19 | 4:23 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Saintala end
|  | 27.10.19 | 5:17 | 27.10.19 | 5:28 | 0.0076389 | 0 | 11 | [5 empty] | Tripped at Saintala end
|  | 26.10.19 | 10:49 | 26.10.19 | 10:52 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Saintala end
|  | 25.10.19 | 10:24 | 25.10.19 | 10:38 | 0.0097222 | 0 | 14 | [5 empty] | Tripped at Tushra end
|  | 25.10.19 | 4:44 | 25.10.19 | 5:40 | 0.038889 | 0 | 56 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 19:30 | 22.10.19 | 19:42 | 0.0083333 | 0 | 12 | [5 empty] | P/S failure from Bolangir New end
|  | 22.10.19 | 6:09 | 22.10.19 | 6:42 | 0.022917 | 0 | 33 | [5 empty] | Tripped at ACME end due to snapping of line conductor
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | At Bolangir New S/S -Tripped due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 13.10.19 | 3:11 | 13.10.19 | 3:17 | 0.0041667 | 0 | 6 | [5 empty] | Trippead at Saintala end
|  | 11.10.19 | 1:10 | 11.10.19 | 1:21 | 0.0076389 | 0 | 11 | [5 empty] | Trippead at Saintala end
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 11:07 | 01.10.19 | 11:12 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at ACME end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:43 | 0.15208 | 0 | 49 | [5 empty] | Tripped at Bolangir New end( Jumper snapped at GSS Sadeipali). Availed P/S at 07:53 Hrs from Kesinga end
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:36 | 0.018056 | 0 | 26 | [5 empty] | Tripped at New Bolangir end.
|  | 26.09.19 | 0:10 | 26.09.19 | 0:30 | 0.013889 | 0 | 20 | [5 empty] | P/S Failure from Bolangir New end
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 23.09.19 | 18:42 | 23.09.19 | 19:12 | 0.020833 | 0 | 30 | [5 empty] | Tripped on overload at New Bolangir end.
|  | 23.09.19 | 15:53 | 23.09.19 | 16:00 | 0.0048611 | 0 | 7 | [5 empty] | Tripped at New Bolangir end.
|  | 17.09.19 | 19:13 | 17.09.19 | 20:56 | 0.071528 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 27.09.19 | 4:03 | 27.09.19 | 4:11 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala-Tripped on E/F
|  | 27.09.19 | 7:56 | 27.09.19 | 8:01 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala-Tripped on Over load
|  | 27.09.19 | 21:41 | 27.09.19 | 21:50 | 0.00625 | 0 | 9 | [5 empty] | At Saintala-Tripped on Over load
|  | 19.09.19 | 12:47 | 19.09.19 | 12:57 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped and At Tusura end also DP operated.
|  | 10.09.19 | 19:45 | 10.09.19 | 21:27 | 0.070833 | 0 | 42 | [5 empty] | At Kesinga-Tripped on over load
|  | 05.09.19 | 17:23 | 05.09.19 | 17:34 | 0.0076389 | 0 | 11 | [5 empty] | At Kesinga-Tripped on over load
|  | 14.09.19 | 11:29 | 14.09.19 | 11:38 | 0.029167 | 0 | 42 | [5 empty] | At Khariar-Tripped on E/F
|  | 21.08.19 | 18:58 | 21.08.19 | 19:06 | 0.0055556 | 0 | 8 | [5 empty] | At Bolangir New-Tripped due to 132KV LA failure
|  | 21.08.19 | 18:32 | 21.08.19 | 18:46 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 13.08.19 | 6:28 | 13.08.19 | 6:32 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala end.
|  | 13.08.19 | 5:53 | 13.08.19 | 6:09 | 0.011111 | 0 | 16 | [5 empty] | P/S failure from New Bolangir end
|  | 21.08.19 | 18:32 | 21.08.19 | 18:42 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:30 | 0.015972 | 0 | 23 | [5 empty] | P/S failure from Bolangir New due to over loading
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 11.08.19 | 5:09 | 11.08.19 | 5:27 | 0.0125 | 0 | 18 | [5 empty] | Tripped on E/F at Bolangir end
|  | 22.07.19 | 3:28 | 22.07.19 | 3:55 | 0.01875 | 0 | 27 | [5 empty] | Tripped at Saintala end
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source at Bolangir.
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 05.07.19 | 15:06 | 05.07.19 | 15:56 | 0.034722 | 0 | 50 | [5 empty] | At Kesinga-Tripped on D/P relay
|  | 20.06.19 | 9:51 | 20.06.19 | 10:02 | 0.0076389 | 0 | 11 | [5 empty] | 132KV Tushra-Saintal line didn’t stand. Power supply resumed from kesinga
|  | 20.06.19 | 14:55 | 20.06.19 | 15:04 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.06.19 | 16:00 | 20.06.19 | 16:12 | 0.0083333 | 0 | 12 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 22.06.19 | 14:13 | 22.06.19 | 14:16 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 25.06.19 | 21:43 | 25.06.19 | 21:47 | 0.0027778 | 0 | 4 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 20:55 | 26.06.19 | 21:00 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:18 | 26.06.19 | 22:23 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:45 | 26.06.19 | 22:54 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 18.06.19 | 1:17 | 18.06.19 | 1:23 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 13.06.19 | 16:55 | 13.06.19 | 16:58 | 0.0020833 | 0 | 3 | [5 empty] | 132KV Saintala I/C pullout
|  | 11.06.19 | 15:29 | 11.06.19 | 15:36 | 0.0048611 | 0 | 7 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.06.19 | 15:55 | 09.06.19 | 16:23 | 0.019444 | 0 | 28 | [5 empty] | 132KV Y-phase CT brust at GSS Saintala
|  | 05.06.19 | 0.92708 | 05.06.19 | 22:18 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.06.19 | 18:00 | 05.06.19 | 18:06 | 0.0041667 | 0 | 6 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 03.06.19 | 6:58 | 03.06.19 | 7:08 | 0.0069444 | 0 | 10 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 02.06.19 | 23:03 | 02.06.19 | 23:26 | 0.015972 | 0 | 23 | [5 empty] | Earth fault located at bolangir
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder). Tripped from Saintala end.
|  | 29.04.19 | 2:34 | 29.04.19 | 2:39 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped on over load.
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 28.05.19 | 16:58 | 28.05.19 | 17:07 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Tusura; LBB Trip Supervision
|  | 17.05.19 | 16:06 | 17.05.19 | 16:12 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from ACME;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 29.05.19 | 21:10 | 29.05.19 | 23:12 | 0.084722 | 2 | 2 | [5 empty] | Tripped from Saintala;CT Brust on 132KV Khariar O/G Feeder at GSS Kesinga
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 21.05.19 | 0:23 | 21.05.19 | 0:31 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 17.05.19 | 22:20 | 17.05.19 | 22:25 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.05.19 | 0:03 | 20.05.19 | 0:09 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 12.05.19 | 16:55 | 12.05.19 | 17:04 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala; Y Phase, E/F on 132 KV Kesinga O/G Feeder
|  | 13.05.19 | 14:39 | 13.05.19 | 14:46 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 6:28 | 11.05.19 | 6:35 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 8:03 | 11.05.19 | 8:08 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.05.19 | 15:53 | 09.05.19 | 15:57 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 4:54 | 11.05.19 | 5:03 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 23:45 | 04.05.19 | 23:48 | 0.0020833 | 0 | 3 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.05.19 | 5:52 | 05.05.19 | 5:59 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 16:25 | 04.05.19 | 16:33 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 22:43 | 01.05.19 | 22:48 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 16:28 | 01.05.19 | 16:30 | 0.0013889 | 0 | 2 | [5 empty] | Due to ckt overloading ; Tripped from New Bolangir
|  | 20.04.19 | 20:12 | 20.04.19 | 20:16 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, Tushra 132KV I/C Pullout; Tripped from Tusura
|  | 21.04.19 | 13:38 | 21.04.19 | 13:50 | 0.0083333 | 0 | 12 | [5 empty] | B Phase Overcurrent ,DP operated; Tripped from Khariar.
|  | 20.04.19 | 10:15 | 20.04.19 | 15:23 | 0.21389 | 5 | 8 | [5 empty] | Y-B Phase Overcurrent, DP operated; Tripped from Khariar
|  | 30.04.19 | 3:43 | 30.04.19 | 7:00 | 0.13681 | 3 | 17 | [5 empty] | Y-Phase Jumper snapped on 132Kesinga-Khariar O/G Feeder at GSS Kesinga, Tripped from Saintala end.
|  | 30.04.19 | 22:32 | 30.04.19 | 22:38 | 0.0041667 | 0 | 6 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 28.04.19 | 16:27 | 28.04.19 | 17:48 | 0.05625 | 1 | 21 | [5 empty] | B-Phase Jumper snapped at Gantry point of 132 Saintala O/G Feeder, Tripped from Tusura end.
|  | 27.04.19 | 22:27 | 27.04.19 | 22:42 | 0.010417 | 0 | 15 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 24.04.19 | 21:22 | 24.04.19 | 21:26 | 0.0027778 | 0 | 4 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 23.04.19 | 22:20 | 23.04.19 | 22:27 | 0.0048611 | 0 | 7 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 21.04.19 | 8:24 | 21.04.19 | 8:40 | 0.011111 | 0 | 16 | [5 empty] | 132KV Saintala O/G Feeder Tripped on E/F, Tripped from Tusura end.
|  | 19.04.19 | 20:08 | 19.04.19 | 20:16 | 0.0055556 | 0 | 8 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 17.04.19 | 5:27 | 17.04.19 | 5:40 | 0.0090278 | 0 | 13 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 29.04.19 | 17:28 | 29.04.19 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 29.04.19 | 16:45 | 29.04.19 | 16:48 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 12.04.19 | 21:37 | 12.04.19 | 21:50 | 0.0090278 | 0 | 13 | [5 empty] | Source Failure
|  | 08.04.19 | 6:52 | 08.04.19 | 6:54 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 08.04.19 | 22:44 | 08.04.19 | 22:46 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:00 | 09.04.19 | 5:07 | 0.0048611 | 0 | 7 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:45 | 09.04.19 | 5:48 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 07.04.19 | 21:51 | 07.04.19 | 21:54 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 05.04.19 | 22:17 | 05.04.19 | 22:22 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 03.04.19 | 20:38 | 03.04.19 | 20:43 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 01.04.19 | 21:57 | 01.04.19 | 22:00 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
314 | 132kV Khurda-Shamuka |  |  |  |  | 1900-01-15 20:37 | 13 | 5 | [7 empty] | 54.742 | 8760 | 99.85% | 716.2078 | 479539.92
|  | 20.01.20 | 18:05 | 20.01.20 | 18:16 | 0.0076389 | 0 | 11 | [5 empty] | Tripped at Khurda end
|  | 29.12.19 | 9:51 | 29.12.19 | 17:15 | 0.30833 | 0 | 38 | [5 empty] | At Samuka end-Tripped on E/F. At 10:29 Hrs P/S availed from Puri end
|  | 22.10.19 | 9:43 | 22.10.19 | 9:48 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Khurda end
|  | 10.10.19 | 9:03 | 10.10.19 | 9:06 | 0.0020833 | 0 | 3 | [5 empty] | Tripped from Khurda end
|  | 09.07.19 | 15:45 | 09.07.19 | 15:53 | 0.0055556 | 0 | 4 | [5 empty] | O/C B-ph,E/E (Tripped at Mendhasal end). 132KV Khurda-Samuka,Khurda-KTSS availing MSAL Supply on reserve bus of khurda.
|  | 02.07.19 | 18:33 | 02.07.19 | 18:48 | 0.010417 | 0 | 4 | [5 empty] | At Mendhasal-Tripped on D/P relay. 132KV Khurda-Samuka,Khurda-KTSS availing MSAL Supply on reserve bus of khurda.
|  | 03.05.19 | 7:29 | 19.05.19 | 20:00 | 1900-01-15 12:31 |  |  |  |  | 396 | 31 |  | Tripped (Due to Cyclone Fani)
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
315 | 132kV Khurda-Kaipadar (T) |  |  |  |  | 0.024306 | 12 | 25 | [7 empty] | 11.259 | 8760 | 99.86% | 139.7993 | 98628.84
|  | 09.07.19 | 15:45 | 09.07.19 | 15:53 | 0.0055556 | 0 | 9 | [5 empty] | O/C B-ph,E/E (Tripped at Mendhasal end). 132KV Khurda-Samuka,Khurda-KTSS availing MSAL Supply on reserve bus of khurda.
|  | 02.07.19 | 18:33 | 02.07.19 | 18:48 | 0.010417 | 0 | 4 | [5 empty] | At Mendhasal-Tripped on D/P relay. 132KV Khurda-Samuka,Khurda-KTSS availing MSAL Supply on reserve bus of khurda.
|  | 05.07.19 | 6:08 | 05.07.19 | 6:16 | 0.0055556 | 0 | 8 | [5 empty] | At Mendhasal end: Zone-4, Master Trip relay operated
|  | 04.07.19 | 10:31 | 04.07.19 | 10:35 | 0.0027778 | 0 | 4 | [5 empty] | At Mendhasal end: D/P, Zone-I, 'B' ph.-E/F, FC-3.5 kA, Dist.-18.7 k.m.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
316 | 132kV Kuchei PG- Bangiriposhi |  |  |  |  | 0.75208 | 17 | 18 | [7 empty] | 31.526 | 8760 | 99.8% | 545.3998 | 276167.76
|  | 13.11.19 | 8:39 | 13.11.19 | 13:29 | 0.20139 |  |  | 0 | 55 |  |  |  | Tripped at both ends due to B-phase LA of 132KV Bangiriposi- PGCIL line burst at PGCIL end. Rairangpur Grid avail P/ S from Karanjia Grid end and Bangiriposi avail P/S from Rairangpur.
|  | 14.06.19 | 16:40 | 14.06.19 | 17:34 | 0.0375 | 0 | 54
|  | 03.06.19 | 20:03 | 03.06.19 | 21:53 | 0.076389 | 1 | 50 | [5 empty] | Tripped from PG end
|  | 06.10.19 | 12:06 | 06.10.19 | 12:16 | 0.0069444 | 0 | 10 | [5 empty] | At Baripada end: O/C & E/F , Zone-I, DISTANCE -O.5 Km,IL-E,IL1=2.92KAmp, IL2=0.22 Kamp,IL3=O.34KAmp
|  | 29.08.19 | 8:58 | 29.08.19 | 9:44 | 0.031944 | 0 | 46 | [5 empty] | Tripped at PGCIL end on Fault B Phase – E,Distance-5.273 Km, Fault Current- 6.139Kamp
|  | 08.05.19 | 12:21 | 08.05.19 | 15:14 | 0.12014 | 0 | 26 | [5 empty] | Tripped at PGCIL end,Zone -1,Y-BPH, Dist-1.47km,IY-6.61KA,IB-6.31KA. But Power supply Restored From Rairangpur end at 12:47 Hrs
|  | 02.05.19 | 15:38 | 02.05.19 | 19:20 | 0.15417 |  |  | 0 | 37 |  |  |  | Incomer Failure L/A Brust at PGCIL end; Power supply extended From Rairangpur Grid end at 16:15 Hr
|  | 07.04.19 | 14:17 | 07.04.19 | 17:15 | 0.12361 | 1 | 12 | [5 empty] | O/C in B- phase Ib-8.59KA,Z1-405m. Then ICT was tripped at PGCIL end & Restricted P/S restored from Rairangpur end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
317 | 132kV Bangiriposhi- Rairangapur |  |  |  |  | 0.45417 | 17 | 46 | [7 empty] | 34.602 | 8760 | 99.8% | 614.7622 | 303113.52
|  | 13.11.19 | 8:39 | 13.11.19 | 9:34 | 0.038194 |  |  | 0 | 55 |  |  |  | Tripped at both ends due to B-phase LA of 132KV Bangiriposi- PGCIL line burst at PGCIL end. Rairangpur Grid avail P/ S from Karanjia Grid end and Bangiriposi avail P/S from Rairangpur.
|  | 14.06.19 | 16:40 | 14.06.19 | 17:34 | 0.0375 | 0 | 54
|  | 03.06.19 | 20:03 | 03.06.19 | 21:53 | 0.076389 | 1 | 50 | [5 empty] | Tripped from PG end
|  | 06.10.19 | 12:06 | 06.10.19 | 12:16 | 0.0069444 | 0 | 10 | [5 empty] | At Baripada end: O/C & E/F , Zone-I, DISTANCE -O.5 Km,IL-E,IL1=2.92KAmp, IL2=0.22 Kamp,IL3=O.34KAmp
|  | 11.08.19 | 6:43 | 11.08.19 | 7:03 | 0.013889 | 0 | 20 | [5 empty] | Tripped at Bangiriposi end on ZONE-I, General Trip,Y-E,Distance-8.7 Km,IL1-0.49Kamp,IL2-2.52Kamp,IL1-0.25Kamp,
|  | 29.08.19 | 8:58 | 29.08.19 | 9:44 | 0.031944 | 0 | 46 | [5 empty] | Tripped at PGCIL end on Fault B Phase – E,Distance-5.273 Km, Fault Current- 6.139Kamp
|  | 13.05.19 | 18:49 | 13.05.19 | 18:57 | 0.0055556 | 0 | 8 | [5 empty] | Bangriposi Incomer Failure.Tripped at Bangriposi Grid End. Fault Distance=7.5 Km, E/F, General Trip, zone-I,L1=O.O1KAmp,L2= 2 .72 Kamp,L3= 1.53KAmp.
|  | 08.05.19 | 12:21 | 08.05.19 | 15:14 | 0.12014 | 0 | 26 | [5 empty] | Tripped at PGCIL end,Zone -1,Y-BPH, Dist-1.47km,IY-6.61KA,IB-6.31KA. But Power supply Restored From Rairangpur end at 12:47 Hrs
|  | 07.04.19 | 14:17 | 07.04.19 | 17:15 | 0.12361 | 1 | 12 | [5 empty] | O/C in B- phase Ib-8.59KA,Z1-405m. Then ICT was tripped at PGCIL end & Restricted P/S restored from Rairangpur end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
318 | 132kV Kuchei PG- Jaleswar ckt - I |  |  |  |  | 0.11736 | 12 | 50 | [7 empty] | 79.282 | 8760 | 99.85% | 1017.4523 | 694510.32
|  | 19.08.19 | 14:53 | 19.08.19 | 16:10 | 0.053472 | 0 | 12 | [5 empty] | Tripped at Baripada(PG) end but Supply availed from Basta end.
|  | 05.08.19 | 15:59 | 05.08.19 | 16:46 | 0.032639 | 0 | 12 | [5 empty] | At Jaleswar end:DP, Zone-I, Y ph. E/F, Dist.-80.3 k.m, FC-9.61 kA But At 16:11 Hrs Jaleswar & Bhograi Grid availed supply from Basta Grid.
|  | 29.06.19 | 15:24 | 29.06.19 | 16:09 | 0.03125 | 0 | 26 | [5 empty] | At Jaleswar end: DP operated, Y-Ø, E/F, Zone-I, 52.4 k.m.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
319 | 132kV Kuchei PG- Bhogarai |  |  |  |  | 0.24444 | 13 | 6 | [7 empty] | 101.907 | 8760 | 99.85% | 1334.9817 | 892705.32
|  | 29.06.19 | 15:37 | 29.06.19 | 18:14 | 0.10903 | 0 | 9 | [5 empty] | P/s availed from Jaleswar end.
|  | 16.06.19 | 1:30 | 16.06.19 | 1:44 | 0.0097222 | 0 | 14 | [5 empty] | Tripped at Bhograi end & P/s availed from Baripada (PG)
|  | 16.06.19 | 1:03 | 16.06.19 | 1:22 | 0.013194 | 0 | 19 | [5 empty] | Tripped at Bhograi end & P/s availed from Baripada (PG)
|  | 19.08.19 | 14:53 | 19.08.19 | 16:20 | 0.060417 | 0 | 12 | [5 empty] | Tripped at Baripada(PG) end but Supply availed from Basta end.
|  | 05.08.19 | 15:59 | 05.08.19 | 17:14 | 0.052083 | 0 | 12 | [5 empty] | At Bhograi end: Zone-I, R ph.-E/F, FC-8.05 kA But At 16:11 Hrs Jaleswar & Bhograi Grid availed supply from Basta Grid.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
320 | 132kV Kuchinda-Bamara(T)-Rajgangpur |  |  |  |  | 0.026389 | 12 | 38 | [7 empty] | 118.4 | 8760 | 99.86% | 1495.7867 | 1037184
|  | 26.11.19 | 16:14 | 26.11.19 | 16:20 | 0.0041667 | 0 | 6 | [5 empty] | At Rajgangpur end: BGT,IB=6850A,IG=6773A,Z-I, 1.79Km
|  | 29.09.19 | 17:34 | 29.09.19 | 17:47 | 0.0090278 | 0 | 13 | [5 empty] | Tripped at Kuchinda end. Availed P/S from Rajgangpur end at 17:47 Hrs
|  | 22.09.19 | 17:25 | 22.09.19 | 17:38 | 0.0090278 | 0 | 13 | [5 empty] | At Rajgangpur-H/T
|  | 25.04.19 | 12:55 | 25.04.19 | 13:01 | 0.0041667 | 0 | 6 | [5 empty] | DP OPERATED, FAULT- L1 TO L2, FAULT CURRENT- L1-1.529kA, L2-1.396kA, LOC- 99.176, ZONE-2
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
321 | 132kV Lapanga - Rengali RTSS |  |  |  |  | 0.23819 | 17 | 43 | [7 empty] | 12.308 | 8760 | 99.8% | 218.0567 | 107818.08
|  | 07.12.19 | 15:15 | 07.12.19 | 16:17 | 0.043056 | 1 | 2 | [5 empty] | At Lapanga end-132KV & 33KV BLACKOUT AT GRID SS LAPANGA DUE TO 132KV B-PH CT OF 160MVA AUTO TFR-I BURSTED
|  | 20.08.19 | 19:46 | 20.08.19 | 20:46 | 0.041667 | 1 | 0 | [5 empty] | GRID BLACK OUT AT 132/33KV LAPANGA DUE TO SNAPPING OF R-PH CROSS BUS OF 132KV BURLA CKT-II & FELL ON 132KV MAIN BUS AND RESERVE BUS AT GRID SS LAPANGA AND CAUSE TRIPPING OF Power TRF.
|  | 15.06.19 | 18:10 | 15.06.19 | 19:07 | 0.039583 | 0 | 57 | [5 empty] | At Lapanga-D/P RELAY: DIST TRIP, ZONE-1,DIST=1.368 KM, A-G, IL1=16.14KA, VA= 18.86V
|  | 14.04.19 | 9:53 | 14.04.19 | 12:37 | 0.11389 | 2 | 44 | [5 empty] | R PH CONDUCTOR OF 132 KV ARYAN ISPAT SNAPPED AND FELL ON B PH CONDUCTOR OF 132 KV RTSS RENGALI
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
322 | 132kV Machkund PH-Jaynagar |  |  |  |  | 0.48333 | 14 | 24 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 43 | 8760 | 99.84% | 619.2 | 376680
|  | 25.07.19 | 17:25 | 25.07.19 | 17:59 | 0.023611 | 1 | 8 | [5 empty] | At Jayanagar end: Z-I, Dist.-27.25 k.m. R,Y,B ph.-E/F
|  | 16.07.19 | 15:47 | 16.07.19 | 23:02 | 0.30208 | 0 | 18 | [5 empty] | Tripped at Machhkund end.Akhusingh GS/S availed P/S from Digapahandi end at 15:56 Hrs.
|  | 17.07.19 | 17:10 | 17.07.19 | 20:57 | 0.15764 | 0 | 58 | [5 empty] | Tripped at Machhkund end: At 17:39 - Akhusingh, Paralakhemundi availed P/S from Digapahandi end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
323 | 132kV Machkund PH- Machkund (T) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 108 | 8760 | 100% | 0 | 946080
324 | 132kV Mendhasal-Chandpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35 | 8760 | 100% | 0 | 306600
325 | 132kV Mendhasal-Khurda |  |  |  |  | 1899-12-31 15:58 | 12 | 20 | [7 empty] | 18 | 8760 | 99.86% | 222 | 157680
|  | 09.07.19 | 15:45 | 09.07.19 | 15:53 | 0.0055556 | 0 | 4 | [5 empty] | O/C B-ph,E/E (Tripped at Mendhasal end). 132KV Khurda-Samuka,Khurda-KTSS availing Mendhasal Supply on reserve bus of khurda.
|  | 02.07.19 | 18:33 | 02.07.19 | 18:48 | 0.010417 | 0 | 4 | [5 empty] | At Mendhasal-Tripped on D/P relay. 132KV Khurda-Samuka,Khurda-KTSS availing MSAL Supply on reserve bus of khurda.
|  | 05.07.19 | 6:08 | 05.07.19 | 6:16 | 0.0055556 | 0 | 8 | [5 empty] | At Mendhasal end: Zone-4, Master Trip relay operated
|  | 04.07.19 | 10:31 | 04.07.19 | 10:35 | 0.0027778 | 0 | 4 | [5 empty] | At Mendhasal end: D/P, Zone-I, 'B' ph.-E/F, FC-3.5 kA, Dist.-18.7 k.m.
|  | 03.05.19 | 10:30 | 04.05.19 | 23:23 | 1899-12-31 15:23 |  |  |  |  | 39 | 23 |  | Tripped during extreme severe cyclone 'FANI
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
326 | 132kV Meramundali-BRG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.55 | 8760 | 100% | 0 | 31098
327 | 132kV Meramundali-Chainpal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.728 | 8760 | 100% | 0 | 15137.28
328 | 132kV Meramundali-Chainpal Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.728 | 8760 | 100% | 0 | 15137.28
329 | 132kV Meramundali-Dhenkanal S/s |  |  |  |  | 0 | 0 | 0 | [7 empty] | 51.916 | 8760 | 100% | 0 | 454784.16
330 | 132kV Meramundali-Kharagprasad Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.517 | 8760 | 100% | 0 | 48328.92
331 | 132kV Meramundali-Kharagprasad Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.517 | 8760 | 100% | 0 | 48328.92
332 | 132kV Meramundali-M.L. Rungta |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.468 | 8760 | 100% | 0 | 65419.68
333 | 132kV Meramundali-Khajuriakata |  |  |  |  | 0.61597 | 13 | 0 | [7 empty] | 33.5 | 8760 | 99.85% | 435.5 | 293460
|  | 19.03.20 | 18:05 | 20.03.20 | 7:25 | 0.55556 | 0 | 14 | [5 empty] | At Khajuriakata end: R-G Fault, Zone-I, Dist- 27.1 kM, FC = 1.6KA
|  | 16.03.20 | 16:36 | 16.03.20 | 16:52 | 0.011111 | 0 | 16 | [5 empty] | At Khajuriakata end: B-G Fault, Zone-III, Dist- 39.02Kms, If=2.6KA
|  | 03.09.19 | 18:29 | 03.09.19 | 18:46 | 0.011806 | 0 | 17 | [5 empty] | At Khajuriakata end:- E/F, Zone-1 (R-G Fault, -55.3 Kms), Fault Current- 1.294 KA
|  | 27.04.19 | 17:27 | 27.04.19 | 18:21 | 0.0375 | 0 | 13 | [5 empty] | Y-G Fault (Zone-1), -1.4 Kms but P/S availed from Nuapatana end at 17:40.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
334 | 132KV Dhenkanal-Nuapatna-Khajuriakata "T" feeder |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 2.4 | 8760 | 100% | 0.32 | 21024
|  | 19.03.20 | 18:44 | 19.03.20 | 18:52 | 0.0055556 | 0 | 8 | [5 empty] | At Dhenkanal end: E/F B/U relay operated. DP Relay:L2_N fault
335 | 132kV Khajuriakata-Nuapatna |  |  |  |  | 1900-01-01 20:45 | 14 | 30 | [7 empty] | 84.79 | 8760 | 99.83% | 1229.455 | 742760.4
|  | 19.03.20 | 18:39 | 19.03.20 | 18:52 | 0.0090278 | 0 | 13 | [5 empty] | At Nuapatna end: Tripped on E/F, B-ph
|  | 16.03.20 | 16:36 | 16.03.20 | 18:53 | 1899-12-31 02:17 | 0 | 16 | [5 empty] | At Khajuriakata end: Zone-III, B-G fault, Dist- 39.02, If= 2.6KA
|  | 03.09.19 | 18:29 | 03.09.19 | 18:50 | 0.014583 | 0 | 21 | [5 empty] | At Khajuriakata end:- E/F, Zone-1 (R-G Fault, 52.4 Kms, Fault Current- 1.35 KA)
|  | 29.05.19 | 0.66944 | 29.05.19 | 0.67361 | 0.0041667 | 0 | 6 | [5 empty] | O/C.
|  | 24.05.19 | 0.56042 | 24.05.19 | 0.56667 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Meramundali
|  | 19.05.19 | 0.74236 | 19.05.19 | 0.75347 | 0.011111 | 0 | 16 | [5 empty] | E/F
|  | 15.05.19 | 0.75833 | 15.05.19 | 0.76111 | 0.0027778 | 0 | 4 | [5 empty] | E/F
|  | 09.05.19 | 0.78611 | 09.05.19 | 0.78958 | 0.0034722 | 0 | 5 | [5 empty] | Due to Ckt Overloading O/C at B phase.
|  | 08.05.19 | 0.16875 | 08.05.19 | 0.17986 | 0.011111 | 0 | 16 | [5 empty] | Due to BIRD, E/F.
|  | 05.05.19 | 0.30625 | 05.05.19 | 0.31458 | 0.0083333 | 0 | 12 | [5 empty] | Tripped from Meramundali
|  | 03.05.19 | 0.26667 | 04.05.19 | 0.94306 | 1899-12-31 16:14 |  |  |  |  | 40 | 14 |  | B phase to ground fault due to severe cyclone FANI
|  | 02.05.19 | 0.55833 | 02.05.19 | 0.57222 | 0.013889 | 0 | 20 | [5 empty] | E/F .
|  | 17.04.19 | 13:02 | 17.04.19 | 13:14 | 0.0083333 | 0 | 12 | [5 empty] | R-Y O/C Fault (Zone-1), 41.1 Kms and P/S failed.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
336 | 132kV Nuapatna-Arati Steel |  |  |  |  | 1899-12-31 17:59 | 13 | 25 | [7 empty] | 67.7 | 8760 | 99.85% | 908.3083 | 593052
|  | 19.03.20 | 18:33 | 19.03.20 | 19:01 | 0.019444 | 0 | 14 | [5 empty] | At Nuapatna end: Tripped on O/C, E/F, R-ph
|  | 29.05.19 | 0.66944 | 29.05.19 | 0.67361 | 0.0041667 | 0 | 6 | [5 empty] | O/C at Y phase.
|  | 24.05.19 | 0.56042 | 24.05.19 | 0.56667 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Meramundali
|  | 19.05.19 | 0.74236 | 19.05.19 | 0.75486 | 0.0125 | 0 | 16 | [5 empty] | R phase O/C and E/F.
|  | 15.05.19 | 0.75833 | 15.05.19 | 0.76389 | 0.0055556 | 0 | 4 | [5 empty] | Y phase O/C.
|  | 08.05.19 | 0.16875 | 08.05.19 | 0.17986 | 0.011111 | 0 | 16 | [5 empty] | O/C fault.
|  | 03.05.19 | 0.425 | 04.05.19 | 0.6375 | 1899-12-31 16:14 |  |  |  |  | 40 | 14 |  | Hand Tripping due to severe cyclonic storm FANI.
|  | 02.05.19 | 0.55833 | 02.05.19 | 0.57222 | 0.013889 | 0 | 20 | [5 empty] | R phase O/C.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
337 | 132kV Mohana-Digapahandi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.882 | 8760 | 100% | 0 | 261766.32
338 | 132kV Muniguda-Bissamcuttack RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.85 | 8760 | 100% | 0 | 121326
339 | 132kV Nalda-Beekay Steel |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.4 | 8760 | 100% | 0 | 47304
340 | 132kV Narendrapur-Berhampur Ckt -I |  |  |  |  | 0.011806 | 0 | 17 | [7 empty] | 10.91 | 8760 | 100% | 3.0912 | 95571.6
|  | 18.09.19 | 12:00 | 18.09.19 | 12:17 | 0.011806 | 0 | 17 | [5 empty] | At Narendrapur end: Zone-I, R ph.-E/F, Dist.-76.25 k.m.
341 | 132kV Narendrapur-Berhampur Ckt - II |  |  |  |  | 0.011806 | 0 | 17 | [7 empty] | 10.91 | 8760 | 100% | 3.0912 | 95571.6
|  | 18.09.19 | 12:00 | 18.09.19 | 12:17 | 0.011806 | 0 | 17 | [5 empty] | At Narendrapur end: Zone-I, R ph.-E/F, Dist.-76.25 k.m.
342 | 132kV Narendrapur-Chatrapur-I |  |  |  |  | 0.44097 | 0 | 22 | [7 empty] | 13.282 | 8760 | 100% | 4.8701 | 116350.32
|  | 15.09.19 | 19:59 | 15.09.19 | 20:12 | 0.0090278 | 0 | 13 | [5 empty] | At Narendrapur-Tripped
|  | 18.09.19 | 12:00 | 18.09.19 | 22:22 | 0.43194 | 0 | 9 | [5 empty] | At Narendrapur end;-DP, ZONE-3, IR=443.6 A, IY=1.359kA, IB=998.8 A,VAN=126.9 KV, VBN=118.8 KV, VCN= 119.9KV,Distance=204.9 km (Problem in line CVT)
343 | 132kV Narendrapur-Chatrapur-II |  |  |  |  | 0.45069 | 12 | 36 | [7 empty] | 13.282 | 8760 | 99.86% | 167.3532 | 116350.32
|  | 15.09.19 | 19:59 | 15.09.19 | 20:12 | 0.0090278 | 0 | 13 | [5 empty] | At Narendrapur-Tripped
|  | 24.09.19 | 2:12 | 24.09.19 | 2:26 | 0.0097222 | 0 | 14 | [5 empty] | At Chhatrapur end: Tripped on Y-G with M/R,Dist-4.29km
|  | 18.09.19 | 12:00 | 18.09.19 | 22:22 | 0.43194 | 0 | 9 | [5 empty] | At Narendrapur end;-DP, ZONE-3, IR=443.6 A, IY=1.359kA, IB=998.8 A,VAN=126.9 KV, VBN=118.8 KV, VCN= 119.9KV,Distance=204.9 km (Problem in line CVT)
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
344 | 132kV Narendrapur-Narendrapur(T) |  |  |  |  | 0.023611 | 0 | 34 | [7 empty] | 0.51 | 8760 | 99.99% | 0.289 | 4467.6
|  | 23.09.19 | 12:00 | 23.09.19 | 12:17 | 0.011806 | 0 | 17 | [5 empty] | At Narendrapur end: Tripped on distance fault. Zone-I, AG trip, dist-88.410km, fault current=1823Amp
|  | 18.09.19 | 12:00 | 18.09.19 | 12:17 | 0.011806 | 0 | 17 | [5 empty] | At Narendrapur end: Zone-I, R ph.-E/F, Dist.-76.25 k.m.
345 | 132kV NBVL-Hind Metals |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1 | 8760 | 100% | 0 | 8760
346 | 132kV Nimapara-Konark |  |  |  |  | 1900-01-10 15:09 | 0 | 5 | [7 empty] | 20.31 | 8760 | 100% | 1.6925 | 177915.6
|  | 11.04.19 | 19:09 | 11.04.19 | 19:14 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at Samangara-DIST.PROTECTION operated.due to 2/3 MULTIPHASE FAULT,86A operated.
|  | 03.05.19 | 8:50 | 14.05.19 | 23:24 | 1900-01-10 15:04 |  |  |  |  | 279 | 4 |  | Tripped during extreme severe cyclone 'FANI
347 | 132kV Nimapara-Puri Ckt-II |  |  |  |  | 1900-01-10 16:11 | 12 | 51 | [7 empty] | 30 | 8760 | 99.85% | 385.5 | 262800
|  | 10.01.20 | 9:15 | 10.01.20 | 9:24 | 0.00625 | 0 | 9 | [5 empty] | Tripped at Nimapara end
|  | 05.01.20 | 16:30 | 05.01.20 | 17:51 | 0.05625 | 0 | 24 | [5 empty] | At Nimapara end: Zone-2, (Y-ph to Earth), Distance= 24.69 KM (LA of 132 kV Shamuka - Puri fdr burst). P/s availed from Khurdha end.
|  | 25.10.19 | 8:37 | 25.10.19 | 8:55 | 0.0125 | 0 | 18 | [5 empty] | At Nimapara end: D/P, Dist.- 1.35KM
|  | 03.05.19 | 8:50 | 14.05.19 | 23:13 | 1900-01-10 14:23 |  |  |  |  | 278 | 23 |  | Tripped during extreme severe cyclone 'FANI; 132 KV Nimapara -Puri fdr charged at 23:13 Hrs on 14.05.19.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
348 | 132kV Nimapara-Samagara |  |  |  |  | 1900-01-11 06:59 | 12 | 58 | [7 empty] | 27.995 | 8760 | 99.85% | 363.0018 | 245236.2
|  | 11.12.19 | 3:27 | 11.12.19 | 4:02 | 0.024306 | 0 | 23 | [5 empty] | Chandaka end-Tripped
|  | 07.03.20 | 6:15 | 07.03.20 | 6:27 | 0.0083333 | 0 | 12 | [5 empty] | At Nimapara end: Tripped
|  | 25.10.19 | 8:37 | 25.10.19 | 9:11 | 0.023611 | 0 | 18 | [5 empty] | At Nimapara end: D/P, Dist.-5.06KM
|  | 11.04.19 | 19:09 | 11.04.19 | 19:14 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at Samangara-DIST.PROTECTION operated.due to 2/3 MULTIPHASE FAULT,86A operated.
|  | 03.05.19 | 8:42 | 15.05.19 | 14:15 | 1900-01-11 05:33 |  |  |  |  | 293 | 33 |  | H/T due to upcoming extreme severe cyclone FANI & charged again by "T" arrangement in 132 KV Nimapara -Puri Line
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
349 | 132kV Nuapara-Nuapara RTSS |  |  |  |  | 1899-12-31 20:06 | 51 | 23 | [7 empty] | 4.528 | 8760 | 99.41% | 232.6637 | 39665.28
|  | 24.03.20 | 19:00 | 24.03.20 | 19:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 25.03.20 | 16:17 | 25.03.20 | 16:31 | 0.0097222 | 0 | 14 | [5 empty] | At Saintala end: Tripped on O/C
|  | 22.03.20 | 7:38 | 22.03.20 | 7:51 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:04 | 19.03.20 | 21:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 21:23 | 19.03.20 | 21:39 | 0.011111 | 0 | 16 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 22:08 | 19.03.20 | 22:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 23:48 | 19.03.20 | 23:56 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:45 | 19.03.20 | 17:48 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 17:28 | 19.03.20 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.03.20 | 6:48 | 19.03.20 | 6:55 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 16.03.20 | 19:12 | 16.03.20 | 19:25 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 15.03.20 | 17:07 | 15.03.20 | 17:12 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 7:20 | 14.03.20 | 7:30 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 8:17 | 14.03.20 | 8:22 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 14.03.20 | 9:04 | 14.03.20 | 9:09 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.03.20 | 18:00 | 13.03.20 | 18:07 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 8:00 | 12.03.20 | 8:06 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 9:10 | 12.03.20 | 9:17 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 12.03.20 | 12:15 | 12.03.20 | 12:26 | 0.0076389 | 0 | 11 | [5 empty] | At Saintala end: Tripped on O/C
|  | 11.03.20 | 7:40 | 11.03.20 | 7:47 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:25 | 03.03.20 | 15:26 | 0.00069444 | 0 | 1 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:32 | 03.03.20 | 15:34 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 15:44 | 03.03.20 | 15:51 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 16:13 | 03.03.20 | 16:26 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 03.03.20 | 17:31 | 03.03.20 | 17:33 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 7:53 | 28.02.20 | 7:59 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 28.02.20 | 10:54 | 28.02.20 | 10:59 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala end: Tripped on O/C
|  | 23.02.20 | 8:52 | 23.02.20 | 8:58 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped
|  | 19.02.20 | 15:49 | 19.02.20 | 15:52 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 16:44 | 19.02.20 | 16:57 | 0.0090278 | 0 | 13 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 18:06 | 19.02.20 | 18:13 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:08 | 20.02.20 | 7:18 | 0.0069444 | 0 | 10 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 7:29 | 20.02.20 | 7:36 | 0.0048611 | 0 | 7 | [5 empty] | At Saintala end: Tripped on O/C
|  | 20.02.20 | 18:36 | 20.02.20 | 18:39 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped on O/C
|  | 21.02.20 | 8:21 | 21.02.20 | 8:27 | 0.0041667 | 0 | 6 | [5 empty] | At Saintala end: Tripped on O/C
|  | 19.02.20 | 4:59 | 19.02.20 | 5:02 | 0.0020833 | 0 | 3 | [5 empty] | At Saintala end: Tripped
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:35 | 12.02.20 | 17:40 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir New end: Tripped on O/C
|  | 12.02.20 | 16:12 | 12.02.20 | 17:18 | 0.045833 | 1 | 6 | [5 empty] | At Bolangir end: Tripped
|  | 20.01.20 | 5:54 | 20.01.20 | 5:56 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end: Tripped on O/C
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 11.01.20 | 5:27 | 11.01.20 | 5:31 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala on E/F
|  | 07.12.19 | 8:22 | 07.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | Kesinga end-Tripped on E/F
|  | 17.12.19 | 8:22 | 17.12.19 | 8:24 | 0.0013889 | 0 | 2 | [5 empty] | At Saintala end-Tripped on E/F
|  | 06.12.19 | 18:28 | 06.12.19 | 18:34 | 0.0041667 | 0 | 6 | [5 empty] | At Kesinga end-Tripped onover loadig and O/C
|  | 30.11.19 | 10:12 | 30.11.19 | 10:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped due to Bolangir-Solar Incomer Breaker Tripped.
|  | 23.11.19 | 16:37 | 23.11.19 | 16:50 | 0.0090278 | 0 | 13 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 23.11.19 | 16:11 | 23.11.19 | 16:20 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 20.11.19 | 11:02 | 20.11.19 | 11:11 | 0.00625 | 0 | 9 | [5 empty] | At Bolangir end :-Tripped (dropping conductor of wave trap b-ph at sadeipali)
|  | 15.11.19 | 2:51 | 15.11.19 | 3:06 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: Tripped on overloading
|  | 12.11.19 | 1:45 | 12.11.19 | 1:47 | 0.0013889 | 0 | 2 | [5 empty] | At Kesinga end :-Tripped on Over loading
|  | 07.11.19 | 3:22 | 07.11.19 | 3:24 | 0.0013889 | 0 | 2 | [5 empty] | At Kesinga end :-Tripped on E/F
|  | 02.11.19 | 9:10 | 02.11.19 | 9:14 | 0.0027778 | 0 | 4 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 01.11.19 | 6:37 | 01.11.19 | 6:47 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 28.10.19 | 4:21 | 28.10.19 | 4:23 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Saintala end
|  | 27.10.19 | 5:17 | 27.10.19 | 5:28 | 0.0076389 | 0 | 11 | [5 empty] | Tripped at Saintala end
|  | 26.10.19 | 10:49 | 26.10.19 | 10:52 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Saintala end
|  | 25.10.19 | 10:24 | 25.10.19 | 10:38 | 0.0097222 | 0 | 14 | [5 empty] | Tripped at Tushra end
|  | 25.10.19 | 4:44 | 25.10.19 | 5:40 | 0.038889 | 0 | 56 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 19:30 | 22.10.19 | 19:42 | 0.0083333 | 0 | 12 | [5 empty] | P/S failure from Bolangir New end
|  | 22.10.19 | 6:09 | 22.10.19 | 6:42 | 0.022917 | 0 | 33 | [5 empty] | Tripped at ACME end due to snapping of line conductor
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | At Bolangir New S/S -Tripped due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 13.10.19 | 3:11 | 13.10.19 | 3:17 | 0.0041667 | 0 | 6 | [5 empty] | Trippead at Saintala end
|  | 11.10.19 | 1:10 | 11.10.19 | 1:21 | 0.0076389 | 0 | 11 | [5 empty] | Trippead at Saintala end
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 11:07 | 01.10.19 | 11:12 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at ACME end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:43 | 0.15208 | 0 | 49 | [5 empty] | Tripped at Bolangir New end( Jumper snapped at GSS Sadeipali). Availed P/S at 07:53 Hrs from Kesinga end
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:36 | 0.018056 | 0 | 26 | [5 empty] | Tripped at New Bolangir end.
|  | 26.09.19 | 0:10 | 26.09.19 | 0:30 | 0.013889 | 0 | 20 | [5 empty] | P/S Failure from Bolangir New end
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 23.09.19 | 18:42 | 23.09.19 | 19:12 | 0.020833 | 0 | 30 | [5 empty] | Tripped on overload at New Bolangir end.
|  | 23.09.19 | 15:53 | 23.09.19 | 16:00 | 0.0048611 | 0 | 7 | [5 empty] | Tripped at New Bolangir end.
|  | 17.09.19 | 19:13 | 17.09.19 | 20:56 | 0.071528 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 27.09.19 | 4:03 | 27.09.19 | 4:11 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala-Tripped on E/F
|  | 27.09.19 | 7:56 | 27.09.19 | 8:01 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala-Tripped on Over load
|  | 27.09.19 | 21:41 | 27.09.19 | 21:50 | 0.00625 | 0 | 9 | [5 empty] | At Saintala-Tripped on Over load
|  | 19.09.19 | 12:47 | 19.09.19 | 12:57 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped and At Tusura end also DP operated.
|  | 10.09.19 | 19:45 | 10.09.19 | 21:27 | 0.070833 | 0 | 42 | [5 empty] | At Kesinga-Tripped on over load
|  | 05.09.19 | 17:23 | 05.09.19 | 17:34 | 0.0076389 | 0 | 11 | [5 empty] | At Kesinga-Tripped on over load
|  | 14.09.19 | 11:29 | 14.09.19 | 11:38 | 0.029167 | 0 | 42 | [5 empty] | At Khariar-Tripped on E/F
|  | 21.08.19 | 18:58 | 21.08.19 | 19:06 | 0.0055556 | 0 | 8 | [5 empty] | At Bolangir New-Tripped due to 132KV LA failure
|  | 21.08.19 | 18:32 | 21.08.19 | 18:46 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 13.08.19 | 6:28 | 13.08.19 | 6:32 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala end.
|  | 13.08.19 | 5:53 | 13.08.19 | 6:09 | 0.011111 | 0 | 16 | [5 empty] | P/S failure from New Bolangir end
|  | 21.08.19 | 18:32 | 21.08.19 | 18:42 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:30 | 0.015972 | 0 | 23 | [5 empty] | P/S failure from Bolangir New due to over loading
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 11.08.19 | 5:09 | 11.08.19 | 5:27 | 0.0125 | 0 | 18 | [5 empty] | Tripped on E/F at Bolangir end
|  | 22.07.19 | 3:28 | 22.07.19 | 3:55 | 0.01875 | 0 | 27 | [5 empty] | Tripped at Saintala end
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 05.07.19 | 15:06 | 05.07.19 | 15:56 | 0.034722 | 0 | 50 | [5 empty] | At Kesinga-Tripped on D/P relay
|  | 20.06.19 | 9:51 | 20.06.19 | 10:02 | 0.0076389 | 0 | 11 | [5 empty] | 132KV Tushra-Saintal line didn’t stand. Power supply resumed from kesinga
|  | 20.06.19 | 14:55 | 20.06.19 | 15:04 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.06.19 | 16:00 | 20.06.19 | 16:12 | 0.0083333 | 0 | 12 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 22.06.19 | 14:13 | 22.06.19 | 14:16 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 25.06.19 | 21:43 | 25.06.19 | 21:47 | 0.0027778 | 0 | 4 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 20:55 | 26.06.19 | 21:00 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:18 | 26.06.19 | 22:23 | 0.0034722 | 0 | 5 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 26.06.19 | 22:45 | 26.06.19 | 22:54 | 0.00625 | 0 | 9 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 18.06.19 | 1:17 | 18.06.19 | 1:23 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 13.06.19 | 16:55 | 13.06.19 | 16:58 | 0.0020833 | 0 | 3 | [5 empty] | 132KV Saintala I/C pullout
|  | 11.06.19 | 15:29 | 11.06.19 | 15:36 | 0.0048611 | 0 | 7 | [5 empty] | Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.06.19 | 15:55 | 09.06.19 | 16:23 | 0.019444 | 0 | 28 | [5 empty] | 132KV Y-phase CT brust at GSS Saintala
|  | 05.06.19 | 0.92708 | 05.06.19 | 22:18 | 0.0020833 | 0 | 3 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.06.19 | 18:00 | 05.06.19 | 18:06 | 0.0041667 | 0 | 6 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 03.06.19 | 6:58 | 03.06.19 | 7:08 | 0.0069444 | 0 | 10 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 02.06.19 | 23:03 | 02.06.19 | 23:26 | 0.015972 | 0 | 23 | [5 empty] | Earth fault located at bolangir
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder). Tripped from Saintala end.
|  | 29.04.19 | 2:34 | 29.04.19 | 2:39 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped on over load.
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV New Bolangir-Bolangir O/G Fdr)
|  | 28.05.19 | 16:58 | 28.05.19 | 17:07 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Tusura; LBB Trip Supervision
|  | 17.05.19 | 16:06 | 17.05.19 | 16:12 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from ACME;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 29.05.19 | 21:10 | 29.05.19 | 23:12 | 0.084722 | 2 | 2 | [5 empty] | Tripped from Saintala;CT Brust on 132KV Khariar O/G Feeder at GSS Kesinga
|  | 31.05.19 | 16:12 | 31.05.19 | 16:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (R & B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 21.05.19 | 0:23 | 21.05.19 | 0:31 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 17.05.19 | 22:20 | 17.05.19 | 22:25 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 20.05.19 | 0:03 | 20.05.19 | 0:09 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 12.05.19 | 16:55 | 12.05.19 | 17:04 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala; Y Phase, E/F on 132 KV Kesinga O/G Feeder
|  | 13.05.19 | 14:39 | 13.05.19 | 14:46 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 6:28 | 11.05.19 | 6:35 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 8:03 | 11.05.19 | 8:08 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 09.05.19 | 15:53 | 09.05.19 | 15:57 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 11.05.19 | 4:54 | 11.05.19 | 5:03 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 23:45 | 04.05.19 | 23:48 | 0.0020833 | 0 | 3 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 05.05.19 | 5:52 | 05.05.19 | 5:59 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 04.05.19 | 16:25 | 04.05.19 | 16:33 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 22:43 | 01.05.19 | 22:48 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from Saintala;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 16:28 | 01.05.19 | 16:30 | 0.0013889 | 0 | 2 | [5 empty] | Due to ckt overloading ; Tripped from New Bolangir
|  | 20.04.19 | 20:12 | 20.04.19 | 20:16 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, Tushra 132KV I/C Pullout; Tripped from Tusura
|  | 21.04.19 | 13:38 | 21.04.19 | 13:50 | 0.0083333 | 0 | 12 | [5 empty] | B Phase Overcurrent ,DP operated; Tripped from Khariar.
|  | 20.04.19 | 10:15 | 20.04.19 | 15:23 | 0.21389 | 5 | 8 | [5 empty] | Y-B Phase Overcurrent, DP operated; Tripped from Khariar
|  | 30.04.19 | 3:43 | 30.04.19 | 7:00 | 0.13681 | 3 | 17 | [5 empty] | Y-Phase Jumper snapped on 132Kesinga-Khariar O/G Feeder at GSS Kesinga, Tripped from Saintala end.
|  | 30.04.19 | 22:32 | 30.04.19 | 22:38 | 0.0041667 | 0 | 6 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 28.04.19 | 16:27 | 28.04.19 | 17:48 | 0.05625 | 1 | 21 | [5 empty] | B-Phase Jumper snapped at Gantry point of 132 Saintala O/G Feeder, Tripped from Tusura end.
|  | 27.04.19 | 22:27 | 27.04.19 | 22:42 | 0.010417 | 0 | 15 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 24.04.19 | 21:22 | 24.04.19 | 21:26 | 0.0027778 | 0 | 4 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 23.04.19 | 22:20 | 23.04.19 | 22:27 | 0.0048611 | 0 | 7 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 21.04.19 | 8:24 | 21.04.19 | 8:40 | 0.011111 | 0 | 16 | [5 empty] | 132KV Saintala O/G Feeder Tripped on E/F, Tripped from Tusura end.
|  | 19.04.19 | 20:08 | 19.04.19 | 20:16 | 0.0055556 | 0 | 8 | [5 empty] | 132KV Saintala I/C pullout, Tripped from Saintala end.
|  | 17.04.19 | 5:27 | 17.04.19 | 5:40 | 0.0090278 | 0 | 13 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 29.04.19 | 17:28 | 29.04.19 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 29.04.19 | 16:45 | 29.04.19 | 16:48 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 12.04.19 | 21:37 | 12.04.19 | 21:50 | 0.0090278 | 0 | 13 | [5 empty] | Source Failure
|  | 08.04.19 | 6:52 | 08.04.19 | 6:54 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 08.04.19 | 22:44 | 08.04.19 | 22:46 | 0.0013889 | 0 | 2 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:00 | 09.04.19 | 5:07 | 0.0048611 | 0 | 7 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 09.04.19 | 5:45 | 09.04.19 | 5:48 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 07.04.19 | 21:51 | 07.04.19 | 21:54 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped from Saintala end.
|  | 05.04.19 | 22:17 | 05.04.19 | 22:22 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 03.04.19 | 20:38 | 03.04.19 | 20:43 | 0.0034722 | 0 | 5 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
|  | 01.04.19 | 21:57 | 01.04.19 | 22:00 | 0.0020833 | 0 | 3 | [5 empty] | Circuit overloading , Tripped on O/C B-Phase. Tripped from Saintala end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
350 | 132kV OCL-Salipur |  |  |  |  | 0.20833 | 12 | 58 | [7 empty] | 38.81 | 8760 | 99.85% | 503.2363 | 339975.6
|  | 23.03.20 | 16:31 | 23.03.20 | 16:45 | 0.0097222 | 0 | 14 | [5 empty] | At Salipur end: Tripped
|  | 19.03.20 | 19:28 | 19.03.20 | 20:33 | 0.045139 | 0 | 14 | [5 empty] | At Salipur end: Tripped. At 19:42 Hrs, P/S availabled from Kendrapara end.
|  | 17.02.20 | 9:13 | 17.02.20 | 12:40 | 0.14375 | 0 | 23 | [5 empty] | At Salipur end: Tripped on O/C, E/F. At 09:36 Hrs, P/S availed from Kendrapara end.
|  | 07.12.19 | 9:20 | 07.12.19 | 9:27 | 0.0048611 | 0 | 7 | [5 empty] | At Salipur end-Tripped on E/F
|  | 03.08.19 | 13:03 | 03.08.19 | 13:10 | 0.0048611 |  |  | 0 | 7 |  |  |  | P/S failed from ICCL end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
351 | 132kV OPCL-Kamakhyanagar |  |  |  |  | 0.041667 | 0 | 46 | [7 empty] | 55 | 8760 | 99.99% | 42.1667 | 481800
|  | 23.09.19 | 3:50 | 23.09.19 | 4:50 | 0.041667 | 0 | 46 | [5 empty] | At Kamakhyanagar end;- Tripped on E/F
352 | 132kV Paradeep-Tirtol |  |  |  |  | 1899-12-31 13:02 | 24 | 58 | [7 empty] | 38.833 | 8760 | 99.71% | 969.5306 | 340177.08
|  | 19.03.20 | 19:51 | 19.03.20 | 17:46 | 0.92014 | 0 | 14 | [5 empty] | At Paradeep end: Tripped (Earthwire snapped at Loc. No:190). At 20:05 Hrs P/S availed from Cuttack end.
|  | 04.03.20 | 15:34 | 04.03.20 | 16:08 | 0.023611 | 0 | 8 | [5 empty] | At Paradeep end: Tripped. At 15:36 Hrs P/S availed from Cuttack end
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 17.01.20 | 17:06 | 0.017361 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F
|  | 29.01.20 | 3:02 | 29.01.20 | 3:10 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Paradeep end on E/F
|  | 04.01.20 | 10:22 | 04.01.20 | 11:01 | 0.027083 | 0 | 9 | [5 empty] | Tripped from Paradeep end
|  | 16.12.19 | 3:53 | 16.12.19 | 3:59 | 0.0041667 | 0 | 6 | [5 empty] | At Tirtol end-Tripped on E/F
|  | 17.12.19 | 4:47 | 17.12.19 | 4:53 | 0.0041667 | 0 | 6 | [5 empty] | At Tirtol end-Tripped on E/F
|  | 17.12.19 | 5:08 | 17.12.19 | 5:13 | 0.0034722 | 0 | 5 | [5 empty] | At Tirtol end-Tripped on E/F
|  | 08.11.19 | 22:09 | 08.11.19 | 22:18 | 0.00625 | 0 | 4 | [5 empty] | At Paradeep end-Tripped. At 22:13 Hrs P/S availed from Cuttack end
|  | 13.06.19 | 2:03 | 13.06.19 | 11:56 | 0.41181 | 9 | 53 | [5 empty] | At Paradeep end: DP relay operated Zn.-I, 'B' ph.-N, Dist.-53.6
|  | 05.06.19 | 21:39 | 05.06.19 | 23:02 | 0.057639 | 1 | 23 | [5 empty] | At Paradeep end: B o - E/F, Zone-1, Dist.-43.4 k.m.
|  | 13.09.19 | 18:49 | 13.09.19 | 20:03 | 0.051389 | 0 | 4 | [5 empty] | Tripped from Paradeep end but at 18:53 hrs, P/S availed from Cuttack end.
|  | 06.09.19 | 13:26 | 06.09.19 | 13:31 | 0.0034722 | 0 | 3 | [5 empty] | Tripped from Paradeep end but P/S availed from Cuttack end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
353 | 132kV Tirtol- Jagatsinghpur |  |  |  |  | 1899-12-31 13:37 | 14 | 18 | [7 empty] | 29.66 | 8760 | 99.84% | 424.138 | 259821.6
|  | 19.03.20 | 19:51 | 19.03.20 | 17:46 | 0.92014 | 0 | 14 | [5 empty] | At Paradeep end: Tripped (Earthwire snapped at Loc. No:190). At 20:05 Hrs P/S availed from Cuttack end.
|  | 04.03.20 | 15:34 | 04.03.20 | 16:08 | 0.023611 | 0 | 8 | [5 empty] | At Paradeep end: Tripped. At 15:36 Hrs P/S availed from Cuttack end
|  | 22.01.20 | 15:07 | 22.01.20 | 15:13 | 0.0041667 | 0 | 6 | [5 empty] | P/S failure Paradeep end
|  | 29.01.20 | 3:02 | 29.01.20 | 3:10 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Paradeep end on E/F
|  | 17.01.20 | 16:41 | 17.01.20 | 17:06 | 0.017361 | 0 | 6 | [5 empty] | Tripped from Paradeep end on E/F
|  | 04.01.20 | 10:22 | 04.01.20 | 10:31 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Paradeep end
|  | 16.12.19 | 3:53 | 16.12.19 | 3:59 | 0.0041667 | 0 | 6 | [5 empty] | At Tirtol end-Tripped on E/F
|  | 17.12.19 | 4:47 | 17.12.19 | 4:53 | 0.0041667 | 0 | 6 | [5 empty] | At Tirtol end-Tripped on E/F
|  | 17.12.19 | 5:08 | 17.12.19 | 5:13 | 0.0034722 | 0 | 5 | [5 empty] | At Tirtol end-Tripped on E/F
|  | 27.11.19 | 5:23 | 27.11.19 | 5:30 | 0.0048611 | 0 | 2 | [5 empty] | P/S failure from Tirtol end. At 05:25 Hrs P/S availed from Cuttack end
|  | 25.11.19 | 4:54 | 25.11.19 | 5:13 | 0.013194 | 0 | 13 | [5 empty] | Tripped at Jagatsinghpur on O/C, E/F. At 05:09 Hrs P/S availed from Cuttack end
|  | 26.11.19 | 4:17 | 26.11.19 | 4:26 | 0.00625 | 0 | 1 | [5 empty] | P/S failure from Tirtol end. At 04:18 Hrs P/S availed from Cuttack end
|  | 08.11.19 | 22:09 | 08.11.19 | 22:18 | 0.00625 | 0 | 4 | [5 empty] | At Paradeep end-Tripped. At 22:13 Hrs P/S availed from Cuttack end
|  | 13.06.19 | 2:03 | 13.06.19 | 11:56 | 0.41181 | 0 | 12 | [5 empty] | At Paradeep end: DP relay operated Zn.-I, 'B' ph.-N, Dist.-53.6. Jagatsingpur GSS availed P/S from Cuttack GSS at 02:15Hrs.
|  | 05.06.19 | 21:39 | 05.06.19 | 23:02 | 0.057639 | 0 | 5 | [5 empty] | At Paradeep end: B o - E/F, Zone-1, Dist.-43.4 k.m.. At 21:44 hrs. Jagatsingpur availed P/S from Cuttack end.
|  | 29.09.19 | 6:58 | 29.09.19 | 7:06 | 0.0055556 |  |  | 0 | 8 |  |  |  | Tripped at Jagatsinghpur end on O/C
|  | 29.09.19 | 7:07 | 29.09.19 | 7:33 | 0.018056 | 0 | 26 | [5 empty] | P/S Failure from Cuttack end
|  | 13.09.19 | 18:49 | 13.09.19 | 20:03 | 0.051389 | 0 | 4 | [5 empty] | Tripped from Paradeep end but at 18:53 hrs, P/S availed from Cuttack end.
|  | 06.09.19 | 13:26 | 06.09.19 | 13:31 | 0.0034722 | 0 | 3 | [5 empty] | Tripped from Paradeep end but P/S availed from Cuttack end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
354 | 132kV Paradeep- IFFCO - I |  |  |  |  | 0.45764 | 22 | 59 | [7 empty] | 7.171 | 8760 | 99.74% | 164.8135 | 62817.96
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 17.01.20 | 17:06 | 0.017361 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F
|  | 21.06.19 | 9:10 | 21.06.19 | 18:10 | 0.375 | 9 | 0
|  | 19.09.19 | 3:48 | 19.09.19 | 5:02 | 0.051389 | 1 | 14 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-2, Dist.-119.2 k.m.
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep-Tripped on TRIPPED ON Y-PH O/C,E/F,Z-1,D-86.6KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
355 | 132kV Paradeep- IFFCO - II |  |  |  |  | 1899-12-31 07:32 | 13 | 59 | [7 empty] | 7.171 | 8760 | 99.84% | 100.2745 | 62817.96
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 17.01.20 | 17:06 | 0.017361 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F
|  | 19.09.19 | 3:48 | 19.09.19 | 5:02 | 0.051389 | 1 | 14 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-2, Dist.-119.2 k.m.
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep-Tripped on TRIPPED ON Y-PH O/C,E/F,Z-1,D-86.6KM
|  | 03.05.19 | 12:40 | 04.05.19 | 42:13 | 1899-12-31 05:33 |  |  |  |  | 29 | 33 |  | Tripped at Paradeep end during extreme severe cyclone 'FANI
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
356 | 132kV Paradeep-PPL-I |  |  |  |  | 0.065278 | 13 | 34 | [7 empty] | 6.2 | 8760 | 99.85% | 84.1133 | 54312
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 19.09.19 | 3:48 | 19.09.19 | 5:02 | 0.051389 | 1 | 14 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-2, Dist.-119.2 k.m.
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep-Tripped on TRIPPED ON Y-PH O/C,E/F,Z-1,D-86.6KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
357 | 132kV Paradeep-PPL-II |  |  |  |  | 0.093056 | 13 | 59 | [7 empty] | 6.2 | 8760 | 99.84% | 86.6967 | 54312
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 17.01.20 | 17:21 | 0.027778 | 0 | 25 | [5 empty] | At Paradeeep end: Tripped on E/F
|  | 19.09.19 | 3:48 | 19.09.19 | 5:02 | 0.051389 | 1 | 14 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-2, Dist.-119.2 k.m.
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep-Tripped on TRIPPED ON Y-PH O/C,E/F,Z-1,D-86.6KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
358 | 132kV Paradeep-PPT-I |  |  |  |  | 0.084722 | 13 | 59 | [7 empty] | 7.65 | 8760 | 99.84% | 106.9725 | 67014
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 17.01.20 | 17:09 | 0.019444 | 0 | 25 | [5 empty] | At Paradeeep end: Tripped on E/F
|  | 19.09.19 | 3:48 | 19.09.19 | 5:02 | 0.051389 | 1 | 14 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-2, Dist.-119.2 k.m.
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep-Tripped on TRIPPED ON Y-PH O/C,E/F,Z-1,D-86.6KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
359 | 132kV Paradeep-PPT-II |  |  |  |  | 0.084722 | 13 | 59 | [7 empty] | 7.65 | 8760 | 99.84% | 106.9725 | 67014
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 17.01.20 | 17:09 | 0.019444 | 0 | 25 | [5 empty] | At Paradeeep end: Tripped on E/F
|  | 19.09.19 | 3:48 | 19.09.19 | 5:02 | 0.051389 | 1 | 14 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-2, Dist.-119.2 k.m.
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep-Tripped on TRIPPED ON Y-PH O/C,E/F,Z-1,D-86.6KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
360 | 132kV Patnagarh-Padampur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 44.636 | 8760 | 100% | 0 | 391011.36
361 | 132kV Padampur-Padampur Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.7 | 8760 | 100% | 0 | 84972
362 | 132kV Pattamundai-Olavar Ckt - I |  |  |  |  | 1899-12-31 16:33 | 15 | 38 | [7 empty] | 24.338 | 8760 | 99.82% | 380.4841 | 213200.88
|  | 19.03.20 | 19:50 | 19.03.20 | 20:26 | 0.025 | 0 | 36 | [5 empty] | At Kendrapara end: DP relay operated (R-phase), Dist - 12.67 kM
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 18.01.20 | 13:21 | 0.85417 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F,O/C RYB PH,Differential R-Y operated ( 132 kV B-ph LA failure)
|  | 09.11.19 | 4:38 | 09.11.19 | 8:30 | 0.16111 | 0 | 29 | [5 empty] | At Paradeep end-Tripped. Availed I/C P/S From Jajpur Road end at 05:06Hrs
|  | 08.11.19 | 22:09 | 08.11.19 | 22:17 | 0.0055556 | 0 | 8 | [5 empty] | At Paradeep end-Tripped
|  | 23.10.19 | 10:34 | 23.10.19 | 10:40 | 0.0041667 | 0 | 6 | [5 empty] | At Kendrapara-TRIPPED ON BACK UP E/F & At Chandikhole end: E/F operated
|  | 01.10.19 | 11:54 | 01.10.19 | 13:18 | 0.058333 | 0 | 11 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1 At Marshaghai-TRIPPED ON O/C & E/F Availed P/S at 12:02 Hrs from Jajpur road end
|  | 01.10.19 | 11:09 | 01.10.19 | 11:13 | 0.0027778 | 0 | 4 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1
|  | 19.09.19 | 3:48 | 19.09.19 | 5:00 | 0.05 | 0 | 45 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-II Dist.-112 k.m, FC-7.83 kA.At 04:33-Kendrapara availed P/S from Jajpur Road end .
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Kendrapara:- Tripped on M/R
|  | 17.08.19 | 20:31 | 17.08.19 | 20:35 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, R-phase at Pattamundai end.
|  | 24.05.19 | 23:44 | 24.05.19 | 23:46 | 0.0013889 | 0 | 2 | [5 empty] | At Paradeep-Tripped on O/C
|  | 24.05.19 | 23:47 | 25.05.19 | 12:02 | 0.51042 | 0 | 28 | [5 empty] | At Paradeep-Tripped on O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
363 | 132kV Pattamundai-Olavar Ckt -II |  |  |  |  | 1900-01-01 20:49 | 15 | 38 | [7 empty] | 24.338 | 8760 | 99.82% | 380.4841 | 213200.88
|  | 19.03.20 | 19:50 | 19.03.20 | 20:26 | 0.025 | 0 | 36 | [5 empty] | At Kendrapara end: DP relay operated (R-phase), Dist - 12.67 kM
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 18.01.20 | 13:21 | 0.85417 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F,O/C RYB PH,Differential R-Y operated ( 132 kV B-ph LA failure)
|  | 09.11.19 | 4:38 | 09.11.19 | 8:30 | 0.16111 | 0 | 29 | [5 empty] | At Paradeep end-Tripped. Availed I/C P/S From Jajpur Road end at 05:06Hrs
|  | 08.11.19 | 22:09 | 08.11.19 | 22:17 | 0.0055556 | 0 | 8 | [5 empty] | At Paradeep end-Tripped
|  | 23.10.19 | 10:34 | 23.10.19 | 10:40 | 0.0041667 | 0 | 6 | [5 empty] | At Kendrapara-TRIPPED ON BACK UP E/F & At Chandikhole end: E/F operated
|  | 01.10.19 | 11:54 | 01.10.19 | 13:18 | 0.058333 | 0 | 11 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1 At Marshaghai-TRIPPED ON O/C & E/F Availed P/S at 12:02 Hrs from Jajpur road end
|  | 01.10.19 | 11:09 | 01.10.19 | 11:13 | 0.0027778 | 0 | 4 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1
|  | 19.09.19 | 3:48 | 19.09.19 | 5:00 | 0.05 | 0 | 45 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-II Dist.-112 k.m, FC-7.83 kA.At 04:33-Kendrapara availed P/S from Jajpur Road end .
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Kendrapara:- Tripped on M/R
|  | 17.08.19 | 20:31 | 17.08.19 | 20:35 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, R-phase at Pattamundai end.
|  | 24.05.19 | 23:44 | 24.05.19 | 23:46 | 0.0013889 | 0 | 2 | [5 empty] | At Paradeep-Tripped on O/C
|  | 24.05.19 | 23:47 | 25.05.19 | 12:02 | 0.51042 | 0 | 28 | [5 empty] | At Paradeep-Tripped on O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
364 | 132kV Olavar - Chandabali Ckt - I |  |  |  |  | 1899-12-31 04:16 | 15 | 8 | [7 empty] | 12.498 | 8760 | 99.83% | 189.1364 | 109482.48
|  | 19.03.20 | 19:50 | 19.03.20 | 20:26 | 0.025 | 0 | 36 | [5 empty] | At Kendrapara end: DP relay operated (R-phase), Dist - 12.67 kM
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 18.01.20 | 13:21 | 0.85417 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F,O/C RYB PH,Differential R-Y operated ( 132 kV B-ph LA failure)
|  | 09.11.19 | 4:38 | 09.11.19 | 8:30 | 0.16111 | 0 | 29 | [5 empty] | At Paradeep end-Tripped. Availed I/C P/S From Jajpur Road end at 05:06Hrs
|  | 08.11.19 | 22:09 | 08.11.19 | 22:17 | 0.0055556 | 0 | 8 | [5 empty] | At Paradeep end-Tripped
|  | 23.10.19 | 10:34 | 23.10.19 | 10:40 | 0.0041667 | 0 | 6 | [5 empty] | At Kendrapara-TRIPPED ON BACK UP E/F & At Chandikhole end: E/F operated
|  | 01.10.19 | 11:54 | 01.10.19 | 13:18 | 0.058333 | 0 | 11 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1 At Marshaghai-TRIPPED ON O/C & E/F Availed P/S at 12:02 Hrs from Jajpur road end
|  | 01.10.19 | 11:09 | 01.10.19 | 11:13 | 0.0027778 | 0 | 4 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1
|  | 19.09.19 | 3:48 | 19.09.19 | 5:00 | 0.05 | 0 | 45 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-II Dist.-112 k.m, FC-7.83 kA.At 04:33-Kendrapara availed P/S from Jajpur Road end .
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Kendrapara:- Tripped on M/R
|  | 17.08.19 | 20:31 | 17.08.19 | 20:35 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, R-phase at Pattamundai end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
365 | 132kV Olavar - Chandabali Ckt - II |  |  |  |  | 1899-12-31 04:16 | 15 | 8 | [7 empty] | 12.498 | 8760 | 99.83% | 189.1364 | 109482.48
|  | 19.03.20 | 19:50 | 19.03.20 | 20:26 | 0.025 | 0 | 36 | [5 empty] | At Kendrapara end: DP relay operated (R-phase), Dist - 12.67 kM
|  | 22.01.20 | 15:07 | 22.01.20 | 15:17 | 0.0069444 | 0 | 10 | [5 empty] | At Paradeep end: Trippped on M/T,E/F
|  | 17.01.20 | 16:41 | 18.01.20 | 13:21 | 0.85417 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F,O/C RYB PH,Differential R-Y operated ( 132 kV B-ph LA failure)
|  | 09.11.19 | 4:38 | 09.11.19 | 8:30 | 0.16111 | 0 | 29 | [5 empty] | At Paradeep end-Tripped. Availed I/C P/S From Jajpur Road end at 05:06Hrs
|  | 08.11.19 | 22:09 | 08.11.19 | 22:17 | 0.0055556 | 0 | 8 | [5 empty] | At Paradeep end-Tripped
|  | 23.10.19 | 10:34 | 23.10.19 | 10:40 | 0.0041667 | 0 | 6 | [5 empty] | At Kendrapara-TRIPPED ON BACK UP E/F & At Chandikhole end: E/F operated
|  | 01.10.19 | 11:54 | 01.10.19 | 13:18 | 0.058333 | 0 | 11 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1 At Marshaghai-TRIPPED ON O/C & E/F Availed P/S at 12:02 Hrs from Jajpur road end
|  | 01.10.19 | 11:09 | 01.10.19 | 11:13 | 0.0027778 | 0 | 4 | [5 empty] | At Kendrapara-TRIPPED ON DP RELAY ZONE-1
|  | 19.09.19 | 3:48 | 19.09.19 | 5:00 | 0.05 | 0 | 45 | [5 empty] | At New Duburi end: R ph.-E/F, Zone-II Dist.-112 k.m, FC-7.83 kA.At 04:33-Kendrapara availed P/S from Jajpur Road end .
|  | 17.08.19 | 22:59 | 17.08.19 | 23:09 | 0.0069444 | 0 | 10 | [5 empty] | At Kendrapara:- Tripped on M/R
|  | 17.08.19 | 20:31 | 17.08.19 | 20:35 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, R-phase at Pattamundai end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
366 | 132kV Palasponga- Keonjhargarh (T) |  |  |  |  | 1899-12-31 02:02 | 17 | 46 | [7 empty] | 19.433 | 8760 | 99.8% | 345.2596 | 170233.08
|  | 19.03.20 | 17:06 | 19.03.20 | 17:34 | 0.019444 | 0 | 28 | [5 empty] | At Polasponga end: E/F ZONE1 , Ia=264A, Ib=240A, Ic=152A, IG= 451A
|  | 17.03.20 | 11:45 | 17.03.20 | 11:47 | 0.0013889 |  |  | 0 | 2 |  |  |  | At Polasponga end: O/C (R PH), Ia=220.1A, Ib=177.7A, Ic=62.14A, In measured= 6.956A, In derived= 6.574A
|  | 12.03.20 | 12:42 | 12.03.20 | 12:55 | 0.0090278 | 0 | 13 | [5 empty] | At Polasponga end: E/F ZONE1 LOC 32.85KM, Ia=202.1A, Ib=203A, Ic=79A, IG= 427A
|  | 08.03.20 | 15:02 | 08.03.20 | 15:04 | 0.0013889 |  |  | 0 | 2 |  |  |  | At Polasponga end: O/C (R PH), Ia=220.1A, Ib=176.3A, Ic=55.53A, In measured= 4.7A, In derived= 5.1A
|  | 09.02.20 | 198:00 | 09.02.20 | 198:43 | 0.03 |  |  | 0 | 43 |  |  |  | At Polasponga end: O/C (R PH), Ia=221.7A, Ib=149.9A, Ic=78.28A, In measured= 6.956A, In derived= 6.039A
|  | 09.02.20 | 174:43 | 09.02.20 | 175:12 | 0.02 |  |  | 0 | 28 |  |  |  | At Polasponga end; O/C (R PH), Ia=219.8A, Ib=183.2A, Ic=41.51A, In measured= 6.901A, In derived= 5.808A
|  | 04.02.20 | 169:12 | 04.02.20 | 169:26 | 0.01 |  |  | 0 | 14 |  |  |  | At Polasponga end: O/C (R PH), Ia=224.1A, Ib=166.2A, Ic=65.04A, In measured= 6.315A, In derived= 5.139A
|  | 28.01.20 | 246:14 | 28.01.20 | 246:43 | 0.02 |  |  | 0 | 28 |  |  |  | At Polasponga end : O/C (R PH), Ia=223.5A, Ib=165.5A, Ic=64.9A, In measured= 6.972A, In derived= 5.372A
|  | 25.01.20 | 251:31 | 25.01.20 | 252:00 | 0.02 |  |  | 0 | 28 |  |  |  | At Polasponga end: O/C (R PH), Ia=220.2A, Ib=142.9A, Ic=107.2A, In measured= 7.011A, In derived= 6.532A
|  | 17.01.20 | 147:50 | 17.01.20 | 148:05 | 0.01 |  |  | 0 | 14 |  |  |  | At Polasponga end: O/C (R PH), Ia=219.9A, Ib=187.9A, Ic=38.14A, In measured= 6.869A, In derived= 5.336A
|  | 10.01.20 | 299:46 | 11.01.20 | 312:14 | 0.52 |  |  | 12 | 28 |  |  |  | At Polasponga end: O/C (R PH), Ia=425.8A, Ib=373.3A, Ic=292.1A, In=0.0A,Ig=4.08A
|  | 06.01.20 | 363:07 | 06.01.20 | 363:36 | 0.02 |  |  | 0 | 28 |  |  |  | At Polasponga end: O/C (R PH), Ia=220.8A, Ib=171.7A, Ic=61.05A, In measured= 6.875A, In derived= 6.713A
|  | 06.01.20 | 366:58 | 06.01.20 | 367:26 | 0.020139 |  |  | 0 | 29 |  |  |  | At Polasponga end: O/C (R PH), Ia=222.5A, Ib=123.3A, Ic=119.5A, In measured= 7.328A, In derived= 7.706A
|  | 03.01.20 | 487:41 | 03.01.20 | 487:55 | 0.01 |  |  | 0 | 14 |  |  |  | At Polasponga end: O/C (R PH), Ia=220.2A, Ib=194.2A, Ic=34.84A, In measured= 6.725A, In derived= 5.003A
|  | 05.11.19 | 412:48 | 05.11.19 | 413:17 | 0.02 |  |  | 0 | 28 |  |  |  | At Polasponga end; O/C (R PH), Ia=220.4A, Ib=144.46A, Ic=87.69A, In measured= 6.830A, In derived= 5.995A
|  | 20.10.19 | 13:49 | 20.10.19 | 13:51 | 0.0013889 |  |  | 0 | 2 |  |  |  | Tripped at Palasponga end; O/C (R PH), Ia=219.5A, Ib=192.6A, Ic=36.19A, In measured=3.223A, In derived= 4.023A
|  | 16.10.19 | 1:27 | 16.10.19 | 1:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Palasponga end; O/C & E/F, Ia=341.3A, Ib=844.1A, Ic=148.9A, In =0.09A, Ig = 386.63A
|  | 07.10.19 | 2:21 | 07.10.19 | 2:23 | 0.0013889 |  |  | 0 | 2 |  |  |  | Tripped at Palasponga end;O/C (R PH), Ia=219.8A, Ib=183.0A, Ic=93.38A, In measured=7.075A, In derived= 6.012A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:15 | 0.028472 | 0 | 41 | [5 empty] | Tripped at Joda end.
|  | 06.10.19 | 11:46 | 06.10.19 | 11:48 | 0.0013889 |  |  | 0 | 2 |  |  |  | Tripped at Palasponga end;O/C (R PH), Ia=219.1A, Ib=182.6A, Ic=48.9A, In measured= 4.753A, In derived= 5.203A
|  | 04.10.19 | 22:29 | 04.10.19 | 22:30 | 0.00069444 |  |  | 0 | 1 |  |  |  | Tripped at Polasponga end;O/C (R PH), Ia=220.1A, Ib=156.6A, Ic=74.68A, In measured= 6.883A, In derived= 6.603A
|  | 04.10.19 | 21:13 | 04.10.19 | 21:15 | 0.0013889 | 0 | 2 | [5 empty] | At Polasponga end: O/C R-ph, Ia=431.3A, Ib=363.6A, Ic=280.1A, In =0.04A
|  | 30.09.19 | 15:24 | 30.09.19 | 15:26 | 0.0013889 |  |  | 0 | 2 |  |  |  | Tripped at Polasponga end; O/C (R PH), Ia=222.3A, Ib=139.8A, Ic=96.89A, In measured=7.142A, In derived=6.831A
|  | 16.09.19 | 16:01 | 16.09.19 | 16:03 | 0.0013889 |  |  | 0 | 2 |  |  |  | At Polasponga end:- O/C (R PH), Ia=219.6A, Ib=183.3A, Ic=45.6A, In measured=5.140A, In derived=4.651A
|  | 15.09.19 | 18:42 | 15.09.19 | 18:46 | 0.0027778 | 0 | 4 | [5 empty] | At Polasponga end;- O/C (R PH), Ia=423.0A, Ib=341.2A, Ic=288.2A, In =0.01A, Ig = 2.91A
|  | 19.07.19 | 19:25 | 19.07.19 | 21:06 | 0.070139 | 0 | 23 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.Polasponga GSS availed P/S at 19:48 Hrs from Karanjia GSS.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 34 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end; E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 23.05.19 | 18:43 | 23.05.19 | 18:45 | 0.0013889 |  |  | 0 | 2 |  |  |  | O/C (R PH), Ia=220.3A, Ib=184.3A, Ic=42.99A, In=6.63A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 09.05.19 | 14.15 | 09.05.19 | 14.18 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Joda end; O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA ,IN=0.0A,IG=1.1
|  | 07.05.19 | 17:37 | 07.05.19 | 19.06 | 0.061806 | 0 | 30 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end; 132KV PPG S/S availed P/S from Karanjia end till restoration of power at Joda end.
|  | 21.04.19 | 15:18 | 21.04.19 | 15:28 | 0.0069444 | 0 | 10 | [5 empty] | Fdr tripped at both ends. At JODA end- DP Relay, zone-1,fault loop=L2_N,fault distance=2.27 km, IL1=161.90A, IL2=6868.97A, IL3=109.93A, IN=6763.22A. At PPG end- DP Relay, zone-1,fault loop=L2_N,fault distance=32.2 km, IL1=176A, IL2=293A, IL3=127A, IN=407A
|  | 19.04.19 | 1:25 | 19.04.19 | 1:43 | 0.0125 | 0 | 18 | [5 empty] | Fdr tripped only at Joda end. At JODA end- DP Relay, zone-1,fault loop=L2_N,fault distance=2.0437 km, IL1=247.75A, IL2=6817.47A, IL3=238.20A, IN=6895.73A
|  | 29.04.19 | 21:33 | 29.04.19 | 21:38 | 0.0034722 | 0 | 5 | [5 empty] | O/C (R PH), Ia= 405A, Ib= 340A, Ic= 242.8A, In= 0.1A, Ig= 4.66A
|  | 28.04.19 | 15:06 | 28.04.19 | 15:09 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R PH), Ia= 423.4A, Ib= 355.9A, Ic= 309.8A, In= 0.09A, Ig= 2.4A
|  | 25.04.19 | 7:58 | 25.04.19 | 8:06 | 0.0055556 | 0 | 8 | [5 empty] | O/C,E/F (Y PH), Ia= 221.5A, Ib= 654.1A, Ic=161.2A, In= 0.1A, Ig= 686.26A
|  | 25.04.19 | 23:41 | 25.04.19 | 23:46 | 0.0034722 | 0 | 5 | [5 empty] | O/C (R PH), Ia= 421A, Ib= 361A, Ic=277.7A, In= 0.03A, Ig= 3.12A
|  | 21.04.19 | 15.35 | 21.04.19 | 16:15 | 0.027778 | 0 | 40 | [5 empty] | SOURCE FAILURE but Restricted P/S availed from Karanjia GSS end.
|  | 19.04.19 | 1:36 | 19.04.19 | 1:55 | 0.013194 |  |  | 0 | 19 |  |  |  | O/C (R PH), Ia=384.A, Ib=1453A, Ic=1123A, IN=0.0, IG =11.0
|  | 19.04.19 | 14:28 | 19.04.19 | 14:30 | 0.02 |  |  | 0 | 2 |  |  |  | O/C (R PH), Ia=219.1A, Ib=1870.0A, Ic39.074A, In=6.68A
|  | 13.04.19 | 5:25 | 13.04.19 | 5:34 | 0.00625 | 0 | 9 | [5 empty] | O/C (B PH), Ia=1532A, Ib= 1037A, Ic=366.2, In= 0.00A, Ig= 4.9A
|  | 12.04.19 | 16:38 | 12.04.19 | 16:40 | 0.0013889 | 0 | 2 | [5 empty] | E/F WITH DP Z, Ia=80.81A, Ib=1.019KA, Ic=55.05, In=1.052KA, Ig= 1.05KA
|  | 07.04.19 | 16:01 | 07.04.19 | 16:03 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R PH), Ia=396.4A, Ib= 376.04A, Ic=388.84A Ig=51.8A
|  | 02.04.19 | 0.275 | 02.04.19 | 6:39 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R PH), Ia=414.1A, Ib= 341.7A, Ic=285.9A, In= 0.09A, Ig= 5.73A
|  | 02.04.19 | 3:02 | 02.04.19 | 3:05 | 0.0020833 | 0 | 3 | [5 empty] | O/C (B PH), Ia= 435.38A, Ib= 355.4A, Ic=333.3A, In= 0.0A, Ig= 3.94A
|  | 01.04.19 | 20:53 | 01.04.19 | 20:55 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R PH), Ia= 421.5A, Ib= 364.0A, Ic= 388.0A, In= 0.05A, Ig= 5.56A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
367 | 132 kV Purusottampur-Chatrapur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.45 | 8760 | 100% | 0 | 135342
368 | 132kV Rairakhole- Rairakhole RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.5 | 8760 | 100% | 0 | 30660
369 | 132kV Rairangapur- Karanjia |  |  |  |  | 0.28264 | 17 | 52 | [7 empty] | 71.54 | 8760 | 99.8% | 1278.1813 | 626690.4
|  | 13.11.19 | 8:39 | 13.11.19 | 9:34 | 0.038194 |  |  | 0 | 55 |  |  |  | Tripped at both ends due to B-phase LA of 132KV Bangiriposi- PGCIL line burst at PGCIL end. Rairangpur Grid avail P/ S from Karanjia Grid end and Bangiriposi avail P/S from Rairangpur.
|  | 14.06.19 | 16:40 | 14.06.19 | 17:34 | 0.0375 | 0 | 54
|  | 03.06.19 | 20:03 | 03.06.19 | 21:53 | 0.076389 | 1 | 50 | [5 empty] | Tripped from PG end
|  | 06.10.19 | 12:06 | 06.10.19 | 12:16 | 0.0069444 | 0 | 10 | [5 empty] | At Baripada end: O/C & E/F , Zone-I, DISTANCE -O.5 Km,IL-E,IL1=2.92KAmp, IL2=0.22 Kamp,IL3=O.34KAmp
|  | 07.04.19 | 14:17 | 07.04.19 | 17:15 | 0.12361 | 2 | 58 | [5 empty] | O/C in B- phase Ib-8.59KA,Z1-405m. Then ICT was tripped at PGCIL end & Restricted P/S restored from Rairangpur end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
370 | 132kV Rajgangpur-OCL |  |  |  |  | 0.063889 | 13 | 32 | [7 empty] | 0.5 | 8760 | 99.85% | 6.7667 | 4380
|  | 23.11.19 | 5:25 | 23.11.19 | 6:13 | 0.033333 | 0 | 48 | [5 empty] | At Rajgangpur end; Tripped on E/F (Y-ph)
|  | 13.11.19 | 14:13 | 13.11.19 | 14:20 | 0.0048611 | 0 | 7 | [5 empty] | At Rajgangpur end. Tripped on E/F
|  | 22.09.19 | 17:25 | 22.09.19 | 17:38 | 0.0090278 | 0 | 13 | [5 empty] | Tripped at Rajgangpur end.
|  | 16.08.19 | 12:58 | 16.08.19 | 13:16 | 0.0125 | 0 | 18 | [5 empty] | Tripped on E/F at Rajgangpur end
|  | 25.04.19 | 12:55 | 25.04.19 | 13:01 | 0.0041667 | 0 | 6 | [5 empty] | At Rajgangpur end - DP OPERATED, FAULT- L1 TO L2, FAULT CURRENT- L1-1.529kA, L2-1.396kA, LOC- 99.176, ZONE-2
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
371 | 132kV Rajgangapur-Rajgangapur (T) |  |  |  |  | 0.013194 | 0 | 19 | [7 empty] | 4.2 | 8760 | 100% | 1.33 | 36792
|  | 22.09.19 | 17:25 | 22.09.19 | 17:38 | 0.0090278 | 0 | 13 | [5 empty] | Tripped at Rajgangpur end.
|  | 25.04.19 | 12:55 | 25.04.19 | 13:01 | 0.0041667 | 0 | 6 | [5 empty] | DP OPERATED, FAULT- L1 TO L2, FAULT CURRENT- L1-1.529kA, L2-1.396kA, LOC- 99.176, ZONE-2
372 | 132kV Rajgangpur-Rourkela |  |  |  |  | 0.0041667 | 0 | 6 | [7 empty] | 27.5 | 8760 | 100% | 2.75 | 240900
|  | 25.04.19 | 12:55 | 25.04.19 | 13:01 | 0.0041667 | 0 | 6 | [5 empty] | DP OPERATED, FAULT- L1 TO L2, FAULT CURRENT- L1-1.529kA, L2-1.396kA, LOC- 99.176, ZONE-2
373 | 132kV Ransinghpur-Badagada |  |  |  |  | 1900-01-14 00:32 | 13 | 29 | [7 empty] | 34.63 | 8760 | 99.85% | 466.9278 | 303358.8
|  | 07.03.20 | 6:12 | 07.03.20 | 6:22 | 0.0069444 | 0 | 10 | [5 empty] | At Chandaka end: Tripped
|  | 11.12.19 | 3:27 | 11.12.19 | 4:02 | 0.024306 | 0 | 35 | [5 empty] | Chandaka end-Tripped
|  | 19.11.19 | 12:07 | 19.11.19 | 12:19 | 0.0083333 | 0 | 12 | [5 empty] | DP relay operated at Ransinghpur end
|  | 15.05.19 | 17:30 | 15.05.19 | 17:33 | 0.0020833 | 0 | 3 | [5 empty] | At Kesura-Tripped
|  | 15.05.19 | 17:57 | 15.05.19 | 18:14 | 0.011806 | 0 | 17 | [5 empty] | At Kesura-Tripped
|  | 31.05.19 | 21:07 | 31.05.19 | 21:16 | 0.00625 | 0 | 9 | [5 empty] | At Kesura-Tripped
|  | 27.05.19 | 14:42 | 27.05.19 | 14:45 | 0.0020833 | 0 | 3 | [5 empty] | At Kesura-Tripped
|  | 03.05.19 | 11:05 | 07.05.19 | 21:50 | 1900-01-03 10:05 |  |  |  |  | 106 | 45 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'. 132 kV Choudwar supply extended to Chandaka Grid by means of special arrangement through 132 kV Bidanasi -BPPL ckt
|  | 03.05.19 | 11:00 | 13.05.19 | 20:58 | 1900-01-09 12:58 |  |  |  |  | 252 | 58 |  | Tripped due to tower collapse during extreme severe cyclone 'FANI'.132kv Ranasinghpur-Kesura Line charged at 20:58 Hrs on 13.05.19 & 132Kv Kesura-Nimapara Line charged at 19:23Hrs on 16.05.19
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
374 | 132kV TS Alloys-Choudwar |  |  |  |  | 0.46319 | 5 | 32 | [7 empty] | 23 | 8760 | 99.94% | 127.2667 | 201480
|  | 19.03.20 | 19:38 | 19.03.20 | 19:52 | 0.0097222 | 0 | 14 | [5 empty] | At both end-Tripped on E/F, O/C
|  | 09.03.20 | 11:45 | 09.03.20 | 17:03 | 0.22083 | 5 | 18 | [5 empty] | At both end-Tripped on E/F, O/C
|  | 03.05.19 | 12:40 | 03.05.19 | 18:15 | 0.23264 |  |  |  |  | 5 | 35 |  | Tripped at Paradeep end during extreme severe cyclone 'FANI
375 | 132kV TS Alloys-Arati Steel |  |  |  |  | 0.23264 | 0 | 0 | [7 empty] | 17.678 | 8760 | 100% | 0 | 154859.28
|  | 03.05.19 | 12:40 | 03.05.19 | 18:15 | 0.23264 |  |  |  |  | 5 | 35 |  | Tripped at Paradeep end during extreme severe cyclone 'FANI
376 | 132kV Rayagada-Akhusingh |  |  |  |  | 0.48333 | 0 | 34 | [7 empty] | 50 | 8760 | 99.99% | 28.3333 | 438000
|  | 25.07.19 | 17:25 | 25.07.19 | 17:59 | 0.023611 | 0 | 34 | [5 empty] | At Jayanagar end: Z-I, Dist.-27.25 k.m. R,Y,B ph.-E/F
|  | 16.07.19 | 15:47 | 16.07.19 | 23:02 | 0.30208 |  |  | 0 | 9 |  |  |  | Tripped at Machhkund end.Akhusingh GS/S availed P/S from Digapahandi end at 15:56 Hrs.15:55-Rayagada load C.O to TVL Auto.
|  | 17.07.19 | 17:10 | 17.07.19 | 20:57 | 0.15764 |  |  | 0 | 29 |  |  |  | Tripped at Machhkund end: At 17:39 - Akhusingh, Paralakhemundi availed P/S from Digapahandi end.Rayagada Load C/O to TVL Load at 17:46 Hrs.
377 | 132kV Rayagada-Rayagada Traction |  |  |  |  | 0.52778 | 13 | 42 | [7 empty] | 2.646 | 8760 | 99.84% | 36.2502 | 23178.96
|  | 31.03.20 | 11:29 | 31.03.20 | 11:34 | 00:05 | 0 | 5 | [5 empty] | At Therubali end: BGT, Ib=3.56 kA
|  | 20.06.19 | 19:08 | 20.06.19 | 19:30 | 0.015278 | 0 | 21 | [5 empty] | #2, #3 running Units of Indravati PH tripped
|  | 25.07.19 | 17:25 | 25.07.19 | 17:59 | 0.023611 | 0 | 34 | [5 empty] | At Jayanagar end: Z-I, Dist.-27.25 k.m. R,Y,B ph.-E/F
|  | 16.07.19 | 15:47 | 16.07.19 | 23:02 | 0.30208 |  |  | 0 | 8 |  |  |  | Tripped at Machhkund end.Akhusingh GS/S availed P/S from Digapahandi end at 15:56 Hrs.15:55-Rayagada load C.O to TVL Auto.
|  | 17.07.19 | 17:10 | 17.07.19 | 20:57 | 0.15764 |  |  | 0 | 36 |  |  |  | Tripped at Machhkund end: At 17:39 - Akhusingh, Paralakhemundi availed P/S from Digapahandi end.Rayagada Load C/O to TVL Load at 17:46 Hrs.
|  | 27.05.19 | 17:50 | 27.05.19 | 18:32 | 0.029167 | 0 | 42 | [5 empty] | Grid disturbance at Therubali S/s but circuit was not tripped at Therubali end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
378 | 132kV Rayagada-VBC Ferro |  |  |  |  | 0.48333 | 0 | 34 | [7 empty] | 0.3 | 8760 | 99.99% | 0.17 | 2628
|  | 25.07.19 | 17:25 | 25.07.19 | 17:59 | 0.023611 | 0 | 34 | [5 empty] | At Jayanagar end: Z-I, Dist.-27.25 k.m. R,Y,B ph.-E/F
|  | 16.07.19 | 15:47 | 16.07.19 | 23:02 | 0.30208 |  |  | 0 | 8 |  |  |  | Tripped at Machhkund end.Akhusingh GS/S availed P/S from Digapahandi end at 15:56 Hrs.15:55-Rayagada load C.O to TVL Auto.
|  | 17.07.19 | 17:10 | 17.07.19 | 20:57 | 0.15764 |  |  | 0 | 36 |  |  |  | Tripped at Machhkund end: At 17:39 - Akhusingh, Paralakhemundi availed P/S from Digapahandi end.Rayagada Load C/O to TVL Load at 17:46 Hrs.
379 | 132kV Rourkela-Bhalulata |  |  |  |  | 0.74722 | 17 | 56 | [7 empty] | 24.29 | 8760 | 99.8% | 435.6007 | 212780.4
|  | 19.09.19 | 3:45 | 19.09.19 | 21:41 | 0.74722 | 17 | 56 | [5 empty] | At Rourkela end:- B ph.-E/F, FC-1.64 KA, Dist.-57.8 k.m.
380 | 132kV Bolangir- ACME |  |  |  |  | 0.68125 | 24 | 36 | [7 empty] | 22.02 | 8760 | 99.72% | 541.692 | 192895.2
|  | 15.03.20 | 17:07 | 15.03.20 | 17:10 | 0.0020833 | 0 | 3 | [5 empty] | At Bolangir end: Tripped on E/F
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:35 | 12.02.20 | 17:40 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir New end: Tripped on O/C
|  | 12.02.20 | 16:12 | 12.02.20 | 17:18 | 0.045833 | 1 | 6 | [5 empty] | At Bolangir end: Tripped
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 23.11.19 | 16:37 | 23.11.19 | 16:50 | 0.0090278 | 0 | 13 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 23.11.19 | 16:11 | 23.11.19 | 16:20 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 20.11.19 | 11:02 | 20.11.19 | 11:16 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end :-Tripped (dropping conductor of wave trap b-ph at sadeipali)
|  | 30.11.19 | 10:12 | 30.11.19 | 10:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped due to Bolangir-Solar Incomer Breaker Tripped.
|  | 01.11.19 | 6:37 | 01.11.19 | 6:47 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 25.10.19 | 4:44 | 25.10.19 | 5:40 | 0.038889 | 0 | 56 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 19:30 | 22.10.19 | 19:42 | 0.0083333 | 0 | 12 | [5 empty] | P/S failure from Bolangir New end
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | At Bolangir New S/S -Tripped due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:43 | 0.15208 | 0 | 49 | [5 empty] | Tripped at Bolangir New end( Jumper snapped at GSS Sadeipali). Availed P/S at 07:53 Hrs from Kesinga end
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:36 | 0.018056 | 0 | 26 | [5 empty] | Tripped at New Bolangir end.
|  | 26.09.19 | 0:10 | 26.09.19 | 0:30 | 0.013889 | 0 | 20 | [5 empty] | P/S Failure from Bolangir New end
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 23.09.19 | 18:42 | 23.09.19 | 19:12 | 0.020833 | 0 | 30 | [5 empty] | Tripped on overload at New Bolangir end.
|  | 23.09.19 | 15:53 | 23.09.19 | 16:00 | 0.0048611 | 0 | 7 | [5 empty] | Tripped at New Bolangir end.
|  | 17.09.19 | 19:13 | 17.09.19 | 20:56 | 0.071528 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 10.09.19 | 19:45 | 10.09.19 | 20:29 | 0.030556 | 0 | 42 | [5 empty] | At Bolangir New end-Tripped on directional O/C and E/F.
|  | 21.08.19 | 18:58 | 21.08.19 | 19:06 | 0.0055556 | 0 | 8 | [5 empty] | At Bolangir New-Tripped due to 132KV LA failure
|  | 21.08.19 | 18:32 | 21.08.19 | 18:46 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 13.08.19 | 5:53 | 13.08.19 | 6:09 | 0.011111 | 0 | 16 | [5 empty] | P/S failure from New Bolangir end
|  | 12.08.19 | 5:07 | 12.08.19 | 5:19 | 0.0083333 | 0 | 12 | [5 empty] | 160 MVA Auto TRF-02 tripped
|  | 21.08.19 | 18:32 | 21.08.19 | 18:42 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:30 | 0.015972 | 0 | 23 | [5 empty] | P/S failure from Bolangir New due to over loading
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 11.08.19 | 5:09 | 11.08.19 | 5:27 | 0.0125 | 0 | 18 | [5 empty] | Tripped on E/F at Bolangir end
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 01.05.19 | 16:28 | 01.05.19 | 16:30 | 0.0013889 | 0 | 2 | [5 empty] | Due to ckt overloading ; Tripped from New Bolangir
|  | 29.04.19 | 17:28 | 29.04.19 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 29.04.19 | 16:45 | 29.04.19 | 16:48 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 12.04.19 | 21:37 | 12.04.19 | 21:50 | 0.0090278 | 0 | 13 | [5 empty] | Source Failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
381 | 132 kV ACME - Tusura |  |  |  |  | 0.70764 | 25 | 14 | [7 empty] | 24.419 | 8760 | 99.71% | 616.1728 | 213910.44
|  | 15.03.20 | 17:07 | 15.03.20 | 17:10 | 0.0020833 | 0 | 3 | [5 empty] | At Bolangir end: Tripped on E/F
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:35 | 12.02.20 | 17:40 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir New end: Tripped on O/C
|  | 12.02.20 | 16:12 | 12.02.20 | 17:18 | 0.045833 | 1 | 6 | [5 empty] | At Bolangir end: Tripped
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 23.11.19 | 16:37 | 23.11.19 | 16:50 | 0.0090278 | 0 | 13 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 23.11.19 | 16:11 | 23.11.19 | 16:20 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 20.11.19 | 11:02 | 20.11.19 | 11:16 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end :-Tripped (dropping conductor of wave trap b-ph at sadeipali)
|  | 30.11.19 | 10:12 | 30.11.19 | 10:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped due to Bolangir-Solar Incomer Breaker Tripped.
|  | 01.11.19 | 6:37 | 01.11.19 | 6:47 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 25.10.19 | 4:44 | 25.10.19 | 5:40 | 0.038889 | 0 | 56 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 19:30 | 22.10.19 | 19:42 | 0.0083333 | 0 | 12 | [5 empty] | P/S failure from Bolangir New end
|  | 22.10.19 | 6:09 | 22.10.19 | 6:42 | 0.022917 | 0 | 33 | [5 empty] | Tripped at ACME end due to snapping of line conductor
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | At Bolangir New S/S -Tripped due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 11:07 | 01.10.19 | 11:12 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at ACME end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:43 | 0.15208 | 0 | 49 | [5 empty] | Tripped at Bolangir New end( Jumper snapped at GSS Sadeipali). Availed P/S at 07:53 Hrs from Kesinga end
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:36 | 0.018056 | 0 | 26 | [5 empty] | Tripped at New Bolangir end.
|  | 26.09.19 | 0:10 | 26.09.19 | 0:30 | 0.013889 | 0 | 20 | [5 empty] | P/S Failure from Bolangir New end
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 23.09.19 | 18:42 | 23.09.19 | 19:12 | 0.020833 | 0 | 30 | [5 empty] | Tripped on overload at New Bolangir end.
|  | 23.09.19 | 15:53 | 23.09.19 | 16:00 | 0.0048611 | 0 | 7 | [5 empty] | Tripped at New Bolangir end.
|  | 17.09.19 | 19:13 | 17.09.19 | 20:56 | 0.071528 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 10.09.19 | 19:45 | 10.09.19 | 20:29 | 0.030556 | 0 | 42 | [5 empty] | At Bolangir New end-Tripped on directional O/C and E/F.
|  | 21.08.19 | 18:58 | 21.08.19 | 19:06 | 0.0055556 | 0 | 8 | [5 empty] | At Bolangir New-Tripped due to 132KV LA failure
|  | 21.08.19 | 18:32 | 21.08.19 | 18:46 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 13.08.19 | 5:53 | 13.08.19 | 6:09 | 0.011111 | 0 | 16 | [5 empty] | P/S failure from New Bolangir end
|  | 12.08.19 | 5:07 | 12.08.19 | 5:19 | 0.0083333 | 0 | 12 | [5 empty] | 160 MVA Auto TRF-02 tripped
|  | 21.08.19 | 18:32 | 21.08.19 | 18:42 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:30 | 0.015972 | 0 | 23 | [5 empty] | P/S failure from Bolangir New due to over loading
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 11.08.19 | 5:09 | 11.08.19 | 5:27 | 0.0125 | 0 | 18 | [5 empty] | Tripped on E/F at Bolangir end
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 01.05.19 | 16:28 | 01.05.19 | 16:30 | 0.0013889 | 0 | 2 | [5 empty] | Due to ckt overloading ; Tripped from New Bolangir
|  | 29.04.19 | 17:28 | 29.04.19 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 29.04.19 | 16:45 | 29.04.19 | 16:48 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 12.04.19 | 21:37 | 12.04.19 | 21:50 | 0.0090278 | 0 | 13 | [5 empty] | Source Failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
382 | 132 kV Tusura- Saintala |  |  |  |  | 0.87569 | 29 | 16 | [7 empty] | 22.779 | 8760 | 99.67% | 666.6654 | 199544.04
|  | 15.03.20 | 17:07 | 15.03.20 | 17:10 | 0.0020833 | 0 | 3 | [5 empty] | At Bolangir end: Tripped on E/F
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:35 | 12.02.20 | 17:40 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir New end: Tripped on O/C
|  | 12.02.20 | 16:12 | 12.02.20 | 17:18 | 0.045833 | 1 | 6 | [5 empty] | At Bolangir end: Tripped
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 23.11.19 | 16:37 | 23.11.19 | 16:50 | 0.0090278 | 0 | 13 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 23.11.19 | 16:11 | 23.11.19 | 16:20 | 0.00625 | 0 | 9 | [5 empty] | At Kesinga-Tripped on Overloading.
|  | 20.11.19 | 11:02 | 20.11.19 | 11:16 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end :-Tripped (dropping conductor of wave trap b-ph at sadeipali)
|  | 30.11.19 | 10:12 | 30.11.19 | 10:18 | 0.0041667 | 0 | 6 | [5 empty] | Tripped due to Bolangir-Solar Incomer Breaker Tripped.
|  | 01.11.19 | 6:37 | 01.11.19 | 6:47 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end :-Tripped on O/C
|  | 25.10.19 | 10:24 | 25.10.19 | 10:38 | 0.0097222 | 0 | 14 | [5 empty] | Tripped at Tushra end
|  | 25.10.19 | 4:44 | 25.10.19 | 5:40 | 0.038889 | 0 | 56 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 22.10.19 | 19:30 | 22.10.19 | 19:42 | 0.0083333 | 0 | 12 | [5 empty] | P/S failure from Bolangir New end
|  | 22.10.19 | 6:09 | 22.10.19 | 6:42 | 0.022917 | 0 | 33 | [5 empty] | Tripped at ACME end due to snapping of line conductor
|  | 14.10.19 | 10:28 | 14.10.19 | 10:50 | 0.015278 | 0 | 22 | [5 empty] | At Bolangir New S/S -Tripped due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 11:07 | 01.10.19 | 11:12 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at ACME end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:43 | 0.15208 | 0 | 49 | [5 empty] | Tripped at Bolangir New end( Jumper snapped at GSS Sadeipali). Availed P/S at 07:53 Hrs from Kesinga end
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:36 | 0.018056 | 0 | 26 | [5 empty] | Tripped at New Bolangir end.
|  | 26.09.19 | 0:10 | 26.09.19 | 0:30 | 0.013889 | 0 | 20 | [5 empty] | P/S Failure from Bolangir New end
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 23.09.19 | 18:42 | 23.09.19 | 19:12 | 0.020833 | 0 | 30 | [5 empty] | Tripped on overload at New Bolangir end.
|  | 23.09.19 | 15:53 | 23.09.19 | 16:00 | 0.0048611 | 0 | 7 | [5 empty] | Tripped at New Bolangir end.
|  | 17.09.19 | 19:13 | 17.09.19 | 20:56 | 0.071528 | 0 | 50 | [5 empty] | At Bolangir New end:-Hand Tripped
|  | 27.09.19 | 4:03 | 27.09.19 | 4:11 | 0.0055556 | 0 | 8 | [5 empty] | At Saintala-Tripped on E/F
|  | 27.09.19 | 7:56 | 27.09.19 | 8:01 | 0.0034722 | 0 | 5 | [5 empty] | At Saintala-Tripped on Over load
|  | 27.09.19 | 21:41 | 27.09.19 | 21:50 | 0.00625 | 0 | 9 | [5 empty] | At Saintala-Tripped on Over load
|  | 19.09.19 | 12:47 | 19.09.19 | 12:57 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga-Tripped and At Tusura end also DP operated.
|  | 10.09.19 | 19:45 | 10.09.19 | 20:29 | 0.030556 | 0 | 42 | [5 empty] | At Bolangir New end-Tripped on directional O/C and E/F.
|  | 05.09.19 | 17:23 | 05.09.19 | 17:34 | 0.0076389 | 0 | 11 | [5 empty] | At Kesinga-Tripped on over load
|  | 21.08.19 | 18:58 | 21.08.19 | 19:06 | 0.0055556 | 0 | 8 | [5 empty] | At Bolangir New-Tripped due to 132KV LA failure
|  | 21.08.19 | 18:32 | 21.08.19 | 18:46 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 13.08.19 | 5:53 | 13.08.19 | 6:09 | 0.011111 | 0 | 16 | [5 empty] | P/S failure from New Bolangir end
|  | 21.08.19 | 18:32 | 21.08.19 | 18:42 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:30 | 0.015972 | 0 | 23 | [5 empty] | P/S failure from Bolangir New due to over loading
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 11.08.19 | 5:09 | 11.08.19 | 5:27 | 0.0125 | 0 | 18 | [5 empty] | Tripped on E/F at Bolangir end
|  | 23.07.19 | 16:26 | 23.07.19 | 16:29 | 0.0020833 | 0 | 3 | [5 empty] | Failure from Source
|  | 20.07.19 | 17:37 | 20.07.19 | 17:41 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir New-Tripped
|  | 20.07.19 | 19:22 | 20.07.19 | 19:28 | 0.0041667 | 0 | 6 | [5 empty] | At Bolangir New-Tripped
|  | 21.07.19 | 9:19 | 21.07.19 | 9:57 | 0.026389 | 0 | 38 | [5 empty] | Tripped from ACME on O/C
|  | 20.06.19 | 9:51 | 20.06.19 | 10:02 | 0.0076389 | 0 | 11 | [5 empty] | 132KV Tushra-Saintal line didn’t stand. Power supply resumed from kesinga
|  | 13.06.19 | 16:55 | 13.06.19 | 16:58 | 0.0020833 | 0 | 3 | [5 empty] | 132KV Saintala I/C pullout
|  | 09.06.19 | 15:55 | 09.06.19 | 16:23 | 0.019444 | 0 | 28 | [5 empty] | 132KV Y-phase CT brust at GSS Saintala
|  | 05.06.19 | 18:00 | 05.06.19 | 18:06 | 0.0041667 | 0 | 6 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 03.06.19 | 6:58 | 03.06.19 | 7:08 | 0.0069444 | 0 | 10 | [5 empty] | Earth fault on Y-phase located at Saintala
|  | 02.06.19 | 23:03 | 02.06.19 | 23:26 | 0.015972 | 0 | 23 | [5 empty] | Earth fault located at bolangir
|  | 16.04.19 | 16:34 | 16.04.19 | 16:40 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on directional o/c and e/f.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 28.05.19 | 16:58 | 28.05.19 | 17:07 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Tusura; LBB Trip Supervision
|  | 17.05.19 | 16:06 | 17.05.19 | 16:12 | 0.0041667 | 0 | 6 | [5 empty] | Tripped from ACME;Due to ckt overloading (B Phase O/C on 132KV Kesinga O/G Feeder)
|  | 01.05.19 | 16:28 | 01.05.19 | 16:30 | 0.0013889 | 0 | 2 | [5 empty] | Due to ckt overloading ; Tripped from New Bolangir
|  | 20.04.19 | 20:12 | 20.04.19 | 20:16 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F, Tushra 132KV I/C Pullout; Tripped from Tusura
|  | 28.04.19 | 16:27 | 28.04.19 | 17:48 | 0.05625 | 1 | 21 | [5 empty] | B-Phase Jumper snapped at Gantry point of 132 Saintala O/G Feeder, Tripped from Tusura end.
|  | 21.04.19 | 8:24 | 21.04.19 | 8:40 | 0.011111 | 0 | 16 | [5 empty] | 132KV Saintala O/G Feeder Tripped on E/F, Tripped from Tusura end.
|  | 29.04.19 | 17:28 | 29.04.19 | 17:31 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 29.04.19 | 16:45 | 29.04.19 | 16:48 | 0.0020833 | 0 | 3 | [5 empty] | Source Failure
|  | 12.04.19 | 21:37 | 12.04.19 | 21:50 | 0.0090278 | 0 | 13 | [5 empty] | Source Failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
383 | 132kV Salipur-Kendrapara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.4 | 8760 | 100% | 0 | 301344
384 | 132kV Samagara-Puri |  |  |  |  | 1900-01-10 14:23 | 0 | 0 | [7 empty] | 3.99 | 8760 | 100% | 0 | 34952.4
|  | 03.05.19 | 8:50 | 14.05.19 | 23:13 | 1900-01-10 14:23 |  |  |  |  | 278 | 23 |  | Tripped during extreme severe cyclone 'FANI; 132 KV Nimapara -Puri fdr charged at 23:13 Hrs on 14.05.19.
385 | 132kV Sambalpur-Shyam DRI |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.31 | 8760 | 100% | 0 | 256755.6
386 | 132kV Shamuka-Puri |  |  |  |  | 1900-01-16 13:39 | 15 | 13 | [5 empty] | At Shamuka end : Tripped |  | 17.3 | 8760 | 99.83% | 263.2483 | 151548
|  | 10.02.20 | 9:12 | 10.02.20 | 393:22 | 0.00625 | 0 | 9 | [5 empty] | At Shamuka end : Tripped
|  | 10.01.20 | 9:15 | 10.01.20 | 9:24 | 0.00625 | 0 | 9 | [5 empty] | Tripped at Nimapara end
|  | 05.01.20 | 16:30 | 06.01.20 | 14:24 | 0.9125 | 0 | 24 | [5 empty] | At Nimapara end: Zone-2, (Y-ph to Earth), Distance= 24.69 KM (LA of 132 kV Shamuka - Puri fdr burst). P/s availed from Khurdha end.
|  | 10.06.19 | 20:15 | 10.06.19 | 23:30 | 0.13542 | 3 | 15 | [5 empty] | R-Ph. jumper snapping at Loc. No.-20. No supply to Puri during the period as it was the source
|  | 27.10.19 | 10:05 | 27.10.19 | 10:21 | 0.011111 | 0 | 16 | [5 empty] | Tripped E/F at Samuka end
|  | 03.05.19 | 8:50 | 19.05.19 | 19:56 | 1900-01-15 11:56 |  |  |  |  | 395 | 56 |  | Tripped during extreme severe cyclone 'FANI due to tower collapse
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
387 | 132kV Shyam DRI-Aryan Ispat |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.2 | 8760 | 100% | 0 | 36792
388 | 132kV Aryan Ispat - Lapanga |  |  |  |  | 0.21111 | 2 | 2 | [7 empty] | 3.9 | 8760 | 99.98% | 7.93 | 34164
|  | 07.12.19 | 15:15 | 07.12.19 | 16:24 | 0.047917 | 1 | 2 | [5 empty] | At Lapanga end-132KV & 33KV BLACKOUT AT GRID SS LAPANGA DUE TO 132KV B-PH CT OF 160MVA AUTO TFR-I BURSTED
|  | 20.08.19 | 19:46 | 20.08.19 | 20:52 | 0.045833 | 1 | 0 | [5 empty] | 132/33KV GRID BLACK OUT AT LAPANGA DUE TO SNAPPING OF R-PH CROSS BUS OF 132KV BURLA CKT-II & FELL ON 132KV MAIN BUS AND RESERVE BUS AT GRID SS LAPANGA AND CAUSE TRIPPING OF Power TRF.
|  | 05.06.19 | 15:45 | 07.06.19 | 18:34 | 0.11736 |  |  | 0 | 32 |  |  |  | Tripped at both ends. CT failure at Aryan end.At 16:17 Hrs, Aryan Ispat availed P/S from Sambalpur GSS.
389 | 132kV Lapanga-SMC Power |  |  |  |  | 0.11736 | 14 | 23 | [7 empty] | 4.7 | 8760 | 99.84% | 67.6017 | 41172
|  | 07.12.19 | 15:15 | 07.12.19 | 16:30 | 0.052083 | 1 | 2 | [5 empty] | At Lapanga end-132KV & 33KV BLACKOUT AT GRID SS LAPANGA DUE TO 132KV B-PH CT OF 160MVA AUTO TFR-I BURSTED
|  | 17.09.19 | 13:55 | 17.09.19 | 14:16 | 0.014583 | 0 | 21 | [5 empty] | At Lapanga end:- Y ph.-E/F, Zone-I, FC-13.76 KA, Dist.-1.2 k.m.
|  | 20.08.19 | 19:46 | 20.08.19 | 20:59 | 0.050694 | 1 | 0 | [5 empty] | 132/33KV GRID BLACK OUT AT LAPANGA DUE TO SNAPPING OF R-PH CROSS BUS OF 132KV BURLA CKT-II & FELL ON 132KV MAIN BUS AND RESERVE BUS AT GRID SS LAPANGA AND CAUSE TRIPPING OF Power TRF.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
390 | 132kV SMC Power-Kuchinda |  |  |  |  | 0.026389 | 0 | 6 | [7 empty] | 53.33 | 8760 | 100% | 5.333 | 467170.8
|  | 23.09.19 | 16:12 | 23.09.19 | 16:31 | 0.013194 | 0 | 1 | [5 empty] | Tripped at Kuchinda end but Availed P/S from Rajgangpur end at 16:13 Hrs
|  | 17.09.19 | 13:57 | 17.09.19 | 14:16 | 0.013194 | 0 | 5 | [5 empty] | Tripped at Kuchinda end but Availed P/S from Rajgangpur end at 14:02 Hrs
391 | 132 kV Sonepur - Boudh |  |  |  |  | 0.92083 | 34 | 6 | [7 empty] | 51.05 | 8760 | 99.61% | 1740.805 | 447198
|  | 28.03.20 | 10:48 | 28.03.20 | 10:51 | 0.0020833 | 0 | 3 | [5 empty] | At Bolangir end: Tripped
|  | 20.03.20 | 4:38 | 20.03.20 | 4:41 | 0.0020833 | 0 | 3 | [5 empty] | At Bolangir end: Tripped
|  | 17.03.20 | 17:36 | 17.03.20 | 17:46 | 0.0069444 | 0 | 10 | [5 empty] | At Bolangir end: Tripped
|  | 04.03.20 | 16:48 | 04.03.20 | 16:52 | 0.0027778 | 0 | 4 | [5 empty] | At Bolangir end: Tripped
|  | 16.02.20 | 8:03 | 16.02.20 | 8:31 | 0.019444 | 0 | 28 | [5 empty] | At Bolangir end: Tripped
|  | 13.02.20 | 16:40 | 13.02.20 | 17:05 | 0.017361 | 0 | 25 | [5 empty] | At Bolangir end: Tripped
|  | 13.02.20 | 17:51 | 13.02.20 | 17:58 | 0.0048611 | 0 | 7 | [5 empty] | At Bolangir end: Tripped
|  | 13.02.20 | 8:03 | 13.02.20 | 8:17 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 13.02.20 | 15:05 | 13.02.20 | 15:19 | 0.0097222 | 0 | 14 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:34 | 12.02.20 | 17:46 | 0.0083333 | 0 | 12 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 16:15 | 12.02.20 | 16:36 | 0.014583 | 0 | 21 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 17:05 | 12.02.20 | 17:10 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir end: Tripped
|  | 12.02.20 | 8:12 | 12.02.20 | 8:33 | 0.014583 | 0 | 21 | [5 empty] | At Bolangir end: Tripped
|  | 03.02.20 | 14:52 | 03.02.20 | 15:04 | 0.0083333 | 0 | 12 | [5 empty] | At Bolangir end: Tripped
|  | 30.01.20 | 10:50 | 30.01.20 | 11:01 | 0.0076389 | 0 | 11 | [5 empty] | At Bolangir end-Tripped
|  | 30.01.20 | 16:22 | 30.01.20 | 16:27 | 0.0034722 | 0 | 5 | [5 empty] | At Bolangir end-Tripped
|  | 28.01.20 | 12:53 | 28.01.20 | 13:25 | 0.022222 | 0 | 32 | [5 empty] | At Bolangir end-Tripped
|  | 28.01.20 | 12:53 | 28.01.20 | 13:22 | 0.020139 | 0 | 29 | [5 empty] | At Sadeipali-Tripped on distance protection as well as on directional o/c and e/f.
|  | 27.01.20 | 18:00 | 27.01.20 | 18:30 | 0.020833 | 0 | 30 | [5 empty] | At Bolangir end-Tripped
|  | 13.01.20 | 6:46 | 13.01.20 | 7:06 | 0.013889 | 0 | 20 | [5 empty] | At Bolangir New end-Tripped on directional o/c and e/f
|  | 30.12.19 | 13:36 | 30.12.19 | 13:45 | 0.00625 | 0 | 9 | [5 empty] | At Bolangir end-Tripped
|  | 29.10.19 | 10:20 | 29.10.19 | 10:25 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on O/C at Bolangir end
|  | 26.10.19 | 11:06 | 26.10.19 | 11:18 | 0.0083333 | 0 | 12 | [5 empty] | Source failure
|  | 26.10.19 | 13:53 | 26.10.19 | 13:57 | 0.0027778 | 0 | 4 | [5 empty] | Source failure
|  | 25.10.19 | 4:44 | 25.10.19 | 5:38 | 0.0375 | 0 | 54 | [5 empty] | Source failure(Grid disturbance at Sadeipali )
|  | 24.10.19 | 4:46 | 24.10.19 | 5:38 | 0.036111 | 0 | 52 | [5 empty] | Source failure
|  | 23.10.19 | 13:06 | 23.10.19 | 13:11 | 0.0034722 | 0 | 5 | [5 empty] | Tripped at Sonepur end
|  | 23.10.19 | 11:07 | 23.10.19 | 11:20 | 0.0090278 | 0 | 13 | [5 empty] | Tripped at Sonepur end
|  | 22.10.19 | 14:34 | 22.10.19 | 15:20 | 0.031944 | 0 | 46 | [5 empty] | P/S failure from Bolangir New end
|  | 16.10.19 | 8:00 | 16.10.19 | 8:30 | 0.020833 | 0 | 30 | [5 empty] | P/S failure from Bolangir New end
|  | 14.10.19 | 10:28 | 14.10.19 | 10:49 | 0.014583 | 0 | 21 | [5 empty] | P/S failure at Bolangir New S/S due to conductor snapping of Auto Transformer jumper at Bolangir New S/Y.
|  | 04.10.19 | 18:06 | 04.10.19 | 18:11 | 0.0034722 | 0 | 5 | [5 empty] | P/S failure from Bolangir New end
|  | 01.10.19 | 7:04 | 01.10.19 | 10:44 | 0.15278 | 3 | 40 | [5 empty] | Tripped at Bolangir New end ( Jumper snapped at GSS Sadeipali)
|  | 27.09.19 | 8:14 | 27.09.19 | 8:32 | 0.0125 | 0 | 18 | [5 empty] | Tripped at New Bolangir end.
|  | 27.09.19 | 14:10 | 27.09.19 | 14:39 | 0.020139 | 0 | 29 | [5 empty] | Tripped at New Bolangir end.
|  | 25.09.19 | 23:09 | 25.09.19 | 23:26 | 0.011806 | 0 | 17 | [5 empty] | At Sonepur end-Tripped
|  | 25.09.19 | 23:40 | 26.09.19 | 0:10 | 0.020833 | 0 | 30 | [5 empty] | At Sonepur end-Tripped
|  | 24.09.19 | 18:50 | 24.09.19 | 19:08 | 0.0125 | 0 | 18 | [5 empty] | P/S Failure from Bolangir New end
|  | 17.09.19 | 19:12 | 17.09.19 | 21:00 | 0.075 | 1 | 48 | [5 empty] | P/S Failure from Bolangir New end
|  | 13.08.19 | 5:53 | 13.08.19 | 6:33 | 0.027778 | 0 | 40 | [5 empty] | Tripped at Bolangir New end. P/s availed from Kesinga.
|  | 21.08.19 | 18:58 | 21.08.19 | 19:07 | 0.00625 | 0 | 9 | [5 empty] | At Bolangir New-Tripped due to over loading
|  | 12.08.19 | 5:07 | 12.08.19 | 5:19 | 0.0083333 | 0 | 12 | [5 empty] | 160 MVA Auto TRF-02 tripped
|  | 12.08.19 | 5:54 | 12.08.19 | 6:10 | 0.011111 | 0 | 16 | [5 empty] | At Bolangir end:- Tripped on O/C
|  | 31.05.19 | 18:57 | 31.05.19 | 19:10 | 0.0090278 | 0 | 13 | [5 empty] | AC Supply failed from Bolangir
|  | 30.05.19 | 19:00 | 30.05.19 | 19:06 | 0.0041667 | 0 | 6 | [5 empty] | AC Supply failed from Bolangir
|  | 29.04.19 | 12:29 | 29.04.19 | 12:32 | 0.0020833 | 0 | 3 | [5 empty] | Tripped
|  | 27.04.19 | 20:01 | 27.04.19 | 20:06 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on directional o/c.
|  | 16.04.19 | 1:03 | 16.04.19 | 1:49 | 0.031944 | 0 | 46 | [5 empty] | Tripped on directional o/c and e/f. (LA Brust on 132KV Sadeipali-Bolangir O/G Fdr)
|  | 12.04.19 | 14:15 | 12.04.19 | 14:29 | 0.0097222 | 0 | 14 | [5 empty] | Tripped on directional o/c and e/f.
|  | 07.04.19 | 11:50 | 07.04.19 | 13:36 | 0.073611 | 1 | 46 | [5 empty] | Trip Relay Faulty
|  | 06.04.19 | 15:48 | 06.04.19 | 16:42 | 0.0375 | 0 | 54 | [5 empty] | Trip Relay Faulty
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
392 | 132kV Soro-Bhadrak |  |  |  |  | 0 | 0 | 0 | [7 empty] | 46.215 | 8760 | 100% | 0 | 404843.4
393 | 132kV Sunabeda-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13 | 8760 | 100% | 0 | 113880
394 | 132kV Sunabeda-HAL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.7 | 8760 | 100% | 0 | 6132
395 | 132kV Sunabeda-Pottangi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.4 | 8760 | 100% | 0 | 292584
396 | 132kV Tarkera-Kalunga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.88 | 8760 | 100% | 0 | 139108.8
397 | 132kV Tarkera-Budhipadar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 110 | 8760 | 100% | 0 | 963600
398 | 132kV Tarkera-Chhend-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.165 | 8760 | 100% | 0 | 54005.4
399 | 132kV Tarkera-Chhend-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.165 | 8760 | 100% | 0 | 54005.4
400 | 132kV Tarkera-Rajgangpur-I |  |  |  |  | 0.13611 | 0 | 19 | [7 empty] | 24.5 | 8760 | 100% | 7.7583 | 214620
|  | 22.09.19 | 17:25 | 22.09.19 | 17:38 | 0.0090278 | 0 | 13 | [5 empty] | At Rajgangpur end:- 64N operated at Rajgangpur end
|  | 25.04.19 | 12:55 | 25.04.19 | 13:10 | 0.010417 | 0 | 6 | [5 empty] | TRIPPED ON OVER CUIRRENT R-PHASE
|  | 03.05.19 | 10:25 | 03.05.19 | 12:51 | 0.10139 |  |  |  |  | 2 | 26 |  | Tripped (Due to Cyclone Fani)
401 | 132kV Tarkera-Rajgangpur-II |  |  |  |  | 0.015278 | 0 | 19 | [7 empty] | 24.5 | 8760 | 100% | 7.7583 | 214620
|  | 22.09.19 | 17:25 | 22.09.19 | 17:38 | 0.0090278 | 0 | 13 | [5 empty] | Tripped at Tarkera end
|  | 25.04.19 | 12:55 | 25.04.19 | 13:04 | 0.00625 | 0 | 6 | [5 empty] | DP OPERATED, FAULT- L1 TO L2, FAULT CURRENT- L1-3.70kA, L2-3.68kA,L3-0.03kA, LOC- 28.704KM, ZONE-2
402 | 132kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
403 | 132kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
404 | 132kV Tarkera-Rourkela-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
405 | 132kV Tarkera-Rourkela-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
406 | 132kV Tarkera-Rourkela-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
407 | 132kV Tentulikhunti-Dabugaon ckt |  |  |  |  | 0.97431 | 35 | 23 | [7 empty] | 43.2 | 8760 | 99.6% | 1528.56 | 378432
|  | 29.03.20 | 11:15 | 29.03.20 | 17:04 | 0.24236 | 5 | 49 | [5 empty] | At Jaynagar end: Tripped on B-ph E/F, Zone -1
|  | 23.03.20 | 21:12 | 23.03.20 | 21:17 | 0.0034722 | 0 | 5 | [5 empty] | At Jaynagar end: Tripped
|  | 29.02.20 | 14:04 | 29.02.20 | 14:15 | 0.0076389 | 0 | 11 | [5 empty] | At Jaynagar end: Tripped on E/F
|  | 25.02.20 | 18:21 | 25.02.20 | 18:39 | 0.0125 | 0 | 18 | [5 empty] | At Jayanagar end: Tripped
|  | 14.02.20 | 9:11 | 14.02.20 | 9:30 | 0.013194 | 0 | 19 | [5 empty] | At Jayanagar end: Tripped
|  | 12.02.20 | 12:08 | 12.02.20 | 12:17 | 0.00625 | 0 | 9 | [5 empty] | At Jayanagar end: Tripped
|  | 09.12.19 | 8:25 | 09.12.19 | 8:44 | 0.013194 | 0 | 19 | [5 empty] | Jayangar end-Tripped
|  | 09.12.19 | 15:08 | 09.12.19 | 15:21 | 0.0090278 | 0 | 13 | [5 empty] | Jayangar end-Tripped
|  | 21.04.19 | 1:00 | 21.04.19 | 11:26 | 0.43472 | 10 | 26 | [5 empty] | Line fault at Tentulikhunti-Dabugaon 132 kV line
|  | 20.04.19 | 18:26 | 20.04.19 | 24:00 | 0.23194 | 5 | 34 | [5 empty] | Line fault at Tentulikhunti-Dabugaon 132 kV line
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
408 | 132kV Tentulikhunti-Vento Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.192 | 8760 | 100% | 0 | 36721.92
409 | 132kV Therubali-IMFAL |  |  |  |  | 0.029167 | 0 | 40 | [7 empty] | 2 | 8760 | 99.99% | 1.3333 | 17520
|  | 27.05.19 | 17:50 | 27.05.19 | 18:32 | 0.029167 | 0 | 40 | [5 empty] | Grid disturbance at Therubali S/s but circuit was not tripped at Therubali end.
410 | 132kV Therubali-JK Pur |  |  |  |  | 0.044444 | 1 | 1 | [7 empty] | 9.68 | 8760 | 99.99% | 9.8413 | 84796.8
|  | 20.06.19 | 19:08 | 20.06.19 | 19:30 | 0.015278 | 0 | 21 | [5 empty] | #2, #3 running Units of Indravati PH tripped
|  | 27.05.19 | 17:50 | 27.05.19 | 18:32 | 0.029167 | 0 | 40 | [5 empty] | Grid disturbance at Therubali S/s but circuit was not tripped at Therubali end.
411 | 132kV Therubali-Rayagada |  |  |  |  | 0.015278 | 0 | 26 | [7 empty] | 20 | 8760 | 100% | 8.6667 | 175200
|  | 31.03.20 | 11:29 | 31.03.20 | 11:34 | 00:05 | 0 | 5 | [5 empty] | At Therubali end: BGT, Ib=3.56 kA
|  | 20.06.19 | 19:08 | 20.06.19 | 19:30 | 0.015278 | 0 | 21 | [5 empty] | #2, #3 running Units of Indravati PH tripped
412 | 132kV Therubali-Muniguda-Vedant Alumina |  |  |  |  | 0.57431 | 16 | 12 | [7 empty] | 76.951 | 8760 | 99.82% | 1246.6062 | 674090.76
|  | 04.03.20 | 16:01 | 04.03.20 | 16:13 | 00:12 | 0 | 12 | [5 empty] | At Therubali end: Zone-2, B-N, 27.99KM ,Ib=3.6 kA
|  | 25.02.20 | 22:23 | 25.02.20 | 22:42 | 0.013194 | 0 | 19 | [5 empty] | At Therubali end: Zone-2,ABT, 31.84Km, Ia= 3.3kA, Ib= 3.1kA
|  | 13.02.20 | 16:37 | 13.02.20 | 16:41 | 0.0027778 | 0 | 4 | [5 empty] | At Therubali end: Tripped on O/ C
|  | 13.01.20 | 14:38 | 13.01.20 | 15:11 | 0.022917 | 0 | 33 | [5 empty] | At Therubali end: Tripped on O/C, D/P Zone-2,B-N, 28.23Km
|  | 02.01.20 | 11:52 | 02.01.20 | 12:12 | 0.013889 | 0 | 20 | [5 empty] | At Therubali end: Tripped on O/C.
|  | 02.10.19 | 16:48 | 02.10.19 | 16:59 | 0.0076389 | 0 | 11 | [5 empty] | At Therubali end: A-N,Z-1, 18.3KM
|  | 30.09.19 | 17:05 | 30.09.19 | 17:20 | 0.010417 | 0 | 15 | [5 empty] | At Theruvali-Tripped
|  | 19.06.19 | 23:33 | 20.06.19 | 9:23 | 0.40972 | 0 | 5 | [5 empty] | At Kesinga -Tripped on D/P ( JUMPER SNAPPED AT LOC-1 OF 132 KV KESINGA-BPT-JUNAGARH LILO LINE)
|  | 10.06.19 | 17:26 | 10.06.19 | 17:33 | 0.0048611 | 0 | 7 | [5 empty] | At Theruvali-Tripped on O/C
|  | 05.06.19 | 21:55 | 05.06.19 | 22:02 | 0.0048611 | 0 | 7 | [5 empty] | At Theruvali-Tripped on O/C
|  | 08.06.19 | 20:56 | 08.06.19 | 20:59 | 0.0020833 | 0 | 3 | [5 empty] | At Theruvali-Tripped on O/C
|  | 03.06.19 | 10:15 | 03.06.19 | 10:44 | 0.020139 | 0 | 29 | [5 empty] | At Theruvali-Tripped (Distance relay indication at Lanjigarh end)
|  | 02.06.19 | 20:40 | 02.06.19 | 20:54 | 0.0097222 | 0 | 14 | [5 empty] | At Theruvali-Tripped
|  | 27.05.19 | 17:50 | 27.05.19 | 18:32 | 0.029167 | 0 | 40 | [5 empty] | Grid disturbance at Therubali S/s but circuit was not tripped at Therubali end.
|  | 29.05.19 | 2:32 | 29.05.19 | 2:38 | 0.0041667 | 0 | 6 | [5 empty] | 132 KV P/S FAIL; TRIPPED FROM THERUVALLI END NAD SUPPLY WAS RESTORED
|  | 27.05.19 | 18:13 | 27.05.19 | 18:30 | 0.011806 | 0 | 17 | [5 empty] | 132 KV P/S FAIL; TRIPPED FROM THERUVALLI END SUPPLY AVAILED FROM BOLANGIR
|  | 27.05.19 | 19:26 | 27.05.19 | 19:31 | 0.0034722 | 0 | 5 | [5 empty] | 132 KV P/S FAIL; INCOMING SUPPLY CHANGED OVER TO THERUVALLI
|  | 29.04.19 | 2:34 | 29.04.19 | 2:39 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped on over load.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
413 | 132kV TTPS-Angul |  |  |  |  | 1899-12-31 09:23 | 21 | 8 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 16 | 8760 | 99.76% | 338.1333 | 140160
|  | 31.05.19 | 20:04 | 31.05.19 | 21:31 | 0.060417 | 1 | 54 | [5 empty] | DP, Fault abs dist 10.863KM, Fault Loop L1N at Angul end.
|  | 27.04.19 | 17:31 | 28.04.19 | 23:55 | 0.26667 | 2 | 20 | [5 empty] | At angul-Tripped with DP relay (Fault Abs Dist 12.859 KM , Fault Loop L2-N)
|  | 23.04.19 | 15:32 | 23.04.19 | 18:33 | 0.12569 | 0 | 36 | [5 empty] | At Angul -\Tripped with DP relay (Fault Abs Dist 12.506KM , Fault Loop L2-N) But Power availed from Chainpal End.
|  | 21.04.19 | 13:10 | 21.04.19 | 13:27 | 0.011111 | 0 | 32 | [5 empty] | Tripped with DP relay (Fault Abs Dist 3.125 KM , Fault Loop L2-N)
|  | 13.04.19 | 13:30 | 14.04.19 | 11:45 | 0.92708 | 3 | 46 | [5 empty] | At Angul-Tripped on E/F with DP relay (Fault Abs Dist 10.197 KM , Fault Loop L3-N). Power availed from Chainpal end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
414 | 132kV TTPS-Chainpal-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
415 | 132kV TTPS-Chainpal-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
416 | 132kV TTPS-Chainpal-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
417 | 132kV TTPS-Jabamayee FAlloys |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.276 | 8760 | 100% | 0 | 668177.76
418 | 132kV TTPS-OPCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31 | 8760 | 100% | 0 | 271560
419 | 132kV Tusura-Vento Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.8 | 8760 | 100% | 0 | 129648
420 | 132kV Vedant Alumina-Kesinga |  |  |  |  | 0.59792 | 16 | 46 | [7 empty] | 58.077 | 8760 | 99.81% | 973.7577 | 508754.52
|  | 04.03.20 | 16:01 | 04.03.20 | 16:13 | 00:12 | 0 | 12 | [5 empty] | At Therubali end: Zone-2, B-N, 27.99KM ,Ib=3.6 kA
|  | 25.02.20 | 22:23 | 25.02.20 | 22:42 | 0.013194 | 0 | 19 | [5 empty] | At Therubali end: Zone-2,ABT, 31.84Km, Ia= 3.3kA, Ib= 3.1kA
|  | 13.02.20 | 16:37 | 13.02.20 | 16:41 | 0.0027778 | 0 | 4 | [5 empty] | At Therubali end: Tripped on O/ C
|  | 13.01.20 | 14:38 | 13.01.20 | 15:11 | 0.022917 | 0 | 33 | [5 empty] | At Therubali end: Tripped on O/C, D/P Zone-2,B-N, 28.23Km
|  | 02.01.20 | 11:52 | 02.01.20 | 12:12 | 0.013889 | 0 | 20 | [5 empty] | At Therubali end: Tripped on O/C.
|  | 20.06.19 | 18:20 | 20.06.19 | 18:54 | 0.023611 | 0 | 34
|  | 02.10.19 | 16:48 | 02.10.19 | 16:59 | 0.0076389 | 0 | 11 | [5 empty] | At Therubali end: A-N,Z-1, 18.3KM
|  | 30.09.19 | 17:05 | 30.09.19 | 17:20 | 0.010417 | 0 | 15 | [5 empty] | At Theruvali-Tripped
|  | 19.06.19 | 23:33 | 20.06.19 | 9:23 | 0.40972 | 0 | 5 | [5 empty] | At Kesinga -Tripped on D/P ( JUMPER SNAPPED AT LOC-1 OF 132 KV KESINGA-BPT-JUNAGARH LILO LINE)
|  | 10.06.19 | 17:26 | 10.06.19 | 17:33 | 0.0048611 | 0 | 7 | [5 empty] | At Theruvali-Tripped on O/C
|  | 05.06.19 | 21:55 | 05.06.19 | 22:02 | 0.0048611 | 0 | 7 | [5 empty] | At Theruvali-Tripped on O/C
|  | 08.06.19 | 20:56 | 08.06.19 | 20:59 | 0.0020833 | 0 | 3 | [5 empty] | At Theruvali-Tripped on O/C
|  | 03.06.19 | 10:15 | 03.06.19 | 10:44 | 0.020139 | 0 | 29 | [5 empty] | At Theruvali-Tripped (Distance relay indication at Lanjigarh end)
|  | 02.06.19 | 20:40 | 02.06.19 | 20:54 | 0.0097222 | 0 | 14 | [5 empty] | At Theruvali-Tripped
|  | 27.05.19 | 17:50 | 27.05.19 | 18:32 | 0.029167 | 0 | 40 | [5 empty] | Grid disturbance at Therubali S/s but circuit was not tripped at Therubali end.
|  | 29.05.19 | 2:32 | 29.05.19 | 2:38 | 0.0041667 | 0 | 6 | [5 empty] | 132 KV P/S FAIL; TRIPPED FROM THERUVALLI END NAD SUPPLY WAS RESTORED
|  | 27.05.19 | 18:13 | 27.05.19 | 18:30 | 0.011806 | 0 | 17 | [5 empty] | 132 KV P/S FAIL; TRIPPED FROM THERUVALLI END SUPPLY AVAILED FROM BOLANGIR
|  | 27.05.19 | 19:26 | 27.05.19 | 19:31 | 0.0034722 | 0 | 5 | [5 empty] | 132 KV P/S FAIL; INCOMING SUPPLY CHANGED OVER TO THERUVALLI
|  | 29.04.19 | 2:34 | 29.04.19 | 2:39 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali-Tripped on over load.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
(17): 7076.071; (20): 80572.4948; (21): 136362818.628 | 0.00059087 | 99.9409
ICTs / AUTOS
1 | New Duburi 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
2 | New Duburi 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
3 | Lapanga 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
4 | Lapanga 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 3876 | 100% | 0 | 3052350
5 | Meramundali 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
6 | Meramundali 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
7 | Mendhasal 315MVA ICT – I |  |  |  |  | 0.60486 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
|  | 03.05.19 | 8:00 | 03.05.19 | 22:31 | 0.60486 |  |  |  |  | 14 | 31 |  | Hand Tripped due to Severe Cyclonic storm FANI
8 | Mendhasal 315MVA ICT – II |  |  |  |  | 0.58681 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
|  | 03.05.19 | 8:00 | 03.05.19 | 22:05 | 0.58681 |  |  |  |  | 14 | 5 |  | Hand Tripped due to Severe Cyclonic storm FANI
9 | Mendhasal 315MVA ICT – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
10 | Aska New 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 7284 | 100% | 0 | 2913600
11 | Aska New 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 6612 | 100% | 0 | 2644800
12 | Atri 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
13 | Atri 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
14 | Balasore 160MVA Auto – I |  |  |  |  | 0.023611 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
15 | Balasore 160MVA Auto – II |  |  |  |  | 0.023611 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
16 | Balasore 160MVA Auto – III |  |  |  |  | 0.023611 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 03.05.19 | 7:05 | 03.05.19 | 7:39 | 0.023611 |  |  |  |  | 0 | 34 |  | Due to Severe Cyclonic Storm FANI, Fault occurs In 132Kv Udala Fdr And Its Bkr Did Not Trip, All The Three Auto Transformer Tripped At That Time. Which Caused The Interruption In All The Feeders
17 | Baragarh New 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
18 | Baragarh New 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
19 | Bidanasi 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
20 | Bidanasi 100MVA Auto - II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
21 | Bidanasi 160MVA Auto - III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
22 | Bhadrak 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
23 | Bhadrak 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
24 | Bhadrak 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
25 | Bhadrak 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
26 | New Bolangir 160MVA Auto I |  |  |  |  | 0.026389 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 17.09.19 | 19:12 | 17.09.19 | 19:50 | 0.026389 |  |  | 0 | 21 |  |  |  | At Bolangir New end:- Tripped on Dir O/C, E/F (Due to snapping of conductor at PGCIL end)
27 | New Bolangir 160 MVA Auto II |  |  |  |  | 0.10139 | 0 | 42 | [6 empty] | 160 |  | 8760 | 99.99% | 280 | 3504000
|  | 17.09.19 | 19:12 | 17.09.19 | 20:56 | 0.072222 |  |  | 0 | 21 |  |  |  | At Bolangir New end:- Tripped on Dir O/C, E/F (Due to snapping of conductor at PGCIL end)
|  | 10.09.19 | 19:45 | 10.09.19 | 20:27 | 0.029167 | 0 | 42 | [5 empty] | At Bolangir New end-Tripped on directional O/C and E/F.
28 | New Bolangir 160 MVA Auto III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 1428 | 100% | 0 | 571200
29 | Bhanjanagar 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
30 | Bhanjanagar 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
31 | Budhipadar 160MVA Auto – I |  |  |  |  | 0.036111 | 0 | 50 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 12.06.19 | 0:37 | 13.06.19 | 1:29 | 0.036111 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
32 | Budhipadar 160MVA Auto – II |  |  |  |  | 0.0375 | 0 | 50 | [6 empty] | 160 |  | 8760 | 99.99% | 333.3333 | 3504000
|  | 12.06.19 | 0:37 | 13.06.19 | 1:31 | 0.0375 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
33 | Chandaka 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
34 | Chandaka 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
35 | Chandaka 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
36 | Chandaka 160MVA Auto – IV |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
37 | Chandaka-B 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
38 | Chandaka-B 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
39 | Cuttack 160MVA Auto – I |  |  |  |  | 1900-01-01 08:45 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 03.05.19 | 11:23 | 05.05.19 | 20:08 | 1900-01-01 08:45 |  |  |  |  | 56 | 45 |  | During severe cyclone,the said feeder tripped on O/C OPTD,VT Fuse fail, V/F warn,V/F trip ,86 A & 86B (Collapsed)
40 | Cuttack 100MVA Auto – II |  |  |  |  | 0.0083333 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
|  | 03.05.19 | 11:23 | 03.05.19 | 11:35 | 0.0083333 |  |  |  |  | 0 | 12 |  | During severe cyclone,the said feeder tripped on O/C OPTD,VT Fuse fail, V/F warn,V/F trip ,86 A & 86B (Collapsed)
41 | Duburi 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
42 | Duburi 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
43 | Duburi 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
44 | Jayanagar 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
45 | Jayanagar 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
46 | Jayapatna 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 6300 | 100% | 0 | 2520000
47 | Jayapatna 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 1644 | 100% | 0 | 657600
48 | Joda 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
49 | Joda 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
50 | Joda 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
51 | Katapalli 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
52 | Katapalli 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
53 | Katapalli 160MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
54 | Lapanga 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
55 | Lapanga 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
56 | Mendhasal 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
57 | Mendhasal 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
58 | Meramundali 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
59 | Meramundali 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
60 | Meramundali 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
61 | Narendrapur 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
62 | Narendrapur 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
63 | Narendrapur 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
64 | Paradeep 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
65 | Paradeep 160 MVA Auto – II |  |  |  |  | 0.017361 | 0 | 25 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 17.01.20 | 16:41 | 17.01.20 | 17:06 | 0.017361 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F
66 | Paradeep 160 MVA Auto – III |  |  |  |  | 0.85417 | 0 | 25 | [6 empty] | 160 |  | 8760 | 100% | 166.6667 | 3504000
|  | 17.01.20 | 16:41 | 18.01.20 | 13:21 | 0.85417 | 0 | 25 | [5 empty] | At Paradeeep end: Trippped on E/F,O/C RYB PH,Differential R-Y operated ( 132 kV B-ph LA failure)
67 | Samagara 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
68 | Samagara 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
69 | Tarkera 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
70 | Tarkera 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
71 | Tarkera 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
72 | Tarkera 100MVA Auto – IV |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
73 | Therubali 100MVA Auto – I |  |  |  |  | 0.05 | 0 | 40 | [6 empty] | 100 |  | 8760 | 99.99% | 166.6667 | 2190000
|  | 27.05.19 | 17:50 | 27.05.19 | 19:02 | 0.05 | 0 | 40 | [5 empty] | Transformer tripped due to disturbance at Therubali Grid S/s.
74 | Therubali 100MVA Auto – II |  |  |  |  | 0.029167 | 0 | 40 | [6 empty] | 100 |  | 8760 | 99.99% | 166.6667 | 2190000
|  | 27.05.19 | 17:50 | 27.05.19 | 18:32 | 0.029167 | 0 | 40 | [5 empty] | R- Phase Over current due to disturbance at Therubali Grid S/s.
75 | Therubali 160MVA Auto –III |  |  |  |  | 0.16806 | 0 | 40 | [6 empty] | 160 |  | 8760 | 99.99% | 266.6667 | 3504000
|  | 27.05.19 | 17:50 | 27.05.19 | 21:52 | 0.16806 | 0 | 40
11775
(16): Sub-total (ICTs / Autos); (20): 1380; (21): 222065700 | 6.2144e-06 | 99.9994
[15 empty] | TOTAL (Lines, ICTs & Autos) |  |  |  | 81952.4948 | 358428518.628
[11 empty] | NAFY |  | [ Σ ( OH l x Cktkm l x NSC l ) + Σ ( OH t x MVA t x 2.5 )] [THY x { Σ (Cktkm l x NSC l ) +Σ (MVA t x 2.5 ) } ] | [5 empty] | 0.00022864
[13 empty] | 100 - (100 X NAFY) | [5 empty] | 99.9771
Note on B95: Added newly
Note on B99: Added newly
Note on B102: Added newly
Note on B119: Added newly
Note on Q170: Confrimed from CP Branch
Note on Q173: Confrimed from CP Branch
Note on B188: Earlier it was Bidanasi- Chandaka
Note on Q197: OPTCL: Chandaka-B LILO charged on 28.03.2017
Note on Q200: OPTCL: Chandaka-B LILO charged on 28.03.2017
Note on B313: Part of 400kV Meramundali Mendhasala Ckt - II
Note on Q313: Data confirmed from Sri DPJena
Note on Q334: Atri LILO ckt is added.
Note on Q338: Atri LILO ckt is added.
Note on Q340: Atri LILO ckt is added.
Note on Q345: Atri LILO ckt is added.
Note on Q348: Atri LILO ckt is added.
Note on Q354: user: 76.22
Note on Q384: 47.884 LILO value was not added
Note on Q785: Bhubaneswar Power on LILO charged on 17.02.2016
Note on Q1014: Kalunga LILO is charged on 07.09.2015
Note on H1134: Multified by factor 2
Note on H1136: Multified by factor 2
Note on Q1181: GRID STEEL on LILO charged on 24.12.2015
Note on R1364: commissioned on 28.02.2018
Note on Q2479: distance between Narendrapur-Balugaon and Balugaon- Khurda added.
Note on Q2898: =1.33+17.43+15.87 km
Note on Q3107: Lapanga LILO charged on 25.11.2015
Note on Q3109: Lapanga LILO charged on 25.11.2015
Note on Q3186: Kalunga LILO is charged on 07.09.2015
Note on R3307: charged on 10.8.2018
Note on R3309: charged on 21.08.2019
Note on R3352: commissioned on 24.09.2017
Note on B3442: Charged on 24.06.2012

## ANNEXURE-III
Transmission Element Data as on 31/03/17 ANNEXURE-III
Name of the Transmission licensee: ODISHA POWER TRANSMISSION CORPORATION LTD
a) Transmission Lines
SL. NO | Name of the Transmission line |  | Voltage Level(in KV) | S/C or D/C | Line Length (in Ckt KM) | Conductor Type & Characteristics | No. of Sub-Conductor (NSC) | Date of Comm. / Comm. Operation
| From | To
1 | Rengali-Kuchei PG | Kolaghat PG | 400 | S/C | 483 | Twin Moose | 2 | 1995
2 | Indravati PH | Indravati PG | 400 | S/C | 7.4 | Twin Moose | 2 | 03/09/09
3 | Meramundal I | Mendhasal I | 400 | D/C | 100.45 | Twin Moose | 2 | 31/01/10
4 | Meramundal I | Mendhasal II | 400 | D/C | 100.45 | Twin Moose | 2 | 31/01/10
3 | Meramundal I | New Duburi | 400 | D/C | 96.8 | Twin Moose | 2 | 19/10/15
4 | Meramundal I | New Duburi | 400 | D/C | 96.8 | Twin Moose | 2 | 19/10/15
5 | Meramundali | JSPL I | 400 | D/C | 75.83 | Twin Moose | 2 | 16/09/2010
6 | Meramundali | JSPL II | 400 | D/C | 75.83 | Twin Moose | 2 | 16/09/2010
7 | Balimela | U. Seluru | 220 | S/C | 24.76 | Single Zebra | 1 | 1982
8 | Balimela | Jayanagar-I | 220 | D/C | 92.072 | Single Zebra | 1 | 1974
9 | Balimela | Jayanagar-II | 220 | D/C | 92.072 | Single Zebra | 1 | 1974
10 | Balimela | Jayanagar-III | 220 | S/C | 93.46 | Single Zebra | 1 | 1982
11 | Balasore | Bhadrak | 220 | S/C | 80 | Single Zebra | 1 | 22.10.08
12 | Barkote | Tarkera | 220 | D/C | 97.48 | Single Zebra | 1 | 1979
13 | Bhanjanagar | Meramundali-I | 220 | D/C | 134.135 | Single Zebra | 1 | 1974
14 | Bhanjanagar | Meramundali-II | 220 | D/C | 134.135 | Single Zebra | 1 | 1974
15 | Bhanjanagar | Mendhasal | 220 | D/C | 156 | Single Zebra | 1 | 1989
16 | Bhanjanagar | Nayagarh | 220 | D/C | 46.47 | Single Zebra | 1 | 1989
17 | Bidanasi | Mendhasal ckt II | 220 | D/C | 15 | Single Zebra | 1 | 2008
18 | Bidanasi | Mendhasal ckt III | 220 | D/C | 15 | Single Zebra | 1 | 2008
19 | Bisra | Tarkera-I | 220 | D/C | 15.335 | Single Zebra | 1 | 1993
20 | Bisra | Tarkera-II | 220 | D/C | 15.335 | Single Zebra | 1 | 1993
21 | Budhipadar | IbTPS -I | 220 | D/C | 26 | Single Zebra | 1 | 1995
22 | Budhipadar | IbTPS -II | 220 | D/C | 26 | Single Zebra | 1 | 1995
23 | Budhipadar | IbTPS -III | 220 | D/C | 25.38 | Single Zebra | 1 | 1995
24 | Budhipadar | IbTPS -IV | 220 | D/C | 25.38 | Single Zebra | 1 | 07/01/08
25 | Budhipadar | Raigarh | 220 | D/C | 60 | Single Zebra | 1 | 1995
26 | Budhipadar | Korba-II | 220 | D/C | 60 | Single Zebra | 1 | 1995
27 | Budhipadar | Katapalli -I | 220 | D/C | 61.679 | Single Zebra | 1 | 20/04/07
28 | Budhipadar | Katapalli -II | 220 | D/C | 61.769 | Single Zebra | 1 | 20/04/07
29 | Budhipadar | SPS I | 220 | D/C | 13.424 | Single Zebra | 1 | 07/11/07
30 | Budhipadar | SPS II | 220 | D/C | 13.424 | Single Zebra | 1 | 07/11/07
31 | Budhipadar | Bhusan Steel-I | 220 | D/C | 14.92 | Single Zebra | 1 | 06/08/05
32 | Budhipadar | Bhusan Steel-II | 220 | D/C | 14.92 | Single Zebra | 1 | 06/08/05
33 | Chandaka | Mendhasal ckt I | 220 | D/C | 19 | Single Zebra | 1 | 2008
34 | Chandaka | Mendhasal ckt II | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
35 | Chandaka | Mendhasal ckt III | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
36 | Chandaka | Mendhasal ckt IV | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
37 | Duburi | Duburi (New) ckt I | 220 | D/C | 11.056 | Single Zebra | 1 | 1996
38 | Duburi | Duburi (New) ckt II | 220 | D/C | 11.056 | Single Zebra | 1 | 1997
39 | Duburi | NINL | 220 | S/C | 6 | Single Zebra | 1 | 01/06/2000
40 | Duburi (New) | Balasore | 220 | D/C | 137.36 | Single Zebra | 1 | 1997
41 | Indravati PH | Therubali-I | 220 | D/C | 86.2 | Single Zebra | 1 | 26/05/01
42 | Indravati PH | Therubali-II | 220 | D/C | 86.2 | Single Zebra | 1 | 26/05/01
43 | Indravati PH | Therubali-III | 220 | D/C | 91 | Single Zebra | 1 | 22/07/05
44 | Indravati PH | Therubali-IV | 220 | D/C | 91 | Single Zebra | 1 | 22/07/05
45 | Jayanagar | Jeyapore PG-I | 220 | D/C | 7.23 | Single Zebra | 1 | 1990
46 | Jayanagar | Jeyapore PG-II | 220 | D/C | 7.23 | Single Zebra | 1 | 1990
47 | Jayanagar | Laxmipur ckt I | 220 | D/C | 65 | Single Zebra | 1 | 1974
48 | Jayanagar | Laxmipur Ckt II | 220 | D/C | 65 | Single Zebra | 1 | 1974
49 | Jindal | Jamsedpur DVC | 220 | S/C | 20.8 | Single Zebra | 1 | 1985
50 | Joda | RCPur PG | 220 | S/C | 15.5 | Single Zebra | 1 | 1985
51 | Joda | Jindal | 220 | S/C | 21 | Single Zebra | 1 | 1985
52 | Joda | TSIL Ckt. | 220 | S/C | 7.3 | Single Zebra | 1 | 23/03/07
53 | Katapali | Bolangir-I | 220 | D/C | 117.85 | Single Zebra | 1 | 2010
54 | Katapali | Bolangir-II | 220 | D/C | 117.85 | Single Zebra | 1 | 2011
55 | Kuchei PG | Balasore Ckt I | 220 | D/C | 76.859 | Single Zebra | 1 | 03/10/07
56 | Kuchei PG | Balasore Ckt II | 220 | D/C | 76.859 | Single Zebra | 1 | 03/10/07
57 | Laxmipur | Therubali Ckt I | 220 | D/C | 56 | Single Zebra | 1 | 1974
58 | Laxmipur | Therubali Ckt II | 220 | D/C | 56 | Single Zebra | 1 | 1974
59 | Laxmipur | Utkal Alu,ina Ckt I | 220 | D/C | 31.04 | Single Zebra | 1 | 2014
60 | Laxmipur | Utkal Alu,ina Ckt II | 220 | D/C | 31.04 | Single Zebra | 1 | 2014
61 | Mendhasal | Bidanasi-II | 220 | D/C | 32.99 | Single Zebra | 1 | 2003
62 | Meramundali | Bidanasi-II | 220 | D/C | 90.94 | Single Zebra | 1 | 2003
63 | Meramundali | Duburi-I | 220 | D/C | 95.556 | Single Zebra | 1 | 1995
64 | Meramundali | Duburi-II | 220 | D/C | 95.556 | Single Zebra | 1 | 1995
65 | Meramundali | BSSL (Bhusan) I | 220 | D/C | 2.4 | Single Zebra | 1 | 22/08/06
66 | Meramundali | BSSL (Bhusan) II | 220 | D/C | 2.4 | Single Zebra | 1 | 22/08/06
67 | NALCO | Meramundali-I | 220 | D/C | 11.465 | Single Zebra | 1 | 27/08/04
68 | NALCO | Meramundali-II | 220 | D/C | 11.465 | Single Zebra | 1 | 27/08/04
69 | NALCO | Rengali PH | 220 | S/C | 71.337 | Single Zebra | 1 | 1984
70 | Nayagarh | Mendhasal | 220 | D/C | 90 | Single Zebra | 1 | 1989
71 | Narendrapur | Mendhasal I | 220 | D/C | 75 | Single Zebra | 1 | 02/07/2010
72 | New Duburi | Paradeep Ckt-I | 220 | D/C | 113.433 | Single Zebra | 1 | 06/05/09
73 | New Duburi | Paradeep Ckt-II | 220 | D/C | 113.433 | Single Zebra | 1 | 06/05/09
74 | Rengali GD | Rengali PG -I | 220 | D/C | 0.4 | Single Zebra | 1 | 1997
75 | Rengali GD | Rengali PG -II | 220 | D/C | 0.4 | Single Zebra | 1 | 1997
76 | Rengali GD | Chandiposh (T) | 220 | D/C | 162.08 | Single Zebra | 1 | 26/03/2000
77 | Rengali GD | Barkote | 220 | D/C | 55 | Single Zebra | 1 | 1979
78 | Rengali PH | Rengali GD -I | 220 | D/C | 5 | Single Zebra | 1 | 1997
79 | Rengali PH | Rengali GD -II | 220 | D/C | 5 | Single Zebra | 1 | 1997
80 | Rengali PH | STPS | 220 | S/C | 29.5 | Single Zebra | 1 | 1984
81 | STPS (Kaniha) | TTPS | 220 | S/C | 34.5 | Single Zebra | 1 | 1984
82 | STPS | Meramundali-I | 220 | D/C | 42.52 | Single Zebra | 1 | 1995
83 | STPS | Meramundali-II | 220 | D/C | 42.52 | Single Zebra | 1 | 1995
84 | Tarkera | Budhipadar-I | 220 | D/C | 109 | Single Zebra | 1 | 1995
85 | Tarkera | Budhipadar-II | 220 | D/C | 109 | Single Zebra | 1 | 1995
86 | Tarkera | RSP I | 220 | D/C | 10 | Single Zebra | 1 | 2008
87 | Tarkera | RSP I | 220 | D/C | 10 | Single Zebra | 1 | 1995
88 | Therubali | Narendrapur-I | 220 | D/C | 196 | Single Zebra | 1 | 2013
89 | Therubali | Narendrapur-II | 220 | D/C | 196 | Single Zebra | 1 | 20/08/2001
90 | Therubali | Bhanjanagar-I | 220 | D/C | 171.46 | Single Zebra | 1 | 1974
91 | Therubali | Bhanjanagar-II | 220 | D/C | 171.46 | Single Zebra | 1 | 1974
92 | TTPS | Meramundali-I | 220 | D/C | 11.155 | Single Zebra | 1 | 1979
93 | TTPS | Meramundali-II | 220 | D/C | 11.155 | Single Zebra | 1 | 1979
94 | TTPS | Joda-I | 220 | D/C | 154 | Single Zebra | 1 | 1967
95 | TTPS | Joda-II | 220 | D/C | 154 | Single Zebra | 1 | 1970
96 | U. Kolab | Jayanagar-I | 220 | D/C | 6 | Single Zebra | 1 | 1987
97 | U. Kolab | Jayanagar-II | 220 | D/C | 6 | Single Zebra | 1 | 1987
98 | U. Kolab | Therubali | 220 | S/C | 128 | Single Zebra | 1 | 1984
Transmission Element Data as on 31/03/17 | [6 empty] | ANNEXURE-III
Name of the Transmission licensee: ODISHA POWER TRANSMISSION CORPORATION LTD
b) Sub Stations
SL. NO | Name of the Sub-Station |  | Voltage Level(in KV) | NO. of ICTs/ AUTOs | MVA Capacity of ICTs / Autos | Date of Commissioning | Date of Comml. Operation
1 | MERAMUNDALI |  | 400/220/132 | 2 | 315 | 02/06/05
|  |  | 220/132 | 2 | 100 | 2002
|  |  |  | 1 | 100 | 2014 | 19.03.2014
2 | MENDHASAL |  | 400/220 | 2 | 315 | 2010
|  |  | 220/132 | 1 | 100 | 2006
|  |  | 220/132 | 1 | 100 | 2010
|  |  | 220/132 | 1 | 100 | 2014
3 | BIDANASI |  | 220/132 | 2 | 100 | 2004
|  |  |  | 1 | 100 | 2013 | 17.07.2013
5 | BHANJANAGAR |  | 220/132 | 2 | 160 | 1984,2014 | 05.01.2014
6 | BHADRAK |  | 220/132 | 2 | 100 | 2008,2009
7 | CHANDAKA |  | 220/132 | 2 | 160 | 2012
|  |  |  | 2 | 100 | 1989
8 | CUTTACK |  | 220/132 | 1 | 160 | 2017
9 | NARENDRAPUR |  | 220/132 | 2 | 160 | 1999
|  |  |  | 1 | 100 | 2012
10 | THERUBALI |  | 220/132 | 2 | 100 | 1981
11 | BALASORE |  | 220/132 | 2 | 160 | 2012
12 | JAYANAGAR |  | 220/132 | 2 | 100 | 1997
13 | DUBURI |  | 220/132 | 3 | 100 | 1989
14 | BUDHIPADAR |  | 220/132 | 2 | 160 | 1995
15 | TARKERA |  | 220/132 | 4 | 100 | 1981
16 | JODA |  | 220/132 | 2 | 100 | 1969
17 | KATAPALLI |  | 220/132 | 2 | 100 | 2007
18 | PARADEEP |  | 220/132 | 2 | 100,160,50 | 2009,2011,2009
19 | BOLANGIR NEW |  | 220/132 | 3 | 100 | 2011,2014 | 05.05.2014
20 | LAPANGA |  | 220/132 | 2 | 160 | 2014
21 | ATRI |  | 220/132 | 2 | 160 | 2016
22 | SAMANGARA |  | 220/132 | 2 | 160 | 2015,2016
Note on E5: Type of tower

## Lines not owned by OPTCL
PERIOD : 2019-20
Sl. No. | Name of the Transmission Element | OUTAGE |  | RESTORATION |  | OUTAGE PERIOD | DURATION OF OUTAGE ATTRIBUTABLE TO | [5 empty] | Deemed Availability | Reason of Outage | MVA capacity for ICTs / Autos | Ckm and number of Sub-Conductor for lines | Time considered for availability (hrs) (365 X 24) | Element wise availbility (C19 - C7 - C8/60) / C19 | ( OH l x Cktkm l x NSC l ) ( OH t x MVA t x 2.5 ) | (THY x Ckt KM X NSC) (THY X MVA x 2.5)
|  | DATE | TIME | DATE | TIME |  | UTILITY ITSELF |  | OTHERS |  | System Constraints/Natural Calamities
|  | dd/mm/yy | hh:mm | dd/mm/yy | hh:mm | hh:mm | Hrs | Min | Hrs | Min | Hrs | Min
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
34 | 220kV Budhipadar-Vedant Ckt.-I |  |  |  |  | 0.040972 | 0 | 50 | [7 empty] | 16.67 | 8760 | 99.99% | 13.8917 | 146029.2
|  | 30.06.19 | 1:06 | 30.06.19 | 1:22 | 0:16 | 0 | 16
|  | 12.06.19 | 0:37 | 13.06.19 | 1:39 | 1:02 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
34 | 220kV Budhipadar-Vedant Ckt.-II |  |  |  |  | 0.040972 | 0 | 50 | [7 empty] | 16.67 | 8760 | 99.99% | 13.8917 | 146029.2
|  | 30.06.19 | 1:05 | 30.06.19 | 1:42 | 0:37 | 0 | 16
|  | 12.06.19 | 0:37 | 13.06.19 | 1:39 | 1:02 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
345 | 132 kV Palasponga - Essar |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 19.093 | 8760 | 100% | 2.5457 | 167254.68
|  | 19.03.20 | 17:06 | 19.03.20 | 17:34 | 0.019444 | 0 | 28 | [5 empty] | At Polasponga end: E/F ZONE1 , Ia=264A, Ib=240A, Ic=152A, IG= 451A
|  | 12.03.20 | 12:42 | 12.03.20 | 12:55 | 0.0090278 | 0 | 13 | [5 empty] | At Polasponga end: E/F ZONE1 LOC 32.85KM, Ia=202.1A, Ib=203A, Ic=79A, IG= 427A
|  | 22.12.19 | 0:25 | 22.12.19 | 0:35 | 0.0069444 | 0 | 10 | [5 empty] | At Polasponga end-Tripped on; O/C & E/F, Ia=0.48KA, Ib=0.54KA, Ic=0.53KA
|  | 26.12.19 | 2:58 | 26.12.19 | 3:06 | 0.0055556 | 0 | 8 | [5 empty] | At Polasponga end-Tripped on;O/C & E/F, Ia=0.16KA, Ib=0.24KA, Ic=0.33KA
|  | 22.10.19 | 15:07 | 22.10.19 | 15:11 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on Over current & Earth Fault at Polasponga end
|  | 06.10.19 | 15:25 | 06.10.19 | 16:00 | 0.024306 | 0 | 35 | [5 empty] | Tripped on E/F at Palasponga end.
|  | 16.10.19 | 1:27 | 16.10.19 | 1:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Palasponga end; O/C & E/F, Ia=341.3A, Ib=844.1A, Ic=148.9A, In =0.09A, Ig = 386.63A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:15 | 0.028472 | 0 | 41 | [5 empty] | Tripped at Joda end.
|  | 04.10.19 | 21:13 | 04.10.19 | 21:15 | 0.0013889 | 0 | 2 | [5 empty] | At Polasponga end: O/C R-ph, Ia=431.3A, Ib=363.6A, Ic=280.1A, In =0.04A
|  | 15.09.19 | 18:42 | 15.09.19 | 18:46 | 0.0027778 | 0 | 4 | [5 empty] | At Polasponga end;- O/C (R PH), Ia=423.0A, Ib=341.2A, Ic=288.2A, In =0.01A, Ig = 2.91A
|  | 19.07.19 | 19:25 | 19.07.19 | 21:06 | 0.070139 | 0 | 23 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.Polasponga GSS availed P/S at 19:48 Hrs from Karanjia GSS.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end; E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 09.05.19 | 14.15 | 09.05.19 | 14.18 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Joda end; O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA ,IN=0.0A,IG=1.1
|  | 07.05.19 | 17:37 | 07.05.19 | 19.06 | 0.061806 | 1 | 29 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end; 132KV PPG S/S availed P/S from Karanjia end till restoration of power at Joda end.
|  | 29.04.19 | 21:33 | 29.04.19 | 21:38 | 0.0034722 | 0 | 5 | [5 empty] | O/C (R PH), Ia= 405A, Ib= 340A, Ic= 242.8A, In= 0.1A, Ig= 4.66A
|  | 28.04.19 | 15:06 | 28.04.19 | 15:09 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R PH), Ia= 423.4A, Ib= 355.9A, Ic= 309.8A, In= 0.09A, Ig= 2.4A
|  | 25.04.19 | 7:58 | 25.04.19 | 8:06 | 0.0055556 | 0 | 8 | [5 empty] | O/C,E/F (Y PH), Ia= 221.5A, Ib= 654.1A, Ic=161.2A, In= 0.1A, Ig= 686.26A
|  | 25.04.19 | 23:41 | 25.04.19 | 23:46 | 0.0034722 | 0 | 5 | [5 empty] | O/C (R PH), Ia= 421A, Ib= 361A, Ic=277.7A, In= 0.03A, Ig= 3.12A
|  | 21.04.19 | 15.35 | 21.04.19 | 16:15 | 0.027778 | 0 | 40 | [5 empty] | SOURCE FAILURE but Restricted P/S availed from Karanjia GSS end.
|  | 16.04.19 | 1:17 | 16.04.19 | 1:21 | 0.0027778 | 0 | 4 | [5 empty] | O/C(R,PH),IA=415.3,IB=381.2,IC=353 IN=0.05,IG2.56
|  | 15.04.19 | 1:18 | 15.04.19 | 1:20 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R,Y PH), Ia= 396.4A, Ib=376.6KA, Ic=388.0KA IN=0.05
|  | 14.04.19 | 0:09 | 14.04.19 | 0:11 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R,Y PH), Ia=416, Ib=338.5KA, Ic=347.5KA,IN=0.05,IG=5.95
|  | 14.04.19 | 4:03 | 14.04.19 | 4:06 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA , IN=0.0A, IG=1.1
|  | 13.04.19 | 5:25 | 13.04.19 | 5:34 | 0.00625 | 0 | 9 | [5 empty] | O/C (B PH), Ia=1532A, Ib= 1037A, Ic=366.2, In= 0.00A, Ig= 4.9A
|  | 12.04.19 | 16:38 | 12.04.19 | 16:40 | 0.0013889 | 0 | 2 | [5 empty] | E/F WITH DP Z, Ia=80.81A, Ib=1.019KA, Ic=55.05, In=1.052KA, Ig= 1.05KA
|  | 07.04.19 | 16:01 | 07.04.19 | 16:03 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R PH), Ia=396.4A, Ib= 376.04A, Ic=388.84A Ig=51.8A
|  | 02.04.19 | 0.275 | 02.04.19 | 6:39 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R PH), Ia=414.1A, Ib= 341.7A, Ic=285.9A, In= 0.09A, Ig= 5.73A
|  | 02.04.19 | 3:02 | 02.04.19 | 3:05 | 0.0020833 | 0 | 3 | [5 empty] | O/C (B PH), Ia= 435.38A, Ib= 355.4A, Ic=333.3A, In= 0.0A, Ig= 3.94A
|  | 01.04.19 | 20:53 | 01.04.19 | 20:55 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R PH), Ia= 421.5A, Ib= 364.0A, Ic= 388.0A, In= 0.05A, Ig= 5.56A
345 | 132 kV Palasponga - MSP | [14 empty] | 7.5 | 8760 | 100% | 0 | 65700
|  | 19.03.20 | 17:06 | 19.03.20 | 17:34 | 0.019444 | 0 | 28 | [5 empty] | At Polasponga end: E/F ZONE1 , Ia=264A, Ib=240A, Ic=152A, IG= 451A
|  | 12.03.20 | 12:42 | 12.03.20 | 12:55 | 0.0090278 | 0 | 13 | [5 empty] | At Polasponga end: E/F ZONE1 LOC 32.85KM, Ia=202.1A, Ib=203A, Ic=79A, IG= 427A
|  | 29.10.19 | 14:05 | 29.10.19 | 14:11 | 0.0041667 | 0 | 6 | [5 empty] | At Palasponga-Tripped
|  | 28.10.19 | 10:17 | 28.10.19 | 10:27 | 0.0069444 | 0 | 10 | [5 empty] | Tripped From Karanjia Grid s/s
|  | 16.10.19 | 1:27 | 16.10.19 | 1:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Palasponga end; O/C & E/F, Ia=341.3A, Ib=844.1A, Ic=148.9A, In =0.09A, Ig = 386.63A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:15 | 0.028472 | 0 | 41 | [5 empty] | Tripped at Joda end.
|  | 04.10.19 | 21:13 | 04.10.19 | 21:15 | 0.0013889 | 0 | 2 | [5 empty] | At Polasponga end: O/C R-ph, Ia=431.3A, Ib=363.6A, Ic=280.1A, In =0.04A
|  | 15.09.19 | 18:42 | 15.09.19 | 18:46 | 0.0027778 | 0 | 4 | [5 empty] | At Polasponga end;- O/C (R PH), Ia=423.0A, Ib=341.2A, Ic=288.2A, In =0.01A, Ig = 2.91A
|  | 19.07.19 | 19:25 | 19.07.19 | 21:06 | 0.070139 | 0 | 23 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.Polasponga GSS availed P/S at 19:48 Hrs from Karanjia GSS.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end; E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 09.05.19 | 14.15 | 09.05.19 | 14.18 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Joda end; O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA ,IN=0.0A,IG=1.1
|  | 07.05.19 | 17:37 | 07.05.19 | 19.06 | 0.061806 | 1 | 29 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end; 132KV PPG S/S availed P/S from Karanjia end till restoration of power at Joda end.