## Qtr.1(2011) (Annex.1)
MONTHWISE SELF CONSUMPTION FOR 1ST QUARTER 2011-12 FROM CGP GENERATION OF M/S BHUSHAN POWER & STEEL LTD. THELKOLOI, SAMBALPUR
Sl. No. | Month | Total Generation (in kWh) | Export to Gridco (in kWh) | Self Consumption (in kWh)
1 | 2011-04-01 | 158396700 | 8459000 | 149937700
2 | 2011-05-01 | 172811300 | 15896000 | 156915300
3 | 2011-06-01 | 163820700 | 10779000 | 153041700
Total |  | 495028700 | 35134000 | 459894700

## Qtr.1(2011) (Annex.II)
CALCULATION OF CO-GENERATION UNITS FROM STEAM FLOW DATA OF INDIVIDUAL BOILERS FOR THE PERIOD OF (APRIL,MAY & JUNE- 2011) OF BHUSHAN POWER & STEEL LTD., THELKOLOI, SAMBALPUR
Month | Generation in kWh | WASTE HEAT RECOVERY BOILER (TON) | [11 empty] | Total Steam from WHRB | Total Steam from 2 AFBC Boilers (T) | Total Steam from 4 CFBC Boilers (T) | Co-generation Units
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
2011-04-01 | 158396700 | 25541 | 24796 | 15512 | 24920 | 24251 | 23827 | 21150 | 26240 | 14044 | 11647 | 12195 | 13514 | 237637 | 144229 | 307503 | 54601986.1611
2011-05-01 | 172811300 | 23965 | 26296 | 25536 | 28164 | 26572 | 25740 | 22256 | 25764 | 15436 | 13356 | 14929 | 14278 | 262292 | 146569 | 344657 | 60153866.9277
2011-06-01 | 163820700 | 25001 | 22969 | 28477 | 28942 | 25032 | 25225 | 26513 | 25854 | 12624 | 11323 | 13373 | 10776 | 256109 | 132251 | 332276 | 58220732.3202
Total | 495028700 | [12 empty] | 756038 | 423049 | 984436 | 172976585.409
Co-generation Units = | Total Energy Generated | WASTE HEAT RECOVERY BOILER (TON) 3: x; WASTE HEAT RECOVERY BOILER (TON) 4: Quantum of Steam Flow from WHRB
| Quantum of Steam Flow from WHRB | WASTE HEAT RECOVERY BOILER (TON) 1: +; WASTE HEAT RECOVERY BOILER (TON) 2: Quantum of Steam Flow from AFBC/ CFBC
Cogeneration units for the = quarter | 172976585 Units
% Co-generation over quarterly consumption = | 172976585 459894700 | WASTE HEAT RECOVERY BOILER (TON) 1: x; WASTE HEAT RECOVERY BOILER (TON) 2: 100 =; WASTE HEAT RECOVERY BOILER (TON) 3: 37.6%

## Qtr.1(2011) Annex.III
DETAILS OF POWER GENERATION & STEAM GENERATION OF INDIVIDUAL BOILERS
FOR THE PERIOD OF 1ST QUARTER OF 2011 ( APRIL ,MAY & JUNE )
Unit:- | 100 MW Power Plant
Month | Power Generation ( kWh) |  |  | Steam Generation
| 40 MW | 60 MW | 100 MW | AFBC-1 | AFBC-2 | Total Steam from AFBC | WHRB-1 | WHRB-2 | WHRB-3 | WHRB-4 | Total Steam from WHRB
Apr'11 | 25244000 | 32415000 | 57659000 | 52633 | 91596 | 144229 | 25541 | 24796 | 15512 | 24920 | 90769
May'11 | 25549000 | 35205000 | 60754000 | 53508 | 93061 | 146569 | 23965 | 26296 | 25536 | 28164 | 103961
Jun'11 | 24416000 | 32457000 | 56873000 | 49789 | 82462 | 132251 | 25001 | 22969 | 28477 | 28942 | 105389
Total |  |  | 175286000 |  |  | 423049 |  |  |  |  | 300119
Unit:- | 2 x 130 MW Power Plant
Month | Power Generation ( kWh) |  |  | Steam Generation
| Unit-I | Unit-II | Total | CFBC-1 | CFBC-2 | CFBC-3 | CFBC-4 | Total Steam from CFBC | WHRB-5 | WHRB-6 | WHRB-7 | WHRB-8 | Total Steam from WHRB
Apr'11 | 58528000 | 35163000 | 93691000 | 102923 | 98299 | 15367 | 90914 | 307503 | 24251 | 23827 | 21150 | 26240 | 95468
May'11 | 58114000 | 45580000 | 103694000 | 104726 | 92219 | 49300 | 98412 | 344657 | 26572 | 25740 | 22256 | 25764 | 100332
Jun'11 | 49776000 | 51132000 | 100908000 | 84769 | 81259 | 74460 | 91788 | 332276 | 25032 | 25225 | 26513 | 25854 | 102624
Total |  |  | 298293000 |  |  |  |  | 984436 |  |  |  |  | 298424
Unit:- | 2 x 8 MW Power Plant
Month | Power Generation ( kWh) |  |  | Steam Generation
| 8 MW unit -1 | 8 MW unit -2 | Total (2 x8 MW) | WHRB-9 | WHRB-10 | WHRB-11 | WHRB-12 | Total Steam from WHRB
Apr'11 | 3727300 | 3319400 | 7046700 | 14044 | 11647 | 12195 | 13514 | 51400
May'11 | 3965700 | 4397600 | 8363300 | 15436 | 13356 | 14929 | 14278 | 57999
Jun'11 | 1400600 | 4639100 | 6039700 | 12624 | 11323 | 13373 | 10776 | 48096
Total |  |  | 21449700 |  |  |  |  | 157495

## Qtr.2 (2011) (Annex.1)
MONTHWISE SELF CONSUMPTION FOR 2ND QUARTER OF 2011-12 FROM CGP GENERATION OF M/S BHUSHAN POWER & STEEL LTD. THELKOLOI, SAMBALPUR
FY-2011-12
Sl. No. | Month | Total Generation (in kWh) | Export to Gridco (in kWh) | Self Consumption (in kWh)
1 | 2011-07-01 | 160658900 | 11704000 | 148954900
2 | 2011-08-01 | 142786600 | 12205000 | 130581600
3 | 2011-09-01 | 95676600 | 1436000 | 94240600
Total |  | 399122100 | 25345000 | 373777100

## Qtr.2(2011)(Annex.II)
CALCULATION OF CO-GENERATION UNITS FROM STEAM FLOW DATA OF INDIVIDUAL BOILERS FOR THE PERIOD OF (JULY, AUGUST & SEPTEMBER- 2011) OF BHUSHAN POWER & STEEL LTD., THELKOLOI, SAMBALPUR
Month | Generation in kWh | WASTE HEAT RECOVERY BOILER (TON) | [11 empty] | Total Steam from WHRB | Total Steam from 2 AFBC Boilers (T) | Total Steam from 4 CFBC Boilers (T) | Co-generation Units
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
2011-07-01 | 160658900 | 9096 | 22682 | 27737 | 29469 | 26394 | 27284 | 26573 | 27464 | 11734 | 11962 | 11838 | 11879 | 244112 | 129026 | 338646 | 55099251.1728
2011-08-01 | 142786600 | 27533 | 24102 | 16067 | 27138 | 16192 | 17392 | 24785 | 18880 | 13420 | 12390 | 13903 | 13618 | 225420 | 121795 | 281570 | 51189127.2406
2011-09-01 | 95676600 | 18662 | 9946 | 26758 | 11477 | 1080 | 5615 | 24462 | 11823 | 11576 | 11038 | 11461 | 10970 | 154868 | 119030 | 162793 | 33930728.3383
Total | 399122100 | [12 empty] | 624400 | 369851 | 783009 | 140219106.7518
Co-generation Units = | Total Energy Generated | WASTE HEAT RECOVERY BOILER (TON) 4: Quantum of Steam Flow from WHRB
x
| Quantum of Steam Flow from WHRB | WASTE HEAT RECOVERY BOILER (TON) 1: +; WASTE HEAT RECOVERY BOILER (TON) 2: Quantum of Steam Flow from AFBC/CFBC
Cogeneration units for = the quarter | 140219107 Units
% Co-generation over quarterly consumption = | 140219107 373777100 | WASTE HEAT RECOVERY BOILER (TON) 1: x; WASTE HEAT RECOVERY BOILER (TON) 2: 100 =; WASTE HEAT RECOVERY BOILER (TON) 3: 37.5%

## Qtr.2 (2011) Annex.III
DETAILS OF POWER GENERATION & STEAM GENERATION OF INDIVIDUAL BOILERS
FOR THE PERIOD OF 2ND QUARTER OF 2011 ( JULY , AUGUST & SEPTEMBER)
Unit:- | 100 MW Power Plant
Month | Power Generation ( kWh) |  |  | Steam Generation (Ton)
| 40 MW | 60 MW | Total (100 MW) | AFBC-1 | AFBC-2 | Total Steam from AFBC | WHRB-1 | WHRB-2 | WHRB-3 | WHRB-4 | Total Steam from WHRB
2011-07-11 | 18874000 | 32774000 | 51648000 | 48145 | 80881 | 129026 | 9096 | 22682 | 27737 | 29469 | 88984
2011-08-11 | 23562000 | 28428000 | 51990000 | 45383 | 76412 | 121795 | 27533 | 24102 | 16067 | 27138 | 94840
2011-09-11 | 16916000 | 26963000 | 43879000 | 42898 | 76132 | 119030 | 18662 | 9946 | 26758 | 11477 | 66843
Total | 59352000 | 88165000 | 147517000 | 136426 | 233425 | 369851 | 55291 | 56730 | 70562 | 68084 | 250667
Unit:- | 2 x 130 MW Power Plant
Month | Power Generation ( kWh) |  |  | Steam Generation (Ton)
| Unit-I | Unit-II | Total | CFBC-1 | CFBC-2 | CFBC-3 | CFBC-4 | Total Steam from CFBC | WHRB-5 | WHRB-6 | WHRB-7 | WHRB-8 | Total Steam from WHRB
2011-07-11 | 52044000 | 51223000 | 103267000 | 89928 | 83307 | 78793 | 86618 | 338646 | 26394 | 27284 | 26573 | 27464 | 107715
2011-08-11 | 34082000 | 49251000 | 83333000 | 64158 | 48396 | 79692 | 89324 | 281570 | 16192 | 17392 | 24785 | 18880 | 77249
2011-09-11 | 7886000 | 38963000 | 46849000 | 21961 | 8119 | 64622 | 68091 | 162793 | 1080 | 5615 | 24462 | 11823 | 42980
Total | 94012000 | 139437000 | 233449000 | 176047 | 139822 | 223107 | 244033 | 783009 | 43666 | 50291 | 75820 | 58167 | 227944
Unit:- | 2 x 8 MW Power Plant
Month | Power Generation ( kWh) |  |  | Steam Generation (Ton)
| 8 MW unit -1 | 8 MW unit -2 | Total (2 x8 MW) | WHRB-9 | WHRB-10 | WHRB-11 | WHRB-12 | Total Steam from WHRB
2011-07-11 | 141900 | 5602000 | 5743900 | 11734 | 11962 | 11838 | 11879 | 47413
2011-08-11 | 2791700 | 4671900 | 7463600 | 13420 | 12390 | 13903 | 13618 | 53331
2011-09-11 | 1809500 | 3139100 | 4948600 | 11576 | 11038 | 11461 | 10970 | 45045
Total | 4743100 | 13413000 | 18156100 | 36730 | 35390 | 37202 | 36467 | 145789